## Input
Building heating/cooling demand |  |  | Green cell: input field |  |  | Red cell: better not change
Orange value: calculated value
Temperature settings | [9 empty] | SCHEDULES USED IN THE CALCULATION | [15 empty] | EXAMPLE SCHEDULES OFFICE | [15 empty] | EXAMPLE SCHEDULES RESIDENTIAL
Indoor setpoint temperature for heating | 20 | °C | Indoor setback temperature for heating | 16 | °C |  |  |  | setback temperatures are used when schedule value for heating/cooling is 0.5
Indoor setpoint temperature for cooling | 24 | °C | Indoor setback temperature for cooling | 24 | °C |  |  |  |  | OCCUPANCY | [7 empty] | VENTILATION AIRFLOW SCHEDULE | [7 empty] | OCCUPANCY | [7 empty] | VENTILATION AIRFLOW SCHEDULE | [7 empty] | PEOPLE | [7 empty] | VENTILATION AIRFLOW SCHEDULE
Geometry |  |  | window percentage of total outside area | [7 empty] | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday
Total façade area (incl. windows) North | 0 | m2 | Window percentage North | 0 | % | Glazing percentage of windows North | 80 | % |  | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) North-East | 836 | m2 | Window percentage North-East | 27 | % | Glazing percentage of windows North-East | 80 | % |  | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) East | 0 | m2 | Window percentage East | 0 | % | Glazing percentage of windows East | 80 | % |  | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) South-East | 390 | m2 | Window percentage South-East | 33 | % | Glazing percentage of windows South-East | 80 | % |  | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) South | 0 | m2 | Window percentage South | 0 | % | Glazing percentage of windows South | 80 | % |  | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) South-West | 836 | m2 | Window percentage South-West | 36 | % | Glazing percentage of windows South-West | 80 | % |  | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) West | 0 | m2 | Window percentage West | 0 | % | Glazing percentage of windows West | 80 | % |  | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Total façade area (incl. windows) North-West | 390 | m2 | Window percentage North-West | 33 | % | Glazing percentage of windows North-West | 80 | % |  | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 8 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Total flat roof area (incl. rooflights) | 410 | m2 | Rooflight percentage roof | 0 | % | Glazing percentage of rooflights | 80 | % |  | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 9 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Ground floor area | 410 | m2 | [6 empty] | Area of floor adjacent to ground | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 10 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 10 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Total floor area (BVO, sum up all floors) | 3690 | m2 | [6 empty] | Sum of all floor areas, taking every building level into consideration | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 11 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 11 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Height of each building level | 3 | m | [6 empty] | Total building volume is calculated from total floor area and level height | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 12 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 12 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
[10 empty] | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 13 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 13 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Transmission | [9 empty] | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 14 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 14 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
U-value windows | 1.8 | W/m2K | [6 empty] | U_window is determined by U_glazing, U_ frame and ψ_spacer | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 15 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 15 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Rc façade | 3.9 | m2K/W | [6 empty] | The ΔU-value depends on amount of thermal bridging in the constructions. | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 16 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 16 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Rc roof | 5.7 | m2K/W | [6 empty] | For a very good design, a value of 0.05 W/m2K may apply. | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 17 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 17 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5
Rc ground floor | 3 | m2K/W | [6 empty] | The graph on the left is from the Dutch Energy Performance Standard and applies in case | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 18 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
ΔU-value offset due to thermal bridges in constructions | 0.15 | W/m2K | [6 empty] | thermal bridges are not explicitly taken into account in the performance calculation. | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[9 empty] | This 'default' ΔU-value depends on the Rc value of the construction. | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Infiltration | [9 empty] | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
ACH (air change rate) due to air leakage | 0.2 | h-1 | [6 empty] | Excellent 0.02 h-1 Good 0.07 h-1 Medium 0.2 h-1 Poor 0.6 h-1 Very poor 1.8 h-1 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[10 empty] | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Ventilation | [9 empty] | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Ventilation flow rate per person | 36 | m3/h pp | [6 empty] | Ventilation for air quality
Total flow rate ventilation (maximum) | 2656.8 | m3/h | [7 empty] | LIGHTING AND EQUIPMENT | [7 empty] | HEATING/COOLING ON/OFF | [7 empty] | LIGHTING AND EQUIPMENT | [7 empty] | HEATING/COOLING ON/OFF | [7 empty] | LIGHTING AND EQUIPMENT | [7 empty] | HEATING/COOLING ON/OFF
Additional natural ventilation for free cooling | 3 | h-1 | [6 empty] | Heat recovery bypassed and additional ventilation with outside air for cooling (operable windows), applies when: | [8 empty] | 0: off |  | 0.5: setback temperatures are used |  |  |  | 1: on | [9 empty] | 0: off |  | 0.5: setback temperatures are used |  |  |  | 1: on | [9 empty] | 0: off |  | 0.5: setback temperatures are used |  |  |  | 1: on
Indoor setpoint temperature for ventilation cooling | 23.9 | °C | MUST be lower than a cooling setpoint temp. | [5 empty] | 1) indoor temperature is higher than this setpoint, AND |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday |  | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday
Flow rate additional natural ventilation | 33210 | m3/h | [6 empty] | 2) indoor temperature is higher than the setpoint temperature for heating, AND | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[9 empty] | 3) indoor temperature is higher than outside temperature | 2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Solar coefficients | [9 empty] | 3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Glazing |  |  | Shading/blinds (including glazing) |  |  | Outside opaque surfaces |  |  | g_shade=1: no shading/blinds; g_shade =0: windows are completely obstructed by blinds/shading | 4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Solar heat coefficient glazing (N) | 0.6 |  | Solar heat coefficient shading (N) | 0.3 |  | Solar absorption coefficient (N) | 0.5 |  |  | 5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Solar heat coefficient glazing (N-E) | 0.6 |  | Solar heat coefficient shading (N-E) | 0.3 |  | Solar absorption coefficient (N-E) | 0.5 |  |  | 6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 6 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Solar heat coefficient glazing (E) | 0.6 |  | Solar heat coefficient shading (E) | 0.3 |  | Solar absorption coefficient (E) | 0.5 |  |  | 7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 7 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 7 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Solar heat coefficient glazing (S-E) | 0.6 |  | Solar heat coefficient shading (S-E) | 0.3 |  | Solar absorption coefficient (S-E) | 0.5 |  |  | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 8 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 8 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar heat coefficient glazing (S) | 0.6 |  | Solar heat coefficient shading (S) | 0.3 |  | Solar absorption coefficient (S) | 0.5 |  |  | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 9 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 9 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 9 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 9 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar heat coefficient glazing (S-W) | 0.6 |  | Solar heat coefficient shading (S-W) | 0.3 |  | Solar absorption coefficient (S-W) | 0.5 |  |  | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 10 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar heat coefficientt glazing (W) | 0.6 |  | Solar heat coefficient shading (W) | 0.3 |  | Solar absorption coefficient (W) | 0.5 |  |  | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 11 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 11 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 11 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar heat coefficient glazing (N-W) | 0.6 |  | Solar heat coefficient shading (N-W) | 0.3 |  | Solar absorption coefficient (N-W) | 0.5 |  |  | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 12 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 12 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar heat coefficient glazing (roof) | 0.6 |  | Solar heat coefficient shading (roof) | 0.3 |  | Solar absorption coefficient (roof) | 0.5 |  |  | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 13 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 13 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[10 empty] | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 14 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 14 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 14 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Solar blinds control | [9 empty] | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 15 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Threshold solar radiation shading/blinds in use | 0 | W/m2 | [6 empty] | The blinds/shading are in use when: | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 16 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 16 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 16 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Indoor setpoint temperature shading/blinds in use | 23.9 | °C | [6 empty] | 1) the incident solar radiation for an orientation is above this value, AND | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 17 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 17 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.5 | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[9 empty] | 2) if the indoor temperature is above this setpoint | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.1 | 0.1 | 18 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 18 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Internal heat gains | [9 empty] | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Number of people (maximum) per m2 floor area | 0.02 | pers/m2 | [6 empty] | Occupancy density | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 20 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Lighting power per square meter (maximum) | 6 | W/m2 | [7 empty] | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 21 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Appliances power per square meter (maximum) | 6 | W/m2 | [7 empty] | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 22 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[10 empty] | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 23 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Ventilation system properties | [8 empty] | Residential: exhaust without heat recovery 200 Pa; supply+exhaust with heat recovery 400 Pa | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 24 | 1 | 1 | 1 | 1 | 1 | 1 | 1
System pressure drop | 200 | Pa | [6 empty] | Non-residential: exhaust without heat recovery 400 Pa, supply+exhaust with heat recovery 800 Pa
Heat recovery efficiency | 0 | [7 empty] | Set heat recovery efficiency to 0 for exhaust only systems. Residential 0.85; Non-residential 0.75
Efficiency fan+motor | 0.6 | [7 empty] | A fan system efficiency of 0.6 is usual
Fan(s) power (maximum) | 246 | W | [6 empty] | In this Excel, it is assumed that 50% of the fan power is given off as heat to indoors
Heating and cooling capacity
Maximum heating power | 1000 | kW | [6 empty] | Set to 0 kW when no active heating is present
Maximum cooling power | 1000 | kW | [6 empty] | Set to 0 kW when no active cooling is present
Thermal capacity
Specific thermal capacity | 360 | kJ/m2K | [6 empty] | Steady-state model 0.001 kJ/m2K; Very light 30 kJ/m2K; light 60 kJ/m2K; …
medium 120 kJ/m2K; heavy 240 kJ/m2K; very heavy 480 kJ/m2K
Urban Heat Island or Climate Change effect
Temperature offset | 0 | °C | [6 empty] | Outside temperature off-set. For Urban Heat Island effect in the Netherlands, see
https://tinyurl.com/ycy7v3ku
Calculations and constants |  |  | `
U facade wall | 0.3939 | W/m2K
U roof | 0.31949 | W/m2K
U floor | 0.4625 | W/m2K
Total Window (glazing + frame) area | 784.08 | m2
Total façade area (excl. windows) North | 0 | m2
Total façade area (excl. windows) North-East | 610.28 | m2
Total façade area (excl. windows) East | 0 | m2
Total façade area (excl. windows) South-East | 261.3 | m2
Total façade area (excl. windows) South | 0 | m2
Total façade area (excl. windows) South-West | 535.04 | m2
Total façade area (excl. windows) West | 0 | m2
Total façade area (excl. windows) North-West | 261.3 | m2
Total Facade wall area | 1667.92 | m2
Total Roof area | 410 | m2
Total Floor Area | 3690 | m2
Total Ground floor area | 410 | m2
Building volume | 11070 | m3
Window area (glazing + frame) (N) | 0 | m2
Window area (glazing + frame) (N-E) | 225.72 | m2
Window area (glazing + frame) (E) | 0 | m2
Window area (glazing + frame) (S-E) | 128.7 | m2
Window area (glazing + frame)(S) | 0 | m2
Window area (glazing + frame) (S-W) | 300.96 | m2
Window area (glazing + frame)(W) | 0 | m2
Window area (glazing + frame) (N-W) | 128.7 | m2
Window area (glazing + frame)(roof) | 0 | m2
Flow rate infiltration | 2214 | m3/h
Thermal capacity building | 1328.4 | MJ/K
Start temperature at 1 January 00:00 | 20 | °C
Ground temperature | 15 | °C
alfai (convection/radiation coefficient indoor) | 7.5 | W/m2K
alfao (convection/radiation coefficient outdoor) | 15 | W/m2K
Dry air heating capacity | 1003 | J/kgK
Density of air | 1.2 | kg/m3
Water density | 1000 | kg/m3
Specific heat of water | 4187 | J/kgK
sensible heat gain per person | 65 | W/pp
Fraction light power thermally released | 1 | Wth/Wel
Lightend floor percentage | 1

## Results
ENERGY DEMAND
Annual energy demand for | [kWh] | [kWh/m2]
Space heating | 83610.961 | 22.6588
Space cooling | 34115.3187 | 9.2453
Lighting (electrical) | 57010.5 | 15.45
Appliances (electrical and thermal) | 57010.5 | 15.45
Fans | 442.431 | 0.1199
Nominal power heating (thermal) | 664.3723 | kW
Nominal power cooling (thermal) | 122.2952 | kW
143628.533 | 38.9237 | 85303.9248 | 23.1176
37269.9761 | 10.1003 | 34115.3187 | 9.2453
57010.5 | 15.45 | 57010.5 | 15.45
57010.5 | 15.45 | 57010.5 | 15.45
442.431 | 0.1199 | 442.431 | 0.1199
90.864 | kW | 90.864 | kW
122.2952 | kW | 122.2952 | kW
40.61% |  | 83610.961 | 22.6588
8.464% |  | 34115.3187 | 9.2453
|  | 57010.5 | 15.45
|  | 57010.5 | 15.45
|  | 442.431 | 0.1199
1.985%
-443.3% |  | 664.3723 | kW
|  | 122.2952 | kW

## Hourly
[11 empty] | don't change these data |  |  |  | weather file NEN5060:2018 Energy
[43 empty] | DO NOT CHANGE | DO NOT CHANGE | DO NOT CHANGE |  | DO NOT CHANGE | DO NOT CHANGE | DO NOT CHANGE | DO NOT CHANGE |  | DO NOT CHANGE | DO NOT CHANGE | DO NOT CHANGE | DO NOT CHANGE
Year | Month | Day | (Hour) (MET) | hour | Outdoor Temperature (oC) | Outdoor Temperature (oC) used | Outdoor daily average Te | Running mean outdoor temperature | Ground temperature | Relative humidity (%) | Relative humidity (%) used | dir | diff | alt | azim | Direct sun radiation (W/m2) | [8 empty] | Diffuse sun radiation (W/m2) | [8 empty] | Total sun radiation (W/m2) | [8 empty] | Presence of people | Lighting & appliances on | System state | Ventilation | Presence of people | Lighting & equipments | System state | Ventilation |  | people | lighting and equipment | system | ventilation
[16 empty] | North | North-East | East | South-East | South | South-West | West | North-West | Horizontal | North | North-East | East | South-East | South | South-West | West | North-West | Horizontal | North | North-East | East | South-East | South | South-West | West | North-West | Horizontal
2001 | 1 | 1 | 1 | 1 | 1.5 | 1.5 |  |  | 15 | 75 | 75 | 0 | 0 | -60.7735 | 8.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 2 | 2 | 1.5 | 1.5 |  |  | 15 | 75 | 75 | 0 | 0 | -57.3909 | 34.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 3 | 3 | 1.7 | 1.7 |  |  | 15 | 73 | 73 | 0 | 0 | -50.8686 | 55.3717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 4 | 4 | 1.5 | 1.5 |  |  | 15 | 77 | 77 | 0 | 0 | -42.6283 | 71.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 5 | 5 | 1.2 | 1.2 |  |  | 15 | 84 | 84 | 0 | 0 | -33.6209 | 84.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 6 | 6 | 1.1 | 1.1 |  |  | 15 | 88 | 88 | 0 | 0 | -24.424 | 96.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 7 | 7 | 1.1 | 1.1 |  |  | 15 | 92 | 92 | 0 | 0 | -15.4363 | 107.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Monday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 1 | 8 | 8 | 1.3 | 1.3 |  |  | 15 | 93 | 93 | 0 | 0 | -6.9947 | 119.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 9 | 9 | 1.5 | 1.5 |  |  | 15 | 95 | 95 | 0 | 0 | 0.56391 | 130.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 10 | 10 | 1.8 | 1.8 |  |  | 15 | 96 | 96 | 0 | 0 | 6.876 | 142.8761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 11 | 11 | 2.2 | 2.2 |  |  | 15 | 96 | 96 | 0.085289 | 5.986 | 11.5588 | 156.0261 | 0 | 0 | 0.051105 | 0.083877 | 0.067514 | 0.011603 | 0 | 0 | 0.013974 | 2.782 | 2.782 | 2.782 | 2.782 | 2.782 | 2.782 | 2.782 | 2.782 | 5.986 | 2.782 | 2.782 | 2.8331 | 2.8658 | 2.8495 | 2.7936 | 2.782 | 2.782 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 12 | 12 | 2.6 | 2.6 |  |  | 15 | 96 | 96 | 0.4444 | 18.899 | 14.2588 | 169.9079 | 0 | 0 | 0.17691 | 0.4064 | 0.39783 | 0.15621 | 0 | 0 | 0.10101 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 18.899 | 8.9264 | 8.9264 | 9.1033 | 9.3328 | 9.3242 | 9.0826 | 8.9264 | 8.9264 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 13 | 13 | 3.4 | 3.4 |  |  | 15 | 95 | 95 | 1.4964 | 38.6195 | 14.7367 | 184.1501 | 0 | 0 | 0.25414 | 1.1894 | 1.4279 | 0.82997 | 0 | 0 | 0.38046 | 18.5989 | 18.5989 | 18.5989 | 18.5989 | 18.5989 | 18.5989 | 18.5989 | 18.5989 | 38.6195 | 18.5989 | 18.5989 | 18.853 | 19.7883 | 20.0268 | 19.4289 | 18.5989 | 18.5989 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 14 | 14 | 4 | 4 |  |  | 15 | 94 | 94 | 1.3974 | 35.6606 | 12.9469 | 198.24 | 0 | 0 | 0 | 0.88396 | 1.3479 | 1.0223 | 0.097805 | 0 | 0.33937 | 17.1043 | 17.1043 | 17.1043 | 17.1043 | 17.1043 | 17.1043 | 17.1043 | 17.1043 | 35.6606 | 17.1043 | 17.1043 | 17.1043 | 17.9882 | 18.4522 | 18.1266 | 17.2021 | 17.1043 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 15 | 15 | 4.4 | 4.4 |  |  | 15 | 93 | 93 | 0.61056 | 18.8816 | 9.0549 | 211.7261 | 0 | 0 | 0 | 0.26792 | 0.56514 | 0.53131 | 0.18625 | 0 | 0.11839 | 8.9055 | 8.9055 | 8.9055 | 8.9055 | 8.9055 | 8.9055 | 8.9055 | 8.9055 | 18.8816 | 8.9055 | 8.9055 | 8.9055 | 9.1735 | 9.4707 | 9.4369 | 9.0918 | 8.9055 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 16 | 16 | 4.4 | 4.4 |  |  | 15 | 95 | 95 | 0.33186 | 7.9632 | 3.3778 | 224.3785 | 0 | 0 | 0 | 0.075248 | 0.27875 | 0.31897 | 0.17234 | 0 | 0.036752 | 3.7099 | 3.7099 | 3.7099 | 3.7099 | 3.7099 | 3.7099 | 3.7099 | 3.7099 | 7.9632 | 3.7099 | 3.7099 | 3.7099 | 3.7852 | 3.9887 | 4.0289 | 3.8823 | 3.7099 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 17 | 17 | 4.5 | 4.5 |  |  | 15 | 95 | 95 | 0 | 3 | -3.7053 | 236.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 3 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Monday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 1 | 18 | 18 | 4.6 | 4.6 |  |  | 15 | 96 | 96 | 0 | 0 | -11.8198 | 247.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 19 | 19 | 4.8 | 4.8 |  |  | 15 | 97 | 97 | 0 | 0 | -20.6191 | 258.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 20 | 20 | 5 | 5 |  |  | 15 | 97 | 97 | 0 | 0 | -29.7715 | 270.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 21 | 21 | 5.2 | 5.2 |  |  | 15 | 97 | 97 | 0 | 0 | -38.9146 | 282.5523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 22 | 22 | 5.8 | 5.8 |  |  | 15 | 94 | 94 | 0 | 0 | -47.5648 | 297.3738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 23 | 23 | 6.1 | 6.1 |  |  | 15 | 91 | 91 | 0 | 0 | -54.9542 | 316.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 1 | 24 | 24 | 6.1 | 6.1 | 3.2208 |  | 15 | 92 | 92 | 0 | 0 | -59.8396 | 340.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Monday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 1 | 25 | 6.2 | 6.2 | 3.2208 |  | 15 | 91 | 91 | 0 | 0 | -60.7735 | 8.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 2 | 26 | 6.1 | 6.1 | 3.2208 |  | 15 | 92 | 92 | 0 | 0 | -57.3551 | 34.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 3 | 27 | 6.1 | 6.1 | 3.2208 |  | 15 | 92 | 92 | 0 | 0 | -50.8582 | 55.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 4 | 28 | 5.8 | 5.8 | 3.2208 |  | 15 | 93 | 93 | 0 | 0 | -42.6318 | 71.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 5 | 29 | 6.6 | 6.6 | 3.2208 |  | 15 | 90 | 90 | 0 | 0 | -33.6299 | 84.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 6 | 30 | 6.8 | 6.8 | 3.2208 |  | 15 | 88 | 88 | 0 | 0 | -24.4327 | 96.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 7 | 31 | 7.4 | 7.4 | 3.2208 |  | 15 | 86 | 86 | 0 | 0 | -15.4402 | 107.7392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Tuesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 2 | 8 | 32 | 7.2 | 7.2 | 3.2208 |  | 15 | 89 | 89 | 0 | 0 | -6.99 | 118.8778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 9 | 33 | 6.7 | 6.7 | 3.2208 |  | 15 | 91 | 91 | 0 | 0 | 0.5807 | 130.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 10 | 34 | 7.5 | 7.5 | 3.2208 |  | 15 | 90 | 90 | 1.6319 | 10.8879 | 6.9081 | 142.7462 | 0 | 0.12956 | 1.2418 | 1.6266 | 1.0586 | 0 | 0 | 0 | 0.11206 | 5.1537 | 5.6933 | 10.326 | 11.9288 | 9.5628 | 5.1537 | 5.1537 | 5.1537 | 10.8879 | 5.1537 | 5.8229 | 11.5678 | 13.5554 | 10.6214 | 5.1537 | 5.1537 | 5.1537 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 11 | 35 | 8.7 | 8.7 | 3.2208 |  | 15 | 84 | 84 | 176.1663 | 79.0101 | 11.6086 | 155.9003 | 0 | 0 | 105.8676 | 173.2915 | 139.2036 | 23.5721 | 0 | 0 | 28.9899 | 40.5534 | 40.5534 | 101.0031 | 139.5018 | 120.0378 | 54.0129 | 40.5534 | 40.5534 | 79.0101 | 40.5534 | 40.5534 | 206.8707 | 312.7933 | 259.2414 | 77.5851 | 40.5534 | 40.5534 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 12 | 36 | 9.9 | 9.9 | 3.2208 |  | 15 | 82 | 82 | 126.6357 | 110.0886 | 14.3273 | 169.7904 | 0 | 0 | 50.651 | 115.8835 | 113.2331 | 44.2522 | 0 | 0 | 28.9114 | 53.3359 | 53.3359 | 103.0447 | 167.0638 | 164.4627 | 96.765 | 53.3359 | 53.3359 | 110.0886 | 53.3359 | 53.3359 | 153.6956 | 282.9474 | 277.6958 | 141.0172 | 53.3359 | 53.3359 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 13 | 37 | 9.9 | 9.9 | 3.2208 |  | 15 | 80 | 80 | 60.5397 | 117.5291 | 14.823 | 184.0456 | 0 | 0 | 10.3969 | 48.1716 | 57.728 | 33.4681 | 0 | 0 | 15.4709 | 55.631 | 55.631 | 69.5422 | 120.0849 | 132.8714 | 100.4115 | 55.631 | 55.631 | 117.5291 | 55.631 | 55.631 | 79.9391 | 168.2565 | 190.5994 | 133.8796 | 55.631 | 55.631 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 14 | 38 | 10.6 | 10.6 | 3.2208 |  | 15 | 76 | 76 | 39.9642 | 107.2312 | 13.0483 | 198.152 | 0 | 0 | 0 | 25.3231 | 38.538 | 29.1778 | 2.7257 | 0 | 9.7688 | 51.2699 | 51.2699 | 51.2699 | 91.6338 | 112.6976 | 97.7779 | 55.6144 | 51.2699 | 107.2312 | 51.2699 | 51.2699 | 51.2699 | 116.9569 | 151.2356 | 126.9557 | 58.3401 | 51.2699 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 15 | 39 | 10.6 | 10.6 | 3.2208 |  | 15 | 73 | 73 | 80.2644 | 92.2898 | 9.1679 | 211.6553 | 0 | 0 | 0 | 35.3135 | 74.3006 | 69.7634 | 24.3598 | 0 | 15.7102 | 45.9411 | 45.9411 | 45.9411 | 82.4546 | 122.7665 | 118.0752 | 71.1287 | 45.9411 | 92.2898 | 45.9411 | 45.9411 | 45.9411 | 117.7681 | 197.0671 | 187.8386 | 95.4885 | 45.9411 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 16 | 40 | 10.3 | 10.3 | 3.2208 |  | 15 | 74 | 74 | 1.4458 | 16.837 | 3.4988 | 224.3234 | 0 | 0 | 0 | 0.32944 | 1.215 | 1.3888 | 0.74908 | 0 | 0.16301 | 7.9682 | 7.9682 | 7.9682 | 7.9682 | 7.9682 | 7.9682 | 7.9682 | 7.9682 | 16.837 | 7.9682 | 7.9682 | 7.9682 | 8.2976 | 9.1832 | 9.357 | 8.7173 | 7.9682 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 17 | 41 | 10.2 | 10.2 | 3.2208 |  | 15 | 74 | 74 | 4.5397 | 0.495 | -3.5793 | 236.1811 | 0 | 0 | 0 | 0.053507 | 3.2417 | 4.531 | 3.166 | 0 | 2.505 | 0.55586 | 0.55586 | 0.55586 | 0.58568 | 2.3627 | 3.0813 | 2.3206 | 0.55586 | 0.495 | 0.55586 | 0.55586 | 0.55586 | 0.63919 | 5.6044 | 7.6123 | 5.4866 | 0.55586 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Tuesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 2 | 18 | 42 | 9.8 | 9.8 | 3.2208 |  | 15 | 78 | 78 | 0 | 0 | -11.691 | 247.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 19 | 43 | 9.8 | 9.8 | 3.2208 |  | 15 | 80 | 80 | 0 | 0 | -20.4888 | 258.5438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 20 | 44 | 9.5 | 9.5 | 3.2208 |  | 15 | 84 | 84 | 0 | 0 | -29.6408 | 269.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 21 | 45 | 9.6 | 9.6 | 3.2208 |  | 15 | 84 | 84 | 0 | 0 | -38.7844 | 282.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 22 | 46 | 9.8 | 9.8 | 3.2208 |  | 15 | 83 | 83 | 0 | 0 | -47.437 | 297.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 23 | 47 | 10 | 10 | 3.2208 |  | 15 | 80 | 80 | 0 | 0 | -54.8335 | 316.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 2 | 24 | 48 | 10.2 | 10.2 | 8.5542 |  | 15 | 78 | 78 | 0 | 0 | -59.7365 | 340.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Tuesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 1 | 49 | 9.8 | 9.8 | 8.5542 |  | 15 | 78 | 78 | 0 | 0 | -60.7024 | 8.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 2 | 50 | 9.4 | 9.4 | 8.5542 |  | 15 | 81 | 81 | 0 | 0 | -57.3116 | 33.9968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 3 | 51 | 8.8 | 8.8 | 8.5542 |  | 15 | 84 | 84 | 0 | 0 | -50.8406 | 54.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 4 | 52 | 7.9 | 7.9 | 8.5542 |  | 15 | 91 | 91 | 0 | 0 | -42.6287 | 71.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 5 | 53 | 7.8 | 7.8 | 8.5542 |  | 15 | 91 | 91 | 0 | 0 | -33.6326 | 84.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 6 | 54 | 7.7 | 7.7 | 8.5542 |  | 15 | 92 | 92 | 0 | 0 | -24.4351 | 96.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 7 | 55 | 7.6 | 7.6 | 8.5542 |  | 15 | 94 | 94 | 0 | 0 | -15.4377 | 107.5973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Wednesday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 3 | 8 | 56 | 7.4 | 7.4 | 8.5542 |  | 15 | 94 | 94 | 0 | 0 | -6.9787 | 118.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 9 | 57 | 7.1 | 7.1 | 8.5542 |  | 15 | 93 | 93 | 0 | 0 | 0.60439 | 130.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 10 | 58 | 6.9 | 6.9 | 8.5542 |  | 15 | 90 | 90 | 6.572 | 21.545 | 6.9473 | 142.6141 | 0 | 0.53718 | 5.0111 | 6.5496 | 4.2514 | 0 | 0 | 0 | 0.45499 | 8.4209 | 14.5862 | 65.9352 | 83.593 | 57.2161 | 8.4209 | 8.4209 | 8.4209 | 21.545 | 8.4209 | 15.1234 | 70.9463 | 90.1427 | 61.4675 | 8.4209 | 8.4209 | 8.4209 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 11 | 59 | 7.1 | 7.1 | 8.5542 |  | 15 | 86 | 86 | 50.6014 | 74.6305 | 11.6657 | 155.7733 | 0 | 0 | 30.4986 | 49.787 | 39.9108 | 6.6555 | 0 | 0 | 8.3695 | 34.1611 | 34.1611 | 105.3644 | 150.3959 | 127.3387 | 49.6992 | 34.1611 | 34.1611 | 74.6305 | 34.1611 | 34.1611 | 135.863 | 200.1829 | 167.2495 | 56.3547 | 34.1611 | 34.1611 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 12 | 60 | 7.6 | 7.6 | 8.5542 |  | 15 | 78 | 78 | 382.3919 | 95.264 | 14.4031 | 169.6728 | 0 | 0 | 153.6726 | 350.1479 | 341.5112 | 132.8219 | 0 | 0 | 87.736 | 55.1753 | 55.1753 | 95.0736 | 146.0848 | 143.8425 | 89.6601 | 55.1753 | 55.1753 | 95.264 | 55.1753 | 55.1753 | 248.7462 | 496.2327 | 485.3537 | 222.4821 | 55.1753 | 55.1753 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 13 | 61 | 7.1 | 7.1 | 8.5542 |  | 15 | 82 | 82 | 10.7735 | 91.2314 | 14.9166 | 183.9423 | 0 | 0 | 1.8707 | 8.5818 | 10.2658 | 5.9363 | 0 | 0 | 2.7686 | 43.1627 | 43.1627 | 47.8757 | 64.7839 | 69.0268 | 58.1188 | 43.1627 | 43.1627 | 91.2314 | 43.1627 | 43.1627 | 49.7463 | 73.3657 | 79.2926 | 64.0551 | 43.1627 | 43.1627 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 14 | 62 | 7.2 | 7.2 | 8.5542 |  | 15 | 80 | 80 | 430.7249 | 96.9786 | 13.1569 | 198.0664 | 0 | 0 | 0 | 273.3745 | 415.2253 | 313.8428 | 28.6154 | 0 | 106.0214 | 58.5312 | 58.5312 | 58.5312 | 125.5697 | 160.3551 | 135.4935 | 65.5485 | 58.5312 | 96.9786 | 58.5312 | 58.5312 | 58.5312 | 398.9442 | 575.5805 | 449.3363 | 94.1638 | 58.5312 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 15 | 63 | 7.4 | 7.4 | 8.5542 |  | 15 | 78 | 78 | 654.2969 | 56.664 | 9.2876 | 211.5881 | 0 | 0 | 0 | 288.5894 | 605.7105 | 568.0145 | 197.5834 | 0 | 129.336 | 42.4123 | 42.4123 | 42.4123 | 79.4563 | 120.1627 | 115.3239 | 67.7745 | 42.4123 | 56.664 | 42.4123 | 42.4123 | 42.4123 | 368.0457 | 725.8731 | 683.3384 | 265.3579 | 42.4123 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 16 | 64 | 7 | 7 | 8.5542 |  | 15 | 77 | 77 | 388.1928 | 47.409 | 3.6259 | 224.2727 | 0 | 0 | 0 | 88.8612 | 326.3417 | 372.6556 | 200.673 | 0 | 44.591 | 29.0329 | 29.0329 | 29.0329 | 48.229 | 99.5302 | 109.5351 | 72.3829 | 29.0329 | 47.409 | 29.0329 | 29.0329 | 29.0329 | 137.0901 | 425.8719 | 482.1907 | 273.0559 | 29.0329 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 17 | 65 | 6 | 6 | 8.5542 |  | 15 | 84 | 84 | 7.6438 | 2.31 | -3.4477 | 236.1436 | 0 | 0 | 0 | 0.096838 | 5.4622 | 7.6279 | 5.3253 | 0 | 11.69 | 2.495 | 2.495 | 2.495 | 2.5933 | 8.0382 | 10.236 | 7.8992 | 2.495 | 2.31 | 2.495 | 2.495 | 2.495 | 2.6901 | 13.5004 | 17.8639 | 13.2245 | 2.495 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Wednesday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 3 | 18 | 66 | 5.4 | 5.4 | 8.5542 |  | 15 | 86 | 86 | 0 | 0 | -11.5568 | 247.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 19 | 67 | 4.8 | 4.8 | 8.5542 |  | 15 | 86 | 86 | 0 | 0 | -20.3535 | 258.5218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 20 | 68 | 4.6 | 4.6 | 8.5542 |  | 15 | 87 | 87 | 0 | 0 | -29.5052 | 269.9534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 21 | 69 | 4.6 | 4.6 | 8.5542 |  | 15 | 87 | 87 | 0 | 0 | -38.6492 | 282.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 22 | 70 | 5 | 5 | 8.5542 |  | 15 | 86 | 86 | 0 | 0 | -47.3038 | 297.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 23 | 71 | 5.4 | 5.4 | 8.5542 |  | 15 | 85 | 85 | 0 | 0 | -54.7065 | 315.9279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 3 | 24 | 72 | 5.2 | 5.2 | 6.8667 |  | 15 | 91 | 91 | 0 | 0 | -59.6262 | 339.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Wednesday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 1 | 73 | 5.8 | 5.8 | 6.8667 |  | 15 | 91 | 91 | 0 | 0 | -60.6235 | 7.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 2 | 74 | 6.5 | 6.5 | 6.8667 |  | 15 | 88 | 88 | 0 | 0 | -57.2604 | 33.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 3 | 75 | 7 | 7 | 6.8667 |  | 15 | 85 | 85 | 0 | 0 | -50.8159 | 54.7271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 4 | 76 | 6.8 | 6.8 | 6.8667 |  | 15 | 86 | 86 | 0 | 0 | -42.6188 | 71.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 5 | 77 | 7 | 7 | 6.8667 |  | 15 | 87 | 87 | 0 | 0 | -33.6288 | 84.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 6 | 78 | 7.1 | 7.1 | 6.8667 |  | 15 | 91 | 91 | 0 | 0 | -24.4311 | 96.2766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 7 | 79 | 6.9 | 6.9 | 6.8667 |  | 15 | 94 | 94 | 0 | 0 | -15.4288 | 107.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Thursday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 4 | 8 | 80 | 7 | 7 | 6.8667 |  | 15 | 95 | 95 | 0 | 0 | -6.9607 | 118.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 9 | 81 | 7.2 | 7.2 | 6.8667 |  | 15 | 95 | 95 | 0 | 0 | 0.63499 | 130.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 10 | 82 | 7.6 | 7.6 | 6.8667 |  | 15 | 93 | 93 | 0.11712 | 2.9918 | 6.9937 | 142.4799 | 0 | 0.0098537 | 0.089488 | 0.1167 | 0.075553 | 0 | 0 | 0 | 0.0081879 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 2.9918 | 1.401 | 1.4109 | 1.4905 | 1.5177 | 1.4766 | 1.401 | 1.401 | 1.401 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 11 | 83 | 8 | 8 | 6.8667 |  | 15 | 91 | 91 | 0.45043 | 13.9251 | 11.7301 | 155.6452 | 0 | 0 | 0.27229 | 0.44327 | 0.35459 | 0.0582 | 0 | 0 | 0.074932 | 6.5856 | 6.5856 | 6.5856 | 6.5856 | 6.5856 | 6.5856 | 6.5856 | 6.5856 | 13.9251 | 6.5856 | 6.5856 | 6.8579 | 7.0289 | 6.9402 | 6.6438 | 6.5856 | 6.5856 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 12 | 84 | 8.5 | 8.5 | 6.8667 |  | 15 | 88 | 88 | 2.108 | 41.5137 | 14.4865 | 169.5553 | 0 | 0 | 0.85115 | 1.9314 | 1.8803 | 0.72771 | 0 | 0 | 0.48631 | 20.2077 | 20.2077 | 20.2077 | 20.2077 | 20.2077 | 20.2077 | 20.2077 | 20.2077 | 41.5137 | 20.2077 | 20.2077 | 21.0588 | 22.1391 | 22.0879 | 20.9354 | 20.2077 | 20.2077 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 13 | 85 | 8.8 | 8.8 | 6.8667 |  | 15 | 86 | 86 | 0.59468 | 24.8463 | 15.0175 | 183.8404 | 0 | 0 | 0.10438 | 0.4742 | 0.56624 | 0.32658 | 0 | 0 | 0.15375 | 11.779 | 11.779 | 11.779 | 11.779 | 11.779 | 11.779 | 11.779 | 11.779 | 24.8463 | 11.779 | 11.779 | 11.8834 | 12.2532 | 12.3453 | 12.1056 | 11.779 | 11.779 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 14 | 86 | 9 | 9 | 6.8667 |  | 15 | 85 | 85 | 0.2989 | 16.9259 | 13.2724 | 197.9833 | 0 | 0 | 0 | 0.19001 | 0.28805 | 0.21735 | 0.019336 | 0 | 0.074121 | 7.9518 | 7.9518 | 7.9518 | 7.9518 | 7.9518 | 7.9518 | 7.9518 | 7.9518 | 16.9259 | 7.9518 | 7.9518 | 7.9518 | 8.1418 | 8.2398 | 8.1691 | 7.9711 | 7.9518 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 15 | 87 | 8.8 | 8.8 | 6.8667 |  | 15 | 88 | 88 | 0.10203 | 7.9796 | 9.4138 | 211.5244 | 0 | 0 | 0 | 0.045109 | 0.094454 | 0.088469 | 0.03066 | 0 | 0.020379 | 3.7119 | 3.7119 | 3.7119 | 3.7119 | 3.7119 | 3.7119 | 3.7119 | 3.7119 | 7.9796 | 3.7119 | 3.7119 | 3.7119 | 3.757 | 3.8064 | 3.8004 | 3.7426 | 3.7119 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 16 | 88 | 8.8 | 8.8 | 6.8667 |  | 15 | 91 | 91 | 0.16696 | 5.9804 | 3.7591 | 224.2263 | 0 | 0 | 0 | 0.038382 | 0.1404 | 0.16017 | 0.086119 | 0 | 0.019551 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 5.9804 | 2.7758 | 2.7758 | 2.7758 | 2.8141 | 2.9162 | 2.9359 | 2.8619 | 2.7758 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 17 | 89 | 8.8 | 8.8 | 6.8667 |  | 15 | 92 | 92 | 0 | 0 | -3.3104 | 236.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Thursday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 4 | 18 | 90 | 8.6 | 8.6 | 6.8667 |  | 15 | 85 | 85 | 0 | 0 | -11.4175 | 247.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 19 | 91 | 8.1 | 8.1 | 6.8667 |  | 15 | 88 | 88 | 0 | 0 | -20.2133 | 258.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 20 | 92 | 7.9 | 7.9 | 6.8667 |  | 15 | 89 | 89 | 0 | 0 | -29.3647 | 269.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 21 | 93 | 8 | 8 | 6.8667 |  | 15 | 87 | 87 | 0 | 0 | -38.5091 | 282.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 22 | 94 | 8.2 | 8.2 | 6.8667 |  | 15 | 84 | 84 | 0 | 0 | -47.1651 | 297.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 23 | 95 | 8.1 | 8.1 | 6.8667 |  | 15 | 84 | 84 | 0 | 0 | -54.5733 | 315.8476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 4 | 24 | 96 | 7.8 | 7.8 | 7.7625 |  | 15 | 85 | 85 | 0 | 0 | -59.5088 | 339.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Thursday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 1 | 97 | 7.4 | 7.4 | 7.7625 |  | 15 | 87 | 87 | 0 | 0 | -60.5366 | 7.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 2 | 98 | 7.5 | 7.5 | 7.7625 |  | 15 | 84 | 84 | 0 | 0 | -57.2014 | 33.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 3 | 99 | 7.3 | 7.3 | 7.7625 |  | 15 | 84 | 84 | 0 | 0 | -50.784 | 54.5027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 4 | 100 | 6.4 | 6.4 | 7.7625 |  | 15 | 88 | 88 | 0 | 0 | -42.6022 | 70.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 5 | 101 | 6.7 | 6.7 | 7.7625 |  | 15 | 88 | 88 | 0 | 0 | -33.6185 | 84.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 6 | 102 | 6.8 | 6.8 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -24.4207 | 96.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 7 | 103 | 6.9 | 6.9 | 7.7625 |  | 15 | 95 | 95 | 0 | 0 | -15.4133 | 107.3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Friday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 5 | 8 | 104 | 7.2 | 7.2 | 7.7625 |  | 15 | 94 | 94 | 0 | 0 | -6.9361 | 118.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 9 | 105 | 7.2 | 7.2 | 7.7625 |  | 15 | 94 | 94 | 0 | 0 | 0.67251 | 130.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 10 | 106 | 7 | 7 | 7.7625 |  | 15 | 92 | 92 | 0 | 0 | 7.0473 | 142.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 11 | 107 | 7.1 | 7.1 | 7.7625 |  | 15 | 94 | 94 | 0 | 0 | 11.8019 | 155.5161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 12 | 108 | 7.4 | 7.4 | 7.7625 |  | 15 | 95 | 95 | 0.042512 | 5.9901 | 14.5772 | 169.438 | 0 | 0 | 0.017246 | 0.038974 | 0.037872 | 0.014584 | 0 | 0 | 0.0098661 | 2.7788 | 2.7788 | 2.7788 | 2.7788 | 2.7788 | 2.7788 | 2.7788 | 2.7788 | 5.9901 | 2.7788 | 2.7788 | 2.7961 | 2.8178 | 2.8167 | 2.7934 | 2.7788 | 2.7788 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 13 | 109 | 8.4 | 8.4 | 7.7625 |  | 15 | 96 | 96 | 0.060116 | 7.9844 | 15.1257 | 183.7399 | 0 | 0 | 0.010664 | 0.047984 | 0.057195 | 0.032902 | 0 | 0 | 0.015643 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 3.7141 | 7.9844 | 3.7141 | 3.7141 | 3.7248 | 3.7621 | 3.7713 | 3.747 | 3.7141 | 3.7141 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 14 | 110 | 9.4 | 9.4 | 7.7625 |  | 15 | 93 | 93 | 0.065166 | 7.9837 | 13.3949 | 197.9029 | 0 | 0 | 0 | 0.041487 | 0.062775 | 0.04729 | 0.0041034 | 0 | 0.016287 | 3.7143 | 3.7143 | 3.7143 | 3.7143 | 3.7143 | 3.7143 | 3.7143 | 3.7143 | 7.9837 | 3.7143 | 3.7143 | 3.7143 | 3.7557 | 3.777 | 3.7615 | 3.7184 | 3.7143 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 15 | 111 | 10.6 | 10.6 | 7.7625 |  | 15 | 87 | 87 | 0.45084 | 16.909 | 9.5466 | 211.4643 | 0 | 0 | 0 | 0.19977 | 0.41734 | 0.39044 | 0.13482 | 0 | 0.091033 | 7.9524 | 7.9524 | 7.9524 | 7.9524 | 7.9524 | 7.9524 | 7.9524 | 7.9524 | 16.909 | 7.9524 | 7.9524 | 7.9524 | 8.1521 | 8.3697 | 8.3428 | 8.0872 | 7.9524 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 16 | 112 | 9.3 | 9.3 | 7.7625 |  | 15 | 88 | 88 | 0.16045 | 5.9808 | 3.8983 | 224.1843 | 0 | 0 | 0 | 0.037033 | 0.13496 | 0.15383 | 0.082588 | 0 | 0.019167 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 5.9808 | 2.7758 | 2.7758 | 2.7758 | 2.8128 | 2.9108 | 2.9296 | 2.8584 | 2.7758 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 17 | 113 | 8.2 | 8.2 | 7.7625 |  | 15 | 95 | 95 | 0 | 0 | -3.1677 | 236.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2 | Friday | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 5 | 18 | 114 | 8.1 | 8.1 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -11.2731 | 247.3926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 19 | 115 | 7.7 | 7.7 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -20.0682 | 258.4959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 20 | 116 | 7.4 | 7.4 | 7.7625 |  | 15 | 94 | 94 | 0 | 0 | -29.2195 | 269.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 21 | 117 | 7.3 | 7.3 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -38.364 | 282.4589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 22 | 118 | 7.4 | 7.4 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -47.0212 | 297.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 23 | 119 | 7.3 | 7.3 | 7.7625 |  | 15 | 93 | 93 | 0 | 0 | -54.4341 | 315.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 5 | 24 | 120 | 7.1 | 7.1 | 7.6292 |  | 15 | 97 | 97 | 0 | 0 | -59.3843 | 339.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Friday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 1 | 121 | 7.1 | 7.1 | 7.6292 |  | 15 | 97 | 97 | 0 | 0 | -60.442 | 7.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 2 | 122 | 7 | 7 | 7.6292 |  | 15 | 98 | 98 | 0 | 0 | -57.1347 | 33.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 3 | 123 | 6.8 | 6.8 | 7.6292 |  | 15 | 97 | 97 | 0 | 0 | -50.7448 | 54.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 4 | 124 | 6.9 | 6.9 | 7.6292 |  | 15 | 95 | 95 | 0 | 0 | -42.5788 | 70.6531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 5 | 125 | 6.1 | 6.1 | 7.6292 |  | 15 | 95 | 95 | 0 | 0 | -33.6016 | 84.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 6 | 126 | 6.1 | 6.1 | 7.6292 |  | 15 | 96 | 96 | 0 | 0 | -24.4038 | 95.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 7 | 127 | 5.6 | 5.6 | 7.6292 |  | 15 | 91 | 91 | 0 | 0 | -15.3912 | 107.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Saturday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 6 | 8 | 128 | 4.7 | 4.7 | 7.6292 |  | 15 | 92 | 92 | 0 | 0 | -6.9047 | 118.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 9 | 129 | 4.9 | 4.9 | 7.6292 |  | 15 | 92 | 92 | 0 | 0 | 0.71695 | 129.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 10 | 130 | 5.7 | 5.7 | 7.6292 |  | 15 | 91 | 91 | 0.79419 | 7.9431 | 7.1079 | 142.2057 | 0 | 0.07073 | 0.60932 | 0.79097 | 0.50929 | 0 | 0 | 0 | 0.056859 | 3.8701 | 3.8701 | 3.8701 | 3.8701 | 3.8701 | 3.8701 | 3.8701 | 3.8701 | 7.9431 | 3.8701 | 3.9408 | 4.4794 | 4.6611 | 4.3794 | 3.8701 | 3.8701 | 3.8701 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 11 | 131 | 6.1 | 6.1 | 7.6292 |  | 15 | 92 | 92 | 8.4333 | 56.5779 | 11.8811 | 155.3861 | 0 | 0 | 5.1285 | 8.3024 | 6.613 | 1.0497 | 0 | 0 | 1.4221 | 25.5332 | 25.5332 | 61.9353 | 84.4642 | 72.4722 | 32.9839 | 25.5332 | 25.5332 | 56.5779 | 25.5332 | 25.5332 | 67.0638 | 92.7667 | 79.0851 | 34.0336 | 25.5332 | 25.5332 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 12 | 132 | 6.6 | 6.6 | 7.6292 |  | 15 | 94 | 94 | 1.511 | 35.6471 | 14.6752 | 169.3209 | 0 | 0 | 0.61584 | 1.386 | 1.3442 | 0.51506 | 0 | 0 | 0.35292 | 17.2091 | 17.2091 | 17.2091 | 17.2091 | 17.2091 | 17.2091 | 17.2091 | 17.2091 | 35.6471 | 17.2091 | 17.2091 | 17.825 | 18.5951 | 18.5534 | 17.7242 | 17.2091 | 17.2091 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 13 | 133 | 7 | 7 | 7.6292 |  | 15 | 91 | 91 | 2.3163 | 49.3931 | 15.2412 | 183.6409 | 0 | 0 | 0.41522 | 1.8506 | 2.2019 | 1.2634 | 0 | 0 | 0.60689 | 24.0443 | 24.0443 | 24.0443 | 24.0443 | 24.0443 | 24.0443 | 24.0443 | 24.0443 | 49.3931 | 24.0443 | 24.0443 | 24.4595 | 25.8949 | 26.2462 | 25.3077 | 24.0443 | 24.0443 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 14 | 134 | 7.4 | 7.4 | 7.6292 |  | 15 | 86 | 86 | 47.7959 | 112.9554 | 13.5243 | 197.8252 | 0 | 0 | 0 | 30.4716 | 46.0218 | 34.613 | 2.9284 | 0 | 12.0446 | 53.9342 | 53.9342 | 53.9342 | 97.0045 | 118.984 | 102.8582 | 58.0734 | 53.9342 | 112.9554 | 53.9342 | 53.9342 | 53.9342 | 127.4761 | 165.0058 | 137.4712 | 61.0018 | 53.9342 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 15 | 135 | 7 | 7 | 7.6292 |  | 15 | 88 | 88 | 10.9659 | 72.7606 | 9.6857 | 211.408 | 0 | 0 | 0 | 4.8693 | 10.15 | 9.4849 | 3.2637 | 0 | 2.2394 | 35.4412 | 35.4412 | 35.4412 | 39.7852 | 44.4962 | 43.9029 | 38.3528 | 35.4412 | 72.7606 | 35.4412 | 35.4412 | 35.4412 | 44.6545 | 54.6462 | 53.3878 | 41.6165 | 35.4412 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 16 | 136 | 6.7 | 6.7 | 7.6292 |  | 15 | 85 | 85 | 238.1718 | 56.9598 | 4.0434 | 224.1468 | 0 | 0 | 0 | 55.1742 | 200.3769 | 228.2015 | 122.3488 | 0 | 29.0402 | 32.2649 | 32.2649 | 32.2649 | 52.8692 | 107.0941 | 117.485 | 77.9551 | 32.2649 | 56.9598 | 32.2649 | 32.2649 | 32.2649 | 108.0434 | 307.471 | 345.6865 | 200.3039 | 32.2649 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 17 | 137 | 6 | 6 | 7.6292 |  | 15 | 89 | 89 | 15.7476 | 3.135 | -3.0195 | 236.0615 | 0 | 0 | 0 | 0.2339 | 11.2717 | 15.7067 | 10.9409 | 0 | 15.865 | 3.4084 | 3.4084 | 3.4084 | 3.6049 | 12.8758 | 16.6008 | 12.5979 | 3.4084 | 3.135 | 3.4084 | 3.4084 | 3.4084 | 3.8388 | 24.1475 | 32.3075 | 23.5389 | 3.4084 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 18 | 138 | 5.5 | 5.5 | 7.6292 |  | 15 | 91 | 91 | 0 | 0 | -11.1236 | 247.3815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 19 | 139 | 4.7 | 4.7 | 7.6292 |  | 15 | 93 | 93 | 0 | 0 | -19.9184 | 258.4921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 20 | 140 | 4.4 | 4.4 | 7.6292 |  | 15 | 94 | 94 | 0 | 0 | -29.0697 | 269.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 21 | 141 | 4.5 | 4.5 | 7.6292 |  | 15 | 92 | 92 | 0 | 0 | -38.2142 | 282.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 22 | 142 | 5.2 | 5.2 | 7.6292 |  | 15 | 91 | 91 | 0 | 0 | -46.8721 | 297.1839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 23 | 143 | 5.2 | 5.2 | 7.6292 |  | 15 | 91 | 91 | 0 | 0 | -54.289 | 315.7116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 6 | 24 | 144 | 5.8 | 5.8 | 5.9583 |  | 15 | 89 | 89 | 0 | 0 | -59.2527 | 339.4738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Saturday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 1 | 145 | 5.9 | 5.9 | 5.9583 |  | 15 | 88 | 88 | 0 | 0 | -60.3395 | 7.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 2 | 146 | 4.7 | 4.7 | 5.9583 |  | 15 | 91 | 91 | 0 | 0 | -57.0602 | 33.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 3 | 147 | 4.2 | 4.2 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | -50.6983 | 54.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 4 | 148 | 4 | 4 | 5.9583 |  | 15 | 93 | 93 | 0 | 0 | -42.5485 | 70.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 5 | 149 | 4.8 | 4.8 | 5.9583 |  | 15 | 93 | 93 | 0 | 0 | -33.5782 | 83.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 6 | 150 | 5 | 5 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | -24.3803 | 95.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 7 | 151 | 5 | 5 | 5.9583 |  | 15 | 91 | 91 | 0 | 0 | -15.3627 | 106.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5 | Sunday | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 7 | 8 | 152 | 4.6 | 4.6 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | -6.8666 | 118.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 9 | 153 | 4.6 | 4.6 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | 0.76832 | 129.7444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 10 | 154 | 4.9 | 4.9 | 5.9583 |  | 15 | 91 | 91 | 0.43443 | 5.9685 | 7.1758 | 142.0658 | 0 | 0.03979 | 0.33401 | 0.43257 | 0.27774 | 0 | 0 | 0 | 0.031541 | 2.8601 | 2.8601 | 2.8601 | 2.8601 | 2.8601 | 2.8601 | 2.8601 | 2.8601 | 5.9685 | 2.8601 | 2.8999 | 3.1941 | 3.2927 | 3.1378 | 2.8601 | 2.8601 | 2.8601 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 11 | 155 | 5.2 | 5.2 | 5.9583 |  | 15 | 91 | 91 | 2.3989 | 32.5924 | 11.9675 | 155.2552 | 0 | 0 | 1.4632 | 2.3621 | 1.8773 | 0.29278 | 0 | 0 | 0.40765 | 16.0228 | 16.0228 | 16.0228 | 16.0228 | 16.0228 | 16.0228 | 16.0228 | 16.0228 | 32.5924 | 16.0228 | 16.0228 | 17.486 | 18.3848 | 17.9 | 16.3156 | 16.0228 | 16.0228 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 12 | 156 | 5.8 | 5.8 | 5.9583 |  | 15 | 89 | 89 | 5.9615 | 70.5979 | 14.7806 | 169.2041 | 0 | 0 | 2.4411 | 5.4712 | 5.2964 | 2.019 | 0 | 0 | 1.4021 | 33.7767 | 33.7767 | 41.1139 | 50.2217 | 49.6962 | 39.8452 | 33.7767 | 33.7767 | 70.5979 | 33.7767 | 33.7767 | 43.555 | 55.6929 | 54.9926 | 41.8643 | 33.7767 | 33.7767 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 13 | 157 | 6.2 | 6.2 | 5.9583 |  | 15 | 88 | 88 | 0.99441 | 32.7375 | 15.3638 | 183.5434 | 0 | 0 | 0.1801 | 0.7952 | 0.94449 | 0.5405 | 0 | 0 | 0.26246 | 15.6491 | 15.6491 | 15.6491 | 15.6491 | 15.6491 | 15.6491 | 15.6491 | 15.6491 | 32.7375 | 15.6491 | 15.6491 | 15.8292 | 16.4443 | 16.5936 | 16.1896 | 15.6491 | 15.6491 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 14 | 158 | 6.5 | 6.5 | 5.9583 |  | 15 | 87 | 87 | 0.94606 | 30.7595 | 13.6605 | 197.7502 | 0 | 0 | 0 | 0.60395 | 0.9105 | 0.68369 | 0.056382 | 0 | 0.24048 | 14.6619 | 14.6619 | 14.6619 | 14.6619 | 14.6619 | 14.6619 | 14.6619 | 14.6619 | 30.7595 | 14.6619 | 14.6619 | 14.6619 | 15.2658 | 15.5724 | 15.3456 | 14.7183 | 14.6619 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 15 | 159 | 6.7 | 6.7 | 5.9583 |  | 15 | 86 | 86 | 0.93106 | 24.8076 | 9.8313 | 211.3554 | 0 | 0 | 0 | 0.41425 | 0.86166 | 0.80432 | 0.27582 | 0 | 0.19239 | 11.7753 | 11.7753 | 11.7753 | 11.7753 | 11.7753 | 11.7753 | 11.7753 | 11.7753 | 24.8076 | 11.7753 | 11.7753 | 11.7753 | 12.1895 | 12.6369 | 12.5796 | 12.0511 | 11.7753 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 16 | 160 | 6.7 | 6.7 | 5.9583 |  | 15 | 86 | 86 | 3.2166 | 27.5995 | 4.1944 | 224.1139 | 0 | 0 | 0 | 0.74765 | 2.7065 | 3.0799 | 1.6492 | 0 | 0.40051 | 13.2743 | 13.2743 | 13.2743 | 13.2743 | 13.2743 | 13.2743 | 13.2743 | 13.2743 | 27.5995 | 13.2743 | 13.2743 | 13.2743 | 14.022 | 15.9808 | 16.3542 | 14.9235 | 13.2743 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 17 | 161 | 6.5 | 6.5 | 5.9583 |  | 15 | 86 | 86 | 22.5892 | 6.4552 | -2.866 | 236.0443 | 0 | 0 | 0 | 0.3484 | 16.1746 | 22.526 | 15.6819 | 0 | 1.5448 | 3.8053 | 3.8053 | 3.8053 | 4.1293 | 18.8479 | 24.7548 | 18.3897 | 3.8053 | 6.4552 | 3.8053 | 3.8053 | 3.8053 | 4.4777 | 35.0225 | 47.2807 | 34.0716 | 3.8053 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 18 | 162 | 5.6 | 5.6 | 5.9583 |  | 15 | 93 | 93 | 0 | 0 | -10.9692 | 247.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 19 | 163 | 5.3 | 5.3 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | -19.764 | 258.4944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 20 | 164 | 5.8 | 5.8 | 5.9583 |  | 15 | 91 | 91 | 0 | 0 | -28.9152 | 269.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 21 | 165 | 5.8 | 5.8 | 5.9583 |  | 15 | 90 | 90 | 0 | 0 | -38.0598 | 282.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 22 | 166 | 5.2 | 5.2 | 5.9583 |  | 15 | 92 | 92 | 0 | 0 | -46.718 | 297.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 23 | 167 | 4.8 | 4.8 | 5.9583 |  | 15 | 91 | 91 | 0 | 0 | -54.138 | 315.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 7 | 24 | 168 | 4 | 4 | 5.325 | 6.4493 | 15 | 95 | 95 | 0 | 0 | -59.1143 | 339.3401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | Sunday | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 1 | 169 | 3.7 | 3.7 | 5.325 | 6.4493 | 15 | 95 | 95 | 0 | 0 | -60.2294 | 6.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 2 | 170 | 2.8 | 2.8 | 5.325 | 6.4493 | 15 | 96 | 96 | 0 | 0 | -56.978 | 32.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 3 | 171 | 2.1 | 2.1 | 5.325 | 6.4493 | 15 | 98 | 98 | 0 | 0 | -50.6444 | 53.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 4 | 172 | 2 | 2 | 5.325 | 6.4493 | 15 | 97 | 97 | 0 | 0 | -42.5113 | 70.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 5 | 173 | 1.7 | 1.7 | 5.325 | 6.4493 | 15 | 96 | 96 | 0 | 0 | -33.5481 | 83.7233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 6 | 174 | 1.7 | 1.7 | 5.325 | 6.4493 | 15 | 96 | 96 | 0 | 0 | -24.3504 | 95.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 7 | 175 | 1.6 | 1.6 | 5.325 | 6.4493 | 15 | 95 | 95 | 0 | 0 | -15.3275 | 106.8291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 8 | 8 | 176 | 1.4 | 1.4 | 5.325 | 6.4493 | 15 | 96 | 96 | 0 | 0 | -6.8218 | 118.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 9 | 177 | 2 | 2 | 5.325 | 6.4493 | 15 | 93 | 93 | 0 | 0 | 0.82662 | 129.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 10 | 178 | 2.9 | 2.9 | 5.325 | 6.4493 | 15 | 92 | 92 | 28.5345 | 30.8964 | 7.2508 | 141.9242 | 0 | 2.6869 | 21.9851 | 28.4047 | 18.1852 | 0 | 0 | 0 | 2.1036 | 12.612 | 22.0446 | 89.7917 | 112.328 | 76.452 | 12.612 | 12.612 | 12.612 | 30.8964 | 12.612 | 24.7316 | 111.7768 | 140.7327 | 94.6372 | 12.612 | 12.612 | 12.612 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 11 | 179 | 4.5 | 4.5 | 5.325 | 6.4493 | 15 | 89 | 89 | 247.5373 | 79.5851 | 12.0612 | 155.1236 | 0 | 0 | 151.4362 | 243.7669 | 193.3022 | 29.6037 | 0 | 0 | 42.4149 | 42.3743 | 42.3743 | 104.6592 | 142.6344 | 121.8785 | 54.5502 | 42.3743 | 42.3743 | 79.5851 | 42.3743 | 42.3743 | 256.0955 | 386.4012 | 315.1807 | 84.1539 | 42.3743 | 42.3743 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 12 | 180 | 4.3 | 4.3 | 5.325 | 6.4493 | 15 | 91 | 91 | 1.9991 | 41.5264 | 14.8933 | 169.0877 | 0 | 0 | 0.82239 | 1.8356 | 1.7736 | 0.67261 | 0 | 0 | 0.47364 | 20.1898 | 20.1898 | 20.1898 | 20.1898 | 20.1898 | 20.1898 | 20.1898 | 20.1898 | 41.5264 | 20.1898 | 20.1898 | 21.0122 | 22.0255 | 21.9634 | 20.8624 | 20.1898 | 20.1898 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 13 | 181 | 4.8 | 4.8 | 5.325 | 6.4493 | 15 | 93 | 93 | 0.56204 | 24.8505 | 15.4935 | 183.4477 | 0 | 0 | 0.10282 | 0.44983 | 0.53334 | 0.30442 | 0 | 0 | 0.14949 | 11.776 | 11.776 | 11.776 | 11.776 | 11.776 | 11.776 | 11.776 | 11.776 | 24.8505 | 11.776 | 11.776 | 11.8788 | 12.2258 | 12.3093 | 12.0804 | 11.776 | 11.776 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 14 | 182 | 5.4 | 5.4 | 5.325 | 6.4493 | 15 | 92 | 92 | 1.8718 | 43.5199 | 13.8035 | 197.6781 | 0 | 0 | 0 | 1.1965 | 1.8005 | 1.3499 | 0.10847 | 0 | 0.48013 | 21.0171 | 21.0171 | 21.0171 | 21.0171 | 21.0171 | 21.0171 | 21.0171 | 21.0171 | 43.5199 | 21.0171 | 21.0171 | 21.0171 | 22.2136 | 22.8176 | 22.367 | 21.1256 | 21.0171 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 15 | 183 | 5.4 | 5.4 | 5.325 | 6.4493 | 15 | 91 | 91 | 2.8147 | 43.4112 | 9.9831 | 211.3066 | 0 | 0 | 0 | 1.2546 | 2.6043 | 2.4285 | 0.83006 | 0 | 0.58877 | 21.053 | 21.053 | 21.053 | 21.053 | 21.053 | 21.053 | 21.053 | 21.053 | 43.4112 | 21.053 | 21.053 | 21.053 | 22.3076 | 23.6573 | 23.4815 | 21.883 | 21.053 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 16 | 184 | 5.4 | 5.4 | 5.325 | 6.4493 | 15 | 92 | 92 | 1.9025 | 21.758 | 4.3511 | 224.0856 | 0 | 0 | 0 | 0.44356 | 1.6009 | 1.8205 | 0.97362 | 0 | 0.24203 | 10.361 | 10.361 | 10.361 | 10.361 | 10.361 | 10.361 | 10.361 | 10.361 | 21.758 | 10.361 | 10.361 | 10.361 | 10.8046 | 11.9619 | 12.1815 | 11.3346 | 10.361 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 17 | 185 | 5.2 | 5.2 | 5.325 | 6.4493 | 15 | 92 | 92 | 11.3595 | 5.8159 | -2.7072 | 236.0323 | 0 | 0 | 0 | 0.18076 | 8.136 | 11.3253 | 7.8804 | 0 | 0.18411 | 3.2417 | 3.2417 | 3.2417 | 3.3358 | 7.478 | 9.1387 | 7.3449 | 3.2417 | 5.8159 | 3.2417 | 3.2417 | 3.2417 | 3.5165 | 15.614 | 20.464 | 15.2253 | 3.2417 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 8 | 18 | 186 | 5.4 | 5.4 | 5.325 | 6.4493 | 15 | 91 | 91 | 0 | 0 | -10.81 | 247.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 19 | 187 | 5.3 | 5.3 | 5.325 | 6.4493 | 15 | 94 | 94 | 0 | 0 | -19.6049 | 258.5029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 20 | 188 | 5 | 5 | 5.325 | 6.4493 | 15 | 95 | 95 | 0 | 0 | -28.7564 | 269.9482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 21 | 189 | 5.2 | 5.2 | 5.325 | 6.4493 | 15 | 97 | 97 | 0 | 0 | -37.9007 | 282.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 22 | 190 | 5.4 | 5.4 | 5.325 | 6.4493 | 15 | 97 | 97 | 0 | 0 | -46.5588 | 297.1636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 23 | 191 | 5.5 | 5.5 | 5.325 | 6.4493 | 15 | 95 | 95 | 0 | 0 | -53.9812 | 315.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 8 | 24 | 192 | 4.9 | 4.9 | 3.9 | 5.9014 | 15 | 95 | 95 | 0 | 0 | -58.969 | 339.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 1 | 193 | 4.5 | 4.5 | 3.9 | 5.9014 | 15 | 96 | 96 | 0 | 0 | -60.1115 | 6.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 2 | 194 | 4.8 | 4.8 | 3.9 | 5.9014 | 15 | 97 | 97 | 0 | 0 | -56.888 | 32.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 3 | 195 | 5 | 5 | 3.9 | 5.9014 | 15 | 96 | 96 | 0 | 0 | -50.5833 | 53.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 4 | 196 | 4.1 | 4.1 | 3.9 | 5.9014 | 15 | 96 | 96 | 0 | 0 | -42.4672 | 70.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 5 | 197 | 3.2 | 3.2 | 3.9 | 5.9014 | 15 | 97 | 97 | 0 | 0 | -33.5113 | 83.5315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 6 | 198 | 3.9 | 3.9 | 3.9 | 5.9014 | 15 | 99 | 99 | 0 | 0 | -24.3138 | 95.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 7 | 199 | 2.7 | 2.7 | 3.9 | 5.9014 | 15 | 98 | 98 | 0 | 0 | -15.2857 | 106.6646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 9 | 8 | 200 | 2.1 | 2.1 | 3.9 | 5.9014 | 15 | 99 | 99 | 0 | 0 | -6.7702 | 117.8461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 9 | 201 | 2.4 | 2.4 | 3.9 | 5.9014 | 15 | 99 | 99 | 0 | 0 | 0.89184 | 129.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 10 | 202 | 3.5 | 3.5 | 3.9 | 5.9014 | 15 | 95 | 95 | 19.191 | 29.5617 | 7.3328 | 141.781 | 0 | 1.8573 | 14.8181 | 19.0986 | 12.1915 | 0 | 0 | 0 | 1.4383 | 12.2867 | 20.8972 | 80.9841 | 100.829 | 68.8071 | 12.2867 | 12.2867 | 12.2867 | 29.5617 | 12.2867 | 22.7545 | 95.8022 | 119.9277 | 80.9985 | 12.2867 | 12.2867 | 12.2867 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 11 | 203 | 4.8 | 4.8 | 3.9 | 5.9014 | 15 | 88 | 88 | 142.2482 | 83.4082 | 12.1621 | 154.9913 | 0 | 0 | 87.2848 | 140.0979 | 110.8436 | 16.6586 | 0 | 0 | 24.5918 | 39.8179 | 39.8179 | 131.4441 | 186.884 | 156.1746 | 57.3051 | 39.8179 | 39.8179 | 83.4082 | 39.8179 | 39.8179 | 218.7288 | 326.9819 | 267.0182 | 73.9637 | 39.8179 | 39.8179 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 12 | 204 | 4.7 | 4.7 | 3.9 | 5.9014 | 15 | 89 | 89 | 39.5205 | 104.5636 | 15.0133 | 168.9718 | 0 | 0 | 16.3325 | 36.3056 | 35.0113 | 13.2079 | 0 | 0 | 9.4364 | 48.9258 | 48.9258 | 83.9618 | 126.8074 | 124.0311 | 77.259 | 48.9258 | 48.9258 | 104.5636 | 48.9258 | 48.9258 | 100.2944 | 163.113 | 159.0424 | 90.4669 | 48.9258 | 48.9258 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 13 | 205 | 5.1 | 5.1 | 3.9 | 5.9014 | 15 | 89 | 89 | 22.0162 | 108.0969 | 15.6303 | 183.3536 | 0 | 0 | 4.0678 | 17.6351 | 20.872 | 11.8824 | 0 | 0 | 5.9031 | 50.0269 | 50.0269 | 58.7188 | 87.7093 | 94.626 | 75.4171 | 50.0269 | 50.0269 | 108.0969 | 50.0269 | 50.0269 | 62.7866 | 105.3444 | 115.498 | 87.2995 | 50.0269 | 50.0269 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 14 | 206 | 5.1 | 5.1 | 3.9 | 5.9014 | 15 | 90 | 90 | 52.7524 | 117.3405 | 13.9532 | 197.6089 | 0 | 0 | 0 | 33.7593 | 50.7146 | 37.962 | 2.9718 | 0 | 13.6595 | 55.9806 | 55.9806 | 55.9806 | 100.7637 | 123.2557 | 106.3388 | 59.9228 | 55.9806 | 117.3405 | 55.9806 | 55.9806 | 55.9806 | 134.523 | 173.9703 | 144.3008 | 62.8946 | 55.9806 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 15 | 207 | 5.5 | 5.5 | 3.9 | 5.9014 | 15 | 91 | 91 | 49.9661 | 95.4157 | 10.1411 | 211.2618 | 0 | 0 | 0 | 22.3092 | 46.2196 | 43.0552 | 14.6697 | 0 | 10.5843 | 46.2658 | 46.2658 | 46.2658 | 71.1066 | 97.7303 | 94.2068 | 62.6001 | 46.2658 | 95.4157 | 46.2658 | 46.2658 | 46.2658 | 93.4158 | 143.9499 | 137.2621 | 77.2698 | 46.2658 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 16 | 208 | 5.1 | 5.1 | 3.9 | 5.9014 | 15 | 92 | 92 | 57.7373 | 59.4927 | 4.5135 | 224.0619 | 0 | 0 | 0 | 13.4976 | 48.5831 | 55.2093 | 29.4946 | 0 | 7.5073 | 30.3885 | 30.3885 | 30.3885 | 44.1018 | 79.748 | 86.4801 | 60.3545 | 30.3885 | 59.4927 | 30.3885 | 30.3885 | 30.3885 | 57.5994 | 128.3311 | 141.6894 | 89.8491 | 30.3885 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 17 | 209 | 4.5 | 4.5 | 3.9 | 5.9014 | 15 | 95 | 95 | 98.2653 | 9.123 | -2.5433 | 236.0255 | 0 | 0 | 0 | 1.6039 | 70.3934 | 97.9474 | 68.1252 | 0 | 1.877 | 5.5241 | 5.5241 | 5.5241 | 6.1788 | 34.2595 | 45.5074 | 33.3336 | 5.5241 | 9.123 | 5.5241 | 5.5241 | 5.5241 | 7.7827 | 104.6529 | 143.4549 | 101.4588 | 5.5241 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 9 | 18 | 210 | 4.2 | 4.2 | 3.9 | 5.9014 | 15 | 95 | 95 | 0 | 0 | -10.646 | 247.3821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 19 | 211 | 4.3 | 4.3 | 3.9 | 5.9014 | 15 | 94 | 94 | 0 | 0 | -19.4414 | 258.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 20 | 212 | 4.2 | 4.2 | 3.9 | 5.9014 | 15 | 93 | 93 | 0 | 0 | -28.5931 | 269.9672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 21 | 213 | 4.2 | 4.2 | 3.9 | 5.9014 | 15 | 91 | 91 | 0 | 0 | -37.7372 | 282.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 22 | 214 | 4.2 | 4.2 | 3.9 | 5.9014 | 15 | 91 | 91 | 0 | 0 | -46.3947 | 297.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 23 | 215 | 4.2 | 4.2 | 3.9 | 5.9014 | 15 | 91 | 91 | 0 | 0 | -53.8188 | 315.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 9 | 24 | 216 | 2.7 | 2.7 | 4.125 | 5.3087 | 15 | 94 | 94 | 0 | 0 | -58.817 | 339.0938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 1 | 217 | 1.2 | 1.2 | 4.125 | 5.3087 | 15 | 97 | 97 | 0 | 0 | -59.9861 | 6.4665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 2 | 218 | 0.8 | 0.8 | 4.125 | 5.3087 | 15 | 98 | 98 | 0 | 0 | -56.7903 | 32.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 3 | 219 | 1.3 | 1.3 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -50.5147 | 53.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 4 | 220 | 1.1 | 1.1 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -42.4162 | 69.8047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 5 | 221 | 0.6 | 0.6 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -33.4678 | 83.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 6 | 222 | 1 | 1 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -24.2707 | 95.2597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 7 | 223 | 0.8 | 0.8 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -15.2373 | 106.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 10 | 8 | 224 | 1 | 1 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | -6.7119 | 117.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 9 | 225 | 1.1 | 1.1 | 4.125 | 5.3087 | 15 | 99 | 99 | 0 | 0 | 0.96399 | 129.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 10 | 226 | 1.4 | 1.4 | 4.125 | 5.3087 | 15 | 97 | 97 | 7.177 | 24.4525 | 7.422 | 141.6362 | 0 | 0.71362 | 5.5536 | 7.1404 | 4.5444 | 0 | 0 | 0 | 0.54745 | 9.5094 | 18.2057 | 77.1872 | 96.5239 | 64.8887 | 9.5094 | 9.5094 | 9.5094 | 24.4525 | 9.5094 | 18.9193 | 82.7408 | 103.6643 | 69.4331 | 9.5094 | 9.5094 | 9.5094 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 11 | 227 | 2.6 | 2.6 | 4.125 | 5.3087 | 15 | 92 | 92 | 64.55 | 80.7345 | 12.2703 | 154.8584 | 0 | 0 | 39.7274 | 63.5803 | 50.1887 | 7.3972 | 0 | 0 | 11.2655 | 36.9906 | 36.9906 | 112.7715 | 158.2713 | 132.7266 | 51.1009 | 36.9906 | 36.9906 | 80.7345 | 36.9906 | 36.9906 | 152.4989 | 221.8516 | 182.9153 | 58.4982 | 36.9906 | 36.9906 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 12 | 228 | 3.3 | 3.3 | 4.125 | 5.3087 | 15 | 89 | 89 | 13.1183 | 88.842 | 15.1404 | 168.8565 | 0 | 0 | 5.4461 | 12.0563 | 11.6042 | 4.3544 | 0 | 0 | 3.158 | 40.9071 | 40.9071 | 60.2542 | 83.7371 | 82.1308 | 56.3762 | 40.9071 | 40.9071 | 88.842 | 40.9071 | 40.9071 | 65.7002 | 95.7935 | 93.735 | 60.7306 | 40.9071 | 40.9071 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 13 | 229 | 3.7 | 3.7 | 4.125 | 5.3087 | 15 | 85 | 85 | 18.491 | 106.0001 | 15.7741 | 183.2613 | 0 | 0 | 3.4496 | 14.8225 | 17.5126 | 9.944 | 0 | 0 | 4.9999 | 49.2861 | 49.2861 | 57.1709 | 83.1659 | 89.3145 | 72.0151 | 49.2861 | 49.2861 | 106.0001 | 49.2861 | 49.2861 | 60.6206 | 97.9884 | 106.8271 | 81.9591 | 49.2861 | 49.2861 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 14 | 230 | 4 | 4 | 4.125 | 5.3087 | 15 | 86 | 86 | 15.1259 | 99.0448 | 14.1096 | 197.5427 | 0 | 0 | 0 | 9.6906 | 14.5327 | 10.8617 | 0.82811 | 0 | 3.9552 | 47.0326 | 47.0326 | 47.0326 | 64.0556 | 72.5615 | 66.1129 | 48.4873 | 47.0326 | 99.0448 | 47.0326 | 47.0326 | 47.0326 | 73.7462 | 87.0942 | 76.9746 | 49.3154 | 47.0326 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 15 | 231 | 3.8 | 3.8 | 4.125 | 5.3087 | 15 | 87 | 87 | 6.7882 | 67.5433 | 10.3053 | 211.2209 | 0 | 0 | 0 | 3.0355 | 6.2772 | 5.8418 | 1.9844 | 0 | 1.4567 | 33.424 | 33.424 | 33.424 | 34.1674 | 34.9613 | 34.8547 | 33.9099 | 33.424 | 67.5433 | 33.424 | 33.424 | 33.424 | 37.2029 | 41.2385 | 40.6965 | 35.8943 | 33.424 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 16 | 232 | 3.2 | 3.2 | 4.125 | 5.3087 | 15 | 89 | 89 | 9.3697 | 45.7543 | 4.6814 | 224.0429 | 0 | 0 | 0 | 2.1957 | 7.8835 | 8.9533 | 4.7783 | 0 | 1.2457 | 22.6102 | 22.6102 | 22.6102 | 22.6102 | 22.6102 | 22.6102 | 22.6102 | 22.6102 | 45.7543 | 22.6102 | 22.6102 | 22.6102 | 24.8059 | 30.4937 | 31.5635 | 27.3885 | 22.6102 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 17 | 233 | 2.8 | 2.8 | 4.125 | 5.3087 | 15 | 90 | 90 | 48.6316 | 9.925 | -2.3742 | 236.0239 | 0 | 0 | 0 | 0.80963 | 34.8407 | 48.4626 | 33.6957 | 0 | 1.075 | 5.7351 | 5.7351 | 5.7351 | 6.373 | 33.1875 | 43.9207 | 32.2853 | 5.7351 | 9.925 | 5.7351 | 5.7351 | 5.7351 | 7.1827 | 68.0282 | 92.3833 | 65.981 | 5.7351 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 10 | 18 | 234 | 3 | 3 | 4.125 | 5.3087 | 15 | 89 | 89 | 0 | 0 | -10.4774 | 247.3937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 19 | 235 | 3.1 | 3.1 | 4.125 | 5.3087 | 15 | 89 | 89 | 0 | 0 | -19.2735 | 258.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 20 | 236 | 3.2 | 3.2 | 4.125 | 5.3087 | 15 | 89 | 89 | 0 | 0 | -28.4256 | 269.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 21 | 237 | 3.1 | 3.1 | 4.125 | 5.3087 | 15 | 89 | 89 | 0 | 0 | -37.5692 | 282.5062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 22 | 238 | 3 | 3 | 4.125 | 5.3087 | 15 | 89 | 89 | 0 | 0 | -46.2258 | 297.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 23 | 239 | 3.1 | 3.1 | 4.125 | 5.3087 | 15 | 87 | 87 | 0 | 0 | -53.6507 | 315.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 10 | 24 | 240 | 2.9 | 2.9 | 2.2958 | 4.4271 | 15 | 87 | 87 | 0 | 0 | -58.6583 | 338.9815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 1 | 241 | 2.7 | 2.7 | 2.2958 | 4.4271 | 15 | 89 | 89 | 0 | 0 | -59.8531 | 6.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 2 | 242 | 2.9 | 2.9 | 2.2958 | 4.4271 | 15 | 87 | 87 | 0 | 0 | -56.685 | 32.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 3 | 243 | 3.2 | 3.2 | 2.2958 | 4.4271 | 15 | 85 | 85 | 0 | 0 | -50.4388 | 53.0757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 4 | 244 | 3.1 | 3.1 | 2.2958 | 4.4271 | 15 | 84 | 84 | 0 | 0 | -42.3581 | 69.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 5 | 245 | 2.5 | 2.5 | 2.2958 | 4.4271 | 15 | 87 | 87 | 0 | 0 | -33.4176 | 83.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 6 | 246 | 1.8 | 1.8 | 2.2958 | 4.4271 | 15 | 90 | 90 | 0 | 0 | -24.2209 | 95.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 7 | 247 | 1.4 | 1.4 | 2.2958 | 4.4271 | 15 | 90 | 90 | 0 | 0 | -15.1822 | 106.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 11 | 8 | 248 | 0.6 | 0.6 | 2.2958 | 4.4271 | 15 | 92 | 92 | 0 | 0 | -6.6469 | 117.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 9 | 249 | 0.7 | 0.7 | 2.2958 | 4.4271 | 15 | 91 | 91 | 0 | 0 | 1.043 | 129.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 10 | 250 | 0.3 | 0.3 | 2.2958 | 4.4271 | 15 | 90 | 90 | 16.0726 | 29.7509 | 7.5183 | 141.49 | 0 | 1.6414 | 12.4643 | 15.9859 | 10.1431 | 0 | 0 | 0 | 1.2491 | 12.509 | 21.2434 | 78.8373 | 97.5769 | 66.485 | 12.509 | 12.509 | 12.509 | 29.7509 | 12.509 | 22.8847 | 91.3016 | 113.5628 | 76.6281 | 12.509 | 12.509 | 12.509 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 11 | 251 | 1.7 | 1.7 | 2.2958 | 4.4271 | 15 | 80 | 80 | 338.7082 | 76.2935 | 12.3856 | 154.725 | 0 | 0 | 209.0841 | 333.6445 | 262.7605 | 37.955 | 0 | 0 | 59.7065 | 42.6704 | 42.6704 | 89.7155 | 117.7423 | 101.793 | 51.2105 | 42.6704 | 42.6704 | 76.2935 | 42.6704 | 42.6704 | 298.7996 | 451.3868 | 364.5536 | 89.1655 | 42.6704 | 42.6704 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 12 | 252 | 2.7 | 2.7 | 2.2958 | 4.4271 | 15 | 74 | 74 | 626.9245 | 72.7745 | 15.2747 | 168.7418 | 0 | 0 | 261.4438 | 576.4037 | 553.7142 | 206.6664 | 0 | 0 | 152.2255 | 51.3031 | 51.3031 | 89.6172 | 135.7739 | 132.4488 | 81.5896 | 51.3031 | 51.3031 | 72.7745 | 51.3031 | 51.3031 | 351.061 | 712.1777 | 686.163 | 288.256 | 51.3031 | 51.3031 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 13 | 253 | 3.6 | 3.6 | 2.2958 | 4.4271 | 15 | 67 | 67 | 781.1145 | 61.9238 | 15.9249 | 183.171 | 0 | 0 | 147.1104 | 626.5895 | 739.021 | 418.544 | 0 | 0 | 213.0762 | 54.7963 | 54.7963 | 67.6311 | 109.4638 | 119.273 | 91.3126 | 54.7963 | 54.7963 | 61.9238 | 54.7963 | 54.7963 | 214.7415 | 736.0533 | 858.294 | 509.8566 | 54.7963 | 54.7963 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 14 | 254 | 4 | 4 | 2.2958 | 4.4271 | 15 | 56 | 56 | 723.6677 | 66.847 | 14.2725 | 197.4795 | 0 | 0 | 0 | 464.0994 | 694.8296 | 518.538 | 38.4938 | 0 | 191.153 | 53.4861 | 53.4861 | 53.4861 | 109.2899 | 137.0332 | 115.8357 | 58.1146 | 53.4861 | 66.847 | 53.4861 | 53.4861 | 53.4861 | 573.3894 | 831.8628 | 634.3737 | 96.6085 | 53.4861 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 15 | 255 | 3.7 | 3.7 | 2.2958 | 4.4271 | 15 | 55 | 55 | 640.1783 | 63.7721 | 10.4755 | 211.184 | 0 | 0 | 0 | 286.6739 | 591.7705 | 550.2159 | 186.3523 | 0 | 139.2279 | 46.7171 | 46.7171 | 46.7171 | 85.7601 | 127.3121 | 121.6527 | 72.097 | 46.7171 | 63.7721 | 46.7171 | 46.7171 | 46.7171 | 372.434 | 719.0826 | 671.8686 | 258.4493 | 46.7171 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 16 | 256 | 2.9 | 2.9 | 2.2958 | 4.4271 | 15 | 53 | 53 | 281.7055 | 61.6918 | 4.8549 | 224.0286 | 0 | 0 | 0 | 66.1512 | 236.9847 | 268.9957 | 143.4328 | 0 | 38.3082 | 35.4802 | 35.4802 | 35.4802 | 56.8012 | 111.8621 | 122.1795 | 81.7096 | 35.4802 | 61.6918 | 35.4802 | 35.4802 | 35.4802 | 122.9524 | 348.8468 | 391.1752 | 225.1424 | 35.4802 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 17 | 257 | 1.4 | 1.4 | 2.2958 | 4.4271 | 15 | 59 | 59 | 82.8624 | 11.9107 | -2.2002 | 236.0276 | 0 | 0 | 0 | 1.3997 | 59.3637 | 82.5532 | 57.3842 | 0 | 2.0893 | 6.9192 | 6.9192 | 6.9192 | 7.6778 | 39.093 | 51.6612 | 38.0201 | 6.9192 | 11.9107 | 6.9192 | 6.9192 | 6.9192 | 9.0775 | 98.4566 | 134.2144 | 95.4043 | 6.9192 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 11 | 18 | 258 | 0.3 | 0.3 | 2.2958 | 4.4271 | 15 | 64 | 64 | 0 | 0 | -10.3042 | 247.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 19 | 259 | -0.7 | -0.7 | 2.2958 | 4.4271 | 15 | 71 | 71 | 0 | 0 | -19.1014 | 258.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 20 | 260 | -0.6 | -0.6 | 2.2958 | 4.4271 | 15 | 70 | 70 | 0 | 0 | -28.2539 | 270.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 21 | 261 | -1 | -1 | 2.2958 | 4.4271 | 15 | 71 | 71 | 0 | 0 | -37.3969 | 282.5374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 22 | 262 | -1 | -1 | 2.2958 | 4.4271 | 15 | 71 | 71 | 0 | 0 | -46.0522 | 297.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 23 | 263 | -1.2 | -1.2 | 2.2958 | 4.4271 | 15 | 75 | 75 | 0 | 0 | -53.4772 | 315.5155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 11 | 24 | 264 | -1.5 | -1.5 | 1.3958 | 3.4476 | 15 | 77 | 77 | 0 | 0 | -58.4931 | 338.8766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 1 | 265 | -1.5 | -1.5 | 1.3958 | 3.4476 | 15 | 75 | 75 | 0 | 0 | -59.7126 | 6.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 2 | 266 | -1.6 | -1.6 | 1.3958 | 3.4476 | 15 | 77 | 77 | 0 | 0 | -56.5719 | 31.7524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 3 | 267 | -2.7 | -2.7 | 1.3958 | 3.4476 | 15 | 86 | 86 | 0 | 0 | -50.3555 | 52.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 4 | 268 | -3.6 | -3.6 | 1.3958 | 3.4476 | 15 | 87 | 87 | 0 | 0 | -42.293 | 69.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 5 | 269 | -2.1 | -2.1 | 1.3958 | 3.4476 | 15 | 88 | 88 | 0 | 0 | -33.3607 | 82.9325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 6 | 270 | -1.1 | -1.1 | 1.3958 | 3.4476 | 15 | 81 | 81 | 0 | 0 | -24.1645 | 94.8904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 7 | 271 | -1.3 | -1.3 | 1.3958 | 3.4476 | 15 | 81 | 81 | 0 | 0 | -15.1205 | 106.1515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 12 | 8 | 272 | -1.1 | -1.1 | 1.3958 | 3.4476 | 15 | 81 | 81 | 0 | 0 | -6.5751 | 117.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 9 | 273 | 0 | 0 | 1.3958 | 3.4476 | 15 | 80 | 80 | 0 | 0 | 1.129 | 128.9805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 10 | 274 | 0.4 | 0.4 | 1.3958 | 3.4476 | 15 | 85 | 85 | 1.9854 | 13.8426 | 7.6216 | 141.3424 | 0 | 0.20816 | 1.5431 | 1.9741 | 1.2487 | 0 | 0 | 0 | 0.15737 | 6.4719 | 7.6821 | 15.4429 | 17.9486 | 13.7314 | 6.4719 | 6.4719 | 6.4719 | 13.8426 | 6.4719 | 7.8902 | 16.986 | 19.9227 | 14.9801 | 6.4719 | 6.4719 | 6.4719 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 11 | 275 | 1.7 | 1.7 | 1.3958 | 3.4476 | 15 | 87 | 87 | 13.9768 | 66.5102 | 12.5081 | 154.5912 | 0 | 0 | 8.6537 | 13.7686 | 10.818 | 1.5304 | 0 | 0 | 2.4898 | 29.3381 | 29.3381 | 80.7502 | 111.1378 | 93.6083 | 38.4301 | 29.3381 | 29.3381 | 66.5102 | 29.3381 | 29.3381 | 89.4039 | 124.9064 | 104.4263 | 39.9605 | 29.3381 | 29.3381 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 12 | 276 | 2.7 | 2.7 | 1.3958 | 3.4476 | 15 | 87 | 87 | 7.3764 | 79.1928 | 15.4161 | 168.6278 | 0 | 0 | 3.0899 | 6.7845 | 6.5048 | 2.4147 | 0 | 0 | 1.8072 | 37.4089 | 37.4089 | 48.4631 | 61.6804 | 60.6797 | 46.0474 | 37.4089 | 37.4089 | 79.1928 | 37.4089 | 37.4089 | 51.553 | 68.4648 | 67.1845 | 48.462 | 37.4089 | 37.4089 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 13 | 277 | 3.3 | 3.3 | 1.3958 | 3.4476 | 15 | 89 | 89 | 5.109 | 76.5936 | 16.0825 | 183.0825 | 0 | 0 | 0.97116 | 4.101 | 4.8285 | 2.7276 | 0 | 0 | 1.4064 | 37.6801 | 37.6801 | 38.4998 | 41.1413 | 41.7554 | 39.9822 | 37.6801 | 37.6801 | 76.5936 | 37.6801 | 37.6801 | 39.4709 | 45.2423 | 46.5839 | 42.7097 | 37.6801 | 37.6801 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 14 | 278 | 3.5 | 3.5 | 1.3958 | 3.4476 | 15 | 90 | 90 | 5.0243 | 73.6589 | 14.4419 | 197.4195 | 0 | 0 | 0 | 3.2252 | 4.8207 | 3.5923 | 0.2596 | 0 | 1.3411 | 36.5981 | 36.5981 | 36.5981 | 36.5981 | 36.5981 | 36.5981 | 36.5981 | 36.5981 | 73.6589 | 36.5981 | 36.5981 | 36.5981 | 39.8232 | 41.4188 | 40.1904 | 36.8577 | 36.5981 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 15 | 279 | 4.1 | 4.1 | 1.3958 | 3.4476 | 15 | 84 | 84 | 66.7162 | 102.2904 | 10.6517 | 211.1512 | 0 | 0 | 0 | 29.9132 | 61.6451 | 57.2661 | 19.3414 | 0 | 14.7096 | 49.6353 | 49.6353 | 49.6353 | 76.7664 | 105.547 | 101.5753 | 67.1779 | 49.6353 | 102.2904 | 49.6353 | 49.6353 | 49.6353 | 106.6796 | 167.192 | 158.8414 | 86.5193 | 49.6353 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 16 | 280 | 4.9 | 4.9 | 1.3958 | 3.4476 | 15 | 79 | 79 | 289.2643 | 62.7538 | 5.0337 | 224.0192 | 0 | 0 | 0 | 68.0452 | 243.2882 | 276.0163 | 147.0577 | 0 | 40.2462 | 36.1847 | 36.1847 | 36.1847 | 57.6421 | 112.9034 | 123.2239 | 82.558 | 36.1847 | 62.7538 | 36.1847 | 36.1847 | 36.1847 | 125.6873 | 356.1916 | 399.2401 | 229.6157 | 36.1847 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 17 | 281 | 3.9 | 3.9 | 1.3958 | 3.4476 | 15 | 85 | 85 | 190.7393 | 13.5773 | -2.0214 | 236.0367 | 0 | 0 | 0 | 3.2524 | 136.633 | 189.9758 | 132.0334 | 0 | 5.4227 | 8.3131 | 8.3131 | 8.3131 | 9.2615 | 48.1581 | 63.714 | 46.8168 | 8.3131 | 13.5773 | 8.3131 | 8.3131 | 8.3131 | 12.514 | 184.7911 | 253.6898 | 178.8501 | 8.3131 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 12 | 18 | 282 | 2.6 | 2.6 | 1.3958 | 3.4476 | 15 | 89 | 89 | 0 | 0 | -10.1265 | 247.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 19 | 283 | 1.9 | 1.9 | 1.3958 | 3.4476 | 15 | 87 | 87 | 0 | 0 | -18.925 | 258.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 20 | 284 | 1.3 | 1.3 | 1.3958 | 3.4476 | 15 | 89 | 89 | 0 | 0 | -28.0781 | 270.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 21 | 285 | 0.4 | 0.4 | 1.3958 | 3.4476 | 15 | 90 | 90 | 0 | 0 | -37.2205 | 282.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 22 | 286 | 0.2 | 0.2 | 1.3958 | 3.4476 | 15 | 93 | 93 | 0 | 0 | -45.874 | 297.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 23 | 287 | 0 | 0 | 1.3958 | 3.4476 | 15 | 92 | 92 | 0 | 0 | -53.2983 | 315.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 12 | 24 | 288 | 0.2 | 0.2 | 0.67083 | 2.5202 | 15 | 90 | 90 | 0 | 0 | -58.3214 | 338.7791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 1 | 289 | 0 | 0 | 0.67083 | 2.5202 | 15 | 91 | 91 | 0 | 0 | -59.5647 | 5.8544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 2 | 290 | -1.2 | -1.2 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -56.4512 | 31.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 3 | 291 | -1.8 | -1.8 | 0.67083 | 2.5202 | 15 | 94 | 94 | 0 | 0 | -50.2648 | 52.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 4 | 292 | -2.2 | -2.2 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -42.2209 | 69.1278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 5 | 293 | -2.4 | -2.4 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -33.297 | 82.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 6 | 294 | -2.5 | -2.5 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -24.1014 | 94.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 7 | 295 | -3 | -3 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -15.0521 | 105.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 13 | 8 | 296 | -3.2 | -3.2 | 0.67083 | 2.5202 | 15 | 93 | 93 | 0 | 0 | -6.4965 | 117.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 9 | 297 | -2.8 | -2.8 | 0.67083 | 2.5202 | 15 | 92 | 92 | 0 | 0 | 1.2218 | 128.8213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 10 | 298 | -1.8 | -1.8 | 0.67083 | 2.5202 | 15 | 87 | 87 | 484.608 | 21.377 | 7.7319 | 141.1935 | 0 | 52.146 | 377.4744 | 481.6834 | 303.7289 | 0 | 0 | 0 | 56.623 | 15.4125 | 16.2326 | 21.3491 | 22.9879 | 20.1893 | 15.4125 | 15.4125 | 15.4125 | 21.377 | 15.4125 | 68.3786 | 398.8235 | 504.6714 | 323.9181 | 15.4125 | 15.4125 | 15.4125 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 11 | 299 | -0.3 | -0.3 | 0.67083 | 2.5202 | 15 | 78 | 78 | 822.4993 | 33.8493 | 12.6377 | 154.457 | 0 | 0 | 510.7674 | 810.2643 | 635.1194 | 87.9302 | 0 | 0 | 160.1507 | 34.3466 | 34.3466 | 86.8487 | 117.6341 | 99.6309 | 43.385 | 34.3466 | 34.3466 | 33.8493 | 34.3466 | 34.3466 | 597.6161 | 927.8985 | 734.7503 | 131.3152 | 34.3466 | 34.3466 | 194 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 12 | 300 | 0.2 | 0.2 | 0.67083 | 2.5202 | 15 | 77 | 77 | 764.6233 | 57.9062 | 15.5646 | 168.5146 | 0 | 0 | 321.7088 | 703.4902 | 673.1766 | 248.5252 | 0 | 0 | 189.0938 | 50.0326 | 50.0326 | 79.0795 | 113.5503 | 110.8133 | 72.4718 | 50.0326 | 50.0326 | 57.9062 | 50.0326 | 50.0326 | 400.7883 | 817.0405 | 783.9899 | 320.997 | 50.0326 | 50.0326 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 13 | 301 | 1.6 | 1.6 | 0.67083 | 2.5202 | 15 | 68 | 68 | 707.3268 | 72.4339 | 16.247 | 182.9961 | 0 | 0 | 135.6766 | 568.1039 | 667.7437 | 376.2282 | 0 | 0 | 196.5661 | 56.4061 | 56.4061 | 73.8461 | 129.4306 | 142.2384 | 104.7668 | 56.4061 | 56.4061 | 72.4339 | 56.4061 | 56.4061 | 209.5227 | 697.5346 | 809.982 | 480.995 | 56.4061 | 56.4061 | 269 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 14 | 302 | 2.2 | 2.2 | 0.67083 | 2.5202 | 15 | 61 | 61 | 568.9343 | 88.4956 | 14.6177 | 197.3626 | 0 | 0 | 0 | 365.5155 | 545.467 | 405.8913 | 28.55 | 0 | 153.5044 | 58.8704 | 58.8704 | 58.8704 | 121.6187 | 152.511 | 128.55 | 63.7716 | 58.8704 | 88.4956 | 58.8704 | 58.8704 | 58.8704 | 487.1342 | 697.978 | 534.4413 | 92.3216 | 58.8704 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 15 | 303 | 2.8 | 2.8 | 0.67083 | 2.5202 | 15 | 57 | 57 | 729.074 | 55.9882 | 10.8338 | 211.1226 | 0 | 0 | 0 | 327.2513 | 673.33 | 624.9811 | 210.5268 | 0 | 163.0118 | 47.0053 | 47.0053 | 47.0053 | 76.4569 | 107.603 | 103.2518 | 65.9521 | 47.0053 | 55.9882 | 47.0053 | 47.0053 | 47.0053 | 403.7082 | 780.933 | 728.2329 | 276.4789 | 47.0053 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 16 | 304 | 1.7 | 1.7 | 0.67083 | 2.5202 | 15 | 71 | 71 | 264.1555 | 65.3874 | 5.2179 | 224.0146 | 0 | 0 | 0 | 62.2273 | 222.1034 | 251.8744 | 134.1008 | 0 | 37.6126 | 37.1428 | 37.1428 | 37.1428 | 58.9228 | 114.8804 | 125.3004 | 84.0789 | 37.1428 | 65.3874 | 37.1428 | 37.1428 | 37.1428 | 121.15 | 336.9838 | 377.1748 | 218.1797 | 37.1428 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 17 | 305 | 1 | 1 | 0.67083 | 2.5202 | 15 | 76 | 76 | 190.4098 | 5.94 | -1.8377 | 236.051 | 0 | 0 | 0 | 3.2612 | 136.3683 | 189.5927 | 131.7563 | 0 | 30.06 | 7.2799 | 7.2799 | 7.2799 | 7.7699 | 27.7683 | 35.7649 | 27.0754 | 7.2799 | 5.94 | 7.2799 | 7.2799 | 7.2799 | 11.0311 | 164.1366 | 225.3577 | 158.8317 | 7.2799 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 18 | 306 | -0.1 | -0.1 | 0.67083 | 2.5202 | 15 | 83 | 83 | 0 | 0 | -9.9445 | 247.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 19 | 307 | -0.7 | -0.7 | 0.67083 | 2.5202 | 15 | 86 | 86 | 0 | 0 | -18.7445 | 258.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 20 | 308 | -1.3 | -1.3 | 0.67083 | 2.5202 | 15 | 88 | 88 | 0 | 0 | -27.8983 | 270.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 21 | 309 | -1.7 | -1.7 | 0.67083 | 2.5202 | 15 | 88 | 88 | 0 | 0 | -37.0399 | 282.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 22 | 310 | -2.2 | -2.2 | 0.67083 | 2.5202 | 15 | 89 | 89 | 0 | 0 | -45.6912 | 297.2512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 23 | 311 | -2.6 | -2.6 | 0.67083 | 2.5202 | 15 | 90 | 90 | 0 | 0 | -53.1141 | 315.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 13 | 24 | 312 | -2.6 | -2.6 | -0.95417 | 1.435 | 15 | 89 | 89 | 0 | 0 | -58.1434 | 338.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 1 | 313 | -3.2 | -3.2 | -0.95417 | 1.435 | 15 | 90 | 90 | 0 | 0 | -59.4094 | 5.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 2 | 314 | -3.5 | -3.5 | -0.95417 | 1.435 | 15 | 92 | 92 | 0 | 0 | -56.3228 | 31.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 3 | 315 | -3.6 | -3.6 | -0.95417 | 1.435 | 15 | 91 | 91 | 0 | 0 | -50.1667 | 52.3227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 4 | 316 | -3.8 | -3.8 | -0.95417 | 1.435 | 15 | 90 | 90 | 0 | 0 | -42.1418 | 68.8956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 5 | 317 | -4.7 | -4.7 | -0.95417 | 1.435 | 15 | 93 | 93 | 0 | 0 | -33.2265 | 82.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 6 | 318 | -4.7 | -4.7 | -0.95417 | 1.435 | 15 | 94 | 94 | 0 | 0 | -24.0317 | 94.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 7 | 319 | -4.7 | -4.7 | -0.95417 | 1.435 | 15 | 94 | 94 | 0 | 0 | -14.9771 | 105.7943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 14 | 8 | 320 | -5 | -5 | -0.95417 | 1.435 | 15 | 94 | 94 | 0 | 0 | -6.4112 | 117.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 9 | 321 | -4.2 | -4.2 | -0.95417 | 1.435 | 15 | 93 | 93 | 0 | 0 | 1.3215 | 128.6603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 10 | 322 | -2.7 | -2.7 | -0.95417 | 1.435 | 15 | 97 | 97 | 3.3633 | 18.722 | 7.8492 | 141.0435 | 0 | 0.37129 | 2.6256 | 3.3418 | 2.1005 | 0 | 0 | 0 | 0.278 | 8.2815 | 11.8259 | 33.3453 | 40.1827 | 28.3329 | 8.2815 | 8.2815 | 8.2815 | 18.722 | 8.2815 | 12.1971 | 35.9709 | 43.5246 | 30.4334 | 8.2815 | 8.2815 | 8.2815 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 11 | 323 | -1.1 | -1.1 | -0.95417 | 1.435 | 15 | 95 | 95 | 2.9168 | 38.4686 | 12.7744 | 154.3226 | 0 | 0 | 1.8167 | 2.8735 | 2.247 | 0.30422 | 0 | 0 | 0.53141 | 18.9587 | 18.9587 | 19.6302 | 20.0208 | 19.7892 | 19.0711 | 18.9587 | 18.9587 | 38.4686 | 18.9587 | 18.9587 | 21.4469 | 22.8943 | 22.0362 | 19.3754 | 18.9587 | 18.9587 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 12 | 324 | -0.2 | -0.2 | -0.95417 | 1.435 | 15 | 94 | 94 | 2.2549 | 46.4369 | 15.7201 | 168.4023 | 0 | 0 | 0.95289 | 2.0753 | 1.982 | 0.72766 | 0 | 0 | 0.56309 | 22.6601 | 22.6601 | 22.6601 | 22.6601 | 22.6601 | 22.6601 | 22.6601 | 22.6601 | 46.4369 | 22.6601 | 22.6601 | 23.613 | 24.7353 | 24.642 | 23.3877 | 22.6601 | 22.6601 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 13 | 325 | 0.5 | 0.5 | -0.95417 | 1.435 | 15 | 93 | 93 | 1.4258 | 41.5999 | 16.4183 | 182.9119 | 0 | 0 | 0.27593 | 1.1458 | 1.3445 | 0.75558 | 0 | 0 | 0.40012 | 20.0387 | 20.0387 | 20.0387 | 20.0387 | 20.0387 | 20.0387 | 20.0387 | 20.0387 | 41.5999 | 20.0387 | 20.0387 | 20.3146 | 21.1845 | 21.3831 | 20.7942 | 20.0387 | 20.0387 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 14 | 326 | 0.6 | 0.6 | -0.95417 | 1.435 | 15 | 90 | 90 | 2.1382 | 49.4167 | 14.7998 | 197.309 | 0 | 0 | 0 | 1.3747 | 2.0483 | 1.5221 | 0.10419 | 0 | 0.58331 | 23.9598 | 23.9598 | 23.9598 | 23.9598 | 23.9598 | 23.9598 | 23.9598 | 23.9598 | 49.4167 | 23.9598 | 23.9598 | 23.9598 | 25.3346 | 26.0082 | 25.4819 | 24.064 | 23.9598 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 15 | 327 | 0.3 | 0.3 | -0.95417 | 1.435 | 15 | 86 | 86 | 0.77338 | 24.8246 | 11.0216 | 211.0981 | 0 | 0 | 0 | 0.34747 | 0.71386 | 0.66209 | 0.22247 | 0 | 0.17541 | 11.7672 | 11.7672 | 11.7672 | 11.7672 | 11.7672 | 11.7672 | 11.7672 | 11.7672 | 24.8246 | 11.7672 | 11.7672 | 11.7672 | 12.1147 | 12.4811 | 12.4293 | 11.9897 | 11.7672 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 16 | 328 | 0.3 | 0.3 | -0.95417 | 1.435 | 15 | 86 | 86 | 1.0817 | 18.8423 | 5.4073 | 224.0148 | 0 | 0 | 0 | 0.25509 | 0.90915 | 1.0306 | 0.54839 | 0 | 0.15766 | 8.9118 | 8.9118 | 8.9118 | 8.9118 | 8.9118 | 8.9118 | 8.9118 | 8.9118 | 18.8423 | 8.9118 | 8.9118 | 8.9118 | 9.1669 | 9.8209 | 9.9424 | 9.4602 | 8.9118 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 17 | 329 | 0.2 | 0.2 | -0.95417 | 1.435 | 15 | 86 | 86 | 1.8519 | 5.9349 | -1.6493 | 236.0708 | 0 | 0 | 0 | 0.0317 | 1.3259 | 1.8434 | 1.281 | 0 | 0.065143 | 3.1741 | 3.1741 | 3.1741 | 3.1741 | 3.1741 | 3.1741 | 3.1741 | 3.1741 | 5.9349 | 3.1741 | 3.1741 | 3.1741 | 3.2058 | 4.5 | 5.0175 | 4.4551 | 3.1741 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 18 | 330 | 0.1 | 0.1 | -0.95417 | 1.435 | 15 | 86 | 86 | 0 | 0 | -9.7582 | 247.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 19 | 331 | -0.1 | -0.1 | -0.95417 | 1.435 | 15 | 85 | 85 | 0 | 0 | -18.5601 | 258.6827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 20 | 332 | -0.4 | -0.4 | -0.95417 | 1.435 | 15 | 85 | 85 | 0 | 0 | -27.7146 | 270.1616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 21 | 333 | -0.9 | -0.9 | -0.95417 | 1.435 | 15 | 87 | 87 | 0 | 0 | -36.8552 | 282.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 22 | 334 | -1.5 | -1.5 | -0.95417 | 1.435 | 15 | 88 | 88 | 0 | 0 | -45.504 | 297.2922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 23 | 335 | -1.8 | -1.8 | -0.95417 | 1.435 | 15 | 87 | 87 | 0 | 0 | -52.9247 | 315.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 14 | 24 | 336 | -2.4 | -2.4 | -1.9375 | 0.35143 | 15 | 90 | 90 | 0 | 0 | -57.9591 | 338.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 1 | 337 | -2.7 | -2.7 | -1.9375 | 0.35143 | 15 | 90 | 90 | 0 | 0 | -59.2469 | 5.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 2 | 338 | -2.7 | -2.7 | -1.9375 | 0.35143 | 15 | 89 | 89 | 0 | 0 | -56.1869 | 30.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 3 | 339 | -2.8 | -2.8 | -1.9375 | 0.35143 | 15 | 89 | 89 | 0 | 0 | -50.0612 | 52.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 4 | 340 | -2.8 | -2.8 | -1.9375 | 0.35143 | 15 | 88 | 88 | 0 | 0 | -42.0556 | 68.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 5 | 341 | -3.4 | -3.4 | -1.9375 | 0.35143 | 15 | 89 | 89 | 0 | 0 | -33.1492 | 82.3021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 6 | 342 | -3.5 | -3.5 | -1.9375 | 0.35143 | 15 | 89 | 89 | 0 | 0 | -23.9553 | 94.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 7 | 343 | -3.9 | -3.9 | -1.9375 | 0.35143 | 15 | 89 | 89 | 0 | 0 | -14.8954 | 105.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 15 | 8 | 344 | -4 | -4 | -1.9375 | 0.35143 | 15 | 88 | 88 | 0 | 0 | -6.3192 | 116.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 9 | 345 | -4 | -4 | -1.9375 | 0.35143 | 15 | 86 | 86 | 0 | 0 | 1.4281 | 128.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 10 | 346 | -3.3 | -3.3 | -1.9375 | 0.35143 | 15 | 84 | 84 | 83.6608 | 39.93 | 7.9735 | 140.8923 | 0 | 9.4715 | 65.4556 | 83.0967 | 52.0609 | 0 | 0 | 0 | 7.07 | 16.5325 | 30.9095 | 115.8896 | 142.6676 | 95.5573 | 16.5325 | 16.5325 | 16.5325 | 39.93 | 16.5325 | 40.381 | 181.3452 | 225.7643 | 147.6183 | 16.5325 | 16.5325 | 16.5325 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 11 | 347 | -2.2 | -2.2 | -1.9375 | 0.35143 | 15 | 78 | 78 | 355.0481 | 78.54 | 12.918 | 154.188 | 0 | 0 | 221.7921 | 349.7579 | 272.8402 | 36.0964 | 0 | 0 | 65.46 | 44.42 | 44.42 | 94.2923 | 123.0668 | 105.771 | 52.5367 | 44.42 | 44.42 | 78.54 | 44.42 | 44.42 | 316.0844 | 472.8246 | 378.6112 | 88.6331 | 44.42 | 44.42 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 12 | 348 | -1 | -1 | -1.9375 | 0.35143 | 15 | 73 | 73 | 621.8596 | 76.1482 | 15.8825 | 168.2909 | 0 | 0 | 263.917 | 572.448 | 545.6467 | 199.213 | 0 | 0 | 156.8518 | 53.289 | 53.289 | 92.7152 | 138.8061 | 134.8023 | 83.0491 | 53.289 | 53.289 | 76.1482 | 53.289 | 53.289 | 356.6322 | 711.2541 | 680.4491 | 282.2621 | 53.289 | 53.289 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 13 | 349 | 0.2 | 0.2 | -1.9375 | 0.35143 | 15 | 71 | 71 | 751.3308 | 68.0285 | 16.5962 | 182.8297 | 0 | 0 | 146.6562 | 604.0581 | 707.611 | 396.6549 | 0 | 0 | 212.9715 | 56.1812 | 56.1812 | 73.3289 | 126.8104 | 138.9183 | 102.5599 | 56.1812 | 56.1812 | 68.0285 | 56.1812 | 56.1812 | 219.9851 | 730.8685 | 846.5293 | 499.2148 | 56.1812 | 56.1812 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 14 | 350 | 0.8 | 0.8 | -1.9375 | 0.35143 | 15 | 69 | 69 | 780.5642 | 62.6255 | 14.9883 | 197.2588 | 0 | 0 | 0 | 502.191 | 747.1349 | 554.4173 | 36.9296 | 0 | 215.3745 | 55.5377 | 55.5377 | 55.5377 | 98.59 | 119.5887 | 103.0673 | 58.7037 | 55.5377 | 62.6255 | 55.5377 | 55.5377 | 55.5377 | 600.781 | 866.7236 | 657.4846 | 95.6333 | 55.5377 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 15 | 351 | 1.3 | 1.3 | -1.9375 | 0.35143 | 15 | 64 | 64 | 789.2241 | 51.3733 | 11.2152 | 211.0779 | 0 | 0 | 0 | 354.8692 | 728.0476 | 674.7456 | 226.1868 | 0 | 181.6267 | 46.7629 | 46.7629 | 46.7629 | 74.6316 | 103.9382 | 99.7522 | 64.5259 | 46.7629 | 51.3733 | 46.7629 | 46.7629 | 46.7629 | 429.5008 | 831.9858 | 774.4979 | 290.7127 | 46.7629 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 16 | 352 | 0.8 | 0.8 | -1.9375 | 0.35143 | 15 | 68 | 68 | 701.9696 | 39.2511 | 5.6018 | 224.02 | 0 | 0 | 0 | 165.6703 | 589.7323 | 668.3371 | 355.4391 | 0 | 104.7489 | 32.7736 | 32.7736 | 32.7736 | 46.8454 | 82.8648 | 89.5414 | 62.9642 | 32.7736 | 39.2511 | 32.7736 | 32.7736 | 32.7736 | 212.5157 | 672.597 | 757.8785 | 418.4033 | 32.7736 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 17 | 353 | -0.1 | -0.1 | -1.9375 | 0.35143 | 15 | 71 | 71 | 266.1779 | 7.755 | -1.4564 | 236.0959 | 0 | 0 | 0 | 4.5309 | 190.4938 | 264.868 | 184.0861 | 0 | 39.245 | 9.3949 | 9.3949 | 9.3949 | 9.9763 | 33.8386 | 43.382 | 33.0163 | 9.3949 | 7.755 | 9.3949 | 9.3949 | 9.3949 | 14.5072 | 224.3323 | 308.25 | 217.1024 | 9.3949 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 15 | 18 | 354 | -0.8 | -0.8 | -1.9375 | 0.35143 | 15 | 75 | 75 | 0 | 0 | -9.5677 | 247.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 19 | 355 | -1.4 | -1.4 | -1.9375 | 0.35143 | 15 | 77 | 77 | 0 | 0 | -18.3717 | 258.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 20 | 356 | -1.9 | -1.9 | -1.9375 | 0.35143 | 15 | 80 | 80 | 0 | 0 | -27.5271 | 270.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 21 | 357 | -2.1 | -2.1 | -1.9375 | 0.35143 | 15 | 82 | 82 | 0 | 0 | -36.6667 | 282.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 22 | 358 | -2.6 | -2.6 | -1.9375 | 0.35143 | 15 | 83 | 83 | 0 | 0 | -45.3124 | 297.3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 23 | 359 | -3 | -3 | -1.9375 | 0.35143 | 15 | 84 | 84 | 0 | 0 | -52.7303 | 315.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 15 | 24 | 360 | -4.2 | -4.2 | -2.0542 | -0.46557 | 15 | 89 | 89 | 0 | 0 | -57.7686 | 338.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 1 | 361 | -4.1 | -4.1 | -2.0542 | -0.46557 | 15 | 89 | 89 | 0 | 0 | -59.0773 | 5.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 2 | 362 | -4.3 | -4.3 | -2.0542 | -0.46557 | 15 | 88 | 88 | 0 | 0 | -56.0435 | 30.7485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 3 | 363 | -4.3 | -4.3 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -49.9483 | 51.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 4 | 364 | -4.7 | -4.7 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -41.9623 | 68.4227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 5 | 365 | -4.9 | -4.9 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -33.065 | 82.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 6 | 366 | -4.9 | -4.9 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -23.8722 | 94.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 7 | 367 | -4.9 | -4.9 | -2.0542 | -0.46557 | 15 | 86 | 86 | 0 | 0 | -14.8071 | 105.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 16 | 8 | 368 | -5.3 | -5.3 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -6.2205 | 116.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 9 | 369 | -6.2 | -6.2 | -2.0542 | -0.46557 | 15 | 89 | 89 | 0 | 0 | 1.5415 | 128.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 10 | 370 | -4.4 | -4.4 | -2.0542 | -0.46557 | 15 | 86 | 86 | 167.1161 | 41.5516 | 8.1047 | 140.7401 | 0 | 19.3954 | 131.0419 | 165.9258 | 103.6127 | 0 | 0 | 0 | 14.4484 | 19.699 | 21.2473 | 30.1596 | 32.9443 | 27.97 | 19.699 | 19.699 | 19.699 | 41.5516 | 19.699 | 40.6427 | 161.2015 | 198.8701 | 131.5827 | 19.699 | 19.699 | 19.699 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 11 | 371 | -2.4 | -2.4 | -2.0542 | -0.46557 | 15 | 77 | 77 | 533.7797 | 64.3677 | 13.0687 | 154.0533 | 0 | 0 | 334.4226 | 525.7985 | 409.1689 | 52.8536 | 0 | 0 | 99.6323 | 40.5378 | 40.5378 | 89.0808 | 116.86 | 99.9306 | 48.2097 | 40.5378 | 40.5378 | 64.3677 | 40.5378 | 40.5378 | 423.5034 | 642.6585 | 509.0995 | 101.0633 | 40.5378 | 40.5378 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 12 | 372 | -0.5 | -0.5 | -2.0542 | -0.46557 | 15 | 63 | 63 | 672.404 | 70.6353 | 16.0518 | 168.1806 | 0 | 0 | 286.5803 | 619.1052 | 588.9666 | 213.8194 | 0 | 0 | 171.3647 | 52.5744 | 52.5744 | 91.5824 | 136.8441 | 132.7417 | 81.6785 | 52.5744 | 52.5744 | 70.6353 | 52.5744 | 52.5744 | 378.1627 | 755.9493 | 721.7084 | 295.4979 | 52.5744 | 52.5744 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 13 | 373 | 0.7 | 0.7 | -2.0542 | -0.46557 | 15 | 64 | 64 | 712.9061 | 73.8229 | 16.7808 | 182.7498 | 0 | 0 | 140.3301 | 573.404 | 670.5857 | 374.9474 | 0 | 0 | 204.1771 | 57.8362 | 57.8362 | 75.7913 | 131.2027 | 143.637 | 105.8104 | 57.8362 | 57.8362 | 73.8229 | 57.8362 | 57.8362 | 216.1214 | 704.6067 | 814.2227 | 480.7577 | 57.8362 | 57.8362 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 14 | 374 | 1.4 | 1.4 | -2.0542 | -0.46557 | 15 | 58 | 58 | 740.1246 | 68.4014 | 15.1829 | 197.2119 | 0 | 0 | 0 | 476.4455 | 707.7915 | 524.5229 | 33.9958 | 0 | 206.5986 | 55.804 | 55.804 | 55.804 | 111.742 | 138.9036 | 117.3866 | 59.7954 | 55.804 | 68.4014 | 55.804 | 55.804 | 55.804 | 588.1875 | 846.6952 | 641.9095 | 93.7912 | 55.804 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 15 | 375 | 1.8 | 1.8 | -2.0542 | -0.46557 | 15 | 56 | 56 | 723.2897 | 59.0628 | 11.4144 | 211.062 | 0 | 0 | 0 | 325.4302 | 666.7828 | 617.5431 | 206.555 | 0 | 168.9372 | 49.0817 | 49.0817 | 49.0817 | 79.0727 | 110.5312 | 105.9933 | 68.1174 | 49.0817 | 59.0628 | 49.0817 | 49.0817 | 49.0817 | 404.503 | 777.314 | 723.5364 | 274.6724 | 49.0817 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 16 | 376 | 1.4 | 1.4 | -2.0542 | -0.46557 | 15 | 54 | 54 | 658.5391 | 43.3773 | 5.8014 | 224.0301 | 0 | 0 | 0 | 155.4863 | 552.9537 | 626.5083 | 333.0628 | 0 | 100.6227 | 34.3664 | 34.3664 | 34.3664 | 49.1227 | 86.8443 | 93.8249 | 65.9756 | 34.3664 | 43.3773 | 34.3664 | 34.3664 | 34.3664 | 204.6091 | 639.798 | 720.3332 | 399.0384 | 34.3664 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 17 | 377 | -0.2 | -0.2 | -2.0542 | -0.46557 | 15 | 58 | 58 | 375.416 | 8.6788 | -1.2589 | 236.1265 | 0 | 0 | 0 | 6.3222 | 268.5322 | 373.4397 | 259.5913 | 0 | 35.3212 | 9.5972 | 9.5972 | 9.5972 | 10.2134 | 35.7703 | 45.9953 | 34.8988 | 9.5972 | 8.6788 | 9.5972 | 9.5972 | 9.5972 | 16.5356 | 304.3025 | 419.435 | 294.4901 | 9.5972 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 16 | 18 | 378 | -1.3 | -1.3 | -2.0542 | -0.46557 | 15 | 69 | 69 | 0 | 0 | -9.3731 | 247.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 19 | 379 | -2.7 | -2.7 | -2.0542 | -0.46557 | 15 | 76 | 76 | 0 | 0 | -18.1796 | 258.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 20 | 380 | -4.2 | -4.2 | -2.0542 | -0.46557 | 15 | 84 | 84 | 0 | 0 | -27.3359 | 270.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 21 | 381 | -4.1 | -4.1 | -2.0542 | -0.46557 | 15 | 87 | 87 | 0 | 0 | -36.4742 | 282.8013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 22 | 382 | -4.9 | -4.9 | -2.0542 | -0.46557 | 15 | 90 | 90 | 0 | 0 | -45.1166 | 297.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 23 | 383 | -4.2 | -4.2 | -2.0542 | -0.46557 | 15 | 89 | 89 | 0 | 0 | -52.5308 | 315.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 16 | 24 | 384 | -5.3 | -5.3 | -3.0208 | -1.3572 | 15 | 93 | 93 | 0 | 0 | -57.5721 | 338.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 1 | 385 | -6.3 | -6.3 | -3.0208 | -1.3572 | 15 | 93 | 93 | 0 | 0 | -58.9005 | 5.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 2 | 386 | -6.7 | -6.7 | -3.0208 | -1.3572 | 15 | 94 | 94 | 0 | 0 | -55.8925 | 30.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 3 | 387 | -6.4 | -6.4 | -3.0208 | -1.3572 | 15 | 94 | 94 | 0 | 0 | -49.8281 | 51.5535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 4 | 388 | -6.8 | -6.8 | -3.0208 | -1.3572 | 15 | 93 | 93 | 0 | 0 | -41.8619 | 68.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 5 | 389 | -7.4 | -7.4 | -3.0208 | -1.3572 | 15 | 92 | 92 | 0 | 0 | -32.9741 | 81.8666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 6 | 390 | -7.7 | -7.7 | -3.0208 | -1.3572 | 15 | 92 | 92 | 0 | 0 | -23.7824 | 93.9118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 7 | 391 | -8.5 | -8.5 | -3.0208 | -1.3572 | 15 | 92 | 92 | 0 | 0 | -14.712 | 105.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 17 | 8 | 392 | -8.7 | -8.7 | -3.0208 | -1.3572 | 15 | 92 | 92 | 0 | 0 | -6.115 | 116.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 9 | 393 | -8.8 | -8.8 | -3.0208 | -1.3572 | 15 | 94 | 94 | 0 | 0 | 1.6616 | 128.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 10 | 394 | -6.8 | -6.8 | -3.0208 | -1.3572 | 15 | 93 | 93 | 118.047 | 42.5522 | 8.2428 | 140.587 | 0 | 14.0395 | 92.7715 | 117.1592 | 72.9166 | 0 | 0 | 0 | 10.4478 | 19.7931 | 21.6278 | 31.9164 | 35.1034 | 29.3218 | 19.7931 | 19.7931 | 19.7931 | 42.5522 | 19.7931 | 35.6673 | 124.6879 | 152.2626 | 102.2384 | 19.7931 | 19.7931 | 19.7931 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 11 | 395 | -5 | -5 | -3.0208 | -1.3572 | 15 | 86 | 86 | 543.2316 | 64.307 | 13.2262 | 153.9186 | 0 | 0 | 341.3375 | 535.0656 | 415.3595 | 52.3414 | 0 | 0 | 102.693 | 40.9304 | 40.9304 | 90.4187 | 118.5061 | 101.1507 | 48.519 | 40.9304 | 40.9304 | 64.307 | 40.9304 | 40.9304 | 431.7562 | 653.5717 | 516.5102 | 100.8605 | 40.9304 | 40.9304 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 12 | 396 | -2.8 | -2.8 | -3.0208 | -1.3572 | 15 | 79 | 79 | 668.1388 | 71.8997 | 16.2279 | 168.0713 | 0 | 0 | 285.954 | 615.2805 | 584.1841 | 210.8806 | 0 | 0 | 172.1003 | 53.2097 | 53.2097 | 92.5582 | 137.8748 | 133.5958 | 82.2278 | 53.2097 | 53.2097 | 71.8997 | 53.2097 | 53.2097 | 378.5121 | 753.1554 | 717.78 | 293.1083 | 53.2097 | 53.2097 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 13 | 397 | -0.4 | -0.4 | -3.0208 | -1.3572 | 15 | 61 | 61 | 1050.0632 | 60.06 | 16.9719 | 182.6723 | 0 | 0 | 208.3944 | 844.8856 | 986.4543 | 550.1714 | 0 | 0 | 303.94 | 62.9226 | 62.9226 | 77.274 | 121.1071 | 130.8564 | 100.8111 | 62.9226 | 62.9226 | 60.06 | 62.9226 | 62.9226 | 285.6684 | 965.9927 | 1117.3107 | 650.9825 | 62.9226 | 62.9226 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 14 | 398 | 0 | 0 | -3.0208 | -1.3572 | 15 | 60 | 60 | 1058.2878 | 59.07 | 15.3836 | 197.1684 | 0 | 0 | 0 | 681.5836 | 1011.0967 | 748.3231 | 47.1919 | 0 | 298.93 | 62.4222 | 62.4222 | 62.4222 | 106.9597 | 128.4915 | 111.3208 | 65.5059 | 62.4222 | 59.07 | 62.4222 | 62.4222 | 62.4222 | 788.5434 | 1139.5882 | 859.6438 | 112.6978 | 62.4222 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 15 | 399 | 0.8 | 0.8 | -3.0208 | -1.3572 | 15 | 59 | 59 | 719.8355 | 60.3209 | 11.6191 | 211.0504 | 0 | 0 | 0 | 324.0318 | 663.1192 | 613.7604 | 204.8691 | 0 | 170.6791 | 49.854 | 49.854 | 49.854 | 80.0644 | 111.6785 | 107.0766 | 68.9546 | 49.854 | 60.3209 | 49.854 | 49.854 | 49.854 | 404.0962 | 774.7977 | 720.837 | 273.8236 | 49.854 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 16 | 400 | 0.5 | 0.5 | -3.0208 | -1.3572 | 15 | 62 | 62 | 419.975 | 62.2839 | 6.0058 | 224.0452 | 0 | 0 | 0 | 99.1679 | 352.4255 | 399.237 | 212.1809 | 0 | 65.7161 | 38.1337 | 38.1337 | 38.1337 | 59.0903 | 112.6098 | 122.5023 | 82.9727 | 38.1337 | 62.2839 | 38.1337 | 38.1337 | 38.1337 | 158.2582 | 465.0353 | 521.7393 | 295.1536 | 38.1337 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 17 | 401 | -0.8 | -0.8 | -3.0208 | -1.3572 | 15 | 72 | 72 | 196.7576 | 21.9355 | -1.0571 | 236.1625 | 0 | 0 | 0 | 3.2606 | 140.6514 | 195.6505 | 136.0401 | 0 | 9.0645 | 13.044 | 13.044 | 13.044 | 14.18 | 62.0467 | 81.2083 | 60.4401 | 13.044 | 21.9355 | 13.044 | 13.044 | 13.044 | 17.4406 | 202.6981 | 276.8587 | 196.4803 | 13.044 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 17 | 18 | 402 | -1.8 | -1.8 | -3.0208 | -1.3572 | 15 | 79 | 79 | 0 | 0 | -9.1746 | 247.6356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 19 | 403 | -2.6 | -2.6 | -3.0208 | -1.3572 | 15 | 84 | 84 | 0 | 0 | -17.9837 | 258.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 20 | 404 | -3.9 | -3.9 | -3.0208 | -1.3572 | 15 | 90 | 90 | 0 | 0 | -27.1411 | 270.3573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 21 | 405 | -4.6 | -4.6 | -3.0208 | -1.3572 | 15 | 89 | 89 | 0 | 0 | -36.2781 | 282.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 22 | 406 | -5.3 | -5.3 | -3.0208 | -1.3572 | 15 | 93 | 93 | 0 | 0 | -44.9166 | 297.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 23 | 407 | -6.3 | -6.3 | -3.0208 | -1.3572 | 15 | 91 | 91 | 0 | 0 | -52.3263 | 315.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 17 | 24 | 408 | -7.3 | -7.3 | -4.7333 | -2.4349 | 15 | 92 | 92 | 0 | 0 | -57.3696 | 338.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 1 | 409 | -7.5 | -7.5 | -4.7333 | -2.4349 | 15 | 93 | 93 | 0 | 0 | -58.7167 | 4.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 2 | 410 | -7.9 | -7.9 | -4.7333 | -2.4349 | 15 | 94 | 94 | 0 | 0 | -55.7341 | 30.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 3 | 411 | -8.2 | -8.2 | -4.7333 | -2.4349 | 15 | 93 | 93 | 0 | 0 | -49.7004 | 51.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 4 | 412 | -8.6 | -8.6 | -4.7333 | -2.4349 | 15 | 92 | 92 | 0 | 0 | -41.7545 | 67.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 5 | 413 | -7.4 | -7.4 | -4.7333 | -2.4349 | 15 | 94 | 94 | 0 | 0 | -32.8763 | 81.6448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 6 | 414 | -7.5 | -7.5 | -4.7333 | -2.4349 | 15 | 92 | 92 | 0 | 0 | -23.6859 | 93.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 7 | 415 | -6.8 | -6.8 | -4.7333 | -2.4349 | 15 | 93 | 93 | 0 | 0 | -14.6104 | 105.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 18 | 8 | 416 | -6.2 | -6.2 | -4.7333 | -2.4349 | 15 | 91 | 91 | 0 | 0 | -6.0029 | 116.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 9 | 417 | -5.9 | -5.9 | -4.7333 | -2.4349 | 15 | 90 | 90 | 0 | 0 | 1.7886 | 127.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 10 | 418 | -5.2 | -5.2 | -4.7333 | -2.4349 | 15 | 90 | 90 | 2.7981 | 18.7464 | 8.3878 | 140.4331 | 0 | 0.34088 | 2.2039 | 2.7759 | 1.7218 | 0 | 0 | 0 | 0.25364 | 8.5717 | 11.318 | 26.3269 | 30.9351 | 22.4431 | 8.5717 | 8.5717 | 8.5717 | 18.7464 | 8.5717 | 11.6588 | 28.5308 | 33.711 | 24.1649 | 8.5717 | 8.5717 | 8.5717 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 11 | 419 | -4 | -4 | -4.7333 | -2.4349 | 15 | 91 | 91 | 0.6268 | 18.88 | 13.3907 | 153.7839 | 0 | 0 | 0.39499 | 0.61731 | 0.47802 | 0.058713 | 0 | 0 | 0.12005 | 8.9784 | 8.9784 | 8.9784 | 8.9784 | 8.9784 | 8.9784 | 8.9784 | 8.9784 | 18.88 | 8.9784 | 8.9784 | 9.3734 | 9.5957 | 9.4564 | 9.0371 | 8.9784 | 8.9784 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 12 | 420 | -3.4 | -3.4 | -4.7333 | -2.4349 | 15 | 92 | 92 | 0.73633 | 27.8082 | 16.4108 | 167.9632 | 0 | 0 | 0.31644 | 0.67817 | 0.64263 | 0.23065 | 0 | 0 | 0.19175 | 13.2476 | 13.2476 | 13.2476 | 13.2476 | 13.2476 | 13.2476 | 13.2476 | 13.2476 | 27.8082 | 13.2476 | 13.2476 | 13.564 | 13.9258 | 13.8902 | 13.4782 | 13.2476 | 13.2476 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 13 | 421 | -2.8 | -2.8 | -4.7333 | -2.4349 | 15 | 93 | 93 | 0.96413 | 35.7179 | 17.1695 | 182.5971 | 0 | 0 | 0.19287 | 0.77597 | 0.90451 | 0.50321 | 0 | 0 | 0.28211 | 17.0859 | 17.0859 | 17.0859 | 17.0859 | 17.0859 | 17.0859 | 17.0859 | 17.0859 | 35.7179 | 17.0859 | 17.0859 | 17.2788 | 17.8619 | 17.9905 | 17.5891 | 17.0859 | 17.0859 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 14 | 422 | -2.2 | -2.2 | -4.7333 | -2.4349 | 15 | 93 | 93 | 0.84858 | 32.7574 | 15.5902 | 197.1285 | 0 | 0 | 0 | 0.54673 | 0.80993 | 0.59869 | 0.036738 | 0 | 0.24261 | 15.6128 | 15.6128 | 15.6128 | 15.6128 | 15.6128 | 15.6128 | 15.6128 | 15.6128 | 32.7574 | 15.6128 | 15.6128 | 15.6128 | 16.1595 | 16.4227 | 16.2114 | 15.6495 | 15.6128 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 15 | 423 | -2 | -2 | -4.7333 | -2.4349 | 15 | 94 | 94 | 0.39668 | 18.9045 | 11.8292 | 211.0433 | 0 | 0 | 0 | 0.17862 | 0.36514 | 0.33777 | 0.11253 | 0 | 0.095503 | 8.8985 | 8.8985 | 8.8985 | 8.8985 | 8.8985 | 8.8985 | 8.8985 | 8.8985 | 18.9045 | 8.8985 | 8.8985 | 8.8985 | 9.0771 | 9.2636 | 9.2363 | 9.011 | 8.8985 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 16 | 424 | -1.7 | -1.7 | -4.7333 | -2.4349 | 15 | 97 | 97 | 0.30007 | 10.9519 | 6.2151 | 224.0654 | 0 | 0 | 0 | 0.070838 | 0.25164 | 0.28503 | 0.15146 | 0 | 0.048089 | 5.1169 | 5.1169 | 5.1169 | 5.1169 | 5.1169 | 5.1169 | 5.1169 | 5.1169 | 10.9519 | 5.1169 | 5.1169 | 5.1169 | 5.1877 | 5.3685 | 5.4019 | 5.2683 | 5.1169 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 17 | 425 | -1.4 | -1.4 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -0.85096 | 236.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 18 | 18 | 426 | -1.2 | -1.2 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -8.9722 | 247.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 19 | 427 | -1.1 | -1.1 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -17.7842 | 258.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 20 | 428 | -1 | -1 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -26.9427 | 270.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 21 | 429 | -0.9 | -0.9 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -36.0782 | 282.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 22 | 430 | -0.8 | -0.8 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -44.7125 | 297.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 23 | 431 | -0.7 | -0.7 | -4.7333 | -2.4349 | 15 | 98 | 98 | 0 | 0 | -52.1171 | 315.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 18 | 24 | 432 | -0.6 | -0.6 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -57.1613 | 338.3524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 1 | 433 | -0.6 | -0.6 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -58.526 | 4.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 2 | 434 | -0.5 | -0.5 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -55.5684 | 30.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 3 | 435 | -0.5 | -0.5 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -49.5655 | 51.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 4 | 436 | -0.6 | -0.6 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -41.64 | 67.6955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 5 | 437 | -0.5 | -0.5 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -32.7717 | 81.4207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 6 | 438 | -0.7 | -0.7 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -23.5828 | 93.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 7 | 439 | -0.8 | -0.8 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -14.5021 | 104.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 19 | 8 | 440 | -0.9 | -0.9 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -5.8841 | 116.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 9 | 441 | -1.2 | -1.2 | -3.9583 | -3.0294 | 15 | 100 | 100 | 0 | 0 | 1.9222 | 127.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 10 | 442 | -1.2 | -1.2 | -3.9583 | -3.0294 | 15 | 100 | 100 | 0.89334 | 10.917 | 8.5395 | 140.2784 | 0 | 0.11144 | 0.7052 | 0.88586 | 0.5476 | 0 | 0 | 0 | 0.082981 | 5.3102 | 5.3102 | 5.3102 | 5.3102 | 5.3102 | 5.3102 | 5.3102 | 5.3102 | 10.917 | 5.3102 | 5.4217 | 6.0154 | 6.1961 | 5.8578 | 5.3102 | 5.3102 | 5.3102 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 11 | 443 | -1.1 | -1.1 | -3.9583 | -3.0294 | 15 | 99 | 99 | 3.7346 | 46.2751 | 13.5619 | 153.6494 | 0 | 0 | 2.3602 | 3.6775 | 2.8407 | 0.33976 | 0 | 0 | 0.72494 | 22.4593 | 22.4593 | 27.8687 | 30.888 | 28.97 | 23.238 | 22.4593 | 22.4593 | 46.2751 | 22.4593 | 22.4593 | 30.2289 | 34.5656 | 31.8106 | 23.5778 | 22.4593 | 22.4593 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 12 | 444 | -1 | -1 | -3.9583 | -3.0294 | 15 | 99 | 99 | 14.6902 | 99.1314 | 16.6004 | 167.8564 | 0 | 0 | 6.3386 | 13.5308 | 12.7968 | 4.5666 | 0 | 0 | 3.8686 | 45.5559 | 45.5559 | 66.7925 | 90.8887 | 88.4296 | 60.8556 | 45.5559 | 45.5559 | 99.1314 | 45.5559 | 45.5559 | 73.1311 | 104.4195 | 101.2263 | 65.4222 | 45.5559 | 45.5559 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 13 | 445 | -0.5 | -0.5 | -3.9583 | -3.0294 | 15 | 99 | 99 | 59.0671 | 135.5246 | 17.3734 | 182.5244 | 0 | 0 | 11.9076 | 47.5503 | 55.3386 | 30.7104 | 0 | 0 | 17.4754 | 63.7975 | 63.7975 | 80.8446 | 131.8709 | 143.0208 | 107.7627 | 63.7975 | 63.7975 | 135.5246 | 63.7975 | 63.7975 | 92.7522 | 179.4212 | 198.3594 | 138.4731 | 63.7975 | 63.7975 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 14 | 446 | -0.9 | -0.9 | -3.9583 | -3.0294 | 15 | 99 | 99 | 3.1148 | 63.0985 | 15.8029 | 197.0921 | 0 | 0 | 0 | 2.0074 | 2.9698 | 2.1926 | 0.13093 | 0 | 0.90152 | 30.9226 | 30.9226 | 30.9226 | 30.9226 | 30.9226 | 30.9226 | 30.9226 | 30.9226 | 63.0985 | 30.9226 | 30.9226 | 30.9226 | 32.93 | 33.8924 | 33.1152 | 31.0535 | 30.9226 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 15 | 447 | -0.9 | -0.9 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0.83543 | 27.7957 | 12.0447 | 211.0405 | 0 | 0 | 0 | 0.37625 | 0.76836 | 0.71037 | 0.23626 | 0 | 0.20426 | 13.2035 | 13.2035 | 13.2035 | 13.2035 | 13.2035 | 13.2035 | 13.2035 | 13.2035 | 27.7957 | 13.2035 | 13.2035 | 13.2035 | 13.5797 | 13.9718 | 13.9138 | 13.4397 | 13.2035 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 16 | 448 | -0.9 | -0.9 | -3.9583 | -3.0294 | 15 | 99 | 99 | 2.2722 | 30.627 | 6.4291 | 224.0906 | 0 | 0 | 0 | 0.53607 | 1.904 | 2.1566 | 1.1459 | 0 | 0.37296 | 14.6942 | 14.6942 | 14.6942 | 14.6942 | 14.6942 | 14.6942 | 14.6942 | 14.6942 | 30.627 | 14.6942 | 14.6942 | 14.6942 | 15.2303 | 16.5982 | 16.8508 | 15.8401 | 14.6942 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 17 | 449 | -0.6 | -0.6 | -3.9583 | -3.0294 | 15 | 100 | 100 | 1.4069 | 7.9243 | -0.64065 | 236.2508 | 0 | 0 | 0 | 0.02219 | 1.0041 | 1.3979 | 0.97275 | 0 | 0.075735 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 7.9243 | 3.707 | 3.707 | 3.707 | 3.7292 | 4.7111 | 5.1049 | 4.6798 | 3.707 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 19 | 18 | 450 | -0.2 | -0.2 | -3.9583 | -3.0294 | 15 | 100 | 100 | 0 | 0 | -8.766 | 247.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 19 | 451 | 0.1 | 0.1 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -17.5813 | 259.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 20 | 452 | 0.2 | 0.2 | -3.9583 | -3.0294 | 15 | 100 | 100 | 0 | 0 | -26.7409 | 270.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 21 | 453 | 0.3 | 0.3 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -35.8748 | 283.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 22 | 454 | 0.3 | 0.3 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -44.5045 | 297.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 23 | 455 | 0 | 0 | -3.9583 | -3.0294 | 15 | 99 | 99 | 0 | 0 | -51.9032 | 315.6261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 19 | 24 | 456 | -0.2 | -0.2 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -56.9472 | 338.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 1 | 457 | 0 | 0 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -58.3285 | 4.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 2 | 458 | 0 | 0 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -55.3954 | 29.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 3 | 459 | 0 | 0 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -49.4233 | 50.7757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 4 | 460 | -0.3 | -0.3 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -41.5185 | 67.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 5 | 461 | -0.9 | -0.9 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -32.6602 | 81.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 6 | 462 | -0.7 | -0.7 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -23.4729 | 93.2924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 7 | 463 | -0.9 | -0.9 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -14.3872 | 104.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 20 | 8 | 464 | -0.2 | -0.2 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -5.7587 | 115.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 9 | 465 | -0.1 | -0.1 | -0.5375 | -2.539 | 15 | 98 | 98 | 0 | 0 | 2.0626 | 127.6595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 10 | 466 | 0.2 | 0.2 | -0.5375 | -2.539 | 15 | 99 | 99 | 0.44972 | 7.9572 | 8.698 | 140.1231 | 0 | 0.057422 | 0.3558 | 0.44575 | 0.27459 | 0 | 0 | 0 | 0.042823 | 3.8006 | 3.8006 | 3.8006 | 3.8006 | 3.8006 | 3.8006 | 3.8006 | 3.8006 | 7.9572 | 3.8006 | 3.858 | 4.1563 | 4.2463 | 4.0751 | 3.8006 | 3.8006 | 3.8006 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 11 | 467 | 0.5 | 0.5 | -0.5375 | -2.539 | 15 | 97 | 97 | 0.79626 | 21.8433 | 13.7399 | 153.5151 | 0 | 0 | 0.50464 | 0.78396 | 0.60404 | 0.070285 | 0 | 0 | 0.1567 | 10.4331 | 10.4331 | 10.4331 | 10.4331 | 10.4331 | 10.4331 | 10.4331 | 10.4331 | 21.8433 | 10.4331 | 10.4331 | 10.9377 | 11.2171 | 11.0371 | 10.5034 | 10.4331 | 10.4331 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 12 | 468 | 0.6 | 0.6 | -0.5375 | -2.539 | 15 | 97 | 97 | 1.1637 | 35.69 | 16.7965 | 167.7509 | 0 | 0 | 0.50413 | 1.0719 | 1.0118 | 0.35898 | 0 | 0 | 0.30999 | 17.1491 | 17.1491 | 17.1491 | 17.1491 | 17.1491 | 17.1491 | 17.1491 | 17.1491 | 35.69 | 17.1491 | 17.1491 | 17.6532 | 18.221 | 18.1609 | 17.5081 | 17.1491 | 17.1491 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 13 | 469 | 0.7 | 0.7 | -0.5375 | -2.539 | 15 | 96 | 96 | 2.394 | 57.2837 | 17.5837 | 182.4542 | 0 | 0 | 0.48626 | 1.9276 | 2.2397 | 1.2399 | 0 | 0 | 0.71633 | 27.9565 | 27.9565 | 27.9565 | 27.9565 | 27.9565 | 27.9565 | 27.9565 | 27.9565 | 57.2837 | 27.9565 | 27.9565 | 28.4428 | 29.8841 | 30.1962 | 29.1964 | 27.9565 | 27.9565 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 14 | 470 | 0.6 | 0.6 | -0.5375 | -2.539 | 15 | 97 | 97 | 1.6387 | 46.5197 | 16.0213 | 197.0594 | 0 | 0 | 0 | 1.0563 | 1.5607 | 1.1509 | 0.066892 | 0 | 0.48025 | 22.4458 | 22.4458 | 22.4458 | 22.4458 | 22.4458 | 22.4458 | 22.4458 | 22.4458 | 46.5197 | 22.4458 | 22.4458 | 22.4458 | 23.5021 | 24.0065 | 23.5967 | 22.5126 | 22.4458 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 15 | 471 | 1.1 | 1.1 | -0.5375 | -2.539 | 15 | 96 | 96 | 4.2313 | 62.9492 | 12.2654 | 211.0423 | 0 | 0 | 0 | 1.9056 | 3.888 | 3.5928 | 1.1931 | 0 | 1.0508 | 30.9678 | 30.9678 | 30.9678 | 30.9678 | 30.9678 | 30.9678 | 30.9678 | 30.9678 | 62.9492 | 30.9678 | 30.9678 | 30.9678 | 32.8733 | 34.8557 | 34.5606 | 32.1608 | 30.9678 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 16 | 472 | 0.3 | 0.3 | -0.5375 | -2.539 | 15 | 96 | 96 | 4.9794 | 46.1628 | 6.6478 | 224.1209 | 0 | 0 | 0 | 1.1736 | 4.1689 | 4.7221 | 2.5091 | 0 | 0.83715 | 22.5883 | 22.5883 | 22.5883 | 22.5883 | 22.5883 | 22.5883 | 22.5883 | 22.5883 | 46.1628 | 22.5883 | 22.5883 | 22.5883 | 23.7619 | 26.7572 | 27.3103 | 25.0974 | 22.5883 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 17 | 473 | 0.1 | 0.1 | -0.5375 | -2.539 | 15 | 97 | 97 | 0 | 0 | -0.42627 | 236.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 18 | 474 | 0.2 | 0.2 | -0.5375 | -2.539 | 15 | 98 | 98 | 0 | 0 | -8.5562 | 247.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 19 | 475 | 0.1 | 0.1 | -0.5375 | -2.539 | 15 | 98 | 98 | 0 | 0 | -17.3749 | 259.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 20 | 476 | 0.2 | 0.2 | -0.5375 | -2.539 | 15 | 98 | 98 | 0 | 0 | -26.5358 | 270.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 21 | 477 | 0.1 | 0.1 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -35.6679 | 283.1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 22 | 478 | 0 | 0 | -0.5375 | -2.539 | 15 | 99 | 99 | 0 | 0 | -44.2925 | 297.6972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 23 | 479 | -0.2 | -0.2 | -0.5375 | -2.539 | 15 | 98 | 98 | 0 | 0 | -51.6846 | 315.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 20 | 24 | 480 | 0 | 0 | 0.058333 | -1.9277 | 15 | 99 | 99 | 0 | 0 | -56.7274 | 338.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 1 | 481 | 0 | 0 | 0.058333 | -1.9277 | 15 | 99 | 99 | 0 | 0 | -58.1242 | 4.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 2 | 482 | 0.1 | 0.1 | 0.058333 | -1.9277 | 15 | 99 | 99 | 0 | 0 | -55.2151 | 29.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 3 | 483 | 0.1 | 0.1 | 0.058333 | -1.9277 | 15 | 99 | 99 | 0 | 0 | -49.2737 | 50.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 4 | 484 | 0.1 | 0.1 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -41.3899 | 67.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 5 | 485 | -0.1 | -0.1 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -32.542 | 80.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 6 | 486 | -0.3 | -0.3 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -23.3565 | 93.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 7 | 487 | -0.4 | -0.4 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -14.2657 | 104.4644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 21 | 8 | 488 | -0.4 | -0.4 | 0.058333 | -1.9277 | 15 | 94 | 94 | 0 | 0 | -5.6267 | 115.7702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 9 | 489 | -0.9 | -0.9 | 0.058333 | -1.9277 | 15 | 94 | 94 | 0 | 0 | 2.2096 | 127.4878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 10 | 490 | -1.7 | -1.7 | 0.058333 | -1.9277 | 15 | 93 | 93 | 20.6045 | 37.0822 | 8.8632 | 139.9672 | 0 | 2.6918 | 16.3371 | 20.4124 | 12.5304 | 0 | 0 | 0 | 1.9178 | 16.1356 | 28.4858 | 91.0929 | 109.791 | 73.627 | 16.1356 | 16.1356 | 16.1356 | 37.0822 | 16.1356 | 31.1776 | 107.43 | 130.2034 | 86.1574 | 16.1356 | 16.1356 | 16.1356 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 11 | 491 | -1.6 | -1.6 | 0.058333 | -1.9277 | 15 | 90 | 90 | 173.1452 | 94.0412 | 13.9245 | 153.3812 | 0 | 0 | 110.0416 | 170.4352 | 130.9902 | 14.8129 | 0 | 0 | 33.9588 | 45.8827 | 45.8827 | 134.2405 | 182.7335 | 151.0612 | 57.7766 | 45.8827 | 45.8827 | 94.0412 | 45.8827 | 45.8827 | 244.2822 | 353.1688 | 282.0513 | 72.5895 | 45.8827 | 45.8827 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 12 | 492 | -0.9 | -0.9 | 0.058333 | -1.9277 | 15 | 82 | 82 | 422.364 | 106.0495 | 16.9993 | 167.6468 | 0 | 0 | 183.6804 | 389.0364 | 366.5001 | 129.2731 | 0 | 0 | 112.9505 | 62.8124 | 62.8124 | 109.0114 | 160.6623 | 154.994 | 95.327 | 62.8124 | 62.8124 | 106.0495 | 62.8124 | 62.8124 | 292.6918 | 549.6987 | 521.4941 | 224.6001 | 62.8124 | 62.8124 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 13 | 493 | -0.3 | -0.3 | 0.058333 | -1.9277 | 15 | 77 | 77 | 506.5144 | 107.9846 | 17.8002 | 182.3865 | 0 | 0 | 103.6282 | 407.8573 | 473.1691 | 261.3049 | 0 | 0 | 153.0154 | 68.1809 | 68.1809 | 90.7539 | 157.0234 | 171.2501 | 125.1002 | 68.1809 | 68.1809 | 107.9846 | 68.1809 | 68.1809 | 194.3821 | 564.8807 | 644.4192 | 386.4051 | 68.1809 | 68.1809 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 14 | 494 | 0.3 | 0.3 | 0.058333 | -1.9277 | 15 | 78 | 78 | 143.0004 | 143.4187 | 16.2454 | 197.0303 | 0 | 0 | 0 | 92.1834 | 136.0366 | 100.2014 | 5.6696 | 0 | 42.5813 | 70.5794 | 70.5794 | 70.5794 | 142.7255 | 177.0466 | 149.0007 | 75.0166 | 70.5794 | 143.4187 | 70.5794 | 70.5794 | 70.5794 | 234.9089 | 313.0832 | 249.2021 | 80.6862 | 70.5794 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 15 | 495 | 0.7 | 0.7 | 0.058333 | -1.9277 | 15 | 76 | 76 | 76.6824 | 119.4654 | 12.4912 | 211.0487 | 0 | 0 | 0 | 34.5284 | 70.3924 | 65.0214 | 21.5618 | 0 | 19.5346 | 57.6399 | 57.6399 | 57.6399 | 88.3866 | 120.3226 | 115.5399 | 76.8402 | 57.6399 | 119.4654 | 57.6399 | 57.6399 | 57.6399 | 122.915 | 190.715 | 180.5614 | 98.402 | 57.6399 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 16 | 496 | 0.6 | 0.6 | 0.058333 | -1.9277 | 15 | 78 | 78 | 18.3107 | 68.778 | 6.8709 | 224.1563 | 0 | 0 | 0 | 4.3102 | 15.316 | 17.3499 | 9.2205 | 0 | 3.222 | 33.8987 | 33.8987 | 33.8987 | 41.9597 | 62.5432 | 66.3472 | 51.1432 | 33.8987 | 68.778 | 33.8987 | 33.8987 | 33.8987 | 46.2699 | 77.8592 | 83.6971 | 60.3637 | 33.8987 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 17 | 497 | 0.7 | 0.7 | 0.058333 | -1.9277 | 15 | 79 | 79 | 5.1557 | 18.6556 | -0.20792 | 236.3611 | 0 | 0 | 0 | 0.075372 | 3.6723 | 5.1181 | 3.5657 | 0 | 0.34439 | 9.7574 | 9.7574 | 9.7574 | 9.8248 | 13.0443 | 14.3383 | 12.9489 | 9.7574 | 18.6556 | 9.7574 | 9.7574 | 9.7574 | 9.9002 | 16.7166 | 19.4564 | 16.5146 | 9.7574 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 18 | 498 | 0.7 | 0.7 | 0.058333 | -1.9277 | 15 | 82 | 82 | 0 | 0 | -8.3428 | 247.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 19 | 499 | 0 | 0 | 0.058333 | -1.9277 | 15 | 91 | 91 | 0 | 0 | -17.1652 | 259.1712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 20 | 500 | -0.2 | -0.2 | 0.058333 | -1.9277 | 15 | 95 | 95 | 0 | 0 | -26.3274 | 270.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 21 | 501 | -0.2 | -0.2 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -35.4577 | 283.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 22 | 502 | -0.1 | -0.1 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -44.0768 | 297.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 23 | 503 | 0.1 | 0.1 | 0.058333 | -1.9277 | 15 | 97 | 97 | 0 | 0 | -51.4615 | 315.7326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 21 | 24 | 504 | 0.4 | 0.4 | -0.1375 | -1.4745 | 15 | 97 | 97 | 0 | 0 | -56.5021 | 338.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 1 | 505 | 0.6 | 0.6 | -0.1375 | -1.4745 | 15 | 96 | 96 | 0 | 0 | -57.9133 | 4.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 2 | 506 | 0.7 | 0.7 | -0.1375 | -1.4745 | 15 | 97 | 97 | 0 | 0 | -55.0276 | 29.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 3 | 507 | 0.7 | 0.7 | -0.1375 | -1.4745 | 15 | 97 | 97 | 0 | 0 | -49.117 | 50.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 4 | 508 | 0.7 | 0.7 | -0.1375 | -1.4745 | 15 | 98 | 98 | 0 | 0 | -41.2543 | 66.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 5 | 509 | 0.8 | 0.8 | -0.1375 | -1.4745 | 15 | 98 | 98 | 0 | 0 | -32.417 | 80.7355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 6 | 510 | 0.8 | 0.8 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0 | 0 | -23.2333 | 92.8686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 7 | 511 | 0.8 | 0.8 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0 | 0 | -14.1376 | 104.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 22 | 8 | 512 | 0.8 | 0.8 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0 | 0 | -5.4881 | 115.5845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 9 | 513 | 0.9 | 0.9 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0 | 0 | 2.3632 | 127.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 10 | 514 | 1.1 | 1.1 | -0.1375 | -1.4745 | 15 | 100 | 100 | 1.3434 | 13.8705 | 9.035 | 139.8108 | 0 | 0.17949 | 1.0675 | 1.3302 | 0.81365 | 0 | 0 | 0 | 0.12955 | 6.8031 | 6.8031 | 6.8031 | 6.8031 | 6.8031 | 6.8031 | 6.8031 | 6.8031 | 13.8705 | 6.8031 | 6.9826 | 7.8706 | 8.1333 | 7.6168 | 6.8031 | 6.8031 | 6.8031 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 11 | 515 | 1.6 | 1.6 | -0.1375 | -1.4745 | 15 | 99 | 99 | 3.9983 | 49.2018 | 14.1158 | 153.2475 | 0 | 0 | 2.5482 | 3.9348 | 3.0165 | 0.33116 | 0 | 0 | 0.7982 | 23.8546 | 23.8546 | 29.7708 | 32.9902 | 30.8582 | 24.6235 | 23.8546 | 23.8546 | 49.2018 | 23.8546 | 23.8546 | 32.319 | 36.925 | 33.8747 | 24.9547 | 23.8546 | 23.8546 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 12 | 516 | 1.8 | 1.8 | -0.1375 | -1.4745 | 15 | 99 | 99 | 4.4982 | 70.7809 | 17.2085 | 167.5441 | 0 | 0 | 1.9637 | 4.143 | 3.8954 | 1.366 | 0 | 0 | 1.2191 | 34.7504 | 34.7504 | 36.8243 | 39.126 | 38.8645 | 36.193 | 34.7504 | 34.7504 | 70.7809 | 34.7504 | 34.7504 | 38.788 | 43.269 | 42.76 | 37.559 | 34.7504 | 34.7504 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 13 | 517 | 2.5 | 2.5 | -0.1375 | -1.4745 | 15 | 99 | 99 | 3.5346 | 70.9193 | 18.0229 | 182.3215 | 0 | 0 | 0.72825 | 2.8462 | 3.2969 | 1.8163 | 0 | 0 | 1.0807 | 35.0138 | 35.0138 | 35.0138 | 35.0138 | 35.0138 | 35.0138 | 35.0138 | 35.0138 | 70.9193 | 35.0138 | 35.0138 | 35.7421 | 37.8601 | 38.3108 | 36.8302 | 35.0138 | 35.0138 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 14 | 518 | 2.8 | 2.8 | -0.1375 | -1.4745 | 15 | 100 | 100 | 2.3601 | 57.2886 | 16.4752 | 197.005 | 0 | 0 | 0 | 1.5213 | 2.2424 | 1.6499 | 0.090909 | 0 | 0.71136 | 27.889 | 27.889 | 27.889 | 27.889 | 27.889 | 27.889 | 27.889 | 27.889 | 57.2886 | 27.889 | 27.889 | 27.889 | 29.4104 | 30.1314 | 29.5389 | 27.9799 | 27.889 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 15 | 519 | 3 | 3 | -0.1375 | -1.4745 | 15 | 100 | 100 | 0.91784 | 30.7629 | 12.722 | 211.0596 | 0 | 0 | 0 | 0.41314 | 0.84167 | 0.77716 | 0.2574 | 0 | 0.23711 | 14.6463 | 14.6463 | 14.6463 | 14.6463 | 14.6463 | 14.6463 | 14.6463 | 14.6463 | 30.7629 | 14.6463 | 14.6463 | 14.6463 | 15.0595 | 15.488 | 15.4235 | 14.9037 | 14.6463 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 16 | 520 | 3.7 | 3.7 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0.95809 | 21.8281 | 7.0985 | 224.1968 | 0 | 0 | 0 | 0.22515 | 0.80058 | 0.90704 | 0.48217 | 0 | 0.17192 | 10.3383 | 10.3383 | 10.3383 | 10.3383 | 10.3383 | 10.3383 | 10.3383 | 10.3383 | 21.8281 | 10.3383 | 10.3383 | 10.3383 | 10.5634 | 11.1389 | 11.2453 | 10.8205 | 10.3383 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 17 | 521 | 4.5 | 4.5 | -0.1375 | -1.4745 | 15 | 99 | 99 | 1.5685 | 10.89 | 0.014291 | 236.4245 | 0 | 0 | 0 | 0.021817 | 1.1159 | 1.5563 | 1.0851 | 0 | 0.10999 | 5.1214 | 5.1214 | 5.1214 | 5.1214 | 5.1214 | 5.1214 | 5.1214 | 5.1214 | 10.89 | 5.1214 | 5.1214 | 5.1214 | 5.1432 | 6.2373 | 6.6777 | 6.2064 | 5.1214 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 22 | 18 | 522 | 5.1 | 5.1 | -0.1375 | -1.4745 | 15 | 100 | 100 | 0 | 0 | -8.126 | 247.9815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 19 | 523 | 5.3 | 5.3 | -0.1375 | -1.4745 | 15 | 100 | 100 | 0 | 0 | -16.9523 | 259.2652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 20 | 524 | 5.3 | 5.3 | -0.1375 | -1.4745 | 15 | 99 | 99 | 0 | 0 | -26.1159 | 270.8124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 21 | 525 | 5.2 | 5.2 | -0.1375 | -1.4745 | 15 | 93 | 93 | 0 | 0 | -35.2441 | 283.3483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 22 | 526 | 5 | 5 | -0.1375 | -1.4745 | 15 | 93 | 93 | 0 | 0 | -43.8573 | 297.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 23 | 527 | 5.1 | 5.1 | -0.1375 | -1.4745 | 15 | 95 | 95 | 0 | 0 | -51.234 | 315.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 22 | 24 | 528 | 4.8 | 4.8 | 2.65 | -0.34243 | 15 | 97 | 97 | 0 | 0 | -56.2714 | 338.2192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 1 | 529 | 4.9 | 4.9 | 2.65 | -0.34243 | 15 | 95 | 95 | 0 | 0 | -57.6959 | 4.1334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 2 | 530 | 5.2 | 5.2 | 2.65 | -0.34243 | 15 | 95 | 95 | 0 | 0 | -54.833 | 29.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 3 | 531 | 5.1 | 5.1 | 2.65 | -0.34243 | 15 | 96 | 96 | 0 | 0 | -48.9531 | 49.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 4 | 532 | 5.2 | 5.2 | 2.65 | -0.34243 | 15 | 97 | 97 | 0 | 0 | -41.1117 | 66.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 5 | 533 | 4.9 | 4.9 | 2.65 | -0.34243 | 15 | 97 | 97 | 0 | 0 | -32.2851 | 80.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 6 | 534 | 5.1 | 5.1 | 2.65 | -0.34243 | 15 | 98 | 98 | 0 | 0 | -23.1036 | 92.6539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 7 | 535 | 6.3 | 6.3 | 2.65 | -0.34243 | 15 | 97 | 97 | 0 | 0 | -14.003 | 104.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 23 | 8 | 536 | 5.5 | 5.5 | 2.65 | -0.34243 | 15 | 95 | 95 | 0 | 0 | -5.3429 | 115.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 9 | 537 | 5.2 | 5.2 | 2.65 | -0.34243 | 15 | 93 | 93 | 0 | 0 | 2.5234 | 127.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 10 | 538 | 5.9 | 5.9 | 2.65 | -0.34243 | 15 | 91 | 91 | 3.9936 | 24.6011 | 9.2134 | 139.654 | 0 | 0.54551 | 3.1804 | 3.9522 | 2.4089 | 0 | 0 | 0 | 0.3989 | 11.0594 | 16.0482 | 40.1446 | 47.2033 | 33.0893 | 11.0594 | 11.0594 | 11.0594 | 24.6011 | 11.0594 | 16.5937 | 43.325 | 51.1555 | 35.4982 | 11.0594 | 11.0594 | 11.0594 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 11 | 539 | 6 | 6 | 2.65 | -0.34243 | 15 | 91 | 91 | 5.7434 | 59.8328 | 14.3137 | 153.1144 | 0 | 0 | 3.6703 | 5.6506 | 4.3209 | 0.46 | 0 | 0 | 1.1672 | 28.1233 | 28.1233 | 46.0586 | 55.7355 | 49.2375 | 30.3711 | 28.1233 | 28.1233 | 59.8328 | 28.1233 | 28.1233 | 49.7289 | 61.3861 | 53.5583 | 30.8311 | 28.1233 | 28.1233 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 12 | 540 | 6.4 | 6.4 | 2.65 | -0.34243 | 15 | 90 | 90 | 3.4597 | 63.0495 | 17.4241 | 167.443 | 0 | 0 | 1.516 | 3.1862 | 2.99 | 1.0423 | 0 | 0 | 0.95049 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 31.1825 | 63.0495 | 31.1825 | 31.1825 | 32.6985 | 34.3687 | 34.1725 | 32.2248 | 31.1825 | 31.1825 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 13 | 541 | 8 | 8 | 2.65 | -0.34243 | 15 | 84 | 84 | 145.4196 | 148.9927 | 18.2516 | 182.2593 | 0 | 0 | 30.1652 | 117.0921 | 135.4281 | 74.4321 | 0 | 0 | 45.0073 | 72.7085 | 72.7085 | 97.8207 | 170.1866 | 185.4512 | 134.6726 | 72.7085 | 72.7085 | 148.9927 | 72.7085 | 72.7085 | 127.9859 | 287.2788 | 320.8793 | 209.1047 | 72.7085 | 72.7085 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 14 | 542 | 7.6 | 7.6 | 2.65 | -0.34243 | 15 | 85 | 85 | 89.5677 | 144.6673 | 16.7106 | 196.9835 | 0 | 0 | 0 | 57.7298 | 84.9955 | 62.472 | 3.3533 | 0 | 27.3327 | 69.0306 | 69.0306 | 69.0306 | 122.4065 | 147.616 | 126.7911 | 72.131 | 69.0306 | 144.6673 | 69.0306 | 69.0306 | 69.0306 | 180.1363 | 232.6114 | 189.2631 | 75.4842 | 69.0306 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 15 | 543 | 7.8 | 7.8 | 2.65 | -0.34243 | 15 | 84 | 84 | 15.0925 | 99.0455 | 12.9577 | 211.0751 | 0 | 0 | 0 | 6.79 | 13.8248 | 12.7612 | 4.2223 | 0 | 3.9545 | 47.5321 | 47.5321 | 47.5321 | 56.6312 | 66.0584 | 64.6331 | 53.1903 | 47.5321 | 99.0455 | 47.5321 | 47.5321 | 47.5321 | 63.4212 | 79.8832 | 77.3944 | 57.4126 | 47.5321 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 16 | 544 | 7.8 | 7.8 | 2.65 | -0.34243 | 15 | 82 | 82 | 5.3467 | 52.0215 | 7.3303 | 224.2426 | 0 | 0 | 0 | 1.2539 | 4.4628 | 5.0575 | 2.6895 | 0 | 0.97852 | 25.5697 | 25.5697 | 25.5697 | 25.5697 | 25.5697 | 25.5697 | 25.5697 | 25.5697 | 52.0215 | 25.5697 | 25.5697 | 25.5697 | 26.8236 | 30.0325 | 30.6272 | 28.2592 | 25.5697 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 17 | 545 | 7.4 | 7.4 | 2.65 | -0.34243 | 15 | 87 | 87 | 1.4265 | 10.8951 | 0.24026 | 236.4934 | 0 | 0 | 0 | 0.018703 | 1.0136 | 1.4147 | 0.98713 | 0 | 0.1049 | 5.1208 | 5.1208 | 5.1208 | 5.1208 | 5.1208 | 5.1208 | 5.1208 | 5.1208 | 10.8951 | 5.1208 | 5.1208 | 5.1208 | 5.1395 | 6.1343 | 6.5355 | 6.1079 | 5.1208 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 23 | 18 | 546 | 7 | 7 | 2.65 | -0.34243 | 15 | 93 | 93 | 0 | 0 | -7.9058 | 248.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 19 | 547 | 7.2 | 7.2 | 2.65 | -0.34243 | 15 | 95 | 95 | 0 | 0 | -16.7363 | 259.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 20 | 548 | 7.8 | 7.8 | 2.65 | -0.34243 | 15 | 95 | 95 | 0 | 0 | -25.9013 | 270.9224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 21 | 549 | 8.1 | 8.1 | 2.65 | -0.34243 | 15 | 96 | 96 | 0 | 0 | -35.0273 | 283.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 22 | 550 | 8.8 | 8.8 | 2.65 | -0.34243 | 15 | 94 | 94 | 0 | 0 | -43.6343 | 297.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 23 | 551 | 9.5 | 9.5 | 2.65 | -0.34243 | 15 | 93 | 93 | 0 | 0 | -51.0022 | 315.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 23 | 24 | 552 | 10.2 | 10.2 | 6.7875 | 1.7118 | 15 | 90 | 90 | 0 | 0 | -56.0353 | 338.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 1 | 553 | 10.5 | 10.5 | 6.7875 | 1.7118 | 15 | 90 | 90 | 0 | 0 | -57.4721 | 3.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 2 | 554 | 10.4 | 10.4 | 6.7875 | 1.7118 | 15 | 95 | 95 | 0 | 0 | -54.6315 | 28.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 3 | 555 | 10.7 | 10.7 | 6.7875 | 1.7118 | 15 | 92 | 92 | 0 | 0 | -48.782 | 49.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 4 | 556 | 11.1 | 11.1 | 6.7875 | 1.7118 | 15 | 86 | 86 | 0 | 0 | -40.9621 | 66.4509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 5 | 557 | 11.8 | 11.8 | 6.7875 | 1.7118 | 15 | 81 | 81 | 0 | 0 | -32.1466 | 80.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 6 | 558 | 10 | 10 | 6.7875 | 1.7118 | 15 | 86 | 86 | 0 | 0 | -22.9672 | 92.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 7 | 559 | 10.5 | 10.5 | 6.7875 | 1.7118 | 15 | 79 | 79 | 0 | 0 | -13.8618 | 103.8642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 24 | 8 | 560 | 8.8 | 8.8 | 6.7875 | 1.7118 | 15 | 83 | 83 | 0 | 0 | -5.1913 | 115.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 9 | 561 | 8.7 | 8.7 | 6.7875 | 1.7118 | 15 | 83 | 83 | 0 | 0 | 2.69 | 126.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 10 | 562 | 9.2 | 9.2 | 6.7875 | 1.7118 | 15 | 84 | 84 | 1.1683 | 13.8792 | 9.3984 | 139.4969 | 0 | 0.16309 | 0.93244 | 1.1556 | 0.70179 | 0 | 0 | 0 | 0.12084 | 6.7726 | 6.7726 | 6.7726 | 6.7726 | 6.7726 | 6.7726 | 6.7726 | 6.7726 | 13.8792 | 6.7726 | 6.9357 | 7.705 | 7.9282 | 7.4744 | 6.7726 | 6.7726 | 6.7726 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 11 | 563 | 9.2 | 9.2 | 6.7875 | 1.7118 | 15 | 83 | 83 | 4.6703 | 55.0336 | 14.518 | 152.9817 | 0 | 0 | 2.9926 | 4.5934 | 3.5035 | 0.36125 | 0 | 0 | 0.96639 | 26.3583 | 26.3583 | 36.7211 | 42.2645 | 38.4903 | 27.6093 | 26.3583 | 26.3583 | 55.0336 | 26.3583 | 26.3583 | 39.7137 | 46.8579 | 41.9937 | 27.9706 | 26.3583 | 26.3583 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 12 | 564 | 10.2 | 10.2 | 6.7875 | 1.7118 | 15 | 79 | 79 | 65.4817 | 128.7616 | 17.646 | 167.3434 | 0 | 0 | 28.7968 | 60.2945 | 56.4724 | 19.5696 | 0 | 0 | 18.2384 | 60.1872 | 60.1872 | 102.1443 | 148.0364 | 142.4677 | 88.7002 | 60.1872 | 60.1872 | 128.7616 | 60.1872 | 60.1872 | 130.9411 | 208.3308 | 198.9401 | 108.2697 | 60.1872 | 60.1872 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 13 | 565 | 9.7 | 9.7 | 6.7875 | 1.7118 | 15 | 79 | 79 | 244.3982 | 145.4189 | 18.4862 | 182.1998 | 0 | 0 | 51.0297 | 196.766 | 227.2394 | 124.5991 | 0 | 0 | 76.5811 | 76.4689 | 76.4689 | 102.8993 | 178.3821 | 194.1655 | 141.0038 | 76.4689 | 76.4689 | 145.4189 | 76.4689 | 76.4689 | 153.929 | 375.1481 | 421.4049 | 265.6029 | 76.4689 | 76.4689 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 14 | 566 | 10.3 | 10.3 | 6.7875 | 1.7118 | 15 | 75 | 75 | 91.6761 | 146.6718 | 16.9513 | 196.9658 | 0 | 0 | 0 | 59.0747 | 86.8816 | 63.7944 | 3.3373 | 0 | 28.3282 | 69.9967 | 69.9967 | 69.9967 | 123.7474 | 149.0483 | 128.0418 | 73.0333 | 69.9967 | 146.6718 | 69.9967 | 69.9967 | 69.9967 | 182.8221 | 235.9298 | 191.8362 | 76.3706 | 69.9967 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 15 | 567 | 9.7 | 9.7 | 6.7875 | 1.7118 | 15 | 78 | 78 | 36.9713 | 115.1732 | 13.1983 | 211.0954 | 0 | 0 | 0 | 16.6215 | 33.8259 | 31.2155 | 10.3196 | 0 | 9.8268 | 55.2044 | 55.2044 | 55.2044 | 81.958 | 109.6498 | 105.4483 | 71.8146 | 55.2044 | 115.1732 | 55.2044 | 55.2044 | 55.2044 | 98.5795 | 143.4757 | 136.6638 | 82.1341 | 55.2044 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 16 | 568 | 9.4 | 9.4 | 6.7875 | 1.7118 | 15 | 78 | 78 | 16.7827 | 71.8671 | 7.5663 | 224.2935 | 0 | 0 | 0 | 3.9265 | 13.9916 | 15.8606 | 8.4387 | 0 | 3.1329 | 35.3825 | 35.3825 | 35.3825 | 43.4084 | 63.9821 | 67.8025 | 52.6317 | 35.3825 | 71.8671 | 35.3825 | 35.3825 | 35.3825 | 47.3349 | 77.9737 | 83.6631 | 61.0704 | 35.3825 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 17 | 569 | 8.8 | 8.8 | 6.7875 | 1.7118 | 15 | 79 | 79 | 95.352 | 36.6539 | 0.46987 | 236.5677 | 0 | 0 | 0 | 1.1655 | 67.6561 | 94.5146 | 66.0078 | 0 | 7.3461 | 20.1215 | 20.1215 | 20.1215 | 20.9862 | 70.3165 | 90.2432 | 69.0936 | 20.1215 | 36.6539 | 20.1215 | 20.1215 | 20.1215 | 22.1517 | 137.9725 | 184.7578 | 135.1014 | 20.1215 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 24 | 18 | 570 | 7.6 | 7.6 | 6.7875 | 1.7118 | 15 | 81 | 81 | 0 | 3 | -7.6824 | 248.1601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 3 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 1.406 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 19 | 571 | 6.5 | 6.5 | 6.7875 | 1.7118 | 15 | 86 | 86 | 0 | 0 | -16.5173 | 259.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 20 | 572 | 6.4 | 6.4 | 6.7875 | 1.7118 | 15 | 86 | 86 | 0 | 0 | -25.6838 | 271.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 21 | 573 | 6.1 | 6.1 | 6.7875 | 1.7118 | 15 | 86 | 86 | 0 | 0 | -34.8074 | 283.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 22 | 574 | 5 | 5 | 6.7875 | 1.7118 | 15 | 90 | 90 | 0 | 0 | -43.4076 | 298.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 23 | 575 | 4.6 | 4.6 | 6.7875 | 1.7118 | 15 | 92 | 92 | 0 | 0 | -50.7661 | 315.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 24 | 24 | 576 | 4 | 4 | 8.7167 | 3.8785 | 15 | 93 | 93 | 0 | 0 | -55.7939 | 338.1972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 1 | 577 | 3 | 3 | 8.7167 | 3.8785 | 15 | 95 | 95 | 0 | 0 | -57.242 | 3.8576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 2 | 578 | 3.3 | 3.3 | 8.7167 | 3.8785 | 15 | 94 | 94 | 0 | 0 | -54.4229 | 28.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 3 | 579 | 3.2 | 3.2 | 8.7167 | 3.8785 | 15 | 93 | 93 | 0 | 0 | -48.6039 | 49.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 4 | 580 | 3.5 | 3.5 | 8.7167 | 3.8785 | 15 | 92 | 92 | 0 | 0 | -40.8056 | 66.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 5 | 581 | 4.1 | 4.1 | 8.7167 | 3.8785 | 15 | 92 | 92 | 0 | 0 | -32.0013 | 80.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 6 | 582 | 5.4 | 5.4 | 8.7167 | 3.8785 | 15 | 89 | 89 | 0 | 0 | -22.8243 | 92.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 7 | 583 | 5.8 | 5.8 | 8.7167 | 3.8785 | 15 | 89 | 89 | 0 | 0 | -13.7142 | 103.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 25 | 8 | 584 | 6.1 | 6.1 | 8.7167 | 3.8785 | 15 | 91 | 91 | 0 | 0 | -5.0332 | 115.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 9 | 585 | 6.4 | 6.4 | 8.7167 | 3.8785 | 15 | 90 | 90 | 0 | 0 | 2.8632 | 126.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 10 | 586 | 7.1 | 7.1 | 8.7167 | 3.8785 | 15 | 87 | 87 | 1.0906 | 13.8832 | 9.5898 | 139.3395 | 0 | 0.15553 | 0.87232 | 1.0781 | 0.65236 | 0 | 0 | 0 | 0.11676 | 6.758 | 6.758 | 6.758 | 6.758 | 6.758 | 6.758 | 6.758 | 6.758 | 13.8832 | 6.758 | 6.9136 | 7.6304 | 7.8362 | 7.4104 | 6.758 | 6.758 | 6.758 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 11 | 587 | 7.8 | 7.8 | 8.7167 | 3.8785 | 15 | 85 | 85 | 18.1462 | 82.1765 | 14.7287 | 152.8497 | 0 | 0 | 11.6584 | 17.8413 | 13.573 | 1.3539 | 0 | 0 | 3.8235 | 36.3768 | 36.3768 | 88.8235 | 116.6381 | 97.4367 | 42.4672 | 36.3768 | 36.3768 | 82.1765 | 36.3768 | 36.3768 | 100.4819 | 134.4794 | 111.0098 | 43.8211 | 36.3768 | 36.3768 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 12 | 588 | 7.8 | 7.8 | 8.7167 | 3.8785 | 15 | 87 | 87 | 5.509 | 81.4442 | 17.8741 | 167.2455 | 0 | 0 | 2.4313 | 5.0715 | 4.7409 | 1.6331 | 0 | 0 | 1.5558 | 39.3827 | 39.3827 | 44.9922 | 51.0837 | 50.3209 | 43.1506 | 39.3827 | 39.3827 | 81.4442 | 39.3827 | 39.3827 | 47.4235 | 56.1552 | 55.0618 | 44.7838 | 39.3827 | 39.3827 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 13 | 589 | 8 | 8 | 8.7167 | 3.8785 | 15 | 85 | 85 | 5.0184 | 87.4077 | 18.7268 | 182.1431 | 0 | 0 | 1.0545 | 4.0396 | 4.6584 | 2.5483 | 0 | 0 | 1.5923 | 43.1034 | 43.1034 | 43.923 | 46.2432 | 46.7242 | 45.0841 | 43.1034 | 43.1034 | 87.4077 | 43.1034 | 43.1034 | 44.9774 | 50.2828 | 51.3825 | 47.6325 | 43.1034 | 43.1034 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 14 | 590 | 7.4 | 7.4 | 8.7167 | 3.8785 | 15 | 91 | 91 | 1.6282 | 49.4905 | 17.1974 | 196.9521 | 0 | 0 | 0 | 1.0488 | 1.541 | 1.1304 | 0.057666 | 0 | 0.50953 | 23.9006 | 23.9006 | 23.9006 | 23.9006 | 23.9006 | 23.9006 | 23.9006 | 23.9006 | 49.4905 | 23.9006 | 23.9006 | 23.9006 | 24.9495 | 25.4416 | 25.031 | 23.9583 | 23.9006 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 15 | 591 | 7.2 | 7.2 | 8.7167 | 3.8785 | 15 | 95 | 95 | 1.698 | 43.5421 | 13.4435 | 211.1203 | 0 | 0 | 0 | 0.76273 | 1.5516 | 1.4316 | 0.47296 | 0 | 0.4579 | 20.9679 | 20.9679 | 20.9679 | 20.9679 | 20.9679 | 20.9679 | 20.9679 | 20.9679 | 43.5421 | 20.9679 | 20.9679 | 20.9679 | 21.7306 | 22.5195 | 22.3995 | 21.4408 | 20.9679 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 16 | 592 | 7.1 | 7.1 | 8.7167 | 3.8785 | 15 | 94 | 94 | 1.3789 | 27.7374 | 7.8064 | 224.3496 | 0 | 0 | 0 | 0.32172 | 1.1481 | 1.302 | 0.69315 | 0 | 0.26259 | 13.2194 | 13.2194 | 13.2194 | 13.2194 | 13.2194 | 13.2194 | 13.2194 | 13.2194 | 27.7374 | 13.2194 | 13.2194 | 13.2194 | 13.5411 | 14.3675 | 14.5214 | 13.9126 | 13.2194 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 17 | 593 | 6.8 | 6.8 | 8.7167 | 3.8785 | 15 | 94 | 94 | 6.1308 | 24.5056 | 0.70302 | 236.6476 | 0 | 0 | 0 | 0.068944 | 4.3434 | 6.0736 | 4.2459 | 0 | 0.49436 | 11.8354 | 11.8354 | 11.8354 | 11.8354 | 11.8354 | 11.8354 | 11.8354 | 11.8354 | 24.5056 | 11.8354 | 11.8354 | 11.8354 | 11.9043 | 16.1788 | 17.909 | 16.0813 | 11.8354 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 25 | 18 | 594 | 5.7 | 5.7 | 8.7167 | 3.8785 | 15 | 95 | 95 | 0 | 6 | -7.4558 | 248.2579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 6 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 2.8758 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 19 | 595 | 5.5 | 5.5 | 8.7167 | 3.8785 | 15 | 97 | 97 | 0 | 0 | -16.2954 | 259.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 20 | 596 | 4.9 | 4.9 | 8.7167 | 3.8785 | 15 | 97 | 97 | 0 | 0 | -25.4634 | 271.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 21 | 597 | 4.3 | 4.3 | 8.7167 | 3.8785 | 15 | 97 | 97 | 0 | 0 | -34.5844 | 283.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 22 | 598 | 4 | 4 | 8.7167 | 3.8785 | 15 | 97 | 97 | 0 | 0 | -43.1776 | 298.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 23 | 599 | 4.1 | 4.1 | 8.7167 | 3.8785 | 15 | 96 | 96 | 0 | 0 | -50.5258 | 316.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 25 | 24 | 600 | 4.1 | 4.1 | 5.525 | 4.6713 | 15 | 95 | 95 | 0 | 0 | -55.5475 | 338.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 1 | 601 | 3.2 | 3.2 | 5.525 | 4.6713 | 15 | 96 | 96 | 0 | 0 | -57.0056 | 3.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 2 | 602 | 3.4 | 3.4 | 5.525 | 4.6713 | 15 | 96 | 96 | 0 | 0 | -54.2076 | 28.3812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 3 | 603 | 3.4 | 3.4 | 5.525 | 4.6713 | 15 | 94 | 94 | 0 | 0 | -48.4187 | 49.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 4 | 604 | 3.2 | 3.2 | 5.525 | 4.6713 | 15 | 94 | 94 | 0 | 0 | -40.6422 | 65.9468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 5 | 605 | 2.8 | 2.8 | 5.525 | 4.6713 | 15 | 95 | 95 | 0 | 0 | -31.8493 | 79.7988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 6 | 606 | 3 | 3 | 5.525 | 4.6713 | 15 | 96 | 96 | 0 | 0 | -22.6748 | 92.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 7 | 607 | 4.2 | 4.2 | 5.525 | 4.6713 | 15 | 94 | 94 | 0 | 0 | -13.5601 | 103.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 26 | 8 | 608 | 4.5 | 4.5 | 5.525 | 4.6713 | 15 | 93 | 93 | 0 | 0 | -4.8687 | 114.8279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 9 | 609 | 4.6 | 4.6 | 5.525 | 4.6713 | 15 | 93 | 93 | 0 | 0 | 3.0428 | 126.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 10 | 610 | 5 | 5 | 5.525 | 4.6713 | 15 | 91 | 91 | 1.5023 | 16.8336 | 9.7876 | 139.1819 | 0 | 0.21877 | 1.2042 | 1.4842 | 0.89476 | 0 | 0 | 0 | 0.16643 | 8.2766 | 8.2766 | 8.2766 | 8.2766 | 8.2766 | 8.2766 | 8.2766 | 8.2766 | 16.8336 | 8.2766 | 8.4954 | 9.4807 | 9.7608 | 9.1714 | 8.2766 | 8.2766 | 8.2766 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 11 | 611 | 5.4 | 5.4 | 5.525 | 4.6713 | 15 | 89 | 89 | 2.6823 | 43.4244 | 14.9458 | 152.7182 | 0 | 0 | 1.7278 | 2.6363 | 2.0004 | 0.19276 | 0 | 0 | 0.57558 | 21.3897 | 21.3897 | 21.3897 | 21.3897 | 21.3897 | 21.3897 | 21.3897 | 21.3897 | 43.4244 | 21.3897 | 21.3897 | 23.1175 | 24.0259 | 23.3901 | 21.5824 | 21.3897 | 21.3897 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 12 | 612 | 5.8 | 5.8 | 5.525 | 4.6713 | 15 | 83 | 83 | 8.0416 | 94.6969 | 18.1084 | 167.1494 | 0 | 0 | 3.5613 | 7.401 | 6.9053 | 2.3645 | 0 | 0 | 2.3031 | 44.7154 | 44.7154 | 56.986 | 70.2158 | 68.5078 | 52.8625 | 44.7154 | 44.7154 | 94.6969 | 44.7154 | 44.7154 | 60.5472 | 77.6168 | 75.4131 | 55.2271 | 44.7154 | 44.7154 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 13 | 613 | 5.7 | 5.7 | 5.525 | 4.6713 | 15 | 85 | 85 | 1.09 | 41.6498 | 18.9731 | 182.0894 | 0 | 0 | 0.23042 | 0.87715 | 1.0101 | 0.55129 | 0 | 0 | 0.35023 | 19.9912 | 19.9912 | 19.9912 | 19.9912 | 19.9912 | 19.9912 | 19.9912 | 19.9912 | 41.6498 | 19.9912 | 19.9912 | 20.2216 | 20.8683 | 21.0012 | 20.5424 | 19.9912 | 19.9912 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 14 | 614 | 5 | 5 | 5.525 | 4.6713 | 15 | 94 | 94 | 0.49785 | 27.8422 | 17.4488 | 196.9423 | 0 | 0 | 0 | 0.32055 | 0.47049 | 0.34482 | 0.017164 | 0 | 0.1578 | 13.1937 | 13.1937 | 13.1937 | 13.1937 | 13.1937 | 13.1937 | 13.1937 | 13.1937 | 27.8422 | 13.1937 | 13.1937 | 13.1937 | 13.5142 | 13.6641 | 13.5385 | 13.2108 | 13.1937 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 15 | 615 | 5.7 | 5.7 | 5.525 | 4.6713 | 15 | 89 | 89 | 1.296 | 38.6454 | 13.6934 | 211.15 | 0 | 0 | 0 | 0.58154 | 1.1827 | 1.0911 | 0.36029 | 0 | 0.35462 | 18.5182 | 18.5182 | 18.5182 | 18.5182 | 18.5182 | 18.5182 | 18.5182 | 18.5182 | 38.6454 | 18.5182 | 18.5182 | 18.5182 | 19.0997 | 19.7009 | 19.6093 | 18.8785 | 18.5182 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 16 | 616 | 6.1 | 6.1 | 5.525 | 4.6713 | 15 | 88 | 88 | 3.2725 | 43.3643 | 8.0504 | 224.411 | 0 | 0 | 0 | 0.7611 | 2.721 | 3.087 | 1.6447 | 0 | 0.63575 | 21.0428 | 21.0428 | 21.0428 | 21.0428 | 21.0428 | 21.0428 | 21.0428 | 21.0428 | 43.3643 | 21.0428 | 21.0428 | 21.0428 | 21.8039 | 23.7638 | 24.1298 | 22.6875 | 21.0428 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 17 | 617 | 6 | 6 | 5.525 | 4.6713 | 15 | 86 | 86 | 14.8181 | 31.7506 | 0.93959 | 236.733 | 0 | 0 | 0 | 0.15083 | 10.4808 | 14.6713 | 10.2675 | 0 | 1.2494 | 16.2595 | 16.2595 | 16.2595 | 16.396 | 25.75 | 29.5445 | 25.5568 | 16.2595 | 31.7506 | 16.2595 | 16.2595 | 16.2595 | 16.5469 | 36.2308 | 44.2157 | 35.8243 | 16.2595 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 26 | 18 | 618 | 5.8 | 5.8 | 5.525 | 4.6713 | 15 | 83 | 83 | 0 | 0 | -7.2263 | 248.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 19 | 619 | 5.7 | 5.7 | 5.525 | 4.6713 | 15 | 84 | 84 | 0 | 0 | -16.0707 | 259.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 20 | 620 | 4.4 | 4.4 | 5.525 | 4.6713 | 15 | 88 | 88 | 0 | 0 | -25.2403 | 271.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 21 | 621 | 4.1 | 4.1 | 5.525 | 4.6713 | 15 | 89 | 89 | 0 | 0 | -34.3585 | 283.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 22 | 622 | 3.2 | 3.2 | 5.525 | 4.6713 | 15 | 92 | 92 | 0 | 0 | -42.9441 | 298.3627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 23 | 623 | 3.6 | 3.6 | 5.525 | 4.6713 | 15 | 92 | 92 | 0 | 0 | -50.2815 | 316.1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 26 | 24 | 624 | 3.2 | 3.2 | 4.4583 | 4.877 | 15 | 91 | 91 | 0 | 0 | -55.296 | 338.2042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 1 | 625 | 3.5 | 3.5 | 4.4583 | 4.877 | 15 | 89 | 89 | 0 | 0 | -56.7632 | 3.6065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 2 | 626 | 3.7 | 3.7 | 4.4583 | 4.877 | 15 | 87 | 87 | 0 | 0 | -53.9855 | 28.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 3 | 627 | 3.8 | 3.8 | 4.4583 | 4.877 | 15 | 87 | 87 | 0 | 0 | -48.2265 | 48.9672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 4 | 628 | 3.8 | 3.8 | 4.4583 | 4.877 | 15 | 89 | 89 | 0 | 0 | -40.472 | 65.6943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 5 | 629 | 3.6 | 3.6 | 4.4583 | 4.877 | 15 | 93 | 93 | 0 | 0 | -31.6906 | 79.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 6 | 630 | 3.7 | 3.7 | 4.4583 | 4.877 | 15 | 95 | 95 | 0 | 0 | -22.5189 | 91.7796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 7 | 631 | 3.8 | 3.8 | 4.4583 | 4.877 | 15 | 95 | 95 | 0 | 0 | -13.3996 | 103.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 27 | 8 | 632 | 3.8 | 3.8 | 4.4583 | 4.877 | 15 | 94 | 94 | 0 | 0 | -4.6979 | 114.6359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 9 | 633 | 3.6 | 3.6 | 4.4583 | 4.877 | 15 | 95 | 95 | 0 | 0 | 3.2287 | 126.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 10 | 634 | 3.3 | 3.3 | 4.4583 | 4.877 | 15 | 94 | 94 | 0.17496 | 5.98 | 9.9918 | 139.0242 | 0 | 0.026008 | 0.14053 | 0.17274 | 0.10375 | 0 | 0 | 0 | 0.020048 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 5.98 | 2.8045 | 2.8305 | 2.945 | 2.9772 | 2.9082 | 2.8045 | 2.8045 | 2.8045 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 11 | 635 | 3.2 | 3.2 | 4.4583 | 4.877 | 15 | 95 | 95 | 0.64666 | 21.8587 | 15.1691 | 152.5876 | 0 | 0 | 0.41761 | 0.63528 | 0.48081 | 0.044693 | 0 | 0 | 0.14132 | 10.4012 | 10.4012 | 10.4012 | 10.4012 | 10.4012 | 10.4012 | 10.4012 | 10.4012 | 21.8587 | 10.4012 | 10.4012 | 10.8188 | 11.0365 | 10.882 | 10.4459 | 10.4012 | 10.4012 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 12 | 636 | 3.3 | 3.3 | 4.4583 | 4.877 | 15 | 96 | 96 | 1.3342 | 41.6125 | 18.3488 | 167.055 | 0 | 0 | 0.59285 | 1.2275 | 1.1431 | 0.3891 | 0 | 0 | 0.38753 | 20.0662 | 20.0662 | 20.0662 | 20.0662 | 20.0662 | 20.0662 | 20.0662 | 20.0662 | 41.6125 | 20.0662 | 20.0662 | 20.659 | 21.2937 | 21.2093 | 20.4553 | 20.0662 | 20.0662 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 13 | 637 | 4.3 | 4.3 | 4.4583 | 4.877 | 15 | 93 | 93 | 2.7047 | 66.1198 | 19.2251 | 182.0386 | 0 | 0 | 0.57508 | 2.1758 | 2.5019 | 1.3625 | 0 | 0 | 0.8802 | 32.4119 | 32.4119 | 32.4119 | 32.4119 | 32.4119 | 32.4119 | 32.4119 | 32.4119 | 66.1198 | 32.4119 | 32.4119 | 32.987 | 34.5877 | 34.9138 | 33.7744 | 32.4119 | 32.4119 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 14 | 638 | 4.3 | 4.3 | 4.4583 | 4.877 | 15 | 95 | 95 | 1.1984 | 43.6152 | 17.7052 | 196.9365 | 0 | 0 | 0 | 0.77115 | 1.1308 | 0.82807 | 0.040251 | 0 | 0.38477 | 20.9447 | 20.9447 | 20.9447 | 20.9447 | 20.9447 | 20.9447 | 20.9447 | 20.9447 | 43.6152 | 20.9447 | 20.9447 | 20.9447 | 21.7159 | 22.0755 | 21.7728 | 20.985 | 20.9447 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 15 | 639 | 5.6 | 5.6 | 4.4583 | 4.877 | 15 | 82 | 82 | 23.1906 | 112.5606 | 13.9477 | 211.1844 | 0 | 0 | 0 | 10.3932 | 21.134 | 19.4947 | 6.4357 | 0 | 6.4394 | 54.0211 | 54.0211 | 54.0211 | 77.9253 | 102.6287 | 98.8584 | 68.8231 | 54.0211 | 112.5606 | 54.0211 | 54.0211 | 54.0211 | 88.3185 | 123.7626 | 118.3531 | 75.2588 | 54.0211 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 16 | 640 | 5.1 | 5.1 | 4.4583 | 4.877 | 15 | 88 | 88 | 15.2257 | 74.9822 | 8.2983 | 224.4776 | 0 | 0 | 0 | 3.5287 | 12.6416 | 14.3492 | 7.6513 | 0 | 3.0178 | 36.5806 | 36.5806 | 36.5806 | 38.9158 | 44.9465 | 46.0765 | 41.644 | 36.5806 | 74.9822 | 36.5806 | 36.5806 | 36.5806 | 42.4444 | 57.588 | 60.4258 | 49.2953 | 36.5806 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 17 | 641 | 5 | 5 | 4.4583 | 4.877 | 15 | 89 | 89 | 9.2862 | 30.1821 | 1.1795 | 236.8239 | 0 | 0 | 0 | 0.083778 | 6.5565 | 9.1886 | 6.4381 | 0 | 0.81794 | 15.4974 | 15.4974 | 15.4974 | 15.599 | 23.4506 | 26.6432 | 23.3068 | 15.4974 | 30.1821 | 15.4974 | 15.4974 | 15.4974 | 15.6828 | 30.0071 | 35.8318 | 29.7449 | 15.4974 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 18 | 642 | 4.5 | 4.5 | 4.4583 | 4.877 | 15 | 88 | 88 | 0 | 6 | -6.9937 | 248.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 6 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 2.8577 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 19 | 643 | 4.3 | 4.3 | 4.4583 | 4.877 | 15 | 90 | 90 | 0 | 0 | -15.8433 | 259.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 20 | 644 | 4.1 | 4.1 | 4.4583 | 4.877 | 15 | 92 | 92 | 0 | 0 | -25.0144 | 271.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 21 | 645 | 3.9 | 3.9 | 4.4583 | 4.877 | 15 | 94 | 94 | 0 | 0 | -34.1298 | 283.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 22 | 646 | 4.8 | 4.8 | 4.4583 | 4.877 | 15 | 90 | 90 | 0 | 0 | -42.7074 | 298.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 23 | 647 | 4.5 | 4.5 | 4.4583 | 4.877 | 15 | 93 | 93 | 0 | 0 | -50.0332 | 316.2299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 27 | 24 | 648 | 4.6 | 4.6 | 4.0875 | 4.95 | 15 | 92 | 92 | 0 | 0 | -55.0396 | 338.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 1 | 649 | 5 | 5 | 4.0875 | 4.95 | 15 | 89 | 89 | 0 | 0 | -56.5147 | 3.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 2 | 650 | 4.2 | 4.2 | 4.0875 | 4.95 | 15 | 89 | 89 | 0 | 0 | -53.7567 | 27.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 3 | 651 | 3 | 3 | 4.0875 | 4.95 | 15 | 92 | 92 | 0 | 0 | -48.0275 | 48.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 4 | 652 | 2.4 | 2.4 | 4.0875 | 4.95 | 15 | 94 | 94 | 0 | 0 | -40.2949 | 65.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 5 | 653 | 2.4 | 2.4 | 4.0875 | 4.95 | 15 | 94 | 94 | 0 | 0 | -31.5253 | 79.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 6 | 654 | 2.3 | 2.3 | 4.0875 | 4.95 | 15 | 96 | 96 | 0 | 0 | -22.3564 | 91.5579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 7 | 655 | 1.9 | 1.9 | 4.0875 | 4.95 | 15 | 95 | 95 | 0 | 0 | -13.2328 | 103.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 28 | 8 | 656 | 1.5 | 1.5 | 4.0875 | 4.95 | 15 | 96 | 96 | 0 | 0 | -4.5207 | 114.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 9 | 657 | 1.5 | 1.5 | 4.0875 | 4.95 | 15 | 97 | 97 | 0 | 0 | 3.4209 | 126.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 10 | 658 | 2.7 | 2.7 | 4.0875 | 4.95 | 15 | 96 | 96 | 28.8311 | 49.5842 | 10.2022 | 138.8665 | 0 | 4.3731 | 23.2063 | 28.4456 | 17.0218 | 0 | 0 | 0 | 3.4158 | 21.6061 | 41.1091 | 125.1007 | 148.4666 | 97.5193 | 21.6061 | 21.6061 | 21.6061 | 49.5842 | 21.6061 | 45.4822 | 148.307 | 176.9122 | 114.5412 | 21.6061 | 21.6061 | 21.6061 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 11 | 659 | 4.9 | 4.9 | 4.0875 | 4.95 | 15 | 90 | 90 | 183.1064 | 106.243 | 15.3986 | 152.4577 | 0 | 0 | 118.5457 | 179.8011 | 135.7314 | 12.1521 | 0 | 0 | 40.757 | 51.9772 | 51.9772 | 142.2729 | 188.9308 | 155.3631 | 61.2334 | 51.9772 | 51.9772 | 106.243 | 51.9772 | 51.9772 | 260.8186 | 368.7319 | 291.0946 | 73.3855 | 51.9772 | 51.9772 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 12 | 660 | 5.8 | 5.8 | 4.0875 | 4.95 | 15 | 85 | 85 | 392.0735 | 120.4891 | 18.5951 | 166.9624 | 0 | 0 | 174.788 | 360.5876 | 335.1599 | 113.4001 | 0 | 0 | 115.5109 | 69.3051 | 69.3051 | 118.8003 | 171.4138 | 164.2134 | 101.417 | 69.3051 | 69.3051 | 120.4891 | 69.3051 | 69.3051 | 293.5883 | 532.0014 | 499.3733 | 214.8171 | 69.3051 | 69.3051 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 13 | 661 | 6.1 | 6.1 | 4.0875 | 4.95 | 15 | 85 | 85 | 53.7956 | 149.2667 | 19.4826 | 181.9907 | 0 | 0 | 11.5022 | 43.2573 | 49.6729 | 26.9908 | 0 | 0 | 17.7333 | 69.9595 | 69.9595 | 88.2615 | 138.7896 | 148.9979 | 112.9066 | 69.9595 | 69.9595 | 149.2667 | 69.9595 | 69.9595 | 99.7637 | 182.0469 | 198.6708 | 139.8974 | 69.9595 | 69.9595 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 14 | 662 | 6.7 | 6.7 | 4.0875 | 4.95 | 15 | 88 | 88 | 25.4809 | 133.7117 | 17.9667 | 196.9348 | 0 | 0 | 0 | 16.3858 | 24.0075 | 17.5659 | 0.83448 | 0 | 8.2883 | 62.6014 | 62.6014 | 62.6014 | 89.1617 | 101.5159 | 91.0746 | 63.9541 | 62.6014 | 133.7117 | 62.6014 | 62.6014 | 62.6014 | 105.5474 | 125.5234 | 108.6405 | 64.7885 | 62.6014 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 15 | 663 | 6.2 | 6.2 | 4.0875 | 4.95 | 15 | 86 | 86 | 532.4661 | 96.9464 | 14.2064 | 211.2237 | 0 | 0 | 0 | 238.2964 | 484.5373 | 446.9429 | 147.5354 | 0 | 150.0536 | 63.1424 | 63.1424 | 63.1424 | 109.9859 | 158.391 | 151.0009 | 92.1444 | 63.1424 | 96.9464 | 63.1424 | 63.1424 | 63.1424 | 348.2822 | 642.9284 | 597.9437 | 239.6798 | 63.1424 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 16 | 664 | 5.4 | 5.4 | 4.0875 | 4.95 | 15 | 95 | 95 | 2.0229 | 35.5909 | 8.55 | 224.5495 | 0 | 0 | 0 | 0.46699 | 1.677 | 1.9046 | 1.0166 | 0 | 0.40907 | 17.0952 | 17.0952 | 17.0952 | 17.0952 | 17.0952 | 17.0952 | 17.0952 | 17.0952 | 35.5909 | 17.0952 | 17.0952 | 17.0952 | 17.5622 | 18.7722 | 18.9998 | 18.1117 | 17.0952 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 17 | 665 | 5.5 | 5.5 | 4.0875 | 4.95 | 15 | 93 | 93 | 7.9293 | 30.2711 | 1.4226 | 236.9203 | 0 | 0 | 0 | 0.061655 | 5.588 | 7.8409 | 5.5008 | 0 | 0.72895 | 15.5524 | 15.5524 | 15.5524 | 15.6361 | 23.1341 | 26.1908 | 23.0158 | 15.5524 | 30.2711 | 15.5524 | 15.5524 | 15.5524 | 15.6977 | 28.722 | 34.0318 | 28.5165 | 15.5524 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 18 | 666 | 5 | 5 | 4.0875 | 4.95 | 15 | 94 | 94 | 0 | 0 | -6.7584 | 248.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 19 | 667 | 3.8 | 3.8 | 4.0875 | 4.95 | 15 | 96 | 96 | 0 | 0 | -15.6132 | 259.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 20 | 668 | 3.6 | 3.6 | 4.0875 | 4.95 | 15 | 97 | 97 | 0 | 0 | -24.786 | 271.5639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 21 | 669 | 3.4 | 3.4 | 4.0875 | 4.95 | 15 | 98 | 98 | 0 | 0 | -33.8983 | 284.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 22 | 670 | 4.2 | 4.2 | 4.0875 | 4.95 | 15 | 99 | 99 | 0 | 0 | -42.4675 | 298.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 23 | 671 | 4 | 4 | 4.0875 | 4.95 | 15 | 99 | 99 | 0 | 0 | -49.7811 | 316.3375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 28 | 24 | 672 | 4.2 | 4.2 | 3.9875 | 4.9337 | 15 | 99 | 99 | 0 | 0 | -54.7784 | 338.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 1 | 673 | 4.1 | 4.1 | 3.9875 | 4.9337 | 15 | 99 | 99 | 0 | 0 | -56.2604 | 3.3803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 2 | 674 | 3.8 | 3.8 | 3.9875 | 4.9337 | 15 | 99 | 99 | 0 | 0 | -53.5214 | 27.7367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 3 | 675 | 3.4 | 3.4 | 3.9875 | 4.9337 | 15 | 99 | 99 | 0 | 0 | -47.8216 | 48.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 4 | 676 | 3.7 | 3.7 | 3.9875 | 4.9337 | 15 | 99 | 99 | 0 | 0 | -40.1111 | 65.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 5 | 677 | 3.6 | 3.6 | 3.9875 | 4.9337 | 15 | 95 | 95 | 0 | 0 | -31.3535 | 79.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 6 | 678 | 3 | 3 | 3.9875 | 4.9337 | 15 | 95 | 95 | 0 | 0 | -22.1876 | 91.3353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 7 | 679 | 1.2 | 1.2 | 3.9875 | 4.9337 | 15 | 95 | 95 | 0 | 0 | -13.0596 | 102.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 29 | 8 | 680 | 0 | 0 | 3.9875 | 4.9337 | 15 | 98 | 98 | 0 | 0 | -4.3373 | 114.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 9 | 681 | -1 | -1 | 3.9875 | 4.9337 | 15 | 98 | 98 | 0 | 3 | 3.6193 | 126.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 10 | 682 | 0.3 | 0.3 | 3.9875 | 4.9337 | 15 | 99 | 99 | 62.758 | 56.3156 | 10.4188 | 138.7089 | 0 | 9.7095 | 50.6183 | 61.8757 | 36.8871 | 0 | 0 | 0 | 7.6844 | 24.7598 | 49.3666 | 153.0426 | 181.5722 | 118.2432 | 24.7598 | 24.7598 | 24.7598 | 56.3156 | 24.7598 | 59.0761 | 203.6609 | 243.4479 | 155.1303 | 24.7598 | 24.7598 | 24.7598 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 11 | 683 | 2.5 | 2.5 | 3.9875 | 4.9337 | 15 | 99 | 99 | 200.7996 | 107.4756 | 15.6343 | 152.3287 | 0 | 0 | 130.3199 | 197.0753 | 148.3866 | 12.775 | 0 | 0 | 45.5244 | 53.0702 | 53.0702 | 142.7092 | 188.6261 | 155.1362 | 61.8573 | 53.0702 | 53.0702 | 107.4756 | 53.0702 | 53.0702 | 273.0292 | 385.7014 | 303.5227 | 74.6324 | 53.0702 | 53.0702 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 12 | 684 | 5.2 | 5.2 | 3.9875 | 4.9337 | 15 | 77 | 77 | 598.5307 | 93.1269 | 18.8473 | 166.8718 | 0 | 0 | 267.6732 | 550.225 | 510.4624 | 171.6779 | 0 | 0 | 178.8731 | 63.0057 | 63.0057 | 106.93 | 153.2958 | 146.7709 | 91.1775 | 63.0057 | 63.0057 | 93.1269 | 63.0057 | 63.0057 | 374.6032 | 703.5208 | 657.2333 | 262.8553 | 63.0057 | 63.0057 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 13 | 685 | 5.5 | 5.5 | 3.9875 | 4.9337 | 15 | 66 | 66 | 511.4554 | 118.2073 | 19.7457 | 181.946 | 0 | 0 | 109.9386 | 411.0558 | 471.3822 | 255.5792 | 0 | 0 | 170.7927 | 74.4306 | 74.4306 | 99.0941 | 166.6463 | 180.1798 | 131.7669 | 74.4306 | 74.4306 | 118.2073 | 74.4306 | 74.4306 | 209.0327 | 577.7021 | 651.5619 | 387.3461 | 74.4306 | 74.4306 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 14 | 686 | 5.7 | 5.7 | 3.9875 | 4.9337 | 15 | 66 | 66 | 533.6357 | 113.1353 | 18.2331 | 196.9372 | 0 | 0 | 0 | 342.8857 | 501.969 | 367.0058 | 17.0555 | 0 | 175.8647 | 72.8139 | 72.8139 | 72.8139 | 145.0492 | 178.5632 | 150.1306 | 76.4069 | 72.8139 | 113.1353 | 72.8139 | 72.8139 | 72.8139 | 487.9349 | 680.5322 | 517.1364 | 93.4624 | 72.8139 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 15 | 687 | 5.8 | 5.8 | 3.9875 | 4.9337 | 15 | 64 | 64 | 112.0497 | 136.9507 | 14.4694 | 211.2678 | 0 | 0 | 0 | 50.066 | 101.8077 | 93.9119 | 31.0037 | 0 | 32.0493 | 67.2097 | 67.2097 | 67.2097 | 112.8959 | 160.1112 | 152.9061 | 95.5012 | 67.2097 | 136.9507 | 67.2097 | 67.2097 | 67.2097 | 162.9618 | 261.9189 | 246.818 | 126.505 | 67.2097 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 16 | 688 | 5.5 | 5.5 | 3.9875 | 4.9337 | 15 | 68 | 68 | 24.0186 | 84.0446 | 8.8052 | 224.6266 | 0 | 0 | 0 | 5.5208 | 19.8787 | 22.592 | 12.0711 | 0 | 4.9554 | 41.0899 | 41.0899 | 41.0899 | 50.4632 | 74.8403 | 79.4469 | 61.5845 | 41.0899 | 84.0446 | 41.0899 | 41.0899 | 41.0899 | 55.984 | 94.719 | 102.0388 | 73.6556 | 41.0899 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 17 | 689 | 4.1 | 4.1 | 3.9875 | 4.9337 | 15 | 78 | 78 | 17.93 | 37.2812 | 1.6688 | 237.0221 | 0 | 0 | 0 | 0.11547 | 12.6104 | 17.7183 | 12.4471 | 0 | 1.7188 | 18.9792 | 18.9792 | 18.9792 | 19.086 | 30.6391 | 35.362 | 30.4881 | 18.9792 | 37.2812 | 18.9792 | 18.9792 | 18.9792 | 19.2015 | 43.2495 | 53.0803 | 42.9352 | 18.9792 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 29 | 18 | 690 | 2 | 2 | 3.9875 | 4.9337 | 15 | 85 | 85 | 0 | 3 | -6.5203 | 248.7058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 3 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 1.3957 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 19 | 691 | 0 | 0 | 3.9875 | 4.9337 | 15 | 94 | 94 | 0 | 0 | -15.3807 | 260.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 20 | 692 | -0.6 | -0.6 | 3.9875 | 4.9337 | 15 | 96 | 96 | 0 | 0 | -24.5551 | 271.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 21 | 693 | 0.1 | 0.1 | 3.9875 | 4.9337 | 15 | 98 | 98 | 0 | 0 | -33.664 | 284.2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 22 | 694 | -0.2 | -0.2 | 3.9875 | 4.9337 | 15 | 97 | 97 | 0 | 0 | -42.2245 | 298.7864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 23 | 695 | -0.1 | -0.1 | 3.9875 | 4.9337 | 15 | 98 | 98 | 0 | 0 | -49.5252 | 316.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 29 | 24 | 696 | 0.8 | 0.8 | 2.4333 | 4.3388 | 15 | 96 | 96 | 0 | 0 | -54.5125 | 338.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 1 | 697 | 2 | 2 | 2.4333 | 4.3388 | 15 | 90 | 90 | 0 | 0 | -56.0004 | 3.2766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 2 | 698 | 1.4 | 1.4 | 2.4333 | 4.3388 | 15 | 94 | 94 | 0 | 0 | -53.2797 | 27.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 3 | 699 | 0.2 | 0.2 | 2.4333 | 4.3388 | 15 | 93 | 93 | 0 | 0 | -47.609 | 48.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 4 | 700 | -1.3 | -1.3 | 2.4333 | 4.3388 | 15 | 97 | 97 | 0 | 0 | -39.9206 | 64.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 5 | 701 | -1.8 | -1.8 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -31.1751 | 78.8461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 6 | 702 | -2.4 | -2.4 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -22.0123 | 91.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 7 | 703 | -2.5 | -2.5 | 2.4333 | 4.3388 | 15 | 99 | 99 | 0 | 0 | -12.8802 | 102.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 30 | 8 | 704 | -2.3 | -2.3 | 2.4333 | 4.3388 | 15 | 99 | 99 | 0 | 0 | -4.1476 | 114.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 9 | 705 | -2.5 | -2.5 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 3 | 3.8239 | 125.9034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 10 | 706 | -1.1 | -1.1 | 2.4333 | 4.3388 | 15 | 99 | 99 | 7.5363 | 41.0467 | 10.6415 | 138.5514 | 0 | 1.1888 | 6.0909 | 7.425 | 4.4096 | 0 | 0 | 0 | 0.95332 | 17.3811 | 33.0579 | 97.6993 | 115.2915 | 75.5291 | 17.3811 | 17.3811 | 17.3811 | 41.0467 | 17.3811 | 34.2467 | 103.7902 | 122.7164 | 79.9387 | 17.3811 | 17.3811 | 17.3811 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 11 | 707 | -0.5 | -0.5 | 2.4333 | 4.3388 | 15 | 99 | 99 | 17.9973 | 89.844 | 15.8759 | 152.2005 | 0 | 0 | 11.7084 | 17.6538 | 13.2579 | 1.0956 | 0 | 0 | 4.156 | 39.8841 | 39.8841 | 91.3585 | 117.4968 | 98.1706 | 44.701 | 39.8841 | 39.8841 | 89.844 | 39.8841 | 39.8841 | 103.0669 | 135.1506 | 111.4285 | 45.7966 | 39.8841 | 39.8841 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 12 | 708 | 0.8 | 0.8 | 2.4333 | 4.3388 | 15 | 99 | 99 | 9.0701 | 103.2502 | 19.1053 | 166.7831 | 0 | 0 | 4.0687 | 8.3339 | 7.7172 | 2.5799 | 0 | 0 | 2.7498 | 48.5141 | 48.5141 | 62.735 | 77.6426 | 75.4871 | 57.5312 | 48.5141 | 48.5141 | 103.2502 | 48.5141 | 48.5141 | 66.8038 | 85.9766 | 83.2043 | 60.111 | 48.5141 | 48.5141 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 13 | 709 | 1.9 | 1.9 | 2.4333 | 4.3388 | 15 | 100 | 100 | 7.2566 | 108.545 | 20.0141 | 181.9044 | 0 | 0 | 1.5677 | 5.8287 | 6.6753 | 3.6116 | 0 | 0 | 2.455 | 52.2966 | 52.2966 | 55.8869 | 65.645 | 67.5838 | 60.5676 | 52.2966 | 52.2966 | 108.545 | 52.2966 | 52.2966 | 57.4547 | 71.4737 | 74.2591 | 64.1791 | 52.2966 | 52.2966 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 14 | 710 | 2.4 | 2.4 | 2.4333 | 4.3388 | 15 | 99 | 99 | 2.7267 | 68.0895 | 18.5043 | 196.9437 | 0 | 0 | 0 | 1.7504 | 2.5606 | 1.8708 | 0.085138 | 0 | 0.9105 | 33.3229 | 33.3229 | 33.3229 | 33.3229 | 33.3229 | 33.3229 | 33.3229 | 33.3229 | 68.0895 | 33.3229 | 33.3229 | 33.3229 | 35.0733 | 35.8835 | 35.1937 | 33.408 | 33.3229 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 15 | 711 | 3.6 | 3.6 | 2.4333 | 4.3388 | 15 | 97 | 97 | 53.7577 | 131.3926 | 14.7365 | 211.3167 | 0 | 0 | 0 | 23.9771 | 48.7656 | 44.9878 | 14.8568 | 0 | 15.6074 | 62.7881 | 62.7881 | 62.7881 | 92.8611 | 123.9516 | 119.2133 | 81.4219 | 62.7881 | 131.3926 | 62.7881 | 62.7881 | 62.7881 | 116.8382 | 172.7171 | 164.2011 | 96.2787 | 62.7881 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 16 | 712 | 4.1 | 4.1 | 2.4333 | 4.3388 | 15 | 93 | 93 | 293.4567 | 94.2291 | 9.064 | 224.709 | 0 | 0 | 0 | 67.135 | 242.4555 | 275.7489 | 147.5123 | 0 | 61.7709 | 52.976 | 52.976 | 52.976 | 76.2202 | 136.9216 | 148.4488 | 104.0493 | 52.976 | 94.2291 | 52.976 | 52.976 | 52.976 | 143.3551 | 379.3771 | 424.1976 | 251.5616 | 52.976 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 17 | 713 | 2.6 | 2.6 | 2.4333 | 4.3388 | 15 | 96 | 96 | 4.0014 | 24.6004 | 1.9179 | 237.1294 | 0 | 0 | 0 | 0.020068 | 2.8083 | 3.9514 | 2.7799 | 0 | 0.39964 | 11.8131 | 11.8131 | 11.8131 | 11.8131 | 11.8131 | 11.8131 | 11.8131 | 11.8131 | 24.6004 | 11.8131 | 11.8131 | 11.8131 | 11.8332 | 14.6214 | 15.7645 | 14.593 | 11.8131 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 30 | 18 | 714 | 2.5 | 2.5 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -6.2796 | 248.8317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 19 | 715 | 2.3 | 2.3 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -15.1457 | 260.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 20 | 716 | 2.4 | 2.4 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -24.3218 | 271.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 21 | 717 | 2.5 | 2.5 | 2.4333 | 4.3388 | 15 | 98 | 98 | 0 | 0 | -33.4272 | 284.4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 22 | 718 | 1.9 | 1.9 | 2.4333 | 4.3388 | 15 | 97 | 97 | 0 | 0 | -41.9785 | 298.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 23 | 719 | 1.6 | 1.6 | 2.4333 | 4.3388 | 15 | 99 | 99 | 0 | 0 | -49.2655 | 316.5725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 30 | 24 | 720 | 0.5 | 0.5 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -54.242 | 338.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 1 | 721 | 1.1 | 1.1 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -55.7347 | 3.1792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 2 | 722 | 0.9 | 0.9 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -53.0316 | 27.3284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 3 | 723 | 0.7 | 0.7 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -47.3897 | 47.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 4 | 724 | 0.7 | 0.7 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -39.7235 | 64.6853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 5 | 725 | 1 | 1 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -30.9902 | 78.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 6 | 726 | 0.8 | 0.8 | 0.7625 | 3.2446 | 15 | 100 | 100 | 0 | 0 | -21.8308 | 90.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 7 | 727 | 0.5 | 0.5 | 0.7625 | 3.2446 | 15 | 100 | 100 | 0 | 0 | -12.6946 | 102.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 1 | 31 | 8 | 728 | 0.3 | 0.3 | 0.7625 | 3.2446 | 15 | 100 | 100 | 0 | 0 | -3.9519 | 113.8595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 9 | 729 | 0.4 | 0.4 | 0.7625 | 3.2446 | 15 | 100 | 100 | 0 | 0 | 4.0346 | 125.7245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 10 | 730 | 0.6 | 0.6 | 0.7625 | 3.2446 | 15 | 100 | 100 | 1.3514 | 18.8235 | 10.8703 | 138.3941 | 0 | 0.21729 | 1.0944 | 1.3305 | 0.78713 | 0 | 0 | 0 | 0.17653 | 9.2005 | 9.2005 | 9.2005 | 9.2005 | 9.2005 | 9.2005 | 9.2005 | 9.2005 | 18.8235 | 9.2005 | 9.4178 | 10.295 | 10.531 | 9.9877 | 9.2005 | 9.2005 | 9.2005 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 11 | 731 | 1.1 | 1.1 | 0.7625 | 3.2446 | 15 | 99 | 99 | 5.1829 | 65.7809 | 16.1235 | 152.0734 | 0 | 0 | 3.3797 | 5.081 | 3.8059 | 0.30134 | 0 | 0 | 1.2191 | 31.2991 | 31.2991 | 44.7352 | 51.4985 | 46.4293 | 32.4971 | 31.2991 | 31.2991 | 65.7809 | 31.2991 | 31.2991 | 48.1149 | 56.5795 | 50.2352 | 32.7984 | 31.2991 | 31.2991 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 12 | 732 | 1.4 | 1.4 | 0.7625 | 3.2446 | 15 | 99 | 99 | 5.9664 | 92.1649 | 19.369 | 166.6965 | 0 | 0 | 2.6844 | 5.4791 | 5.0642 | 1.6828 | 0 | 0 | 1.8351 | 44.3147 | 44.3147 | 51.6941 | 59.3768 | 58.2363 | 48.9407 | 44.3147 | 44.3147 | 92.1649 | 44.3147 | 44.3147 | 54.3785 | 64.8559 | 63.3005 | 50.6235 | 44.3147 | 44.3147 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 13 | 733 | 1.5 | 1.5 | 0.7625 | 3.2446 | 15 | 100 | 100 | 7.5834 | 111.4007 | 20.2878 | 181.8659 | 0 | 0 | 1.6463 | 6.0871 | 6.9622 | 3.759 | 0 | 0 | 2.5993 | 53.563 | 53.563 | 57.4653 | 67.9918 | 70.0661 | 62.4732 | 53.563 | 53.563 | 111.4007 | 53.563 | 53.563 | 59.1115 | 74.0789 | 77.0284 | 66.2322 | 53.563 | 53.563 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 14 | 734 | 2.2 | 2.2 | 0.7625 | 3.2446 | 15 | 99 | 99 | 9.2875 | 115.8573 | 18.7802 | 196.9544 | 0 | 0 | 0 | 5.956 | 8.7067 | 6.3571 | 0.28364 | 0 | 3.1427 | 55.8263 | 55.8263 | 55.8263 | 67.0548 | 72.2405 | 67.811 | 56.3611 | 55.8263 | 115.8573 | 55.8263 | 55.8263 | 55.8263 | 73.0108 | 80.9472 | 74.1682 | 56.6447 | 55.8263 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 15 | 735 | 2.5 | 2.5 | 0.7625 | 3.2446 | 15 | 93 | 93 | 60.8494 | 135.0671 | 15.0076 | 211.3706 | 0 | 0 | 0 | 27.0866 | 55.1059 | 50.8449 | 16.7996 | 0 | 17.9329 | 64.5681 | 64.5681 | 64.5681 | 95.5382 | 127.5747 | 122.7028 | 83.7763 | 64.5681 | 135.0671 | 64.5681 | 64.5681 | 64.5681 | 122.6249 | 182.6807 | 173.5477 | 100.576 | 64.5681 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 16 | 736 | 3.4 | 3.4 | 0.7625 | 3.2446 | 15 | 89 | 89 | 52.046 | 96.823 | 9.3262 | 224.7967 | 0 | 0 | 0 | 11.8458 | 42.9221 | 48.8551 | 26.1695 | 0 | 11.177 | 47.2179 | 47.2179 | 47.2179 | 58.8583 | 89.3957 | 95.2259 | 72.9336 | 47.2179 | 96.823 | 47.2179 | 47.2179 | 47.2179 | 70.7041 | 132.3178 | 144.081 | 99.1032 | 47.2179 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 17 | 737 | 2.6 | 2.6 | 0.7625 | 3.2446 | 15 | 88 | 88 | 12.224 | 37.7292 | 2.17 | 237.2422 | 0 | 0 | 0 | 0.042799 | 8.5596 | 12.0623 | 8.4991 | 0 | 1.2708 | 19.2043 | 19.2043 | 19.2043 | 19.2582 | 29.9908 | 34.4048 | 29.9145 | 19.2043 | 37.7292 | 19.2043 | 19.2043 | 19.2043 | 19.301 | 38.5504 | 46.4671 | 38.4136 | 19.2043 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 1 | 31 | 18 | 738 | 1.5 | 1.5 | 0.7625 | 3.2446 | 15 | 95 | 95 | 0 | 3 | -6.0365 | 248.9632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 3 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 19 | 739 | 2.2 | 2.2 | 0.7625 | 3.2446 | 15 | 98 | 98 | 0 | 0 | -14.9084 | 260.3745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 20 | 740 | 3.5 | 3.5 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -24.0861 | 272.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 21 | 741 | 4 | 4 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -33.1879 | 284.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 22 | 742 | 4.1 | 4.1 | 0.7625 | 3.2446 | 15 | 99 | 99 | 0 | 0 | -41.7295 | 299.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 23 | 743 | 4.5 | 4.5 | 0.7625 | 3.2446 | 15 | 96 | 96 | 0 | 0 | -49.0023 | 316.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 1 | 31 | 24 | 744 | 4.7 | 4.7 | 1.925 | 2.649 | 15 | 94 | 94 | 0 | 0 | -53.967 | 338.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 1 | 745 | 5.9 | 5.9 | 1.925 | 2.649 | 15 | 91 | 91 | 0 | 0 | -55.4634 | 3.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 2 | 746 | 5.5 | 5.5 | 1.925 | 2.649 | 15 | 84 | 84 | 0 | 0 | -52.7772 | 27.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 3 | 747 | 5.9 | 5.9 | 1.925 | 2.649 | 15 | 82 | 82 | 0 | 0 | -47.1638 | 47.7162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 4 | 748 | 6.3 | 6.3 | 1.925 | 2.649 | 15 | 85 | 85 | 0 | 0 | -39.5198 | 64.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 5 | 749 | 6.9 | 6.9 | 1.925 | 2.649 | 15 | 85 | 85 | 0 | 0 | -30.799 | 78.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 6 | 750 | 7.1 | 7.1 | 1.925 | 2.649 | 15 | 93 | 93 | 0 | 0 | -21.643 | 90.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 7 | 751 | 7.6 | 7.6 | 1.925 | 2.649 | 15 | 92 | 92 | 0 | 0 | -12.5028 | 102.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 1 | 8 | 752 | 7.9 | 7.9 | 1.925 | 2.649 | 15 | 93 | 93 | 0 | 0 | -3.7501 | 113.6637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 9 | 753 | 8.7 | 8.7 | 1.925 | 2.649 | 15 | 92 | 92 | 0 | 0 | 4.2513 | 125.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 10 | 754 | 10.1 | 10.1 | 1.925 | 2.649 | 15 | 89 | 89 | 1.7011 | 21.7706 | 11.105 | 138.237 | 0 | 0.27866 | 1.3803 | 1.6734 | 0.98621 | 0 | 0 | 0 | 0.22936 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 21.7706 | 10.7173 | 10.996 | 12.0976 | 12.3907 | 11.7035 | 10.7173 | 10.7173 | 10.7173 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 11 | 755 | 10.6 | 10.6 | 1.925 | 2.649 | 15 | 83 | 83 | 5.7708 | 70.6174 | 16.3769 | 151.9473 | 0 | 0 | 3.7717 | 5.6537 | 4.2239 | 0.31975 | 0 | 0 | 1.3826 | 33.288 | 33.288 | 50.745 | 59.4559 | 52.838 | 34.7679 | 33.288 | 33.288 | 70.6174 | 33.288 | 33.288 | 54.5166 | 65.1096 | 57.0618 | 35.0877 | 33.288 | 33.288 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 12 | 756 | 11.5 | 11.5 | 1.925 | 2.649 | 15 | 76 | 76 | 317.7661 | 136.8403 | 19.6382 | 166.6119 | 0 | 0 | 143.3771 | 291.6341 | 269.0557 | 88.8682 | 0 | 0 | 99.1597 | 74.9636 | 74.9636 | 130.573 | 188.075 | 179.3179 | 109.4314 | 74.9636 | 74.9636 | 136.8403 | 74.9636 | 74.9636 | 273.9501 | 479.7091 | 448.3737 | 198.2996 | 74.9636 | 74.9636 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 13 | 757 | 11.8 | 11.8 | 1.925 | 2.649 | 15 | 73 | 73 | 492.7768 | 125.861 | 20.5667 | 181.8306 | 0 | 0 | 107.4637 | 395.2476 | 451.5008 | 243.271 | 0 | 0 | 171.139 | 77.7158 | 77.7158 | 103.4332 | 172.3032 | 185.7653 | 135.9334 | 77.7158 | 77.7158 | 125.861 | 77.7158 | 77.7158 | 210.8969 | 567.5509 | 637.2661 | 379.2044 | 77.7158 | 77.7158 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 14 | 758 | 12.1 | 12.1 | 1.925 | 2.649 | 15 | 72 | 72 | 275.6934 | 155.4647 | 19.0607 | 196.9693 | 0 | 0 | 0 | 176.5959 | 257.9901 | 188.2572 | 8.2458 | 0 | 94.5353 | 82.743 | 82.743 | 82.743 | 165.6522 | 203.8655 | 171.127 | 86.6143 | 82.743 | 155.4647 | 82.743 | 82.743 | 82.743 | 342.248 | 461.8556 | 359.3841 | 94.8601 | 82.743 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 15 | 759 | 11.1 | 11.1 | 1.925 | 2.649 | 15 | 73 | 73 | 86.3063 | 141.18 | 15.2827 | 211.4294 | 0 | 0 | 0 | 38.3354 | 78.0227 | 72.0054 | 23.8083 | 0 | 25.82 | 67.8525 | 67.8525 | 67.8525 | 100.7774 | 134.8634 | 129.6953 | 88.3005 | 67.8525 | 141.18 | 67.8525 | 67.8525 | 67.8525 | 139.1128 | 212.8861 | 201.7007 | 112.1088 | 67.8525 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 16 | 760 | 10.6 | 10.6 | 1.925 | 2.649 | 15 | 74 | 74 | 106.7279 | 104.6172 | 9.5916 | 224.8897 | 0 | 0 | 0 | 24.1574 | 87.8487 | 100.0794 | 53.6849 | 0 | 23.3828 | 52.4637 | 52.4637 | 52.4637 | 71.4247 | 121.4156 | 131.0154 | 94.6007 | 52.4637 | 104.6172 | 52.4637 | 52.4637 | 52.4637 | 95.5822 | 209.2643 | 231.0948 | 148.2856 | 52.4637 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 17 | 761 | 9.5 | 9.5 | 1.925 | 2.649 | 15 | 80 | 80 | 5.252 | 30.4321 | 2.4248 | 237.3604 | 0 | 0 | 0 | 0.0099712 | 3.6688 | 5.1785 | 3.6547 | 0 | 0.56789 | 14.7287 | 14.7287 | 14.7287 | 14.7287 | 14.7287 | 14.7287 | 14.7287 | 14.7287 | 30.4321 | 14.7287 | 14.7287 | 14.7287 | 14.7387 | 18.3976 | 19.9073 | 18.3835 | 14.7287 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 1 | 18 | 762 | 9.2 | 9.2 | 1.925 | 2.649 | 15 | 82 | 82 | 0 | 0 | -5.7909 | 249.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 19 | 763 | 9.5 | 9.5 | 1.925 | 2.649 | 15 | 80 | 80 | 0 | 0 | -14.6689 | 260.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 20 | 764 | 10.1 | 10.1 | 1.925 | 2.649 | 15 | 78 | 78 | 0 | 0 | -23.8482 | 272.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 21 | 765 | 9.7 | 9.7 | 1.925 | 2.649 | 15 | 80 | 80 | 0 | 0 | -32.9461 | 284.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 22 | 766 | 10 | 10 | 1.925 | 2.649 | 15 | 86 | 86 | 0 | 0 | -41.4776 | 299.2667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 23 | 767 | 9.9 | 9.9 | 1.925 | 2.649 | 15 | 91 | 91 | 0 | 0 | -48.7356 | 316.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 1 | 24 | 768 | 10.7 | 10.7 | 9.0917 | 4.2155 | 15 | 92 | 92 | 0 | 0 | -53.6876 | 338.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 1 | 769 | 11.2 | 11.2 | 9.0917 | 4.2155 | 15 | 85 | 85 | 0 | 0 | -55.1868 | 3.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 2 | 770 | 10.8 | 10.8 | 9.0917 | 4.2155 | 15 | 84 | 84 | 0 | 0 | -52.5167 | 26.9383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 3 | 771 | 10.8 | 10.8 | 9.0917 | 4.2155 | 15 | 85 | 85 | 0 | 0 | -46.9315 | 47.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 4 | 772 | 10.8 | 10.8 | 9.0917 | 4.2155 | 15 | 84 | 84 | 0 | 0 | -39.3096 | 64.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 5 | 773 | 10.8 | 10.8 | 9.0917 | 4.2155 | 15 | 82 | 82 | 0 | 0 | -30.6013 | 78.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 6 | 774 | 10.6 | 10.6 | 9.0917 | 4.2155 | 15 | 85 | 85 | 0 | 0 | -21.449 | 90.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 7 | 775 | 10.5 | 10.5 | 9.0917 | 4.2155 | 15 | 86 | 86 | 0 | 0 | -12.3049 | 101.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 2 | 8 | 776 | 10.1 | 10.1 | 9.0917 | 4.2155 | 15 | 92 | 92 | 0 | 0 | -3.5422 | 113.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 9 | 777 | 10 | 10 | 9.0917 | 4.2155 | 15 | 94 | 94 | 0 | 0 | 4.4739 | 125.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 10 | 778 | 9.8 | 9.8 | 9.0917 | 4.2155 | 15 | 93 | 93 | 0.1189 | 5.9835 | 11.3456 | 138.0802 | 0 | 0.019837 | 0.09666 | 0.11686 | 0.068607 | 0 | 0 | 0 | 0.01654 | 2.793 | 2.793 | 2.793 | 2.793 | 2.793 | 2.793 | 2.793 | 2.793 | 5.9835 | 2.793 | 2.8129 | 2.8897 | 2.9099 | 2.8616 | 2.793 | 2.793 | 2.793 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 11 | 779 | 9.6 | 9.6 | 9.0917 | 4.2155 | 15 | 95 | 95 | 0.12988 | 10.9683 | 16.636 | 151.8223 | 0 | 0 | 0.085073 | 0.12715 | 0.094749 | 0.0068423 | 0 | 0 | 0.031693 | 5.1245 | 5.1245 | 5.1245 | 5.1245 | 5.1245 | 5.1245 | 5.1245 | 5.1245 | 10.9683 | 5.1245 | 5.1245 | 5.2096 | 5.2517 | 5.2193 | 5.1314 | 5.1245 | 5.1245 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 12 | 780 | 9.7 | 9.7 | 9.0917 | 4.2155 | 15 | 96 | 96 | 0.4999 | 27.8417 | 19.913 | 166.5294 | 0 | 0 | 0.22618 | 0.45848 | 0.42221 | 0.13862 | 0 | 0 | 0.15827 | 13.2129 | 13.2129 | 13.2129 | 13.2129 | 13.2129 | 13.2129 | 13.2129 | 13.2129 | 27.8417 | 13.2129 | 13.2129 | 13.4391 | 13.6714 | 13.6351 | 13.3515 | 13.2129 | 13.2129 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 13 | 781 | 9.9 | 9.9 | 9.0917 | 4.2155 | 15 | 97 | 97 | 0.24981 | 21.9121 | 20.8507 | 181.7986 | 0 | 0 | 0.054713 | 0.2002 | 0.22841 | 0.12282 | 0 | 0 | 0.087908 | 10.328 | 10.328 | 10.328 | 10.328 | 10.328 | 10.328 | 10.328 | 10.328 | 21.9121 | 10.328 | 10.328 | 10.3827 | 10.5282 | 10.5564 | 10.4508 | 10.328 | 10.328 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 14 | 782 | 10.5 | 10.5 | 9.0917 | 4.2155 | 15 | 96 | 96 | 0.41496 | 27.8558 | 19.3457 | 196.9885 | 0 | 0 | 0 | 0.26547 | 0.3876 | 0.28268 | 0.012172 | 0 | 0.1442 | 13.1908 | 13.1908 | 13.1908 | 13.1908 | 13.1908 | 13.1908 | 13.1908 | 13.1908 | 27.8558 | 13.1908 | 13.1908 | 13.1908 | 13.4563 | 13.5784 | 13.4735 | 13.203 | 13.1908 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 15 | 783 | 11.6 | 11.6 | 9.0917 | 4.2155 | 15 | 93 | 93 | 0.66594 | 30.7978 | 15.5615 | 211.4931 | 0 | 0 | 0 | 0.2951 | 0.60092 | 0.55473 | 0.18359 | 0 | 0.20225 | 14.6302 | 14.6302 | 14.6302 | 14.6302 | 14.6302 | 14.6302 | 14.6302 | 14.6302 | 30.7978 | 14.6302 | 14.6302 | 14.6302 | 14.9253 | 15.2311 | 15.1849 | 14.8138 | 14.6302 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 16 | 784 | 11.7 | 11.7 | 9.0917 | 4.2155 | 15 | 90 | 90 | 1.6583 | 35.6294 | 9.8602 | 224.9879 | 0 | 0 | 0 | 0.37312 | 1.3622 | 1.5533 | 0.83453 | 0 | 0.37063 | 17.0728 | 17.0728 | 17.0728 | 17.0728 | 17.0728 | 17.0728 | 17.0728 | 17.0728 | 35.6294 | 17.0728 | 17.0728 | 17.0728 | 17.4459 | 18.435 | 18.6261 | 17.9073 | 17.0728 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 17 | 785 | 11.3 | 11.3 | 9.0917 | 4.2155 | 15 | 89 | 89 | 3.1637 | 24.6445 | 2.6822 | 237.4839 | 0 | 0 | 0 | 0.0006565 | 2.2045 | 3.117 | 2.2036 | 0 | 0.3555 | 11.801 | 11.801 | 11.801 | 11.801 | 11.801 | 11.801 | 11.801 | 11.801 | 24.6445 | 11.801 | 11.801 | 11.801 | 11.8016 | 14.0055 | 14.918 | 14.0046 | 11.801 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 2 | 18 | 786 | 10.7 | 10.7 | 9.0917 | 4.2155 | 15 | 89 | 89 | 0 | 3 | -5.543 | 249.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 3 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 1.3907 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 19 | 787 | 10.4 | 10.4 | 9.0917 | 4.2155 | 15 | 89 | 89 | 0 | 0 | -14.4272 | 260.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 20 | 788 | 10.7 | 10.7 | 9.0917 | 4.2155 | 15 | 87 | 87 | 0 | 0 | -23.6082 | 272.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 21 | 789 | 11 | 11 | 9.0917 | 4.2155 | 15 | 86 | 86 | 0 | 0 | -32.702 | 284.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 22 | 790 | 11 | 11 | 9.0917 | 4.2155 | 15 | 83 | 83 | 0 | 0 | -41.223 | 299.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 23 | 791 | 11 | 11 | 9.0917 | 4.2155 | 15 | 82 | 82 | 0 | 0 | -48.4654 | 316.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 2 | 24 | 792 | 11.3 | 11.3 | 10.6583 | 5.9092 | 15 | 82 | 82 | 0 | 0 | -53.4039 | 338.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 1 | 793 | 11.4 | 11.4 | 10.6583 | 5.9092 | 15 | 82 | 82 | 0 | 0 | -54.9048 | 2.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 2 | 794 | 11.4 | 11.4 | 10.6583 | 5.9092 | 15 | 82 | 82 | 0 | 0 | -52.2502 | 26.7503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 3 | 795 | 11.4 | 11.4 | 10.6583 | 5.9092 | 15 | 79 | 79 | 0 | 0 | -46.6927 | 47.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 4 | 796 | 11.1 | 11.1 | 10.6583 | 5.9092 | 15 | 80 | 80 | 0 | 0 | -39.0929 | 63.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 5 | 797 | 11.2 | 11.2 | 10.6583 | 5.9092 | 15 | 81 | 81 | 0 | 0 | -30.3974 | 77.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 6 | 798 | 11.4 | 11.4 | 10.6583 | 5.9092 | 15 | 82 | 82 | 0 | 0 | -21.2488 | 90.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 7 | 799 | 11.7 | 11.7 | 10.6583 | 5.9092 | 15 | 83 | 83 | 0 | 0 | -12.101 | 101.7852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 3 | 8 | 800 | 11.9 | 11.9 | 10.6583 | 5.9092 | 15 | 84 | 84 | 0 | 0 | -3.3285 | 113.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 9 | 801 | 12.3 | 12.3 | 10.6583 | 5.9092 | 15 | 83 | 83 | 0 | 0 | 4.7024 | 125.1867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 10 | 802 | 12.8 | 12.8 | 10.6583 | 5.9092 | 15 | 83 | 83 | 0.60881 | 13.9127 | 11.592 | 137.9238 | 0 | 0.10342 | 0.49589 | 0.59788 | 0.34964 | 0 | 0 | 0 | 0.087345 | 6.6524 | 6.6524 | 6.6524 | 6.6524 | 6.6524 | 6.6524 | 6.6524 | 6.6524 | 13.9127 | 6.6524 | 6.7558 | 7.1483 | 7.2502 | 7.002 | 6.6524 | 6.6524 | 6.6524 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 11 | 803 | 13.4 | 13.4 | 10.6583 | 5.9092 | 15 | 82 | 82 | 2.5875 | 49.3569 | 16.9008 | 151.6984 | 0 | 0 | 1.6986 | 2.5315 | 1.8814 | 0.12929 | 0 | 0 | 0.64311 | 24.2931 | 24.2931 | 24.2931 | 24.2931 | 24.2931 | 24.2931 | 24.2931 | 24.2931 | 49.3569 | 24.2931 | 24.2931 | 25.9917 | 26.8246 | 26.1746 | 24.4224 | 24.2931 | 24.2931 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 12 | 804 | 14.3 | 14.3 | 10.6583 | 5.9092 | 15 | 76 | 76 | 14.5342 | 120.3311 | 20.1932 | 166.4491 | 0 | 0 | 6.5932 | 13.3201 | 12.2442 | 3.9958 | 0 | 0 | 4.6689 | 55.5751 | 55.5751 | 76.7189 | 98.291 | 94.8407 | 68.3892 | 55.5751 | 55.5751 | 120.3311 | 55.5751 | 55.5751 | 83.3121 | 111.611 | 107.0849 | 72.385 | 55.5751 | 55.5751 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 13 | 805 | 15.4 | 15.4 | 10.6583 | 5.9092 | 15 | 71 | 71 | 224.7577 | 166.855 | 21.1396 | 181.7699 | 0 | 0 | 49.4258 | 179.9561 | 205.0706 | 110.0575 | 0 | 0 | 80.145 | 84.1022 | 84.1022 | 110.9902 | 181.9995 | 195.6619 | 143.9742 | 84.1022 | 84.1022 | 166.855 | 84.1022 | 84.1022 | 160.416 | 361.9557 | 400.7325 | 254.0317 | 84.1022 | 84.1022 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 14 | 806 | 15.5 | 15.5 | 10.6583 | 5.9092 | 15 | 70 | 70 | 66.3747 | 162.6245 | 19.635 | 197.012 | 0 | 0 | 0 | 42.4026 | 61.8785 | 45.1067 | 1.9121 | 0 | 23.3755 | 76.6817 | 76.6817 | 76.6817 | 130.0054 | 154.4973 | 133.4059 | 79.0863 | 76.6817 | 162.6245 | 76.6817 | 76.6817 | 76.6817 | 172.408 | 216.3758 | 178.5127 | 80.9984 | 76.6817 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 15 | 807 | 15.7 | 15.7 | 10.6583 | 5.9092 | 15 | 67 | 67 | 79.3536 | 144.5347 | 15.844 | 211.5618 | 0 | 0 | 0 | 35.0742 | 71.4691 | 65.9983 | 21.8666 | 0 | 24.4653 | 69.2359 | 69.2359 | 69.2359 | 102.0535 | 136.1068 | 130.988 | 89.6957 | 69.2359 | 144.5347 | 69.2359 | 69.2359 | 69.2359 | 137.1277 | 207.5759 | 196.9863 | 111.5623 | 69.2359 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 16 | 808 | 15.5 | 15.5 | 10.6583 | 5.9092 | 15 | 62 | 62 | 6.5223 | 70.513 | 10.1319 | 225.0915 | 0 | 0 | 0 | 1.4582 | 5.3464 | 6.1027 | 3.2842 | 0 | 1.487 | 34.9921 | 34.9921 | 34.9921 | 34.9921 | 34.9921 | 34.9921 | 34.9921 | 34.9921 | 70.513 | 34.9921 | 34.9921 | 34.9921 | 36.4503 | 40.3385 | 41.0948 | 38.2763 | 34.9921 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 17 | 809 | 15.2 | 15.2 | 10.6583 | 5.9092 | 15 | 62 | 62 | 2.2729 | 21.7348 | 2.9422 | 237.6129 | 0 | 0 | 0 | 0 | 1.5796 | 2.2374 | 1.5846 | 0.0035718 | 0.2652 | 10.35 | 10.35 | 10.35 | 10.35 | 10.35 | 10.35 | 10.35 | 10.35 | 21.7348 | 10.35 | 10.35 | 10.35 | 10.35 | 11.9296 | 12.5875 | 11.9346 | 10.3536 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 18 | 810 | 14.8 | 14.8 | 10.6583 | 5.9092 | 15 | 62 | 62 | 0 | 0 | -5.2929 | 249.3903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 19 | 811 | 14.5 | 14.5 | 10.6583 | 5.9092 | 15 | 62 | 62 | 0 | 0 | -14.1835 | 260.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 20 | 812 | 14.4 | 14.4 | 10.6583 | 5.9092 | 15 | 64 | 64 | 0 | 0 | -23.3661 | 272.5265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 21 | 813 | 14.3 | 14.3 | 10.6583 | 5.9092 | 15 | 64 | 64 | 0 | 0 | -32.4555 | 285.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 22 | 814 | 13.9 | 13.9 | 10.6583 | 5.9092 | 15 | 65 | 65 | 0 | 0 | -40.9656 | 299.6167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 23 | 815 | 13.8 | 13.8 | 10.6583 | 5.9092 | 15 | 67 | 67 | 0 | 0 | -48.1918 | 317.1187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 3 | 24 | 816 | 13.9 | 13.9 | 13.3833 | 7.9368 | 15 | 67 | 67 | 0 | 0 | -53.116 | 338.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 1 | 817 | 14.2 | 14.2 | 13.3833 | 7.9368 | 15 | 67 | 67 | 0 | 0 | -54.6177 | 2.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 2 | 818 | 14 | 14 | 13.3833 | 7.9368 | 15 | 68 | 68 | 0 | 0 | -51.9778 | 26.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 3 | 819 | 13.6 | 13.6 | 13.3833 | 7.9368 | 15 | 69 | 69 | 0 | 0 | -46.4476 | 46.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 4 | 820 | 13.7 | 13.7 | 13.3833 | 7.9368 | 15 | 70 | 70 | 0 | 0 | -38.8699 | 63.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 5 | 821 | 13.4 | 13.4 | 13.3833 | 7.9368 | 15 | 71 | 71 | 0 | 0 | -30.1872 | 77.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 6 | 822 | 11.8 | 11.8 | 13.3833 | 7.9368 | 15 | 85 | 85 | 0 | 0 | -21.0425 | 89.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 7 | 823 | 12 | 12 | 13.3833 | 7.9368 | 15 | 82 | 82 | 0 | 0 | -11.8912 | 101.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 4 | 8 | 824 | 12.7 | 12.7 | 13.3833 | 7.9368 | 15 | 78 | 78 | 0 | 0 | -3.1089 | 113.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 9 | 825 | 11.6 | 11.6 | 13.3833 | 7.9368 | 15 | 94 | 94 | 1.8992 | 2.9669 | 4.9366 | 125.0072 | 0 | 0.70812 | 1.7447 | 1.7592 | 0.74323 | 0 | 0 | 0 | 0.033063 | 1.0997 | 2.0569 | 3.4579 | 3.4775 | 2.1043 | 1.0997 | 1.0997 | 1.0997 | 2.9669 | 1.0997 | 2.765 | 5.2026 | 5.2367 | 2.8475 | 1.0997 | 1.0997 | 1.0997 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 10 | 826 | 13.1 | 13.1 | 13.3833 | 7.9368 | 15 | 83 | 83 | 3.7895 | 35.4396 | 11.8441 | 137.7679 | 0 | 0.65513 | 3.0924 | 3.7182 | 2.1659 | 0 | 0 | 0 | 0.56044 | 16.4577 | 22.5754 | 45.3349 | 51.1785 | 36.6832 | 16.4577 | 16.4577 | 16.4577 | 35.4396 | 16.4577 | 23.2305 | 48.4273 | 54.8967 | 38.8491 | 16.4577 | 16.4577 | 16.4577 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 11 | 827 | 14.2 | 14.2 | 13.3833 | 7.9368 | 15 | 73 | 73 | 20.8387 | 100.7252 | 17.1712 | 151.5757 | 0 | 0 | 13.7082 | 20.3712 | 15.101 | 0.98488 | 0 | 0 | 5.2748 | 44.6378 | 44.6378 | 98.8311 | 125.1723 | 104.3374 | 48.5313 | 44.6378 | 44.6378 | 100.7252 | 44.6378 | 44.6378 | 112.5393 | 145.5435 | 119.4385 | 49.5162 | 44.6378 | 44.6378 | 106 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 12 | 828 | 15 | 15 | 13.3833 | 7.9368 | 15 | 66 | 66 | 5.3196 | 92.2662 | 20.4787 | 166.371 | 0 | 0 | 2.4193 | 4.8713 | 4.4698 | 1.4499 | 0 | 0 | 1.7338 | 44.8185 | 44.8185 | 49.8358 | 54.9211 | 54.0884 | 47.8256 | 44.8185 | 44.8185 | 92.2662 | 44.8185 | 44.8185 | 52.2551 | 59.7924 | 58.5582 | 49.2755 | 44.8185 | 44.8185 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 13 | 829 | 14 | 14 | 13.3833 | 7.9368 | 15 | 72 | 72 | 1.6478 | 57.4046 | 21.4334 | 181.7446 | 0 | 0 | 0.36374 | 1.318 | 1.5002 | 0.8036 | 0 | 0 | 0.59541 | 27.8332 | 27.8332 | 27.8332 | 27.8332 | 27.8332 | 27.8332 | 27.8332 | 27.8332 | 57.4046 | 27.8332 | 27.8332 | 28.1969 | 29.1512 | 29.3334 | 28.6368 | 27.8332 | 27.8332 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 14 | 830 | 15.5 | 15.5 | 13.3833 | 7.9368 | 15 | 61 | 61 | 4.2492 | 90.4834 | 19.9285 | 197.0398 | 0 | 0 | 0 | 2.7104 | 3.9535 | 2.8807 | 0.12042 | 0 | 1.5166 | 44.9213 | 44.9213 | 44.9213 | 44.9213 | 44.9213 | 44.9213 | 44.9213 | 44.9213 | 90.4834 | 44.9213 | 44.9213 | 44.9213 | 47.6317 | 48.8748 | 47.802 | 45.0418 | 44.9213 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 15 | 831 | 16 | 16 | 13.3833 | 7.9368 | 15 | 61 | 61 | 5.1713 | 87.3814 | 16.1301 | 211.6354 | 0 | 0 | 0 | 2.2794 | 4.6483 | 4.2942 | 1.4246 | 0 | 1.6186 | 43.4483 | 43.4483 | 43.4483 | 43.4483 | 43.4483 | 43.4483 | 43.4483 | 43.4483 | 87.3814 | 43.4483 | 43.4483 | 43.4483 | 45.7277 | 48.0965 | 47.7424 | 44.8729 | 43.4483 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 16 | 832 | 16.4 | 16.4 | 13.3833 | 7.9368 | 15 | 59 | 59 | 6.2159 | 70.5546 | 10.4065 | 225.2003 | 0 | 0 | 0 | 1.3802 | 5.0839 | 5.8095 | 3.132 | 0 | 1.4454 | 34.9781 | 34.9781 | 34.9781 | 34.9781 | 34.9781 | 34.9781 | 34.9781 | 34.9781 | 70.5546 | 34.9781 | 34.9781 | 34.9781 | 36.3583 | 40.062 | 40.7876 | 38.11 | 34.9781 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 17 | 833 | 16.1 | 16.1 | 13.3833 | 7.9368 | 15 | 61 | 61 | 1.261 | 16.8473 | 3.2047 | 237.7473 | 0 | 0 | 0 | 0 | 0.87396 | 1.2403 | 0.88009 | 0.0043354 | 0.15267 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 16.8473 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 8.8293 | 9.1956 | 8.8354 | 7.9596 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 18 | 834 | 15.6 | 15.6 | 13.3833 | 7.9368 | 15 | 64 | 64 | 0 | 3 | -5.0407 | 249.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 3 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 1.389 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 19 | 835 | 15.4 | 15.4 | 13.3833 | 7.9368 | 15 | 63 | 63 | 0 | 0 | -13.9379 | 261.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 20 | 836 | 15.4 | 15.4 | 13.3833 | 7.9368 | 15 | 62 | 62 | 0 | 0 | -23.122 | 272.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 21 | 837 | 15.6 | 15.6 | 13.3833 | 7.9368 | 15 | 60 | 60 | 0 | 0 | -32.2069 | 285.3253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 22 | 838 | 16 | 16 | 13.3833 | 7.9368 | 15 | 57 | 57 | 0 | 0 | -40.7057 | 299.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 23 | 839 | 15.5 | 15.5 | 13.3833 | 7.9368 | 15 | 58 | 58 | 0 | 0 | -47.9151 | 317.2702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 4 | 24 | 840 | 14.9 | 14.9 | 14.4042 | 9.8782 | 15 | 61 | 61 | 0 | 0 | -52.824 | 338.5735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 1 | 841 | 14.5 | 14.5 | 14.4042 | 9.8782 | 15 | 64 | 64 | 0 | 0 | -54.3255 | 2.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 2 | 842 | 14.1 | 14.1 | 14.4042 | 9.8782 | 15 | 68 | 68 | 0 | 0 | -51.6996 | 26.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 3 | 843 | 13.9 | 13.9 | 14.4042 | 9.8782 | 15 | 73 | 73 | 0 | 0 | -46.1963 | 46.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 4 | 844 | 13.5 | 13.5 | 14.4042 | 9.8782 | 15 | 79 | 79 | 0 | 0 | -38.6407 | 63.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 5 | 845 | 12.2 | 12.2 | 14.4042 | 9.8782 | 15 | 91 | 91 | 0 | 0 | -29.9709 | 77.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 6 | 846 | 11.6 | 11.6 | 14.4042 | 9.8782 | 15 | 94 | 94 | 0 | 0 | -20.8303 | 89.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 7 | 847 | 11.5 | 11.5 | 14.4042 | 9.8782 | 15 | 93 | 93 | 0 | 0 | -11.6755 | 101.3618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 5 | 8 | 848 | 11.4 | 11.4 | 14.4042 | 9.8782 | 15 | 94 | 94 | 0 | 0 | -2.8835 | 112.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 9 | 849 | 11.3 | 11.3 | 14.4042 | 9.8782 | 15 | 95 | 95 | 0 | 0 | 5.1766 | 124.8278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 10 | 850 | 11.3 | 11.3 | 14.4042 | 9.8782 | 15 | 94 | 94 | 0.79619 | 16.8787 | 12.1018 | 137.6124 | 0 | 0.14004 | 0.65091 | 0.78048 | 0.45286 | 0 | 0 | 0 | 0.12133 | 8.1145 | 8.1145 | 8.1145 | 8.1145 | 8.1145 | 8.1145 | 8.1145 | 8.1145 | 16.8787 | 8.1145 | 8.2546 | 8.7654 | 8.895 | 8.5674 | 8.1145 | 8.1145 | 8.1145 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 11 | 851 | 11.8 | 11.8 | 14.4042 | 9.8782 | 15 | 92 | 92 | 2.4069 | 49.3796 | 17.447 | 151.4543 | 0 | 0 | 1.5865 | 2.351 | 1.7382 | 0.10727 | 0 | 0 | 0.62044 | 24.2506 | 24.2506 | 24.2506 | 24.2506 | 24.2506 | 24.2506 | 24.2506 | 24.2506 | 49.3796 | 24.2506 | 24.2506 | 25.8371 | 26.6015 | 25.9888 | 24.3578 | 24.2506 | 24.2506 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 12 | 852 | 12 | 12 | 14.4042 | 9.8782 | 15 | 90 | 90 | 2.3961 | 63.2076 | 20.7694 | 166.2951 | 0 | 0 | 1.0923 | 2.1923 | 2.008 | 0.64748 | 0 | 0 | 0.79239 | 30.9699 | 30.9699 | 30.9699 | 30.9699 | 30.9699 | 30.9699 | 30.9699 | 30.9699 | 63.2076 | 30.9699 | 30.9699 | 32.0623 | 33.1622 | 32.978 | 31.6174 | 30.9699 | 30.9699 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 13 | 853 | 12.2 | 12.2 | 14.4042 | 9.8782 | 15 | 89 | 89 | 1.6052 | 57.4122 | 21.7319 | 181.7226 | 0 | 0 | 0.35559 | 1.2825 | 1.4582 | 0.77964 | 0 | 0 | 0.58776 | 27.8263 | 27.8263 | 27.8263 | 27.8263 | 27.8263 | 27.8263 | 27.8263 | 27.8263 | 57.4122 | 27.8263 | 27.8263 | 28.1819 | 29.1089 | 29.2845 | 28.606 | 27.8263 | 27.8263 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 14 | 854 | 12.6 | 12.6 | 14.4042 | 9.8782 | 15 | 89 | 89 | 1.8192 | 60.3419 | 20.2262 | 197.0719 | 0 | 0 | 0 | 1.1585 | 1.6892 | 1.2304 | 0.0508 | 0 | 0.65808 | 29.2783 | 29.2783 | 29.2783 | 29.2783 | 29.2783 | 29.2783 | 29.2783 | 29.2783 | 60.3419 | 29.2783 | 29.2783 | 29.2783 | 30.4369 | 30.9675 | 30.5087 | 29.3291 | 29.2783 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 15 | 855 | 12.2 | 12.2 | 14.4042 | 9.8782 | 15 | 92 | 92 | 1.1179 | 41.6448 | 16.4197 | 211.7141 | 0 | 0 | 0 | 0.49128 | 1.0027 | 0.92677 | 0.30794 | 0 | 0.35518 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 41.6448 | 19.9497 | 19.9497 | 19.9497 | 20.441 | 20.9524 | 20.8765 | 20.2577 | 19.9497 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 16 | 856 | 12.1 | 12.1 | 14.4042 | 9.8782 | 15 | 94 | 94 | 0.41062 | 18.9026 | 10.6839 | 225.3144 | 0 | 0 | 0 | 0.090516 | 0.33506 | 0.38333 | 0.20705 | 0 | 0.097382 | 8.8956 | 8.8956 | 8.8956 | 8.8956 | 8.8956 | 8.8956 | 8.8956 | 8.8956 | 18.9026 | 8.8956 | 8.8956 | 8.8956 | 8.9861 | 9.2306 | 9.2789 | 9.1026 | 8.8956 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 17 | 857 | 12 | 12 | 14.4042 | 9.8782 | 15 | 95 | 95 | 0.14619 | 5.9817 | 3.4694 | 237.8869 | 0 | 0 | 0 | 0 | 0.10102 | 0.14365 | 0.10213 | 0.00078813 | 0.018349 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 5.9817 | 2.7758 | 2.7758 | 2.7758 | 2.7758 | 2.8768 | 2.9195 | 2.8779 | 2.7766 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 5 | 18 | 858 | 11.9 | 11.9 | 14.4042 | 9.8782 | 15 | 97 | 97 | 0 | 0 | -4.7865 | 249.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 19 | 859 | 12.1 | 12.1 | 14.4042 | 9.8782 | 15 | 97 | 97 | 0 | 0 | -13.6904 | 261.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 20 | 860 | 11.9 | 11.9 | 14.4042 | 9.8782 | 15 | 97 | 97 | 0 | 0 | -22.876 | 272.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 21 | 861 | 12.1 | 12.1 | 14.4042 | 9.8782 | 15 | 89 | 89 | 0 | 0 | -31.9562 | 285.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 22 | 862 | 11.6 | 11.6 | 14.4042 | 9.8782 | 15 | 90 | 90 | 0 | 0 | -40.4431 | 299.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 23 | 863 | 11 | 11 | 14.4042 | 9.8782 | 15 | 96 | 96 | 0 | 0 | -47.6351 | 317.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 5 | 24 | 864 | 10.9 | 10.9 | 12.1542 | 10.8956 | 15 | 96 | 96 | 0 | 0 | -52.528 | 338.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 1 | 865 | 10.6 | 10.6 | 12.1542 | 10.8956 | 15 | 95 | 95 | 0 | 0 | -54.0284 | 2.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 2 | 866 | 10.5 | 10.5 | 12.1542 | 10.8956 | 15 | 95 | 95 | 0 | 0 | -51.4157 | 26.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 3 | 867 | 10.1 | 10.1 | 12.1542 | 10.8956 | 15 | 95 | 95 | 0 | 0 | -45.9389 | 46.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 4 | 868 | 10.3 | 10.3 | 12.1542 | 10.8956 | 15 | 94 | 94 | 0 | 0 | -38.4053 | 63.1954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 5 | 869 | 10.4 | 10.4 | 12.1542 | 10.8956 | 15 | 92 | 92 | 0 | 0 | -29.7485 | 77.1712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 6 | 870 | 10.4 | 10.4 | 12.1542 | 10.8956 | 15 | 91 | 91 | 0 | 0 | -20.6121 | 89.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 7 | 871 | 10.6 | 10.6 | 12.1542 | 10.8956 | 15 | 91 | 91 | 0 | 0 | -11.454 | 101.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 6 | 8 | 872 | 10.8 | 10.8 | 12.1542 | 10.8956 | 15 | 91 | 91 | 0 | 0 | -2.6524 | 112.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 9 | 873 | 10.9 | 10.9 | 12.1542 | 10.8956 | 15 | 90 | 90 | 3.3912 | 5.9116 | 5.4222 | 124.6484 | 0 | 1.2865 | 3.1256 | 3.1337 | 1.3062 | 0 | 0 | 0 | 0.08839 | 2.1909 | 4.1295 | 6.9007 | 6.9129 | 4.1591 | 2.1909 | 2.1909 | 2.1909 | 5.9116 | 2.1909 | 5.416 | 10.0263 | 10.0467 | 5.4652 | 2.1909 | 2.1909 | 2.1909 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 10 | 874 | 11 | 11 | 12.1542 | 10.8956 | 15 | 90 | 90 | 1.6238 | 24.7452 | 12.365 | 137.4575 | 0 | 0.29047 | 1.3298 | 1.5902 | 0.91906 | 0 | 0 | 0 | 0.25485 | 12.1304 | 12.1304 | 12.1304 | 12.1304 | 12.1304 | 12.1304 | 12.1304 | 12.1304 | 24.7452 | 12.1304 | 12.4209 | 13.4603 | 13.7206 | 13.0495 | 12.1304 | 12.1304 | 12.1304 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 11 | 875 | 11.2 | 11.2 | 12.1542 | 10.8956 | 15 | 90 | 90 | 0.26841 | 16.9295 | 17.7283 | 151.3341 | 0 | 0 | 0.17727 | 0.26194 | 0.19317 | 0.011242 | 0 | 0 | 0.070456 | 7.9678 | 7.9678 | 7.9678 | 7.9678 | 7.9678 | 7.9678 | 7.9678 | 7.9678 | 16.9295 | 7.9678 | 7.9678 | 8.1451 | 8.2297 | 8.161 | 7.979 | 7.9678 | 7.9678 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 12 | 876 | 11.5 | 11.5 | 12.1542 | 10.8956 | 15 | 86 | 86 | 0.73672 | 35.7528 | 21.0651 | 166.2216 | 0 | 0 | 0.33662 | 0.67341 | 0.61572 | 0.19735 | 0 | 0 | 0.24719 | 17.0772 | 17.0772 | 17.0772 | 17.0772 | 17.0772 | 17.0772 | 17.0772 | 17.0772 | 35.7528 | 17.0772 | 17.0772 | 17.4139 | 17.7506 | 17.693 | 17.2746 | 17.0772 | 17.0772 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 13 | 877 | 11.8 | 11.8 | 12.1542 | 10.8956 | 15 | 84 | 84 | 0.60244 | 35.7765 | 22.0351 | 181.704 | 0 | 0 | 0.13389 | 0.48076 | 0.546 | 0.2914 | 0 | 0 | 0.22353 | 17.0454 | 17.0454 | 17.0454 | 17.0454 | 17.0454 | 17.0454 | 17.0454 | 17.0454 | 35.7765 | 17.0454 | 17.0454 | 17.1793 | 17.5262 | 17.5914 | 17.3368 | 17.0454 | 17.0454 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 14 | 878 | 12.4 | 12.4 | 12.1542 | 10.8956 | 15 | 84 | 84 | 0.1376 | 16.9496 | 20.5279 | 197.1085 | 0 | 0 | 0 | 0.087472 | 0.1275 | 0.092836 | 0.003793 | 0 | 0.050448 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 7.9581 | 16.9496 | 7.9581 | 7.9581 | 7.9581 | 8.0456 | 8.0856 | 8.0509 | 7.9619 | 7.9581 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 15 | 879 | 12.8 | 12.8 | 12.1542 | 10.8956 | 15 | 82 | 82 | 0.38446 | 24.876 | 16.7126 | 211.7977 | 0 | 0 | 0 | 0.16843 | 0.34412 | 0.31822 | 0.10592 | 0 | 0.12401 | 11.7537 | 11.7537 | 11.7537 | 11.7537 | 11.7537 | 11.7537 | 11.7537 | 11.7537 | 24.876 | 11.7537 | 11.7537 | 11.7537 | 11.9222 | 12.0979 | 12.072 | 11.8597 | 11.7537 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 16 | 880 | 12.8 | 12.8 | 12.1542 | 10.8956 | 15 | 79 | 79 | 0.13239 | 10.968 | 10.964 | 225.4337 | 0 | 0 | 0 | 0.028959 | 0.10777 | 0.12345 | 0.066812 | 0 | 0.032018 | 5.1202 | 5.1202 | 5.1202 | 5.1202 | 5.1202 | 5.1202 | 5.1202 | 5.1202 | 10.968 | 5.1202 | 5.1202 | 5.1202 | 5.1492 | 5.228 | 5.2436 | 5.187 | 5.1202 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 17 | 881 | 11.8 | 11.8 | 12.1542 | 10.8956 | 15 | 85 | 85 | 0.13625 | 5.9823 | 3.7364 | 238.0319 | 0 | 0 | 0 | 0 | 0.093863 | 0.13375 | 0.095295 | 0.0010124 | 0.017717 | 2.776 | 2.776 | 2.776 | 2.776 | 2.776 | 2.776 | 2.776 | 2.776 | 5.9823 | 2.776 | 2.776 | 2.776 | 2.776 | 2.8699 | 2.9098 | 2.8713 | 2.777 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 6 | 18 | 882 | 11.2 | 11.2 | 12.1542 | 10.8956 | 15 | 92 | 92 | 0 | 0 | -4.5304 | 249.8656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 19 | 883 | 10.9 | 10.9 | 12.1542 | 10.8956 | 15 | 94 | 94 | 0 | 0 | -13.4411 | 261.3653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 20 | 884 | 11 | 11 | 12.1542 | 10.8956 | 15 | 92 | 92 | 0 | 0 | -22.6282 | 273.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 21 | 885 | 11.2 | 11.2 | 12.1542 | 10.8956 | 15 | 90 | 90 | 0 | 0 | -31.7034 | 285.7159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 22 | 886 | 11 | 11 | 12.1542 | 10.8956 | 15 | 90 | 90 | 0 | 0 | -40.1781 | 300.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 23 | 887 | 10.8 | 10.8 | 12.1542 | 10.8956 | 15 | 85 | 85 | 0 | 0 | -47.3521 | 317.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 6 | 24 | 888 | 9.8 | 9.8 | 11.075 | 11.4496 | 15 | 83 | 83 | 0 | 0 | -52.2282 | 338.7247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 1 | 889 | 9.8 | 9.8 | 11.075 | 11.4496 | 15 | 76 | 76 | 0 | 0 | -53.7264 | 2.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 2 | 890 | 9.2 | 9.2 | 11.075 | 11.4496 | 15 | 77 | 77 | 0 | 0 | -51.1263 | 26.0469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 3 | 891 | 8.7 | 8.7 | 11.075 | 11.4496 | 15 | 78 | 78 | 0 | 0 | -45.6754 | 46.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 4 | 892 | 8.6 | 8.6 | 11.075 | 11.4496 | 15 | 80 | 80 | 0 | 0 | -38.1638 | 62.9519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 5 | 893 | 8.4 | 8.4 | 11.075 | 11.4496 | 15 | 77 | 77 | 0 | 0 | -29.5201 | 76.9335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 6 | 894 | 6.9 | 6.9 | 11.075 | 11.4496 | 15 | 89 | 89 | 0 | 0 | -20.3881 | 89.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 7 | 895 | 7 | 7 | 11.075 | 11.4496 | 15 | 82 | 82 | 0 | 0 | -11.2268 | 100.9377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 7 | 8 | 896 | 7.3 | 7.3 | 11.075 | 11.4496 | 15 | 78 | 78 | 0 | 0 | -2.4157 | 112.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 9 | 897 | 7 | 7 | 11.075 | 11.4496 | 15 | 85 | 85 | 0.61971 | 2.9811 | 5.6733 | 124.4692 | 0 | 0.23712 | 0.5721 | 0.57195 | 0.23677 | 0 | 0 | 0 | 0.018896 | 1.4045 | 1.6749 | 2.057 | 2.0568 | 1.6745 | 1.4045 | 1.4045 | 1.4045 | 2.9811 | 1.4045 | 1.912 | 2.6291 | 2.6288 | 1.9113 | 1.4045 | 1.4045 | 1.4045 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 10 | 898 | 6.5 | 6.5 | 11.075 | 11.4496 | 15 | 87 | 87 | 0.48065 | 13.9223 | 12.6336 | 137.3032 | 0 | 0.087415 | 0.39432 | 0.47024 | 0.2707 | 0 | 0 | 0 | 0.077659 | 6.6199 | 6.6199 | 6.6199 | 6.6199 | 6.6199 | 6.6199 | 6.6199 | 6.6199 | 13.9223 | 6.6199 | 6.7073 | 7.0143 | 7.0902 | 6.8906 | 6.6199 | 6.6199 | 6.6199 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 11 | 899 | 6 | 6 | 11.075 | 11.4496 | 15 | 90 | 90 | 0.32349 | 18.9135 | 18.0147 | 151.2152 | 0 | 0 | 0.21405 | 0.3154 | 0.23199 | 0.012685 | 0 | 0 | 0.086463 | 8.9219 | 8.9219 | 8.9219 | 8.9219 | 8.9219 | 8.9219 | 8.9219 | 8.9219 | 18.9135 | 8.9219 | 8.9219 | 9.1359 | 9.2373 | 9.1539 | 8.9346 | 8.9219 | 8.9219 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 12 | 900 | 7.5 | 7.5 | 11.075 | 11.4496 | 15 | 80 | 80 | 0.97444 | 41.6683 | 21.3659 | 166.1504 | 0 | 0 | 0.44621 | 0.88981 | 0.81217 | 0.25877 | 0 | 0 | 0.33172 | 20.0032 | 20.0032 | 20.0032 | 20.0032 | 20.0032 | 20.0032 | 20.0032 | 20.0032 | 41.6683 | 20.0032 | 20.0032 | 20.4494 | 20.893 | 20.8154 | 20.262 | 20.0032 | 20.0032 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 13 | 901 | 8.4 | 8.4 | 11.075 | 11.4496 | 15 | 75 | 75 | 32.6699 | 159.7164 | 22.3427 | 181.6889 | 0 | 0 | 7.2829 | 26.0378 | 29.5401 | 15.7382 | 0 | 0 | 12.2836 | 74.5327 | 74.5327 | 92.2647 | 137.9281 | 146.4554 | 112.8513 | 74.5327 | 74.5327 | 159.7164 | 74.5327 | 74.5327 | 99.5476 | 163.9659 | 175.9955 | 128.5895 | 74.5327 | 74.5327 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 14 | 902 | 8.7 | 8.7 | 11.075 | 11.4496 | 15 | 71 | 71 | 107.2764 | 177.1409 | 20.8336 | 197.1494 | 0 | 0 | 0 | 68.0628 | 99.1797 | 72.1985 | 2.9244 | 0 | 39.8591 | 84.2959 | 84.2959 | 84.2959 | 141.8643 | 168.1834 | 145.3624 | 86.7694 | 84.2959 | 177.1409 | 84.2959 | 84.2959 | 84.2959 | 209.9271 | 267.3631 | 217.5608 | 89.6938 | 84.2959 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 15 | 903 | 8.7 | 8.7 | 11.075 | 11.4496 | 15 | 69 | 69 | 149.93 | 156.9101 | 17.0086 | 211.8863 | 0 | 0 | 0 | 65.4628 | 133.897 | 123.8962 | 41.3186 | 0 | 49.0899 | 77.5072 | 77.5072 | 77.5072 | 124.9707 | 174.5885 | 167.3374 | 107.465 | 77.5072 | 156.9101 | 77.5072 | 77.5072 | 77.5072 | 190.4335 | 308.4856 | 291.2336 | 148.7836 | 77.5072 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 16 | 904 | 8.3 | 8.3 | 11.075 | 11.4496 | 15 | 69 | 69 | 129.0472 | 118.1768 | 11.2467 | 225.5583 | 0 | 0 | 0 | 27.9981 | 104.781 | 120.1846 | 65.1857 | 0 | 31.8232 | 59.3294 | 59.3294 | 59.3294 | 78.6728 | 131.7208 | 142.3629 | 104.3651 | 59.3294 | 118.1768 | 59.3294 | 59.3294 | 59.3294 | 106.6709 | 236.5018 | 262.5475 | 169.5508 | 59.3294 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 17 | 905 | 7.8 | 7.8 | 11.075 | 11.4496 | 15 | 73 | 73 | 24.1305 | 54.7515 | 4.0055 | 238.1821 | 0 | 0 | 0 | 0 | 16.5713 | 23.666 | 16.8974 | 0.23059 | 3.2485 | 27.4534 | 27.4534 | 27.4534 | 27.4534 | 44.8843 | 52.3469 | 45.2273 | 27.696 | 54.7515 | 27.4534 | 27.4534 | 27.4534 | 27.4534 | 61.4556 | 76.0129 | 62.1247 | 27.9266 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 7 | 18 | 906 | 7.4 | 7.4 | 11.075 | 11.4496 | 15 | 78 | 78 | 0 | 6 | -4.2725 | 250.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 6 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 2.8034 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 19 | 907 | 7.3 | 7.3 | 11.075 | 11.4496 | 15 | 82 | 82 | 0 | 0 | -13.1902 | 261.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 20 | 908 | 5 | 5 | 11.075 | 11.4496 | 15 | 90 | 90 | 0 | 0 | -22.3787 | 273.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 21 | 909 | 5.8 | 5.8 | 11.075 | 11.4496 | 15 | 87 | 87 | 0 | 0 | -31.4486 | 285.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 22 | 910 | 6.3 | 6.3 | 11.075 | 11.4496 | 15 | 87 | 87 | 0 | 0 | -39.9107 | 300.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 23 | 911 | 6.1 | 6.1 | 11.075 | 11.4496 | 15 | 73 | 73 | 0 | 0 | -47.066 | 317.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 7 | 24 | 912 | 6.1 | 6.1 | 7.45 | 10.8352 | 15 | 71 | 71 | 0 | 0 | -51.9246 | 338.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 1 | 913 | 5.9 | 5.9 | 7.45 | 10.8352 | 15 | 77 | 77 | 0 | 0 | -53.4198 | 2.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 2 | 914 | 5.4 | 5.4 | 7.45 | 10.8352 | 15 | 85 | 85 | 0 | 0 | -50.8315 | 25.8835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 3 | 915 | 1.9 | 1.9 | 7.45 | 10.8352 | 15 | 94 | 94 | 0 | 0 | -45.4061 | 46.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 4 | 916 | 2.8 | 2.8 | 7.45 | 10.8352 | 15 | 89 | 89 | 0 | 0 | -37.9163 | 62.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 5 | 917 | 4.2 | 4.2 | 7.45 | 10.8352 | 15 | 74 | 74 | 0 | 0 | -29.2858 | 76.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 6 | 918 | 2.7 | 2.7 | 7.45 | 10.8352 | 15 | 91 | 91 | 0 | 0 | -20.1583 | 89.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 7 | 919 | 4.4 | 4.4 | 7.45 | 10.8352 | 15 | 84 | 84 | 0 | 0 | -10.9939 | 100.7257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 8 | 8 | 920 | 3.4 | 3.4 | 7.45 | 10.8352 | 15 | 85 | 85 | 0 | 0 | -2.1735 | 112.2852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 9 | 921 | 2.7 | 2.7 | 7.45 | 10.8352 | 15 | 85 | 85 | 16.7425 | 13.4143 | 5.9298 | 124.2902 | 0 | 6.4604 | 15.4808 | 15.4328 | 6.3445 | 0 | 0 | 0 | 0.58568 | 4.8562 | 10.1318 | 17.4979 | 17.4587 | 10.0371 | 4.8562 | 4.8562 | 4.8562 | 13.4143 | 4.8562 | 16.5921 | 32.9787 | 32.8915 | 16.3816 | 4.8562 | 4.8562 | 4.8562 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 10 | 922 | 4.7 | 4.7 | 7.45 | 10.8352 | 15 | 77 | 77 | 30.4828 | 69.932 | 12.9076 | 137.1495 | 0 | 5.6344 | 25.05 | 29.7916 | 17.0817 | 0 | 0 | 0 | 5.068 | 31.1832 | 57.1217 | 146.5026 | 168.3309 | 109.8199 | 31.1832 | 31.1832 | 31.1832 | 69.932 | 31.1832 | 62.7562 | 171.5525 | 198.1224 | 126.9016 | 31.1832 | 31.1832 | 31.1832 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 11 | 923 | 5.2 | 5.2 | 7.45 | 10.8352 | 15 | 73 | 73 | 90.0055 | 128.5068 | 18.3064 | 151.0978 | 0 | 0 | 59.6649 | 87.6695 | 64.3185 | 3.2906 | 0 | 0 | 24.4932 | 59.5365 | 59.5365 | 137.1153 | 173.5281 | 143.1661 | 63.815 | 59.5365 | 59.5365 | 128.5068 | 59.5365 | 59.5365 | 196.7802 | 261.1976 | 207.4846 | 67.1056 | 59.5365 | 59.5365 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 12 | 924 | 6.8 | 6.8 | 7.45 | 10.8352 | 15 | 66 | 66 | 781.4101 | 77.117 | 21.6715 | 166.0815 | 0 | 0 | 358.5548 | 712.7748 | 649.4611 | 205.7019 | 0 | 0 | 269.883 | 66.0641 | 66.0641 | 107.6272 | 148.6878 | 141.3486 | 89.9088 | 66.0641 | 66.0641 | 77.117 | 66.0641 | 66.0641 | 466.182 | 861.4627 | 790.8097 | 295.6106 | 66.0641 | 66.0641 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 13 | 925 | 4.4 | 4.4 | 7.45 | 10.8352 | 15 | 83 | 83 | 8.5766 | 127.7323 | 22.6548 | 181.6773 | 0 | 0 | 1.9172 | 6.8261 | 7.7364 | 4.1148 | 0 | 0 | 3.2677 | 61.158 | 61.158 | 65.9822 | 78.3342 | 80.6247 | 71.5118 | 61.158 | 61.158 | 127.7323 | 61.158 | 61.158 | 67.8994 | 85.1603 | 88.361 | 75.6265 | 61.158 | 61.158 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 14 | 926 | 2.8 | 2.8 | 7.45 | 10.8352 | 15 | 89 | 89 | 1.8498 | 63.3034 | 21.1429 | 197.1948 | 0 | 0 | 0 | 1.1713 | 1.7064 | 1.2419 | 0.049967 | 0 | 0.69658 | 30.7482 | 30.7482 | 30.7482 | 30.7482 | 30.7482 | 30.7482 | 30.7482 | 30.7482 | 63.3034 | 30.7482 | 30.7482 | 30.7482 | 31.9195 | 32.4546 | 31.9902 | 30.7982 | 30.7482 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 15 | 927 | 5.6 | 5.6 | 7.45 | 10.8352 | 15 | 78 | 78 | 217.0682 | 155.856 | 17.3078 | 211.98 | 0 | 0 | 0 | 94.4389 | 193.4072 | 179.0801 | 59.8504 | 0 | 72.144 | 79.5094 | 79.5094 | 79.5094 | 125.7091 | 174.1247 | 167.1159 | 108.7883 | 79.5094 | 155.856 | 79.5094 | 79.5094 | 79.5094 | 220.1481 | 367.5319 | 346.196 | 168.6387 | 79.5094 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 16 | 928 | 5.4 | 5.4 | 7.45 | 10.8352 | 15 | 69 | 69 | 31.2852 | 106.1344 | 11.5319 | 225.6881 | 0 | 0 | 0 | 6.7292 | 25.3355 | 29.1007 | 15.8191 | 0 | 7.8656 | 51.3731 | 51.3731 | 51.3731 | 61.9931 | 91.3577 | 97.2999 | 76.3388 | 51.3731 | 106.1344 | 51.3731 | 51.3731 | 51.3731 | 68.7222 | 116.6933 | 126.4006 | 92.1579 | 51.3731 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 17 | 929 | 4.9 | 4.9 | 7.45 | 10.8352 | 15 | 77 | 77 | 6.5461 | 43.0883 | 4.2765 | 238.3375 | 0 | 0 | 0 | 0 | 4.4806 | 6.4135 | 4.5895 | 0.077022 | 0.91166 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 43.0883 | 21.0806 | 21.0806 | 21.0806 | 21.0806 | 25.5612 | 27.4941 | 25.6701 | 21.1576 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 8 | 18 | 930 | 4.4 | 4.4 | 7.45 | 10.8352 | 15 | 82 | 82 | 14.7314 | 0.99 | -4.0129 | 250.2085 | 0 | 0 | 0 | 0 | 7.7112 | 14.2942 | 12.5038 | 3.3889 | 5.01 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 3.7647 | 6.0325 | 5.4158 | 2.2757 | 0.99 | 1.1082 | 1.1082 | 1.1082 | 1.1082 | 11.4759 | 20.3267 | 17.9195 | 5.6646 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 19 | 931 | 3.7 | 3.7 | 7.45 | 10.8352 | 15 | 89 | 89 | 0 | 0 | -12.9377 | 261.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 20 | 932 | 2.9 | 2.9 | 7.45 | 10.8352 | 15 | 92 | 92 | 0 | 0 | -22.1275 | 273.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 21 | 933 | 4.5 | 4.5 | 7.45 | 10.8352 | 15 | 74 | 74 | 0 | 0 | -31.1919 | 286.1273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 22 | 934 | 4.6 | 4.6 | 7.45 | 10.8352 | 15 | 72 | 72 | 0 | 0 | -39.641 | 300.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 23 | 935 | 4.2 | 4.2 | 7.45 | 10.8352 | 15 | 64 | 64 | 0 | 0 | -46.777 | 317.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 8 | 24 | 936 | 3.3 | 3.3 | 4.2 | 9.1554 | 15 | 72 | 72 | 0 | 0 | -51.6173 | 338.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 1 | 937 | 3.8 | 3.8 | 4.2 | 9.1554 | 15 | 70 | 70 | 0 | 0 | -53.1086 | 2.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 2 | 938 | 3 | 3 | 4.2 | 9.1554 | 15 | 73 | 73 | 0 | 0 | -50.5314 | 25.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 3 | 939 | 3.4 | 3.4 | 4.2 | 9.1554 | 15 | 70 | 70 | 0 | 0 | -45.1311 | 45.8493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 4 | 940 | 2.2 | 2.2 | 4.2 | 9.1554 | 15 | 90 | 90 | 0 | 0 | -37.6629 | 62.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 5 | 941 | 2.9 | 2.9 | 4.2 | 9.1554 | 15 | 78 | 78 | 0 | 0 | -29.0457 | 76.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 6 | 942 | 2.8 | 2.8 | 4.2 | 9.1554 | 15 | 74 | 74 | 0 | 0 | -19.9228 | 88.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 7 | 943 | 2.3 | 2.3 | 4.2 | 9.1554 | 15 | 79 | 79 | 0 | 0 | -10.7555 | 100.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 9 | 8 | 944 | 2.5 | 2.5 | 4.2 | 9.1554 | 15 | 81 | 81 | 0 | 0 | -1.9259 | 112.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 9 | 945 | 3.1 | 3.1 | 4.2 | 9.1554 | 15 | 81 | 81 | 153.6722 | 18.9248 | 6.1917 | 124.1115 | 0 | 59.7933 | 142.3133 | 141.4681 | 57.7528 | 0 | 0 | 0 | 6.0752 | 9.7904 | 12.0569 | 15.185 | 15.1529 | 11.9796 | 9.7904 | 9.7904 | 9.7904 | 18.9248 | 9.7904 | 71.8502 | 157.4983 | 156.621 | 69.7324 | 9.7904 | 9.7904 | 9.7904 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 10 | 946 | 3.8 | 3.8 | 4.2 | 9.1554 | 15 | 77 | 77 | 62.2793 | 78.3499 | 13.1868 | 136.9965 | 0 | 11.6958 | 51.2632 | 60.8013 | 34.7228 | 0 | 0 | 0 | 10.6501 | 34.7473 | 65.662 | 170.2475 | 195.4588 | 126.5275 | 34.7473 | 34.7473 | 34.7473 | 78.3499 | 34.7473 | 77.3578 | 221.5107 | 256.2601 | 161.2503 | 34.7473 | 34.7473 | 34.7473 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 11 | 947 | 4.8 | 4.8 | 4.2 | 9.1554 | 15 | 74 | 74 | 30.5594 | 116.534 | 18.6031 | 150.9817 | 0 | 0 | 20.2932 | 29.7355 | 21.7591 | 1.0366 | 0 | 0 | 8.466 | 53.8393 | 53.8393 | 115.2347 | 143.8016 | 119.6698 | 56.9754 | 53.8393 | 53.8393 | 116.534 | 53.8393 | 53.8393 | 135.5279 | 173.5371 | 141.429 | 58.012 | 53.8393 | 53.8393 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 12 | 948 | 5 | 5 | 4.2 | 9.1554 | 15 | 76 | 76 | 12.1594 | 126.7394 | 21.9819 | 166.015 | 0 | 0 | 5.5902 | 11.0787 | 10.0774 | 3.1729 | 0 | 0 | 4.2606 | 59.0235 | 59.0235 | 77.4914 | 95.6233 | 92.3154 | 69.5057 | 59.0235 | 59.0235 | 126.7394 | 59.0235 | 59.0235 | 83.0816 | 106.7019 | 102.3928 | 72.6786 | 59.0235 | 59.0235 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 13 | 949 | 3.5 | 3.5 | 4.2 | 9.1554 | 15 | 80 | 80 | 17.5714 | 149.2162 | 22.9712 | 181.6692 | 0 | 0 | 3.9377 | 13.9645 | 15.8111 | 8.3957 | 0 | 0 | 6.7838 | 69.7286 | 69.7286 | 78.9363 | 102.3821 | 106.7 | 89.3605 | 69.7286 | 69.7286 | 149.2162 | 69.7286 | 69.7286 | 82.8741 | 116.3467 | 122.511 | 97.7562 | 69.7286 | 69.7286 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 14 | 950 | 5.7 | 5.7 | 4.2 | 9.1554 | 15 | 71 | 71 | 99.1642 | 181.1567 | 21.456 | 197.2447 | 0 | 0 | 0 | 62.6514 | 91.2619 | 66.4124 | 2.6594 | 0 | 37.8433 | 85.8534 | 85.8534 | 85.8534 | 143.3914 | 169.6668 | 146.8454 | 88.2958 | 85.8534 | 181.1567 | 85.8534 | 85.8534 | 85.8534 | 206.0428 | 260.9286 | 213.2578 | 90.9552 | 85.8534 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 15 | 951 | 5.6 | 5.6 | 4.2 | 9.1554 | 15 | 70 | 70 | 44.4772 | 148.9955 | 17.61 | 212.0786 | 0 | 0 | 0 | 19.2775 | 39.534 | 36.6321 | 12.2716 | 0 | 15.0045 | 70.6492 | 70.6492 | 70.6492 | 100.7367 | 132.3524 | 127.8232 | 89.8023 | 70.6492 | 148.9955 | 70.6492 | 70.6492 | 70.6492 | 120.0142 | 171.8865 | 164.4554 | 102.0739 | 70.6492 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 16 | 952 | 4.9 | 4.9 | 4.2 | 9.1554 | 15 | 75 | 75 | 14.8322 | 96.1986 | 11.8194 | 225.8231 | 0 | 0 | 0 | 3.1613 | 11.9787 | 13.7791 | 7.508 | 0 | 3.8014 | 46.7899 | 46.7899 | 46.7899 | 49.5017 | 57.0653 | 58.6097 | 53.2303 | 46.7899 | 96.1986 | 46.7899 | 46.7899 | 46.7899 | 52.6629 | 69.0439 | 72.3889 | 60.7383 | 46.7899 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 17 | 953 | 3.4 | 3.4 | 4.2 | 9.1554 | 15 | 81 | 81 | 5.4516 | 41.2151 | 4.5495 | 238.4981 | 0 | 0 | 0 | 0 | 3.7185 | 5.3354 | 3.8269 | 0.076649 | 0.78489 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 41.2151 | 20.0862 | 20.0862 | 20.0862 | 20.0862 | 23.8047 | 25.4217 | 23.9131 | 20.1629 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 9 | 18 | 954 | 3 | 3 | 4.2 | 9.1554 | 15 | 88 | 88 | 22.3495 | 1.815 | -3.7517 | 250.3876 | 0 | 0 | 0 | 0 | 11.6414 | 21.6637 | 18.9956 | 5.2002 | 9.185 | 2.0256 | 2.0256 | 2.0256 | 2.0256 | 6.8225 | 10.9522 | 9.8528 | 4.1684 | 1.815 | 2.0256 | 2.0256 | 2.0256 | 2.0256 | 18.4639 | 32.6158 | 28.8485 | 9.3686 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 19 | 955 | 2.8 | 2.8 | 4.2 | 9.1554 | 15 | 88 | 88 | 0 | 0 | -12.6836 | 261.9309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 20 | 956 | 2.7 | 2.7 | 4.2 | 9.1554 | 15 | 90 | 90 | 0 | 0 | -21.8748 | 273.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 21 | 957 | 2.7 | 2.7 | 4.2 | 9.1554 | 15 | 90 | 90 | 0 | 0 | -30.9334 | 286.3404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 22 | 958 | 2.8 | 2.8 | 4.2 | 9.1554 | 15 | 93 | 93 | 0 | 0 | -39.369 | 300.7977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 23 | 959 | 2.3 | 2.3 | 4.2 | 9.1554 | 15 | 94 | 94 | 0 | 0 | -46.4852 | 318.1097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 9 | 24 | 960 | 1.8 | 1.8 | 3.3667 | 7.5247 | 15 | 95 | 95 | 0 | 0 | -51.3064 | 338.9938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 1 | 961 | 1.7 | 1.7 | 3.3667 | 7.5247 | 15 | 94 | 94 | 0 | 0 | -52.7929 | 2.5419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 2 | 962 | 2.5 | 2.5 | 3.3667 | 7.5247 | 15 | 89 | 89 | 0 | 0 | -50.2261 | 25.5716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 3 | 963 | 1.1 | 1.1 | 3.3667 | 7.5247 | 15 | 91 | 91 | 0 | 0 | -44.8503 | 45.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 4 | 964 | 1.6 | 1.6 | 3.3667 | 7.5247 | 15 | 85 | 85 | 0 | 0 | -37.4037 | 62.2323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 5 | 965 | 0.9 | 0.9 | 3.3667 | 7.5247 | 15 | 87 | 87 | 0 | 0 | -28.7998 | 76.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 6 | 966 | 0.3 | 0.3 | 3.3667 | 7.5247 | 15 | 88 | 88 | 0 | 0 | -19.6817 | 88.6339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 7 | 967 | 0.7 | 0.7 | 3.3667 | 7.5247 | 15 | 88 | 88 | 0 | 0 | -10.5117 | 100.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 10 | 8 | 968 | 0.8 | 0.8 | 3.3667 | 7.5247 | 15 | 90 | 90 | 0 | 0 | -1.6729 | 111.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 9 | 969 | 1.8 | 1.8 | 3.3667 | 7.5247 | 15 | 87 | 87 | 0.29595 | 2.9869 | 6.4588 | 123.9331 | 0 | 0.11611 | 0.27449 | 0.27209 | 0.1103 | 0 | 0 | 0 | 0.013065 | 1.4066 | 1.6845 | 2.0635 | 2.0577 | 1.6706 | 1.4066 | 1.4066 | 1.4066 | 2.9869 | 1.4066 | 1.8006 | 2.338 | 2.3298 | 1.7809 | 1.4066 | 1.4066 | 1.4066 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 10 | 970 | 2.8 | 2.8 | 3.3667 | 7.5247 | 15 | 82 | 82 | 4.5798 | 46.1948 | 13.4711 | 136.8443 | 0 | 0.87354 | 3.7757 | 4.4661 | 2.5404 | 0 | 0 | 0 | 0.80519 | 21.3348 | 28.8861 | 53.9737 | 59.9419 | 43.2946 | 21.3348 | 21.3348 | 21.3348 | 46.1948 | 21.3348 | 29.7596 | 57.7494 | 64.4081 | 45.835 | 21.3348 | 21.3348 | 21.3348 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 11 | 971 | 3.4 | 3.4 | 3.3667 | 7.5247 | 15 | 82 | 82 | 5.2872 | 79.509 | 18.9047 | 150.867 | 0 | 0 | 3.5168 | 5.139 | 3.7509 | 0.16548 | 0 | 0 | 1.491 | 37.9738 | 37.9738 | 50.7342 | 56.6201 | 51.5833 | 38.5742 | 37.9738 | 37.9738 | 79.509 | 37.9738 | 37.9738 | 54.2511 | 61.7592 | 55.3342 | 38.7397 | 37.9738 | 37.9738 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 12 | 972 | 4.5 | 4.5 | 3.3667 | 7.5247 | 15 | 79 | 79 | 26.5969 | 146.5457 | 22.297 | 165.951 | 0 | 0 | 12.2499 | 24.2035 | 21.979 | 6.8795 | 0 | 0 | 9.4543 | 66.6387 | 66.6387 | 96.5369 | 125.7117 | 120.2824 | 83.4294 | 66.6387 | 66.6387 | 146.5457 | 66.6387 | 66.6387 | 108.7868 | 149.9153 | 142.2615 | 90.3089 | 66.6387 | 66.6387 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 13 | 973 | 4.7 | 4.7 | 3.3667 | 7.5247 | 15 | 77 | 77 | 13.6774 | 144.6494 | 23.2918 | 181.6646 | 0 | 0 | 3.072 | 10.8528 | 12.2763 | 6.5084 | 0 | 0 | 5.3506 | 68.123 | 68.123 | 75.8203 | 95.3165 | 98.8831 | 84.4308 | 68.123 | 68.123 | 144.6494 | 68.123 | 68.123 | 78.8923 | 106.1693 | 111.1593 | 90.9393 | 68.123 | 68.123 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 14 | 974 | 4.8 | 4.8 | 3.3667 | 7.5247 | 15 | 77 | 77 | 2.4101 | 74.0679 | 21.7726 | 197.299 | 0 | 0 | 0 | 1.5192 | 2.2127 | 1.6101 | 0.064304 | 0 | 0.93208 | 36.2229 | 36.2229 | 36.2229 | 36.2229 | 36.2229 | 36.2229 | 36.2229 | 36.2229 | 74.0679 | 36.2229 | 36.2229 | 36.2229 | 37.742 | 38.4356 | 37.833 | 36.2872 | 36.2229 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 15 | 975 | 5 | 5 | 3.3667 | 7.5247 | 15 | 79 | 79 | 2.0339 | 60.3036 | 17.915 | 212.1823 | 0 | 0 | 0 | 0.87802 | 1.8034 | 1.6723 | 0.56165 | 0 | 0.69641 | 29.2636 | 29.2636 | 29.2636 | 29.2636 | 29.2636 | 29.2636 | 29.2636 | 29.2636 | 60.3036 | 29.2636 | 29.2636 | 29.2636 | 30.1416 | 31.0669 | 30.9359 | 29.8252 | 29.2636 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 16 | 976 | 5.2 | 5.2 | 3.3667 | 7.5247 | 15 | 80 | 80 | 3.8466 | 62.9952 | 12.1092 | 225.9632 | 0 | 0 | 0 | 0.812 | 3.0978 | 3.5689 | 1.9494 | 0 | 1.0048 | 30.8524 | 30.8524 | 30.8524 | 30.8524 | 30.8524 | 30.8524 | 30.8524 | 30.8524 | 62.9952 | 30.8524 | 30.8524 | 30.8524 | 31.6644 | 33.9502 | 34.4213 | 32.8018 | 30.8524 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 17 | 977 | 5.1 | 5.1 | 3.3667 | 7.5247 | 15 | 84 | 84 | 3.1544 | 32.5308 | 4.8243 | 238.6639 | 0 | 0 | 0 | 0 | 2.1439 | 3.0838 | 2.2172 | 0.051849 | 0.46919 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 32.5308 | 15.6534 | 15.6534 | 15.6534 | 15.6534 | 17.7973 | 18.7372 | 17.8707 | 15.7053 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 18 | 978 | 4.9 | 4.9 | 3.3667 | 7.5247 | 15 | 86 | 86 | 3.6191 | 2.9543 | -3.489 | 250.5717 | 0 | 0 | 0 | 0 | 1.8755 | 3.5043 | 3.0803 | 0.8519 | 0.045688 | 1.6597 | 1.6597 | 1.6597 | 1.6597 | 3.1075 | 4.3649 | 4.0376 | 2.3173 | 2.9543 | 1.6597 | 1.6597 | 1.6597 | 1.6597 | 4.983 | 7.8692 | 7.1179 | 3.1692 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 19 | 979 | 4.8 | 4.8 | 3.3667 | 7.5247 | 15 | 93 | 93 | 0 | 0 | -12.4282 | 262.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 20 | 980 | 5.4 | 5.4 | 3.3667 | 7.5247 | 15 | 93 | 93 | 0 | 0 | -21.6205 | 273.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 21 | 981 | 6 | 6 | 3.3667 | 7.5247 | 15 | 93 | 93 | 0 | 0 | -30.6731 | 286.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 22 | 982 | 6.7 | 6.7 | 3.3667 | 7.5247 | 15 | 94 | 94 | 0 | 0 | -39.0948 | 301.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 23 | 983 | 7.3 | 7.3 | 3.3667 | 7.5247 | 15 | 95 | 95 | 0 | 0 | -46.1906 | 318.2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 10 | 24 | 984 | 7.7 | 7.7 | 3.7375 | 6.2192 | 15 | 96 | 96 | 0 | 0 | -50.992 | 339.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 1 | 985 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 96 | 96 | 0 | 0 | -52.4729 | 2.5104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 2 | 986 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0 | 0 | -49.9157 | 25.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 3 | 987 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0 | 0 | -44.564 | 45.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 4 | 988 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0 | 0 | -37.1388 | 61.9964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 5 | 989 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 98 | 98 | 0 | 0 | -28.5483 | 75.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 6 | 990 | 7.7 | 7.7 | 3.7375 | 6.2192 | 15 | 98 | 98 | 0 | 0 | -19.4351 | 88.4098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 7 | 991 | 7.6 | 7.6 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0 | 0 | -10.2624 | 100.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 11 | 8 | 992 | 7.4 | 7.4 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0 | 0 | -1.4147 | 111.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 9 | 993 | 7.1 | 7.1 | 3.7375 | 6.2192 | 15 | 97 | 97 | 0.24212 | 2.9882 | 6.731 | 123.755 | 0 | 0.095764 | 0.2249 | 0.2223 | 0.089474 | 0 | 0 | 0 | 0.011819 | 1.4071 | 1.6873 | 2.0652 | 2.0576 | 1.6689 | 1.4071 | 1.4071 | 1.4071 | 2.9882 | 1.4071 | 1.7831 | 2.2901 | 2.2799 | 1.7584 | 1.4071 | 1.4071 | 1.4071 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 10 | 994 | 7.6 | 7.6 | 3.7375 | 6.2192 | 15 | 97 | 97 | 16.4662 | 69.025 | 13.7604 | 136.6928 | 0 | 3.1888 | 13.596 | 16.0388 | 9.0863 | 0 | 0 | 0 | 2.975 | 29.0066 | 55.1181 | 140.3362 | 160.3388 | 103.4088 | 29.0066 | 29.0066 | 29.0066 | 69.025 | 29.0066 | 58.307 | 153.9321 | 176.3776 | 112.4951 | 29.0066 | 29.0066 | 29.0066 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 11 | 995 | 7.7 | 7.7 | 3.7375 | 6.2192 | 15 | 95 | 95 | 3.705 | 67.9366 | 19.2113 | 150.7539 | 0 | 0 | 2.4684 | 3.5971 | 2.6187 | 0.10631 | 0 | 0 | 1.0634 | 33.3902 | 33.3902 | 36.0477 | 37.263 | 36.2096 | 33.5047 | 33.3902 | 33.3902 | 67.9366 | 33.3902 | 33.3902 | 38.5161 | 40.86 | 38.8283 | 33.611 | 33.3902 | 33.3902 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 12 | 996 | 7.9 | 7.9 | 3.7375 | 6.2192 | 15 | 89 | 89 | 6.0746 | 108.8095 | 22.6166 | 165.8894 | 0 | 0 | 2.8025 | 5.5208 | 5.0051 | 1.5574 | 0 | 0 | 2.1905 | 52.3904 | 52.3904 | 60.0781 | 67.5347 | 66.12 | 56.6627 | 52.3904 | 52.3904 | 108.8095 | 52.3904 | 52.3904 | 62.8807 | 73.0555 | 71.125 | 58.2201 | 52.3904 | 52.3904 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 13 | 997 | 8 | 8 | 3.7375 | 6.2192 | 15 | 85 | 85 | 8.5345 | 132.6171 | 23.6164 | 181.6636 | 0 | 0 | 1.9207 | 6.7608 | 7.6405 | 4.0445 | 0 | 0 | 3.3829 | 63.5489 | 63.5489 | 68.3671 | 80.509 | 82.7159 | 73.695 | 63.5489 | 63.5489 | 132.6171 | 63.5489 | 63.5489 | 70.2877 | 87.2698 | 90.3564 | 77.7396 | 63.5489 | 63.5489 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 14 | 998 | 7.1 | 7.1 | 3.7375 | 6.2192 | 15 | 84 | 84 | 2.1637 | 71.152 | 22.0926 | 197.3577 | 0 | 0 | 0 | 1.3605 | 1.9816 | 1.4419 | 0.057552 | 0 | 0.84797 | 34.7124 | 34.7124 | 34.7124 | 34.7124 | 34.7124 | 34.7124 | 34.7124 | 34.7124 | 71.152 | 34.7124 | 34.7124 | 34.7124 | 36.0729 | 36.694 | 36.1543 | 34.7699 | 34.7124 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 15 | 999 | 6.1 | 6.1 | 3.7375 | 6.2192 | 15 | 85 | 85 | 1.1726 | 46.5925 | 18.2228 | 212.291 | 0 | 0 | 0 | 0.5041 | 1.0371 | 0.96252 | 0.32415 | 0 | 0.4075 | 22.3722 | 22.3722 | 22.3722 | 22.3722 | 22.3722 | 22.3722 | 22.3722 | 22.3722 | 46.5925 | 22.3722 | 22.3722 | 22.3722 | 22.8763 | 23.4093 | 23.3348 | 22.6964 | 22.3722 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 16 | 1000 | 5.1 | 5.1 | 3.7375 | 6.2192 | 15 | 86 | 86 | 1.9982 | 46.468 | 12.4011 | 226.1086 | 0 | 0 | 0 | 0.41757 | 1.6045 | 1.8515 | 1.014 | 0 | 0.53195 | 22.4101 | 22.4101 | 22.4101 | 22.4101 | 22.4101 | 22.4101 | 22.4101 | 22.4101 | 46.468 | 22.4101 | 22.4101 | 22.4101 | 22.8276 | 24.0145 | 24.2616 | 23.424 | 22.4101 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 17 | 1001 | 4.6 | 4.6 | 3.7375 | 6.2192 | 15 | 89 | 89 | 0.32894 | 10.9495 | 5.1007 | 238.8347 | 0 | 0 | 0 | 0 | 0.22273 | 0.3212 | 0.23152 | 0.0062156 | 0.050513 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 10.9495 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.338 | 5.4365 | 5.3468 | 5.1215 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 18 | 1002 | 4.1 | 4.1 | 3.7375 | 6.2192 | 15 | 89 | 89 | 0 | 0 | -3.2248 | 250.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 19 | 1003 | 4 | 4 | 3.7375 | 6.2192 | 15 | 90 | 90 | 0 | 0 | -12.1714 | 262.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 20 | 1004 | 4.1 | 4.1 | 3.7375 | 6.2192 | 15 | 89 | 89 | 0 | 0 | -21.3648 | 274.1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 21 | 1005 | 3.6 | 3.6 | 3.7375 | 6.2192 | 15 | 86 | 86 | 0 | 0 | -30.4111 | 286.7809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 22 | 1006 | 3.7 | 3.7 | 3.7375 | 6.2192 | 15 | 85 | 85 | 0 | 0 | -38.8185 | 301.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 23 | 1007 | 3.7 | 3.7 | 3.7375 | 6.2192 | 15 | 85 | 85 | 0 | 0 | -45.8933 | 318.4809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 11 | 24 | 1008 | 3.6 | 3.6 | 6.2583 | 5.8162 | 15 | 87 | 87 | 0 | 0 | -50.6743 | 339.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 1 | 1009 | 3.2 | 3.2 | 6.2583 | 5.8162 | 15 | 88 | 88 | 0 | 0 | -52.1486 | 2.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 2 | 1010 | 2.4 | 2.4 | 6.2583 | 5.8162 | 15 | 92 | 92 | 0 | 0 | -49.6005 | 25.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 3 | 1011 | 1.9 | 1.9 | 6.2583 | 5.8162 | 15 | 94 | 94 | 0 | 0 | -44.2723 | 45.2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 4 | 1012 | 2.3 | 2.3 | 6.2583 | 5.8162 | 15 | 94 | 94 | 0 | 0 | -36.8683 | 61.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 5 | 1013 | 2.5 | 2.5 | 6.2583 | 5.8162 | 15 | 94 | 94 | 0 | 0 | -28.2913 | 75.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 6 | 1014 | 2.5 | 2.5 | 6.2583 | 5.8162 | 15 | 90 | 90 | 0 | 0 | -19.1831 | 88.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 7 | 1015 | 2.5 | 2.5 | 6.2583 | 5.8162 | 15 | 90 | 90 | 0 | 0 | -10.0079 | 99.8793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 12 | 8 | 1016 | 2.6 | 2.6 | 6.2583 | 5.8162 | 15 | 92 | 92 | 0 | 0 | -1.1513 | 111.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 9 | 1017 | 3.5 | 3.5 | 6.2583 | 5.8162 | 15 | 89 | 89 | 2.7069 | 10.8551 | 7.0083 | 123.5774 | 0 | 1.0793 | 2.5181 | 2.4818 | 0.99178 | 0 | 0 | 0 | 0.14493 | 4.8233 | 6.7989 | 9.4328 | 9.3665 | 6.6388 | 4.8233 | 4.8233 | 4.8233 | 10.8551 | 4.8233 | 7.8782 | 11.9509 | 11.8483 | 7.6306 | 4.8233 | 4.8233 | 4.8233 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 10 | 1018 | 4.3 | 4.3 | 6.2583 | 5.8162 | 15 | 85 | 85 | 8.7064 | 62.3842 | 14.0547 | 136.5421 | 0 | 1.7114 | 7.1995 | 8.4702 | 4.7792 | 0 | 0 | 0 | 1.6158 | 27.274 | 44.6882 | 100.5329 | 113.4636 | 75.9055 | 27.274 | 27.274 | 27.274 | 62.3842 | 27.274 | 46.3996 | 107.7324 | 121.9338 | 80.6847 | 27.274 | 27.274 | 27.274 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 11 | 1019 | 5.1 | 5.1 | 6.2583 | 5.8162 | 15 | 84 | 84 | 40.1491 | 127.2729 | 19.5225 | 150.6422 | 0 | 0 | 26.7887 | 38.9331 | 28.271 | 1.0481 | 0 | 0 | 11.7271 | 58.6351 | 58.6351 | 124.7448 | 154.7149 | 128.4027 | 61.2216 | 58.6351 | 58.6351 | 127.2729 | 58.6351 | 58.6351 | 151.5335 | 193.6479 | 156.6737 | 62.2697 | 58.6351 | 58.6351 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 12 | 1020 | 6 | 6 | 6.2583 | 5.8162 | 15 | 86 | 86 | 5.906 | 108.8398 | 22.9407 | 165.8303 | 0 | 0 | 2.729 | 5.3603 | 4.8516 | 1.5009 | 0 | 0 | 2.1602 | 52.5452 | 52.5452 | 59.5799 | 66.3626 | 65.0513 | 56.414 | 52.5452 | 52.5452 | 108.8398 | 52.5452 | 52.5452 | 62.3089 | 71.7229 | 69.9028 | 57.9149 | 52.5452 | 52.5452 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 13 | 1021 | 6.1 | 6.1 | 6.2583 | 5.8162 | 15 | 87 | 87 | 6.7188 | 125.3017 | 23.945 | 181.6661 | 0 | 0 | 1.5146 | 5.313 | 5.9991 | 3.171 | 0 | 0 | 2.6983 | 60.752 | 60.752 | 63.9599 | 72.0044 | 73.4575 | 67.4679 | 60.752 | 60.752 | 125.3017 | 60.752 | 60.752 | 65.4745 | 77.3175 | 79.4566 | 70.6389 | 60.752 | 60.752 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 14 | 1022 | 6.7 | 6.7 | 6.2583 | 5.8162 | 15 | 88 | 88 | 5.5662 | 114.7895 | 22.416 | 197.421 | 0 | 0 | 0 | 3.491 | 5.085 | 3.7002 | 0.14791 | 0 | 2.2105 | 56.7977 | 56.7977 | 56.7977 | 59.4095 | 60.6021 | 59.566 | 56.9083 | 56.7977 | 114.7895 | 56.7977 | 56.7977 | 56.7977 | 62.9006 | 65.687 | 63.2663 | 57.0563 | 56.7977 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 15 | 1023 | 7.3 | 7.3 | 6.2583 | 5.8162 | 15 | 90 | 90 | 4.0842 | 87.5596 | 18.5332 | 212.4046 | 0 | 0 | 0 | 1.748 | 3.6024 | 3.3466 | 1.1304 | 0 | 1.4404 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 43.3032 | 87.5596 | 43.3032 | 43.3032 | 43.3032 | 45.0512 | 46.9056 | 46.6498 | 44.4336 | 43.3032 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 16 | 1024 | 7.7 | 7.7 | 6.2583 | 5.8162 | 15 | 88 | 88 | 3.5701 | 63.0316 | 12.6951 | 226.2591 | 0 | 0 | 0 | 0.73814 | 2.8579 | 3.3035 | 1.814 | 0 | 0.9684 | 30.8293 | 30.8293 | 30.8293 | 30.8293 | 30.8293 | 30.8293 | 30.8293 | 30.8293 | 63.0316 | 30.8293 | 30.8293 | 30.8293 | 31.5674 | 33.6872 | 34.1328 | 32.6433 | 30.8293 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 17 | 1025 | 7.7 | 7.7 | 6.2583 | 5.8162 | 15 | 87 | 87 | 6.5415 | 48.9636 | 5.3788 | 239.0106 | 0 | 0 | 0 | 0 | 4.4122 | 6.3801 | 4.6105 | 0.14022 | 1.0364 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 48.9636 | 24.0247 | 24.0247 | 24.0247 | 24.0247 | 28.437 | 30.4048 | 28.6353 | 24.165 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 12 | 18 | 1026 | 7.5 | 7.5 | 6.2583 | 5.8162 | 15 | 90 | 90 | 4.8013 | 5.8947 | -2.9593 | 250.9547 | 0 | 0 | 0 | 0 | 2.4612 | 4.638 | 4.0978 | 1.1573 | 0.10528 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 5.8947 | 3.1566 | 3.1566 | 3.1566 | 3.1566 | 5.6178 | 7.7946 | 7.2545 | 4.3139 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 19 | 1027 | 6.9 | 6.9 | 6.2583 | 5.8162 | 15 | 91 | 91 | 0 | 0 | -11.9133 | 262.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 20 | 1028 | 6.7 | 6.7 | 6.2583 | 5.8162 | 15 | 93 | 93 | 0 | 0 | -21.1077 | 274.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 21 | 1029 | 6.7 | 6.7 | 6.2583 | 5.8162 | 15 | 95 | 95 | 0 | 0 | -30.1475 | 287.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 22 | 1030 | 6.6 | 6.6 | 6.2583 | 5.8162 | 15 | 95 | 95 | 0 | 0 | -38.5401 | 301.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 23 | 1031 | 6.6 | 6.6 | 6.2583 | 5.8162 | 15 | 95 | 95 | 0 | 0 | -45.5934 | 318.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 12 | 24 | 1032 | 6.7 | 6.7 | 5.0833 | 5.3015 | 15 | 95 | 95 | 0 | 0 | -50.3533 | 339.3098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 1 | 1033 | 6.7 | 6.7 | 5.0833 | 5.3015 | 15 | 95 | 95 | 0 | 0 | -51.8202 | 2.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 2 | 1034 | 6.7 | 6.7 | 5.0833 | 5.3015 | 15 | 95 | 95 | 0 | 0 | -49.2804 | 25.1412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 3 | 1035 | 6.6 | 6.6 | 5.0833 | 5.3015 | 15 | 97 | 97 | 0 | 0 | -43.9753 | 44.9952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 4 | 1036 | 6.7 | 6.7 | 5.0833 | 5.3015 | 15 | 97 | 97 | 0 | 0 | -36.5924 | 61.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 5 | 1037 | 6.8 | 6.8 | 5.0833 | 5.3015 | 15 | 98 | 98 | 0 | 0 | -28.0289 | 75.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 6 | 1038 | 6.9 | 6.9 | 5.0833 | 5.3015 | 15 | 99 | 99 | 0 | 0 | -18.9258 | 87.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 7 | 1039 | 6.8 | 6.8 | 5.0833 | 5.3015 | 15 | 99 | 99 | 0 | 0 | -9.7482 | 99.6686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 13 | 8 | 1040 | 6.6 | 6.6 | 5.0833 | 5.3015 | 15 | 99 | 99 | 0 | 0 | -0.88289 | 111.3014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 9 | 1041 | 6.8 | 6.8 | 5.0833 | 5.3015 | 15 | 99 | 99 | 0.679 | 5.9604 | 7.2905 | 123.4002 | 0 | 0.27288 | 0.63254 | 0.62167 | 0.24664 | 0 | 0 | 0 | 0.039601 | 2.8052 | 3.3758 | 4.1279 | 4.1052 | 3.321 | 2.8052 | 2.8052 | 2.8052 | 5.9604 | 2.8052 | 3.6487 | 4.7604 | 4.7268 | 3.5676 | 2.8052 | 2.8052 | 2.8052 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 10 | 1042 | 7.4 | 7.4 | 5.0833 | 5.3015 | 15 | 95 | 95 | 1.924 | 32.6334 | 14.3537 | 136.3922 | 0 | 0.38373 | 1.5932 | 1.8694 | 1.0506 | 0 | 0 | 0 | 0.36663 | 16.0352 | 16.0352 | 16.0352 | 16.0352 | 16.0352 | 16.0352 | 16.0352 | 16.0352 | 32.6334 | 16.0352 | 16.4189 | 17.6284 | 17.9046 | 17.0858 | 16.0352 | 16.0352 | 16.0352 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 11 | 1043 | 8.4 | 8.4 | 5.0833 | 5.3015 | 15 | 88 | 88 | 4.4187 | 76.6867 | 19.8384 | 150.532 | 0 | 0 | 2.9525 | 4.2795 | 3.0996 | 0.10401 | 0 | 0 | 1.3133 | 37.2409 | 37.2409 | 43.9659 | 46.9883 | 44.3009 | 37.4778 | 37.2409 | 37.2409 | 76.6867 | 37.2409 | 37.2409 | 46.9184 | 51.2678 | 47.4005 | 37.5818 | 37.2409 | 37.2409 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 12 | 1044 | 9.2 | 9.2 | 5.0833 | 5.3015 | 15 | 82 | 82 | 4.6611 | 98.2707 | 23.269 | 165.7737 | 0 | 0 | 2.1569 | 4.2243 | 3.8172 | 1.1741 | 0 | 0 | 1.7293 | 48.3355 | 48.3355 | 50.9029 | 53.3639 | 52.8793 | 49.733 | 48.3355 | 48.3355 | 98.2707 | 48.3355 | 48.3355 | 53.0598 | 57.5882 | 56.6966 | 50.9071 | 48.3355 | 48.3355 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 13 | 1045 | 9.5 | 9.5 | 5.0833 | 5.3015 | 15 | 82 | 82 | 3.6461 | 95.5164 | 24.2774 | 181.6723 | 0 | 0 | 0.82316 | 2.8779 | 3.2468 | 1.7138 | 0 | 0 | 1.4836 | 47.4071 | 47.4071 | 47.4071 | 47.4071 | 47.4071 | 47.4071 | 47.4071 | 47.4071 | 95.5164 | 47.4071 | 47.4071 | 48.2302 | 50.285 | 50.6539 | 49.1209 | 47.4071 | 47.4071 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 14 | 1046 | 9.6 | 9.6 | 5.0833 | 5.3015 | 15 | 83 | 83 | 4.6211 | 106.1404 | 22.7425 | 197.4888 | 0 | 0 | 0 | 2.8904 | 4.2106 | 3.0643 | 0.12293 | 0 | 1.8596 | 52.9598 | 52.9598 | 52.9598 | 52.9598 | 52.9598 | 52.9598 | 52.9598 | 52.9598 | 106.1404 | 52.9598 | 52.9598 | 52.9598 | 55.8503 | 57.1704 | 56.0241 | 53.0828 | 52.9598 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 15 | 1047 | 9.6 | 9.6 | 5.0833 | 5.3015 | 15 | 83 | 83 | 4.713 | 95.3133 | 18.8461 | 212.5233 | 0 | 0 | 0 | 2.0078 | 4.1457 | 3.8551 | 1.3062 | 0 | 1.6867 | 47.3677 | 47.3677 | 47.3677 | 47.3677 | 47.3677 | 47.3677 | 47.3677 | 47.3677 | 95.3133 | 47.3677 | 47.3677 | 47.3677 | 49.3755 | 51.5134 | 51.2228 | 48.6739 | 47.3677 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 16 | 1048 | 9.7 | 9.7 | 5.0833 | 5.3015 | 15 | 76 | 76 | 12.055 | 99.6687 | 12.9909 | 226.4146 | 0 | 0 | 0 | 2.4648 | 9.6195 | 11.1393 | 6.1338 | 0 | 3.3313 | 48.6728 | 48.6728 | 48.6728 | 50.7856 | 56.9184 | 58.2211 | 53.9306 | 48.6728 | 99.6687 | 48.6728 | 48.6728 | 48.6728 | 53.2503 | 66.5379 | 69.3604 | 60.0644 | 48.6728 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 17 | 1049 | 9 | 9 | 5.0833 | 5.3015 | 15 | 79 | 79 | 2.31 | 30.6226 | 5.6583 | 239.1914 | 0 | 0 | 0 | 0 | 1.5518 | 2.2501 | 1.6304 | 0.055567 | 0.37738 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 30.6226 | 14.6665 | 14.6665 | 14.6665 | 14.6665 | 16.2183 | 16.9167 | 16.2969 | 14.7221 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 13 | 18 | 1050 | 8.5 | 8.5 | 5.0833 | 5.3015 | 15 | 80 | 80 | 3.2486 | 5.9134 | -2.6926 | 251.1534 | 0 | 0 | 0 | 0 | 1.6557 | 3.1341 | 2.7766 | 0.79255 | 0.086619 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 5.9134 | 3.1656 | 3.1656 | 3.1656 | 3.1656 | 4.8213 | 6.2997 | 5.9422 | 3.9582 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 19 | 1051 | 8 | 8 | 5.0833 | 5.3015 | 15 | 83 | 83 | 0 | 0 | -11.6541 | 262.7533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 20 | 1052 | 7.9 | 7.9 | 5.0833 | 5.3015 | 15 | 82 | 82 | 0 | 0 | -20.8494 | 274.5519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 21 | 1053 | 8 | 8 | 5.0833 | 5.3015 | 15 | 79 | 79 | 0 | 0 | -29.8824 | 287.2397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 22 | 1054 | 8 | 8 | 5.0833 | 5.3015 | 15 | 77 | 77 | 0 | 0 | -38.2598 | 301.6831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 23 | 1055 | 7.7 | 7.7 | 5.0833 | 5.3015 | 15 | 80 | 80 | 0 | 0 | -45.291 | 318.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 13 | 24 | 1056 | 7.4 | 7.4 | 7.8542 | 5.6951 | 15 | 84 | 84 | 0 | 0 | -50.029 | 339.4248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 1 | 1057 | 7 | 7 | 7.8542 | 5.6951 | 15 | 87 | 87 | 0 | 0 | -51.4879 | 2.4485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 2 | 1058 | 6.9 | 6.9 | 7.8542 | 5.6951 | 15 | 88 | 88 | 0 | 0 | -48.9557 | 25.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 3 | 1059 | 6.7 | 6.7 | 7.8542 | 5.6951 | 15 | 90 | 90 | 0 | 0 | -43.6731 | 44.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 4 | 1060 | 6.6 | 6.6 | 7.8542 | 5.6951 | 15 | 90 | 90 | 0 | 0 | -36.3111 | 61.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 5 | 1061 | 6.2 | 6.2 | 7.8542 | 5.6951 | 15 | 91 | 91 | 0 | 0 | -27.7611 | 75.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 6 | 1062 | 6.3 | 6.3 | 7.8542 | 5.6951 | 15 | 89 | 89 | 0 | 0 | -18.6633 | 87.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 7 | 1063 | 5.9 | 5.9 | 7.8542 | 5.6951 | 15 | 91 | 91 | 0 | 0 | -9.4835 | 99.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 14 | 8 | 1064 | 6 | 6 | 7.8542 | 5.6951 | 15 | 92 | 92 | 0 | 0 | -0.60953 | 111.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 9 | 1065 | 6.4 | 6.4 | 7.8542 | 5.6951 | 15 | 95 | 95 | 1.0298 | 7.935 | 7.5775 | 123.2236 | 0 | 0.41712 | 0.9607 | 0.94152 | 0.37081 | 0 | 0 | 0 | 0.065039 | 3.7331 | 4.501 | 5.5018 | 5.4665 | 4.4158 | 3.7331 | 3.7331 | 3.7331 | 7.935 | 3.7331 | 4.9182 | 6.4625 | 6.408 | 4.7866 | 3.7331 | 3.7331 | 3.7331 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 10 | 1066 | 7.3 | 7.3 | 7.8542 | 5.6951 | 15 | 92 | 92 | 5.6443 | 56.8961 | 14.6575 | 136.2432 | 0 | 1.1419 | 4.6805 | 5.4773 | 3.0656 | 0 | 0 | 0 | 1.1039 | 25.9265 | 36.096 | 67.6094 | 74.7054 | 53.2275 | 25.9265 | 25.9265 | 25.9265 | 56.8961 | 25.9265 | 37.2379 | 72.2898 | 80.1827 | 56.2931 | 25.9265 | 25.9265 | 25.9265 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 11 | 1067 | 8.1 | 8.1 | 7.8542 | 5.6951 | 15 | 83 | 83 | 19.8132 | 119.0089 | 20.1588 | 150.4233 | 0 | 0 | 13.2569 | 19.1639 | 13.845 | 0.41589 | 0 | 0 | 5.9911 | 53.2965 | 53.2965 | 102.3628 | 124.2261 | 104.5397 | 54.8357 | 53.2965 | 53.2965 | 119.0089 | 53.2965 | 53.2965 | 115.6197 | 143.39 | 118.3847 | 55.2516 | 53.2965 | 53.2965 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 12 | 1068 | 8.8 | 8.8 | 7.8542 | 5.6951 | 15 | 81 | 81 | 32.8832 | 159.6269 | 23.6016 | 165.7196 | 0 | 0 | 15.2365 | 29.7572 | 26.8465 | 8.2095 | 0 | 0 | 12.3731 | 73.9799 | 73.9799 | 114.134 | 152.4018 | 144.7311 | 95.6152 | 73.9799 | 73.9799 | 159.6269 | 73.9799 | 73.9799 | 129.3705 | 182.1589 | 171.5776 | 103.8248 | 73.9799 | 73.9799 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 13 | 1069 | 8.8 | 8.8 | 7.8542 | 5.6951 | 15 | 81 | 81 | 22.6369 | 165.6689 | 24.6136 | 181.6821 | 0 | 0 | 5.1167 | 17.8326 | 20.1024 | 10.5965 | 0 | 0 | 9.3311 | 76.9843 | 76.9843 | 87.8025 | 114.6876 | 119.4866 | 99.3884 | 76.9843 | 76.9843 | 165.6689 | 76.9843 | 76.9843 | 92.9193 | 132.5202 | 139.589 | 109.9848 | 76.9843 | 76.9843 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 14 | 1070 | 8.5 | 8.5 | 7.8542 | 5.6951 | 15 | 84 | 84 | 6.0322 | 122.5405 | 23.0721 | 197.5611 | 0 | 0 | 0 | 3.7624 | 5.4818 | 3.99 | 0.16098 | 0 | 2.4595 | 60.298 | 60.298 | 60.298 | 64.6617 | 66.6558 | 64.9257 | 60.4847 | 60.298 | 122.5405 | 60.298 | 60.298 | 60.298 | 68.424 | 72.1376 | 68.9157 | 60.6457 | 60.298 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 15 | 1071 | 8.5 | 8.5 | 7.8542 | 5.6951 | 15 | 84 | 84 | 2.9611 | 76.9247 | 19.1614 | 212.6469 | 0 | 0 | 0 | 1.2553 | 2.5973 | 2.4178 | 0.82196 | 0 | 1.0753 | 37.716 | 37.716 | 37.716 | 37.716 | 37.716 | 37.716 | 37.716 | 37.716 | 76.9247 | 37.716 | 37.716 | 37.716 | 38.9713 | 40.3133 | 40.1337 | 38.5379 | 37.716 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 16 | 1072 | 8.6 | 8.6 | 7.8542 | 5.6951 | 15 | 83 | 83 | 2.2753 | 52.3595 | 13.2886 | 226.5753 | 0 | 0 | 0 | 0.4598 | 1.8097 | 2.0995 | 1.1594 | 0 | 0.64047 | 25.3465 | 25.3465 | 25.3465 | 25.3465 | 25.3465 | 25.3465 | 25.3465 | 25.3465 | 52.3595 | 25.3465 | 25.3465 | 25.3465 | 25.8063 | 27.1562 | 27.446 | 26.5059 | 25.3465 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 17 | 1073 | 8.4 | 8.4 | 7.8542 | 5.6951 | 15 | 80 | 80 | 3.9945 | 41.3275 | 5.9392 | 239.3772 | 0 | 0 | 0 | 0 | 2.6723 | 3.8861 | 2.8234 | 0.10687 | 0.67248 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 41.3275 | 20.0429 | 20.0429 | 20.0429 | 20.0429 | 22.7152 | 23.929 | 22.8664 | 20.1498 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 14 | 18 | 1074 | 8.2 | 8.2 | 7.8542 | 5.6951 | 15 | 82 | 82 | 4.1523 | 7.8694 | -2.4247 | 251.3569 | 0 | 0 | 0 | 0 | 2.1038 | 4.0007 | 3.554 | 1.0255 | 0.1306 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 7.8694 | 4.2174 | 4.2174 | 4.2174 | 4.2174 | 6.3212 | 8.2181 | 7.7715 | 5.243 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 19 | 1075 | 7.7 | 7.7 | 7.8542 | 5.6951 | 15 | 87 | 87 | 0 | 0 | -11.3937 | 262.9705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 20 | 1076 | 7.7 | 7.7 | 7.8542 | 5.6951 | 15 | 88 | 88 | 0 | 0 | -20.5898 | 274.7804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 21 | 1077 | 7.3 | 7.3 | 7.8542 | 5.6951 | 15 | 89 | 89 | 0 | 0 | -29.6157 | 287.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 22 | 1078 | 6.9 | 6.9 | 7.8542 | 5.6951 | 15 | 90 | 90 | 0 | 0 | -37.9776 | 301.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 23 | 1079 | 5 | 5 | 7.8542 | 5.6951 | 15 | 96 | 96 | 0 | 0 | -44.9861 | 319.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 14 | 24 | 1080 | 3.5 | 3.5 | 7.1375 | 6.0382 | 15 | 97 | 97 | 0 | 0 | -49.7017 | 339.5443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 1 | 1081 | 2.6 | 2.6 | 7.1375 | 6.0382 | 15 | 98 | 98 | 0 | 0 | -51.1517 | 2.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 2 | 1082 | 3.1 | 3.1 | 7.1375 | 6.0382 | 15 | 98 | 98 | 0 | 0 | -48.6265 | 24.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 3 | 1083 | 4 | 4 | 7.1375 | 6.0382 | 15 | 98 | 98 | 0 | 0 | -43.3658 | 44.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 4 | 1084 | 5 | 5 | 7.1375 | 6.0382 | 15 | 99 | 99 | 0 | 0 | -36.0246 | 61.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 5 | 1085 | 4.9 | 4.9 | 7.1375 | 6.0382 | 15 | 99 | 99 | 0 | 0 | -27.4881 | 75.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 6 | 1086 | 4.8 | 4.8 | 7.1375 | 6.0382 | 15 | 99 | 99 | 0 | 0 | -18.3957 | 87.5205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 7 | 1087 | 4.8 | 4.8 | 7.1375 | 6.0382 | 15 | 99 | 99 | 0 | 0 | -9.2138 | 99.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 15 | 8 | 1088 | 4.7 | 4.7 | 7.1375 | 6.0382 | 15 | 99 | 99 | 0 | 0 | -0.33133 | 110.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 9 | 1089 | 5 | 5 | 7.1375 | 6.0382 | 15 | 99 | 99 | 1.6783 | 10.8858 | 7.8692 | 123.0474 | 0 | 0.685 | 1.5677 | 1.5321 | 0.59896 | 0 | 0 | 0 | 0.11418 | 5.1184 | 6.1849 | 7.5592 | 7.5037 | 6.0509 | 5.1184 | 5.1184 | 5.1184 | 10.8858 | 5.1184 | 6.8699 | 9.1269 | 9.0358 | 6.6499 | 5.1184 | 5.1184 | 5.1184 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 10 | 1090 | 6 | 6 | 7.1375 | 6.0382 | 15 | 99 | 99 | 3.523 | 46.2931 | 14.9658 | 136.0951 | 0 | 0.72274 | 2.9252 | 3.4141 | 1.9031 | 0 | 0 | 0 | 0.70686 | 22.1418 | 25.459 | 35.5679 | 37.812 | 30.8766 | 22.1418 | 22.1418 | 22.1418 | 46.2931 | 22.1418 | 26.1818 | 38.4931 | 41.2261 | 32.7797 | 22.1418 | 22.1418 | 22.1418 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 11 | 1091 | 7 | 7 | 7.1375 | 6.0382 | 15 | 93 | 93 | 14.3643 | 114.5816 | 20.4836 | 150.3163 | 0 | 0 | 9.6232 | 13.8745 | 9.9983 | 0.26521 | 0 | 0 | 4.4184 | 51.9572 | 51.9572 | 92.3445 | 110.1865 | 93.9186 | 53.0703 | 51.9572 | 51.9572 | 114.5816 | 51.9572 | 51.9572 | 101.9677 | 124.061 | 103.9169 | 53.3355 | 51.9572 | 51.9572 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 12 | 1092 | 7.7 | 7.7 | 7.1375 | 6.0382 | 15 | 85 | 85 | 10.9202 | 134.8329 | 23.9383 | 165.668 | 0 | 0 | 5.0659 | 9.8664 | 8.8873 | 2.7022 | 0 | 0 | 4.1671 | 63.1952 | 63.1952 | 79.8415 | 95.6157 | 92.3984 | 72.0743 | 63.1952 | 63.1952 | 134.8329 | 63.1952 | 63.1952 | 84.9074 | 105.4821 | 101.2858 | 74.7765 | 63.1952 | 63.1952 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 13 | 1093 | 8.1 | 8.1 | 7.1375 | 6.0382 | 15 | 75 | 75 | 33.9222 | 177.8348 | 24.9533 | 181.6955 | 0 | 0 | 7.6748 | 26.6679 | 30.0394 | 15.8141 | 0 | 0 | 14.1652 | 82.5721 | 82.5721 | 101.425 | 148.0811 | 156.3629 | 121.4191 | 82.5721 | 82.5721 | 177.8348 | 82.5721 | 82.5721 | 109.0998 | 174.749 | 186.4023 | 137.2332 | 82.5721 | 82.5721 | 192 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 14 | 1094 | 7.9 | 7.9 | 7.1375 | 6.0382 | 15 | 76 | 76 | 5.3281 | 116.799 | 23.4047 | 197.6379 | 0 | 0 | 0 | 3.3133 | 4.8286 | 3.5154 | 0.14293 | 0 | 2.201 | 57.9871 | 57.9871 | 57.9871 | 59.8028 | 60.6331 | 59.9135 | 58.0655 | 57.9871 | 116.799 | 57.9871 | 57.9871 | 57.9871 | 63.1161 | 65.4618 | 63.4289 | 58.2084 | 57.9871 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 15 | 1095 | 7.9 | 7.9 | 7.1375 | 6.0382 | 15 | 78 | 78 | 3.7465 | 87.6197 | 19.4789 | 212.7755 | 0 | 0 | 0 | 1.5803 | 3.2766 | 3.0536 | 1.0418 | 0 | 1.3803 | 43.2582 | 43.2582 | 43.2582 | 43.2582 | 43.2582 | 43.2582 | 43.2582 | 43.2582 | 87.6197 | 43.2582 | 43.2582 | 43.2582 | 44.8385 | 46.5349 | 46.3118 | 44.3 | 43.2582 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 16 | 1096 | 7.9 | 7.9 | 7.1375 | 6.0382 | 15 | 81 | 81 | 4.0501 | 70.8389 | 13.588 | 226.7409 | 0 | 0 | 0 | 0.8085 | 3.2104 | 3.7317 | 2.067 | 0 | 1.1611 | 34.8085 | 34.8085 | 34.8085 | 34.8085 | 34.8085 | 34.8085 | 34.8085 | 34.8085 | 70.8389 | 34.8085 | 34.8085 | 34.8085 | 35.617 | 38.0189 | 38.5402 | 36.8755 | 34.8085 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 17 | 1097 | 7.7 | 7.7 | 7.1375 | 6.0382 | 15 | 80 | 80 | 3.2486 | 38.4368 | 6.2214 | 239.5679 | 0 | 0 | 0 | 0 | 2.1639 | 3.1562 | 2.2996 | 0.09593 | 0.56324 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 38.4368 | 18.5604 | 18.5604 | 18.5604 | 18.5604 | 20.7244 | 21.7167 | 20.8601 | 18.6564 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 15 | 18 | 1098 | 7.2 | 7.2 | 7.1375 | 6.0382 | 15 | 84 | 84 | 0.43875 | 2.9841 | -2.1558 | 251.565 | 0 | 0 | 0 | 0 | 0.22092 | 0.42214 | 0.37607 | 0.10971 | 0.015923 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 2.9841 | 1.3789 | 1.3789 | 1.3789 | 1.3789 | 1.5999 | 1.8011 | 1.755 | 1.4886 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 19 | 1099 | 6.7 | 6.7 | 7.1375 | 6.0382 | 15 | 87 | 87 | 0 | 0 | -11.1323 | 263.1922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 20 | 1100 | 6.3 | 6.3 | 7.1375 | 6.0382 | 15 | 87 | 87 | 0 | 0 | -20.3291 | 275.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 21 | 1101 | 6.2 | 6.2 | 7.1375 | 6.0382 | 15 | 89 | 89 | 0 | 0 | -29.3476 | 287.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 22 | 1102 | 5.9 | 5.9 | 7.1375 | 6.0382 | 15 | 89 | 89 | 0 | 0 | -37.6934 | 302.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 23 | 1103 | 5.5 | 5.5 | 7.1375 | 6.0382 | 15 | 91 | 91 | 0 | 0 | -44.6789 | 319.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 15 | 24 | 1104 | 5.1 | 5.1 | 5.9167 | 6.0997 | 15 | 91 | 91 | 0 | 0 | -49.3714 | 339.6682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 1 | 1105 | 3.6 | 3.6 | 5.9167 | 6.0997 | 15 | 93 | 93 | 0 | 0 | -50.8118 | 2.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 2 | 1106 | 1.4 | 1.4 | 5.9167 | 6.0997 | 15 | 97 | 97 | 0 | 0 | -48.2929 | 24.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 3 | 1107 | 0.2 | 0.2 | 5.9167 | 6.0997 | 15 | 98 | 98 | 0 | 0 | -43.0537 | 44.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 4 | 1108 | -0.5 | -0.5 | 5.9167 | 6.0997 | 15 | 98 | 98 | 0 | 0 | -35.7329 | 60.8515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 5 | 1109 | -0.5 | -0.5 | 5.9167 | 6.0997 | 15 | 99 | 99 | 0 | 0 | -27.21 | 74.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 6 | 1110 | 0 | 0 | 5.9167 | 6.0997 | 15 | 99 | 99 | 0 | 0 | -18.1231 | 87.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 7 | 1111 | 0.4 | 0.4 | 5.9167 | 6.0997 | 15 | 100 | 100 | 0 | 0 | -8.9392 | 99.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 16 | 8 | 1112 | 0.9 | 0.9 | 5.9167 | 6.0997 | 15 | 100 | 100 | 0 | 0 | -0.048415 | 110.7152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 9 | 1113 | 1.7 | 1.7 | 5.9167 | 6.0997 | 15 | 100 | 100 | 3.4863 | 16.7456 | 8.1655 | 122.8718 | 0 | 1.4338 | 3.2609 | 3.1778 | 1.2332 | 0 | 0 | 0 | 0.25439 | 7.8647 | 9.5327 | 11.6583 | 11.5616 | 9.2993 | 7.8647 | 7.8647 | 7.8647 | 16.7456 | 7.8647 | 10.9665 | 14.9192 | 14.7394 | 10.5325 | 7.8647 | 7.8647 | 7.8647 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 10 | 1114 | 2.5 | 2.5 | 5.9167 | 6.0997 | 15 | 100 | 100 | 5.6453 | 59.8384 | 15.2786 | 135.9479 | 0 | 1.1741 | 4.6934 | 5.4634 | 3.033 | 0 | 0 | 0 | 1.1616 | 27.3917 | 37.1025 | 66.2112 | 72.58 | 52.4781 | 27.3917 | 27.3917 | 27.3917 | 59.8384 | 27.3917 | 38.2765 | 70.9046 | 78.0434 | 55.5111 | 27.3917 | 27.3917 | 27.3917 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 11 | 1115 | 3 | 3 | 5.9167 | 6.0997 | 15 | 100 | 100 | 8.1925 | 103.4369 | 20.8126 | 150.2107 | 0 | 0 | 5.495 | 7.9019 | 5.6799 | 0.13074 | 0 | 0 | 2.5631 | 48.115 | 48.115 | 73.6452 | 84.8276 | 74.5043 | 48.7224 | 48.115 | 48.115 | 103.4369 | 48.115 | 48.115 | 79.1403 | 92.7295 | 80.1842 | 48.8531 | 48.115 | 48.115 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 12 | 1116 | 3.5 | 3.5 | 5.9167 | 6.0997 | 15 | 100 | 100 | 6.0747 | 116.6494 | 24.2789 | 165.619 | 0 | 0 | 2.821 | 5.4793 | 4.9279 | 1.4898 | 0 | 0 | 2.3506 | 56.2606 | 56.2606 | 63.8007 | 70.9059 | 69.4321 | 60.2426 | 56.2606 | 56.2606 | 116.6494 | 56.2606 | 56.2606 | 66.6217 | 76.3852 | 74.36 | 61.7324 | 56.2606 | 56.2606 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 13 | 1117 | 4.2 | 4.2 | 5.9167 | 6.0997 | 15 | 99 | 99 | 4.6655 | 112.0266 | 25.2966 | 181.7125 | 0 | 0 | 1.0563 | 3.6599 | 4.1196 | 2.1661 | 0 | 0 | 1.9734 | 55.7083 | 55.7083 | 56.1477 | 57.2309 | 57.4222 | 56.6095 | 55.7083 | 55.7083 | 112.0266 | 55.7083 | 55.7083 | 57.204 | 60.8908 | 61.5418 | 58.7755 | 55.7083 | 55.7083 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 14 | 1118 | 4.6 | 4.6 | 5.9167 | 6.0997 | 15 | 99 | 99 | 5.7304 | 122.6019 | 23.74 | 197.7192 | 0 | 0 | 0 | 3.5523 | 5.1786 | 3.7713 | 0.15483 | 0 | 2.3981 | 60.5665 | 60.5665 | 60.5665 | 63.8481 | 65.3505 | 64.0504 | 60.7095 | 60.5665 | 122.6019 | 60.5665 | 60.5665 | 60.5665 | 67.4004 | 70.529 | 67.8217 | 60.8643 | 60.5665 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 15 | 1119 | 5 | 5 | 5.9167 | 6.0997 | 15 | 88 | 88 | 20.8473 | 148.2078 | 19.7986 | 212.9091 | 0 | 0 | 0 | 8.7468 | 18.1779 | 16.9606 | 5.808 | 0 | 7.7922 | 70.5483 | 70.5483 | 70.5483 | 83.0243 | 96.4762 | 94.7399 | 78.8325 | 70.5483 | 148.2078 | 70.5483 | 70.5483 | 70.5483 | 91.7711 | 114.6541 | 111.7005 | 84.6405 | 70.5483 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 16 | 1120 | 5.1 | 5.1 | 5.9167 | 6.0997 | 15 | 89 | 89 | 40.5314 | 127.1689 | 13.8889 | 226.9115 | 0 | 0 | 0 | 7.988 | 32.0161 | 37.2895 | 20.7193 | 0 | 11.8311 | 61.0667 | 61.0667 | 61.0667 | 72.4427 | 106.6616 | 114.1717 | 90.5736 | 61.0667 | 127.1689 | 61.0667 | 61.0667 | 61.0667 | 80.4307 | 138.6777 | 151.4612 | 111.2929 | 61.0667 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 17 | 1121 | 4.9 | 4.9 | 5.9167 | 6.0997 | 15 | 88 | 88 | 26.3001 | 73.3066 | 6.5048 | 239.7633 | 0 | 0 | 0 | 0 | 17.441 | 25.517 | 18.6454 | 0.85163 | 4.6934 | 36.2779 | 36.2779 | 36.2779 | 36.2779 | 58.2937 | 68.488 | 59.814 | 37.3529 | 73.3066 | 36.2779 | 36.2779 | 36.2779 | 36.2779 | 75.7348 | 94.005 | 78.4595 | 38.2045 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 16 | 18 | 1122 | 3 | 3 | 5.9167 | 6.0997 | 15 | 94 | 94 | 8.2943 | 13.6584 | -1.8859 | 251.7777 | 0 | 0 | 0 | 0 | 4.1499 | 7.9688 | 7.1198 | 2.1 | 0.34155 | 7.2347 | 7.2347 | 7.2347 | 7.2347 | 8.2089 | 9.1054 | 8.9061 | 7.7277 | 13.6584 | 7.2347 | 7.2347 | 7.2347 | 7.2347 | 12.3588 | 17.0743 | 16.0258 | 9.8277 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 19 | 1123 | 2.6 | 2.6 | 5.9167 | 6.0997 | 15 | 96 | 96 | 0 | 0 | -10.87 | 263.4182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 20 | 1124 | 3.4 | 3.4 | 5.9167 | 6.0997 | 15 | 95 | 95 | 0 | 0 | -20.0672 | 275.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 21 | 1125 | 3.2 | 3.2 | 5.9167 | 6.0997 | 15 | 95 | 95 | 0 | 0 | -29.0781 | 287.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 22 | 1126 | 2.8 | 2.8 | 5.9167 | 6.0997 | 15 | 96 | 96 | 0 | 0 | -37.4075 | 302.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 23 | 1127 | 2.6 | 2.6 | 5.9167 | 6.0997 | 15 | 96 | 96 | 0 | 0 | -44.3693 | 319.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 16 | 24 | 1128 | 2.8 | 2.8 | 2.5167 | 5.2942 | 15 | 96 | 96 | 0 | 0 | -49.0382 | 339.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 1 | 1129 | 2.9 | 2.9 | 2.5167 | 5.2942 | 15 | 95 | 95 | 0 | 0 | -50.4682 | 2.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 2 | 1130 | 2.1 | 2.1 | 2.5167 | 5.2942 | 15 | 96 | 96 | 0 | 0 | -47.955 | 24.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 3 | 1131 | 1.6 | 1.6 | 2.5167 | 5.2942 | 15 | 98 | 98 | 0 | 0 | -42.7367 | 44.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 4 | 1132 | 1.8 | 1.8 | 2.5167 | 5.2942 | 15 | 98 | 98 | 0 | 0 | -35.4363 | 60.6299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 5 | 1133 | 2.2 | 2.2 | 2.5167 | 5.2942 | 15 | 99 | 99 | 0 | 0 | -26.927 | 74.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 6 | 1134 | 2.4 | 2.4 | 2.5167 | 5.2942 | 15 | 99 | 99 | 0 | 0 | -17.8456 | 87.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 7 | 1135 | 2.6 | 2.6 | 2.5167 | 5.2942 | 15 | 99 | 99 | 0 | 0 | -8.6599 | 98.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 17 | 8 | 1136 | 2.9 | 2.9 | 2.5167 | 5.2942 | 15 | 99 | 99 | 0 | 0 | 0.23911 | 110.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 9 | 1137 | 3.3 | 3.3 | 2.5167 | 5.2942 | 15 | 97 | 97 | 0.38073 | 5.9703 | 8.4664 | 122.6968 | 0 | 0.15776 | 0.35657 | 0.34651 | 0.13346 | 0 | 0 | 0 | 0.029677 | 2.8862 | 2.8862 | 2.8862 | 2.8862 | 2.8862 | 2.8862 | 2.8862 | 2.8862 | 5.9703 | 2.8862 | 3.044 | 3.2428 | 3.2327 | 3.0197 | 2.8862 | 2.8862 | 2.8862 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 10 | 1138 | 3.8 | 3.8 | 2.5167 | 5.2942 | 15 | 96 | 96 | 0.69913 | 21.8525 | 15.5957 | 135.8016 | 0 | 0.14735 | 0.58193 | 0.67563 | 0.37355 | 0 | 0 | 0 | 0.14745 | 10.4485 | 10.4485 | 10.4485 | 10.4485 | 10.4485 | 10.4485 | 10.4485 | 10.4485 | 21.8525 | 10.4485 | 10.5959 | 11.0304 | 11.1241 | 10.8221 | 10.4485 | 10.4485 | 10.4485 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 11 | 1139 | 4.5 | 4.5 | 2.5167 | 5.2942 | 15 | 93 | 93 | 1.9908 | 55.3666 | 21.1459 | 150.1068 | 0 | 0 | 1.3368 | 1.9173 | 1.3747 | 0.026825 | 0 | 0 | 0.63337 | 27.0575 | 27.0575 | 27.0575 | 27.0575 | 27.0575 | 27.0575 | 27.0575 | 27.0575 | 55.3666 | 27.0575 | 27.0575 | 28.3942 | 28.9747 | 28.4322 | 27.0843 | 27.0575 | 27.0575 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 12 | 1140 | 5.5 | 5.5 | 2.5167 | 5.2942 | 15 | 88 | 88 | 17.4879 | 151.1386 | 24.6234 | 165.5725 | 0 | 0 | 8.1288 | 15.7467 | 14.1404 | 4.2508 | 0 | 0 | 6.8614 | 69.759 | 69.759 | 93.0237 | 114.8259 | 110.2286 | 81.9247 | 69.759 | 69.759 | 151.1386 | 69.759 | 69.759 | 101.1525 | 130.5726 | 124.3689 | 86.1755 | 69.759 | 69.759 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 13 | 1141 | 6.6 | 6.6 | 2.5167 | 5.2942 | 15 | 82 | 82 | 187.2903 | 202.758 | 25.6431 | 181.7332 | 0 | 0 | 42.4208 | 146.5908 | 164.8899 | 86.5987 | 0 | 0 | 80.242 | 98.9609 | 98.9609 | 129.1804 | 203.3885 | 216.4243 | 160.6516 | 98.9609 | 98.9609 | 202.758 | 98.9609 | 98.9609 | 171.6012 | 349.9793 | 381.3142 | 247.2504 | 98.9609 | 98.9609 | 283 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 14 | 1142 | 7 | 7 | 2.5167 | 5.2942 | 15 | 75 | 75 | 13.2083 | 155.4005 | 24.0781 | 197.805 | 0 | 0 | 0 | 8.1613 | 11.9019 | 8.6706 | 0.36015 | 0 | 5.5995 | 74.1454 | 74.1454 | 74.1454 | 90.6243 | 98.1773 | 91.6527 | 74.8726 | 74.1454 | 155.4005 | 74.1454 | 74.1454 | 74.1454 | 98.7856 | 110.0792 | 100.3233 | 75.2327 | 74.1454 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 15 | 1143 | 6.6 | 6.6 | 2.5167 | 5.2942 | 15 | 79 | 79 | 3.3058 | 84.7466 | 20.1204 | 213.0475 | 0 | 0 | 0 | 1.3793 | 2.8736 | 2.6845 | 0.92288 | 0 | 1.2534 | 41.7135 | 41.7135 | 41.7135 | 41.7135 | 41.7135 | 41.7135 | 41.7135 | 41.7135 | 84.7466 | 41.7135 | 41.7135 | 41.7135 | 43.0928 | 44.5871 | 44.398 | 42.6364 | 41.7135 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 16 | 1144 | 6.4 | 6.4 | 2.5167 | 5.2942 | 15 | 81 | 81 | 0.69924 | 30.7922 | 14.1913 | 227.0871 | 0 | 0 | 0 | 0.13598 | 0.55035 | 0.64233 | 0.35805 | 0 | 0.20779 | 14.6246 | 14.6246 | 14.6246 | 14.6246 | 14.6246 | 14.6246 | 14.6246 | 14.6246 | 30.7922 | 14.6246 | 14.6246 | 14.6246 | 14.7605 | 15.1749 | 15.2669 | 14.9826 | 14.6246 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 17 | 1145 | 6.5 | 6.5 | 2.5167 | 5.2942 | 15 | 80 | 80 | 2.4711 | 35.5464 | 6.7893 | 239.9635 | 0 | 0 | 0 | 0 | 1.6312 | 2.3941 | 1.7546 | 0.08725 | 0.45364 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 35.5464 | 17.0824 | 17.0824 | 17.0824 | 17.0824 | 18.7136 | 19.4765 | 18.837 | 17.1696 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 18 | 1146 | 5.7 | 5.7 | 2.5167 | 5.2942 | 15 | 88 | 88 | 0.27194 | 2.9875 | -1.615 | 251.9949 | 0 | 0 | 0 | 0 | 0.13517 | 0.26088 | 0.23377 | 0.069725 | 0.012541 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38 | 2.9875 | 1.38 | 1.38 | 1.38 | 1.38 | 1.5152 | 1.6409 | 1.6138 | 1.4497 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 19 | 1147 | 5.6 | 5.6 | 2.5167 | 5.2942 | 15 | 91 | 91 | 0 | 0 | -10.6068 | 263.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 20 | 1148 | 5.7 | 5.7 | 2.5167 | 5.2942 | 15 | 93 | 93 | 0 | 0 | -19.8044 | 275.4914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 21 | 1149 | 5.9 | 5.9 | 2.5167 | 5.2942 | 15 | 91 | 91 | 0 | 0 | -28.8073 | 288.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 22 | 1150 | 4.6 | 4.6 | 2.5167 | 5.2942 | 15 | 91 | 91 | 0 | 0 | -37.1199 | 302.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 23 | 1151 | 2.9 | 2.9 | 2.5167 | 5.2942 | 15 | 96 | 96 | 0 | 0 | -44.0575 | 319.6983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 17 | 24 | 1152 | 3 | 3 | 4.2542 | 5.0802 | 15 | 97 | 97 | 0 | 0 | -48.7022 | 339.9285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 1 | 1153 | 3.8 | 3.8 | 4.2542 | 5.0802 | 15 | 95 | 95 | 0 | 0 | -50.1211 | 2.4373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 2 | 1154 | 4.6 | 4.6 | 4.2542 | 5.0802 | 15 | 86 | 86 | 0 | 0 | -47.613 | 24.5218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 3 | 1155 | 4.6 | 4.6 | 4.2542 | 5.0802 | 15 | 86 | 86 | 0 | 0 | -42.4152 | 44.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 4 | 1156 | 4.6 | 4.6 | 4.2542 | 5.0802 | 15 | 85 | 85 | 0 | 0 | -35.1348 | 60.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 5 | 1157 | 5.1 | 5.1 | 4.2542 | 5.0802 | 15 | 81 | 81 | 0 | 0 | -26.639 | 74.3916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 6 | 1158 | 3.1 | 3.1 | 4.2542 | 5.0802 | 15 | 89 | 89 | 0 | 0 | -17.5633 | 86.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 7 | 1159 | 2.8 | 2.8 | 4.2542 | 5.0802 | 15 | 91 | 91 | 0 | 0 | -8.3759 | 98.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 18 | 8 | 1160 | 3.7 | 3.7 | 4.2542 | 5.0802 | 15 | 92 | 92 | 0 | 0 | 0.53114 | 110.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 9 | 1161 | 5.6 | 5.6 | 4.2542 | 5.0802 | 15 | 86 | 86 | 205.3435 | 38.9627 | 8.7715 | 122.5225 | 0 | 85.7148 | 192.5476 | 186.5886 | 71.3285 | 0 | 0 | 0 | 17.0373 | 11.3528 | 11.3528 | 11.3528 | 11.3528 | 11.3528 | 11.3528 | 11.3528 | 11.3528 | 38.9627 | 11.3528 | 97.0676 | 203.9003 | 197.9413 | 82.6813 | 11.3528 | 11.3528 | 11.3528 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 10 | 1162 | 6.3 | 6.3 | 4.2542 | 5.0802 | 15 | 84 | 84 | 128.9133 | 103.1405 | 15.9171 | 135.6562 | 0 | 27.5268 | 107.4259 | 124.3963 | 68.4971 | 0 | 0 | 0 | 27.8595 | 48.0835 | 83.205 | 185.1485 | 206.8012 | 135.4792 | 48.0835 | 48.0835 | 48.0835 | 103.1405 | 48.0835 | 110.7318 | 292.5744 | 331.1975 | 203.9762 | 48.0835 | 48.0835 | 48.0835 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 11 | 1163 | 6.9 | 6.9 | 4.2542 | 5.0802 | 15 | 82 | 82 | 14.3479 | 120.3586 | 21.4832 | 150.0044 | 0 | 0 | 9.6441 | 13.7969 | 9.8676 | 0.15803 | 0 | 0 | 4.6414 | 54.725 | 54.725 | 93.9815 | 110.8853 | 94.8912 | 55.3683 | 54.725 | 54.725 | 120.3586 | 54.725 | 54.725 | 103.6256 | 124.6822 | 104.7588 | 55.5263 | 54.725 | 54.725 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 12 | 1164 | 7.5 | 7.5 | 4.2542 | 5.0802 | 15 | 80 | 80 | 34.1832 | 169.4023 | 24.9717 | 165.5286 | 0 | 0 | 15.902 | 30.7238 | 27.548 | 8.235 | 0 | 0 | 13.5977 | 78.3411 | 78.3411 | 119.5296 | 157.9202 | 149.6944 | 99.6708 | 78.3411 | 78.3411 | 169.4023 | 78.3411 | 78.3411 | 135.4317 | 188.644 | 177.2424 | 107.9057 | 78.3411 | 78.3411 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 13 | 1165 | 8 | 8 | 4.2542 | 5.0802 | 15 | 72 | 72 | 42.035 | 189.7602 | 25.993 | 181.7575 | 0 | 0 | 9.5224 | 32.8231 | 36.8964 | 19.3563 | 0 | 0 | 18.2398 | 87.8593 | 87.8593 | 107.9964 | 157.2702 | 165.8841 | 128.7921 | 87.8593 | 87.8593 | 189.7602 | 87.8593 | 87.8593 | 117.5188 | 190.0932 | 202.7805 | 148.1485 | 87.8593 | 87.8593 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 14 | 1166 | 7.6 | 7.6 | 4.2542 | 5.0802 | 15 | 75 | 75 | 9.9819 | 148.7136 | 24.4189 | 197.8953 | 0 | 0 | 0 | 6.1468 | 8.968 | 6.5359 | 0.27518 | 0 | 4.2864 | 71.6127 | 71.6127 | 71.6127 | 83.9819 | 89.6592 | 84.765 | 72.1664 | 71.6127 | 148.7136 | 71.6127 | 71.6127 | 71.6127 | 90.1287 | 98.6272 | 91.3009 | 72.4416 | 71.6127 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 15 | 1167 | 7 | 7 | 4.2542 | 5.0802 | 15 | 79 | 79 | 40.5172 | 167.418 | 20.4441 | 213.1909 | 0 | 0 | 0 | 16.809 | 35.108 | 32.8411 | 11.3364 | 0 | 15.582 | 78.8202 | 78.8202 | 78.8202 | 108.9869 | 141.8275 | 137.7592 | 99.1653 | 78.8202 | 167.418 | 78.8202 | 78.8202 | 78.8202 | 125.7959 | 176.9354 | 170.6004 | 110.5017 | 78.8202 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 16 | 1168 | 5.9 | 5.9 | 4.2542 | 5.0802 | 15 | 89 | 89 | 2.8778 | 63.1295 | 14.4951 | 227.2676 | 0 | 0 | 0 | 0.55185 | 2.2566 | 2.6394 | 1.4762 | 0 | 0.87048 | 30.7711 | 30.7711 | 30.7711 | 30.7711 | 30.7711 | 30.7711 | 30.7711 | 30.7711 | 63.1295 | 30.7711 | 30.7711 | 30.7711 | 31.323 | 33.0277 | 33.4106 | 32.2473 | 30.7711 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 17 | 1169 | 6.3 | 6.3 | 4.2542 | 5.0802 | 15 | 88 | 88 | 3.4937 | 43.3406 | 7.0747 | 240.1684 | 0 | 0 | 0 | 0 | 2.2953 | 3.3799 | 2.4846 | 0.13383 | 0.6594 | 20.999 | 20.999 | 20.999 | 20.999 | 20.999 | 20.999 | 20.999 | 20.999 | 43.3406 | 20.999 | 20.999 | 20.999 | 20.999 | 23.2943 | 24.3789 | 23.4836 | 21.1328 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 18 | 1170 | 5.7 | 5.7 | 4.2542 | 5.0802 | 15 | 91 | 91 | 1.5758 | 7.9195 | -1.3434 | 252.2165 | 0 | 0 | 0 | 0 | 0.77793 | 1.5093 | 1.3566 | 0.40919 | 0.080518 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 7.9195 | 3.7018 | 3.7018 | 3.7018 | 3.7018 | 4.4798 | 5.2112 | 5.0585 | 4.111 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 19 | 1171 | 5.9 | 5.9 | 4.2542 | 5.0802 | 15 | 89 | 89 | 0 | 0 | -10.3428 | 263.8829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 20 | 1172 | 4 | 4 | 4.2542 | 5.0802 | 15 | 89 | 89 | 0 | 0 | -19.5406 | 275.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 21 | 1173 | 4.7 | 4.7 | 4.2542 | 5.0802 | 15 | 89 | 89 | 0 | 0 | -28.5352 | 288.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 22 | 1174 | 4.4 | 4.4 | 4.2542 | 5.0802 | 15 | 89 | 89 | 0 | 0 | -36.8306 | 302.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 23 | 1175 | 3.5 | 3.5 | 4.2542 | 5.0802 | 15 | 88 | 88 | 0 | 0 | -43.7436 | 319.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 18 | 24 | 1176 | 3.1 | 3.1 | 5.1958 | 5.0777 | 15 | 89 | 89 | 0 | 0 | -48.3634 | 340.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 1 | 1177 | 2.5 | 2.5 | 5.1958 | 5.0777 | 15 | 89 | 89 | 0 | 0 | -49.7706 | 2.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 2 | 1178 | 2.1 | 2.1 | 5.1958 | 5.0777 | 15 | 88 | 88 | 0 | 0 | -47.267 | 24.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 3 | 1179 | 1.6 | 1.6 | 5.1958 | 5.0777 | 15 | 86 | 86 | 0 | 0 | -42.089 | 43.8251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 4 | 1180 | 1.2 | 1.2 | 5.1958 | 5.0777 | 15 | 87 | 87 | 0 | 0 | -34.8286 | 60.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 5 | 1181 | 0.8 | 0.8 | 5.1958 | 5.0777 | 15 | 88 | 88 | 0 | 0 | -26.3463 | 74.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 6 | 1182 | 0.4 | 0.4 | 5.1958 | 5.0777 | 15 | 89 | 89 | 0 | 0 | -17.2764 | 86.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 7 | 1183 | 0.4 | 0.4 | 5.1958 | 5.0777 | 15 | 91 | 91 | 0 | 0 | -8.0875 | 98.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 19 | 8 | 1184 | 0.5 | 0.5 | 5.1958 | 5.0777 | 15 | 89 | 89 | 0 | 0 | 0.82755 | 110.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 9 | 1185 | 0.4 | 0.4 | 5.1958 | 5.0777 | 15 | 89 | 89 | 71.5072 | 40.7049 | 9.081 | 122.3488 | 0 | 30.0658 | 67.1305 | 64.8711 | 24.611 | 0 | 0 | 0 | 6.2951 | 15.0995 | 79.191 | 158.2021 | 153.3856 | 67.563 | 15.0995 | 15.0995 | 15.0995 | 40.7049 | 15.0995 | 109.2568 | 225.3326 | 218.2567 | 92.174 | 15.0995 | 15.0995 | 15.0995 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 10 | 1186 | 1.4 | 1.4 | 5.1958 | 5.0777 | 15 | 84 | 84 | 381.3901 | 90.5805 | 16.2426 | 135.5118 | 0 | 82.4836 | 318.1626 | 367.4662 | 201.5131 | 0 | 0 | 0 | 84.4195 | 51.5807 | 69.0161 | 118.834 | 129.2558 | 94.1766 | 51.5807 | 51.5807 | 51.5807 | 90.5805 | 51.5807 | 151.4998 | 436.9966 | 496.7221 | 295.6898 | 51.5807 | 51.5807 | 51.5807 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 11 | 1187 | 2.6 | 2.6 | 5.1958 | 5.0777 | 15 | 79 | 79 | 575.4317 | 104.7599 | 21.8244 | 149.9036 | 0 | 0 | 387.1457 | 552.4418 | 394.1249 | 4.9351 | 0 | 0 | 189.2401 | 70.2828 | 70.2828 | 143.0851 | 174.1688 | 144.3976 | 71.2109 | 70.2828 | 70.2828 | 104.7599 | 70.2828 | 70.2828 | 530.2308 | 726.6106 | 538.5225 | 76.1459 | 70.2828 | 70.2828 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 12 | 1188 | 3.2 | 3.2 | 5.1958 | 5.0777 | 15 | 72 | 72 | 577.8341 | 127.9831 | 25.3235 | 165.4872 | 0 | 0 | 268.9908 | 518.3742 | 464.101 | 137.9637 | 0 | 0 | 233.0169 | 84.7978 | 84.7978 | 140.0873 | 191.3467 | 180.1911 | 113.1555 | 84.7978 | 84.7978 | 127.9831 | 84.7978 | 84.7978 | 409.0781 | 709.7209 | 644.2921 | 251.1192 | 84.7978 | 84.7978 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 13 | 1189 | 3.2 | 3.2 | 5.1958 | 5.0777 | 15 | 63 | 63 | 233.8401 | 203.2416 | 26.3459 | 181.7855 | 0 | 0 | 52.9684 | 182.1463 | 204.6253 | 107.2377 | 0 | 0 | 102.7584 | 101.6373 | 101.6373 | 131.2123 | 203.3391 | 215.8903 | 161.5137 | 101.6373 | 101.6373 | 203.2416 | 101.6373 | 101.6373 | 184.1807 | 385.4853 | 420.5156 | 268.7513 | 101.6373 | 101.6373 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 14 | 1190 | 4.5 | 4.5 | 5.1958 | 5.0777 | 15 | 61 | 61 | 661.7571 | 120.1842 | 24.762 | 197.9901 | 0 | 0 | 0 | 406.0602 | 592.7331 | 432.191 | 18.4773 | 0 | 287.8158 | 86.1508 | 86.1508 | 86.1508 | 152.444 | 182.9202 | 156.7101 | 89.1674 | 86.1508 | 120.1842 | 86.1508 | 86.1508 | 86.1508 | 558.5042 | 775.6532 | 588.9011 | 107.6447 | 86.1508 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 15 | 1191 | 4.4 | 4.4 | 5.1958 | 5.0777 | 15 | 56 | 56 | 691.9899 | 102.1016 | 20.7696 | 213.3391 | 0 | 0 | 0 | 285.3682 | 597.644 | 559.8281 | 194.0725 | 0 | 269.8984 | 76.9871 | 76.9871 | 76.9871 | 118.0356 | 162.9547 | 157.5151 | 104.9033 | 76.9871 | 102.1016 | 76.9871 | 76.9871 | 76.9871 | 403.4038 | 760.5987 | 717.3432 | 298.9758 | 76.9871 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 16 | 1192 | 3.6 | 3.6 | 5.1958 | 5.0777 | 15 | 59 | 59 | 254.9747 | 140.5112 | 14.8002 | 227.4529 | 0 | 0 | 0 | 48.1861 | 199.1712 | 233.4844 | 131.0257 | 0 | 78.4888 | 74.9411 | 74.9411 | 74.9411 | 97.8222 | 169.5172 | 185.8108 | 137.1584 | 74.9411 | 140.5112 | 74.9411 | 74.9411 | 74.9411 | 146.0083 | 368.6884 | 419.2952 | 268.1841 | 74.9411 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 17 | 1193 | 3.1 | 3.1 | 5.1958 | 5.0777 | 15 | 59 | 59 | 219.6613 | 90.3995 | 7.3611 | 240.3779 | 0 | 0 | 0 | 0 | 143.6062 | 212.1789 | 156.4601 | 9.0891 | 42.6005 | 49.332 | 49.332 | 49.332 | 49.332 | 113.7525 | 144.5137 | 119.5187 | 53.4093 | 90.3995 | 49.332 | 49.332 | 49.332 | 49.332 | 257.3587 | 356.6926 | 275.9788 | 62.4984 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 19 | 18 | 1194 | 2.3 | 2.3 | 5.1958 | 5.0777 | 15 | 61 | 61 | 165.6746 | 26.7023 | -1.071 | 252.4424 | 0 | 0 | 0 | 0 | 81.2143 | 158.4265 | 142.8346 | 43.5722 | 9.2977 | 15.4548 | 15.4548 | 15.4548 | 15.4548 | 47.1094 | 77.2041 | 71.127 | 32.4378 | 26.7023 | 15.4548 | 15.4548 | 15.4548 | 15.4548 | 128.3237 | 235.6306 | 213.9616 | 76.01 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 19 | 1195 | 1.4 | 1.4 | 5.1958 | 5.0777 | 15 | 66 | 66 | 0 | 0 | -10.078 | 264.1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 20 | 1196 | 0.8 | 0.8 | 5.1958 | 5.0777 | 15 | 70 | 70 | 0 | 0 | -19.2758 | 275.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 21 | 1197 | 0.5 | 0.5 | 5.1958 | 5.0777 | 15 | 70 | 70 | 0 | 0 | -28.262 | 288.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 22 | 1198 | 0.2 | 0.2 | 5.1958 | 5.0777 | 15 | 70 | 70 | 0 | 0 | -36.5397 | 303.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 23 | 1199 | -0.4 | -0.4 | 5.1958 | 5.0777 | 15 | 69 | 69 | 0 | 0 | -43.4275 | 320.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 19 | 24 | 1200 | -0.5 | -0.5 | 1.675 | 4.1372 | 15 | 68 | 68 | 0 | 0 | -48.0221 | 340.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 1 | 1201 | -1 | -1 | 1.675 | 4.1372 | 15 | 71 | 71 | 0 | 0 | -49.4169 | 2.4599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 2 | 1202 | -1.1 | -1.1 | 1.675 | 4.1372 | 15 | 70 | 70 | 0 | 0 | -46.9172 | 24.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 3 | 1203 | -1.3 | -1.3 | 1.675 | 4.1372 | 15 | 71 | 71 | 0 | 0 | -41.7586 | 43.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 4 | 1204 | -1.6 | -1.6 | 1.675 | 4.1372 | 15 | 72 | 72 | 0 | 0 | -34.5177 | 59.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 5 | 1205 | -2 | -2 | 1.675 | 4.1372 | 15 | 75 | 75 | 0 | 0 | -26.049 | 73.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 6 | 1206 | -2 | -2 | 1.675 | 4.1372 | 15 | 73 | 73 | 0 | 0 | -16.985 | 86.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 7 | 1207 | -2.3 | -2.3 | 1.675 | 4.1372 | 15 | 75 | 75 | 0 | 0 | -7.7946 | 98.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 20 | 8 | 1208 | -2.4 | -2.4 | 1.675 | 4.1372 | 15 | 75 | 75 | 0 | 0 | 1.1282 | 109.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 9 | 1209 | -1.6 | -1.6 | 1.675 | 4.1372 | 15 | 71 | 71 | 221.7264 | 43.3481 | 9.3946 | 122.1757 | 0 | 93.8942 | 208.3922 | 200.8169 | 75.6057 | 0 | 0 | 0 | 20.6519 | 14.6233 | 14.6233 | 14.6233 | 14.6233 | 14.6233 | 14.6233 | 14.6233 | 14.6233 | 43.3481 | 14.6233 | 108.5176 | 223.0155 | 215.4402 | 90.229 | 14.6233 | 14.6233 | 14.6233 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 10 | 1210 | -0.2 | -0.2 | 1.675 | 4.1372 | 15 | 62 | 62 | 527.7878 | 77.3926 | 16.5721 | 135.3684 | 0 | 115.5778 | 440.738 | 507.72 | 277.2864 | 0 | 0 | 0 | 119.6074 | 50.0653 | 69.9648 | 125.949 | 137.4815 | 97.8069 | 50.0653 | 50.0653 | 50.0653 | 77.3926 | 50.0653 | 185.5426 | 566.687 | 645.2015 | 375.0933 | 50.0653 | 50.0653 | 50.0653 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 11 | 1211 | 1 | 1 | 1.675 | 4.1372 | 15 | 62 | 62 | 727.4061 | 81.846 | 22.1694 | 149.8044 | 0 | 0 | 489.8085 | 697.1762 | 496.1476 | 4.4824 | 0 | 0 | 243.154 | 65.1274 | 65.1274 | 128.6632 | 155.562 | 129.4855 | 65.7089 | 65.1274 | 65.1274 | 81.846 | 65.1274 | 65.1274 | 618.4717 | 852.7382 | 625.6331 | 70.1913 | 65.1274 | 65.1274 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 12 | 1212 | 2.1 | 2.1 | 1.675 | 4.1372 | 15 | 57 | 57 | 812.0719 | 85.0556 | 25.6789 | 165.4484 | 0 | 0 | 378.2395 | 727.0722 | 649.9959 | 192.1608 | 0 | 0 | 331.9444 | 77.5287 | 77.5287 | 111.3492 | 142.5403 | 135.6485 | 94.7109 | 77.5287 | 77.5287 | 85.0556 | 77.5287 | 77.5287 | 489.5887 | 869.6125 | 785.6444 | 286.8716 | 77.5287 | 77.5287 | 417 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 13 | 1213 | 3.2 | 3.2 | 1.675 | 4.1372 | 15 | 53 | 53 | 847.6153 | 86.8214 | 26.7019 | 181.8171 | 0 | 0 | 191.9317 | 658.5492 | 739.3975 | 387.1168 | 0 | 0 | 377.1786 | 82.9014 | 82.9014 | 98.9038 | 137.8081 | 144.5488 | 115.1773 | 82.9014 | 82.9014 | 86.8214 | 82.9014 | 82.9014 | 290.8355 | 796.3573 | 883.9463 | 502.2941 | 82.9014 | 82.9014 | 464 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 14 | 1214 | 3.8 | 3.8 | 1.675 | 4.1372 | 15 | 49 | 49 | 853.3663 | 85.1176 | 25.1076 | 198.0894 | 0 | 0 | 0 | 521.7055 | 761.977 | 555.8926 | 24.1739 | 0 | 375.8824 | 81.9956 | 81.9956 | 81.9956 | 124.1498 | 143.5639 | 126.9122 | 83.9488 | 81.9956 | 85.1176 | 81.9956 | 81.9956 | 81.9956 | 645.8553 | 905.5409 | 682.8048 | 108.1228 | 81.9956 | 461 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 15 | 1215 | 4.7 | 4.7 | 1.675 | 4.1372 | 15 | 49 | 49 | 810.028 | 82.6188 | 21.0968 | 213.4922 | 0 | 0 | 0 | 331.9775 | 697.2364 | 654.0637 | 227.7493 | 0 | 320.3812 | 75.3822 | 75.3822 | 75.3822 | 103.6355 | 134.7214 | 131.0471 | 94.7651 | 75.3822 | 82.6188 | 75.3822 | 75.3822 | 75.3822 | 435.613 | 831.9577 | 785.1107 | 322.5144 | 75.3822 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 16 | 1216 | 4.3 | 4.3 | 1.675 | 4.1372 | 15 | 51 | 51 | 650.9442 | 88.1162 | 15.1064 | 227.643 | 0 | 0 | 0 | 121.1603 | 506.4761 | 595.105 | 335.1296 | 0 | 203.8838 | 64.3673 | 64.3673 | 64.3673 | 81.9276 | 137.7731 | 150.6185 | 112.9391 | 64.3673 | 88.1162 | 64.3673 | 64.3673 | 64.3673 | 203.0878 | 644.2492 | 745.7235 | 448.0686 | 64.3673 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 17 | 1217 | 3.8 | 3.8 | 1.675 | 4.1372 | 15 | 53 | 53 | 369.0022 | 82.5036 | 7.6483 | 240.5919 | 0 | 0 | 0 | 0 | 240.0234 | 355.8718 | 263.2553 | 16.4274 | 73.4964 | 48.8853 | 48.8853 | 48.8853 | 48.8853 | 112.6823 | 143.4742 | 118.8572 | 53.2516 | 82.5036 | 48.8853 | 48.8853 | 48.8853 | 48.8853 | 352.7057 | 499.346 | 382.1125 | 69.679 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 20 | 18 | 1218 | 2.6 | 2.6 | 1.675 | 4.1372 | 15 | 59 | 59 | 112.9793 | 29.0873 | -0.79797 | 252.6725 | 0 | 0 | 0 | 0 | 54.9823 | 107.8536 | 97.5457 | 30.0969 | 6.9127 | 16.3134 | 16.3134 | 16.3134 | 16.3134 | 44.994 | 72.5733 | 67.1964 | 32.0129 | 29.0873 | 16.3134 | 16.3134 | 16.3134 | 16.3134 | 99.9763 | 180.4269 | 164.7421 | 62.1098 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 19 | 1219 | 1.6 | 1.6 | 1.675 | 4.1372 | 15 | 63 | 63 | 0 | 0 | -9.8125 | 264.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 20 | 1220 | 0.8 | 0.8 | 1.675 | 4.1372 | 15 | 67 | 67 | 0 | 0 | -19.0103 | 276.2381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 21 | 1221 | 0.2 | 0.2 | 1.675 | 4.1372 | 15 | 70 | 70 | 0 | 0 | -27.9876 | 288.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 22 | 1222 | -0.3 | -0.3 | 1.675 | 4.1372 | 15 | 70 | 70 | 0 | 0 | -36.2472 | 303.3896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 23 | 1223 | -0.4 | -0.4 | 1.675 | 4.1372 | 15 | 71 | 71 | 0 | 0 | -43.1095 | 320.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 20 | 24 | 1224 | -0.5 | -0.5 | 0.475 | 2.9655 | 15 | 72 | 72 | 0 | 0 | -47.6782 | 340.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 1 | 1225 | -1.1 | -1.1 | 0.475 | 2.9655 | 15 | 74 | 74 | 0 | 0 | -49.06 | 2.4777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 2 | 1226 | -1.6 | -1.6 | 0.475 | 2.9655 | 15 | 77 | 77 | 0 | 0 | -46.5636 | 24.2063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 3 | 1227 | -1.2 | -1.2 | 0.475 | 2.9655 | 15 | 73 | 73 | 0 | 0 | -41.4238 | 43.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 4 | 1228 | -1.2 | -1.2 | 0.475 | 2.9655 | 15 | 71 | 71 | 0 | 0 | -34.2024 | 59.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 5 | 1229 | -1.5 | -1.5 | 0.475 | 2.9655 | 15 | 71 | 71 | 0 | 0 | -25.7472 | 73.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 6 | 1230 | -1.9 | -1.9 | 0.475 | 2.9655 | 15 | 72 | 72 | 0 | 0 | -16.6891 | 86.2153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 7 | 1231 | -2.4 | -2.4 | 0.475 | 2.9655 | 15 | 74 | 74 | 0 | 0 | -7.4975 | 98.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 21 | 8 | 1232 | -2.4 | -2.4 | 0.475 | 2.9655 | 15 | 75 | 75 | 0 | 0 | 1.433 | 109.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 9 | 1233 | -1.7 | -1.7 | 0.475 | 2.9655 | 15 | 72 | 72 | 114.6908 | 46.7275 | 9.7121 | 122.0033 | 0 | 48.91 | 107.9111 | 103.6994 | 38.7419 | 0 | 0 | 0 | 11.2725 | 20.0769 | 20.0769 | 20.0769 | 20.0769 | 20.0769 | 20.0769 | 20.0769 | 20.0769 | 46.7275 | 20.0769 | 68.9869 | 127.988 | 123.7762 | 58.8188 | 20.0769 | 20.0769 | 20.0769 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 10 | 1234 | -0.9 | -0.9 | 0.475 | 2.9655 | 15 | 71 | 71 | 59.1719 | 105.2763 | 16.9055 | 135.2259 | 0 | 13.1167 | 49.4596 | 56.8298 | 30.9098 | 0 | 0 | 0 | 13.7237 | 47.6364 | 76.6913 | 157.1944 | 173.5199 | 116.1046 | 47.6364 | 47.6364 | 47.6364 | 105.2763 | 47.6364 | 89.808 | 206.654 | 230.3496 | 147.0144 | 47.6364 | 47.6364 | 47.6364 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 11 | 1235 | 0.2 | 0.2 | 0.475 | 2.9655 | 15 | 72 | 72 | 50.824 | 151.7343 | 22.5181 | 149.7068 | 0 | 0 | 34.2491 | 48.6273 | 34.5202 | 0.19171 | 0 | 0 | 17.2657 | 69.8026 | 69.8026 | 139.6174 | 168.9264 | 140.1701 | 70.1934 | 69.8026 | 69.8026 | 151.7343 | 69.8026 | 69.8026 | 173.8665 | 217.5537 | 174.6903 | 70.3851 | 69.8026 | 69.8026 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 12 | 1236 | 0.6 | 0.6 | 0.475 | 2.9655 | 15 | 70 | 70 | 43.7689 | 181.8668 | 26.0376 | 165.4121 | 0 | 0 | 20.3948 | 39.1072 | 34.9111 | 10.2645 | 0 | 0 | 18.1332 | 83.8811 | 83.8811 | 128.0284 | 168.5337 | 159.4507 | 106.1 | 83.8811 | 83.8811 | 181.8668 | 83.8811 | 83.8811 | 148.4232 | 207.6409 | 194.3618 | 116.3646 | 83.8811 | 83.8811 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 13 | 1237 | 0.7 | 0.7 | 0.475 | 2.9655 | 15 | 72 | 72 | 6.5579 | 139.0452 | 27.0607 | 181.8524 | 0 | 0 | 1.4841 | 5.0816 | 5.7024 | 2.9828 | 0 | 0 | 2.9548 | 67.6473 | 67.6473 | 70.6652 | 77.9809 | 79.2433 | 73.713 | 67.6473 | 67.6473 | 139.0452 | 67.6473 | 67.6473 | 72.1493 | 83.0625 | 84.9457 | 76.6958 | 67.6473 | 67.6473 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 14 | 1238 | 1.2 | 1.2 | 0.475 | 2.9655 | 15 | 73 | 73 | 4.5813 | 116.9565 | 25.4554 | 198.1931 | 0 | 0 | 0 | 2.7901 | 4.0777 | 2.9766 | 0.13188 | 0 | 2.0435 | 58.4637 | 58.4637 | 58.4637 | 58.4637 | 58.4637 | 58.4637 | 58.4637 | 58.4637 | 116.9565 | 58.4637 | 58.4637 | 58.4637 | 61.2538 | 62.5413 | 61.4403 | 58.5955 | 58.4637 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 15 | 1239 | 1.5 | 1.5 | 0.475 | 2.9655 | 15 | 70 | 70 | 41.9907 | 175.1603 | 21.4257 | 213.65 | 0 | 0 | 0 | 17.0987 | 36.0189 | 33.8397 | 11.8376 | 0 | 16.8397 | 82.2585 | 82.2585 | 82.2585 | 112.7922 | 146.5784 | 142.6869 | 103.3973 | 82.2585 | 175.1603 | 82.2585 | 82.2585 | 82.2585 | 129.8909 | 182.5973 | 176.5266 | 115.2349 | 82.2585 | 192 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 16 | 1240 | 1.6 | 1.6 | 0.475 | 2.9655 | 15 | 72 | 72 | 10.1979 | 110.7507 | 15.4138 | 227.8378 | 0 | 0 | 0 | 1.8683 | 7.9024 | 9.3075 | 5.2603 | 0 | 3.2493 | 54.2306 | 54.2306 | 54.2306 | 55.9385 | 61.4547 | 62.7391 | 59.0394 | 54.2306 | 110.7507 | 54.2306 | 54.2306 | 54.2306 | 57.8068 | 69.3571 | 72.0466 | 64.2997 | 54.2306 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 17 | 1241 | 1.4 | 1.4 | 0.475 | 2.9655 | 15 | 73 | 73 | 2.3421 | 38.5212 | 7.9363 | 240.8104 | 0 | 0 | 0 | 0 | 1.5155 | 2.2551 | 1.6736 | 0.11178 | 0.47884 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 38.5212 | 18.5284 | 18.5284 | 18.5284 | 18.5284 | 20.0439 | 20.7835 | 20.202 | 18.6402 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 21 | 18 | 1242 | 1.3 | 1.3 | 0.475 | 2.9655 | 15 | 74 | 74 | 0.52728 | 5.965 | -0.52434 | 252.9068 | 0 | 0 | 0 | 0 | 0.25469 | 0.50247 | 0.45591 | 0.14228 | 0.034954 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 5.965 | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 3.0269 | 3.2747 | 3.2281 | 2.9145 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 19 | 1243 | 1.2 | 1.2 | 0.475 | 2.9655 | 15 | 75 | 75 | 0 | 0 | -9.5465 | 264.6103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 20 | 1244 | 1.1 | 1.1 | 0.475 | 2.9655 | 15 | 76 | 76 | 0 | 0 | -18.7439 | 276.4944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 21 | 1245 | 1 | 1 | 0.475 | 2.9655 | 15 | 76 | 76 | 0 | 0 | -27.7121 | 289.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 22 | 1246 | 1.1 | 1.1 | 0.475 | 2.9655 | 15 | 76 | 76 | 0 | 0 | -35.9532 | 303.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 23 | 1247 | 1 | 1 | 0.475 | 2.9655 | 15 | 76 | 76 | 0 | 0 | -42.7894 | 320.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 21 | 24 | 1248 | 1 | 1 | -0.041667 | 1.9951 | 15 | 76 | 76 | 0 | 0 | -47.3318 | 340.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 1 | 1249 | 1.1 | 1.1 | -0.041667 | 1.9951 | 15 | 75 | 75 | 0 | 0 | -48.7001 | 2.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 2 | 1250 | 1.1 | 1.1 | -0.041667 | 1.9951 | 15 | 76 | 76 | 0 | 0 | -46.2065 | 24.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 3 | 1251 | 1.2 | 1.2 | -0.041667 | 1.9951 | 15 | 78 | 78 | 0 | 0 | -41.085 | 43.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 4 | 1252 | 1.2 | 1.2 | -0.041667 | 1.9951 | 15 | 79 | 79 | 0 | 0 | -33.8827 | 59.5616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 5 | 1253 | 1 | 1 | -0.041667 | 1.9951 | 15 | 83 | 83 | 0 | 0 | -25.4411 | 73.5136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 6 | 1254 | 1.7 | 1.7 | -0.041667 | 1.9951 | 15 | 84 | 84 | 0 | 0 | -16.389 | 86.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 7 | 1255 | 2.2 | 2.2 | -0.041667 | 1.9951 | 15 | 82 | 82 | 0 | 0 | -7.1962 | 97.7997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 22 | 8 | 1256 | 2.7 | 2.7 | -0.041667 | 1.9951 | 15 | 78 | 78 | 0 | 0 | 1.7419 | 109.5577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 9 | 1257 | 3 | 3 | -0.041667 | 1.9951 | 15 | 77 | 77 | 2.1714 | 18.7753 | 10.0336 | 121.8316 | 0 | 0.93241 | 2.0452 | 1.9599 | 0.72655 | 0 | 0 | 0 | 0.22467 | 8.5309 | 18.9772 | 31.4441 | 30.4888 | 16.6708 | 8.5309 | 8.5309 | 8.5309 | 18.7753 | 8.5309 | 19.9096 | 33.4893 | 32.4487 | 17.3974 | 8.5309 | 8.5309 | 8.5309 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 10 | 1258 | 3.8 | 3.8 | -0.041667 | 1.9951 | 15 | 71 | 71 | 2.8595 | 49.3215 | 17.2426 | 135.0844 | 0 | 0.64148 | 2.3923 | 2.7418 | 1.4851 | 0 | 0 | 0 | 0.67848 | 24.2325 | 24.8937 | 26.6981 | 27.0583 | 25.7632 | 24.2325 | 24.2325 | 24.2325 | 49.3215 | 24.2325 | 25.5351 | 29.0904 | 29.8 | 27.2483 | 24.2325 | 24.2325 | 24.2325 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 11 | 1259 | 5.1 | 5.1 | -0.041667 | 1.9951 | 15 | 66 | 66 | 324.4434 | 149.0064 | 22.8704 | 149.6108 | 0 | 0 | 218.7828 | 309.8619 | 219.4281 | 0.45625 | 0 | 0 | 111.9936 | 81.2341 | 81.2341 | 167.2622 | 203.0757 | 167.516 | 81.4135 | 81.2341 | 81.2341 | 149.0064 | 81.2341 | 81.2341 | 386.0451 | 512.9375 | 386.944 | 81.8698 | 81.2341 | 81.2341 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 12 | 1260 | 6.6 | 6.6 | -0.041667 | 1.9951 | 15 | 64 | 64 | 330.4327 | 180.2659 | 26.3996 | 165.3784 | 0 | 0 | 154.0157 | 294.6105 | 262.6265 | 76.7994 | 0 | 0 | 138.7341 | 97.1636 | 97.1636 | 162.1766 | 221.5244 | 208.0233 | 129.5822 | 97.1636 | 97.1636 | 180.2659 | 97.1636 | 97.1636 | 316.1923 | 516.135 | 470.6498 | 206.3816 | 97.1636 | 97.1636 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 13 | 1261 | 5.4 | 5.4 | -0.041667 | 1.9951 | 15 | 74 | 74 | 40.7339 | 198.4184 | 27.4224 | 181.8912 | 0 | 0 | 9.2103 | 31.4766 | 35.3043 | 18.4512 | 0 | 0 | 18.5816 | 91.6393 | 91.6393 | 111.9613 | 161.0905 | 169.5362 | 132.3509 | 91.6393 | 91.6393 | 198.4184 | 91.6393 | 91.6393 | 121.1716 | 192.5671 | 204.8405 | 150.8021 | 91.6393 | 91.6393 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 14 | 1262 | 6.1 | 6.1 | -0.041667 | 1.9951 | 15 | 66 | 66 | 14.6306 | 168.3922 | 25.8053 | 198.3013 | 0 | 0 | 0 | 8.8749 | 12.9796 | 9.481 | 0.42859 | 0 | 6.6078 | 80.1567 | 80.1567 | 80.1567 | 97.9527 | 106.1835 | 99.1681 | 81.0161 | 80.1567 | 168.3922 | 80.1567 | 80.1567 | 80.1567 | 106.8276 | 119.1631 | 108.6491 | 81.4447 | 80.1567 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 15 | 1263 | 5.8 | 5.8 | -0.041667 | 1.9951 | 15 | 59 | 59 | 41.3608 | 177.1835 | 21.7559 | 213.8126 | 0 | 0 | 0 | 16.7302 | 35.3528 | 33.2662 | 11.6927 | 0 | 16.8165 | 83.1393 | 83.1393 | 83.1393 | 113.5955 | 147.4967 | 143.6982 | 104.4252 | 83.1393 | 177.1835 | 83.1393 | 83.1393 | 83.1393 | 130.3257 | 182.8495 | 176.9644 | 116.1179 | 83.1393 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 16 | 1264 | 5.1 | 5.1 | -0.041667 | 1.9951 | 15 | 53 | 53 | 621.0532 | 95.7339 | 15.722 | 228.0372 | 0 | 0 | 0 | 111.9128 | 479.2546 | 565.8556 | 320.986 | 0 | 201.2661 | 67.345 | 67.345 | 67.345 | 85.0192 | 143.0327 | 156.7094 | 118.0376 | 67.345 | 95.7339 | 67.345 | 67.345 | 67.345 | 196.932 | 622.2873 | 722.5649 | 439.0236 | 67.345 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 17 | 1265 | 3.9 | 3.9 | -0.041667 | 1.9951 | 15 | 60 | 60 | 41.1816 | 91.3618 | 8.2249 | 241.0332 | 0 | 0 | 0 | 0 | 26.5058 | 39.5852 | 29.4761 | 2.1004 | 8.6382 | 44.8228 | 44.8228 | 44.8228 | 44.8228 | 72.325 | 85.8961 | 75.407 | 47.0021 | 91.3618 | 44.8228 | 44.8228 | 44.8228 | 44.8228 | 98.8308 | 125.4813 | 104.8832 | 49.1025 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 22 | 18 | 1266 | 2.7 | 2.7 | -0.041667 | 1.9951 | 15 | 66 | 66 | 15.4607 | 26.8956 | -0.25018 | 253.1451 | 0 | 0 | 0 | 0 | 7.4106 | 14.7065 | 13.3874 | 4.2262 | 1.1044 | 13.9355 | 13.9355 | 13.9355 | 13.9355 | 18.1426 | 22.2845 | 21.5357 | 16.3348 | 26.8956 | 13.9355 | 13.9355 | 13.9355 | 13.9355 | 25.5532 | 36.991 | 34.9231 | 20.561 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 19 | 1267 | 0.7 | 0.7 | -0.041667 | 1.9951 | 15 | 78 | 78 | 0 | 0 | -9.2798 | 264.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 20 | 1268 | 0.3 | 0.3 | -0.041667 | 1.9951 | 15 | 74 | 74 | 0 | 0 | -18.4768 | 276.7542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 21 | 1269 | -0.5 | -0.5 | -0.041667 | 1.9951 | 15 | 73 | 73 | 0 | 0 | -27.4355 | 289.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 22 | 1270 | -1.5 | -1.5 | -0.041667 | 1.9951 | 15 | 80 | 80 | 0 | 0 | -35.6578 | 303.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 23 | 1271 | -0.4 | -0.4 | -0.041667 | 1.9951 | 15 | 75 | 75 | 0 | 0 | -42.4676 | 320.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 22 | 24 | 1272 | -1.6 | -1.6 | 2.3625 | 1.9236 | 15 | 80 | 80 | 0 | 0 | -46.9832 | 340.6441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 1 | 1273 | -0.2 | -0.2 | 2.3625 | 1.9236 | 15 | 88 | 88 | 0 | 0 | -48.3372 | 2.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 2 | 1274 | -0.6 | -0.6 | 2.3625 | 1.9236 | 15 | 88 | 88 | 0 | 0 | -45.8459 | 24.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 3 | 1275 | -0.7 | -0.7 | 2.3625 | 1.9236 | 15 | 92 | 92 | 0 | 0 | -40.7422 | 43.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 4 | 1276 | -0.9 | -0.9 | 2.3625 | 1.9236 | 15 | 85 | 85 | 0 | 0 | -33.5588 | 59.3561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 5 | 1277 | -1.7 | -1.7 | 2.3625 | 1.9236 | 15 | 82 | 82 | 0 | 0 | -25.1306 | 73.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 6 | 1278 | -1.2 | -1.2 | 2.3625 | 1.9236 | 15 | 82 | 82 | 0 | 0 | -16.0847 | 85.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 7 | 1279 | -2.3 | -2.3 | 2.3625 | 1.9236 | 15 | 88 | 88 | 0 | 0 | -6.8909 | 97.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 23 | 8 | 1280 | 0.2 | 0.2 | 2.3625 | 1.9236 | 15 | 83 | 83 | 0 | 3 | 2.0546 | 109.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 9 | 1281 | 0.6 | 0.6 | 2.3625 | 1.9236 | 15 | 86 | 86 | 14.4701 | 40.4273 | 10.3589 | 121.6606 | 0 | 6.2558 | 13.6425 | 13.0376 | 4.7955 | 0 | 0 | 0 | 1.5727 | 16.8174 | 69.1124 | 130.861 | 125.8044 | 56.9047 | 16.8174 | 16.8174 | 16.8174 | 40.4273 | 16.8174 | 75.3682 | 144.5035 | 138.842 | 61.7001 | 16.8174 | 16.8174 | 16.8174 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 10 | 1282 | 2.5 | 2.5 | 2.3625 | 1.9236 | 15 | 80 | 80 | 398.8653 | 97.2187 | 17.5834 | 134.9438 | 0 | 90.526 | 333.9695 | 381.7783 | 205.9465 | 0 | 0 | 0 | 96.7813 | 56.1323 | 76.2958 | 130.5198 | 141.1686 | 102.0043 | 56.1323 | 56.1323 | 56.1323 | 97.2187 | 56.1323 | 166.8218 | 464.4894 | 522.9469 | 307.9508 | 56.1323 | 56.1323 | 56.1323 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 11 | 1283 | 3.9 | 3.9 | 2.3625 | 1.9236 | 15 | 63 | 63 | 685.92 | 92.4585 | 23.2262 | 149.5163 | 0 | 0.64136 | 462.811 | 653.8722 | 461.904 | 0 | 0 | 0 | 240.5415 | 69.364 | 69.4559 | 135.6852 | 163.0645 | 135.5553 | 69.364 | 69.364 | 69.364 | 92.4585 | 69.364 | 70.0973 | 598.4962 | 816.9367 | 597.4592 | 69.364 | 69.364 | 69.364 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 12 | 1284 | 5 | 5 | 2.3625 | 1.9236 | 15 | 62 | 62 | 475.9853 | 155.4963 | 26.7648 | 165.3472 | 0 | 0 | 221.8947 | 423.4455 | 376.9476 | 109.639 | 0 | 0 | 202.5037 | 92.9992 | 92.9992 | 153.5947 | 208.6346 | 195.9369 | 122.9397 | 92.9992 | 92.9992 | 155.4963 | 92.9992 | 92.9992 | 375.4894 | 632.0801 | 572.8845 | 232.5786 | 92.9992 | 92.9992 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 13 | 1285 | 5.8 | 5.8 | 2.3625 | 1.9236 | 15 | 51 | 51 | 378.9509 | 189.0012 | 27.7866 | 181.9337 | 0 | 0 | 85.5898 | 291.9903 | 327.3468 | 170.948 | 0 | 0 | 174.9988 | 104.2903 | 104.2903 | 136.3305 | 213.5956 | 226.8312 | 168.284 | 104.2903 | 104.2903 | 189.0012 | 104.2903 | 104.2903 | 221.9204 | 505.5859 | 554.178 | 339.232 | 104.2903 | 104.2903 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 14 | 1286 | 6.4 | 6.4 | 2.3625 | 1.9236 | 15 | 49 | 49 | 750.6515 | 106.7543 | 26.1572 | 198.4139 | 0 | 0 | 0 | 453.4727 | 663.7156 | 485.1629 | 22.4084 | 0 | 343.2457 | 86.2044 | 86.2044 | 86.2044 | 146.6275 | 174.6413 | 150.85 | 89.1902 | 86.2044 | 106.7543 | 86.2044 | 86.2044 | 86.2044 | 600.1002 | 838.357 | 636.013 | 111.5986 | 86.2044 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 15 | 1287 | 5.5 | 5.5 | 2.3625 | 1.9236 | 15 | 51 | 51 | 674.8774 | 110.8499 | 22.0876 | 213.98 | 0 | 0 | 0 | 271.1037 | 574.7461 | 541.7101 | 191.3476 | 0 | 278.1501 | 81.4145 | 81.4145 | 81.4145 | 122.9385 | 169.4463 | 164.3863 | 110.7226 | 81.4145 | 110.8499 | 81.4145 | 81.4145 | 81.4145 | 394.0422 | 744.1925 | 706.0964 | 302.0701 | 81.4145 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 16 | 1288 | 3.6 | 3.6 | 2.3625 | 1.9236 | 15 | 62 | 62 | 70.1566 | 151.8802 | 16.0312 | 228.2413 | 0 | 0 | 0 | 12.4264 | 53.9066 | 63.8091 | 36.3331 | 0 | 23.1198 | 72.7385 | 72.7385 | 72.7385 | 85.0463 | 126.1307 | 135.9387 | 108.7248 | 72.7385 | 151.8802 | 72.7385 | 72.7385 | 72.7385 | 97.4727 | 180.0374 | 199.7478 | 145.0579 | 72.7385 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 17 | 1289 | 4.4 | 4.4 | 2.3625 | 1.9236 | 15 | 58 | 58 | 449.8242 | 81.2435 | 8.514 | 241.2604 | 0 | 0 | 0 | 0 | 287.9303 | 431.6396 | 322.5003 | 24.4446 | 96.7565 | 50.6849 | 50.6849 | 50.6849 | 50.6849 | 112.3742 | 143.164 | 119.7808 | 55.9221 | 81.2435 | 50.6849 | 50.6849 | 50.6849 | 50.6849 | 400.3045 | 574.8036 | 442.281 | 80.3668 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 23 | 18 | 1290 | 2.4 | 2.4 | 2.3625 | 1.9236 | 15 | 64 | 64 | 24.7222 | 31.1059 | 0.024416 | 253.3874 | 0 | 0 | 0 | 0 | 11.7562 | 23.4718 | 21.4379 | 6.846 | 1.8941 | 16.0537 | 16.0537 | 16.0537 | 16.0537 | 21.6218 | 27.1707 | 26.2074 | 19.2962 | 31.1059 | 16.0537 | 16.0537 | 16.0537 | 16.0537 | 33.378 | 50.6425 | 47.6453 | 26.1422 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 19 | 1291 | 0.3 | 0.3 | 2.3625 | 1.9236 | 15 | 76 | 76 | 0 | 0 | -9.0127 | 265.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 20 | 1292 | -1.5 | -1.5 | 2.3625 | 1.9236 | 15 | 82 | 82 | 0 | 0 | -18.209 | 277.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 21 | 1293 | -2 | -2 | 2.3625 | 1.9236 | 15 | 90 | 90 | 0 | 0 | -27.158 | 289.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 22 | 1294 | -2.5 | -2.5 | 2.3625 | 1.9236 | 15 | 93 | 93 | 0 | 0 | -35.361 | 304.1715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 23 | 1295 | -2.4 | -2.4 | 2.3625 | 1.9236 | 15 | 92 | 92 | 0 | 0 | -42.1439 | 321.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 23 | 24 | 1296 | -2.4 | -2.4 | 0.925 | 1.6071 | 15 | 91 | 91 | 0 | 0 | -46.6322 | 340.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 1 | 1297 | -2.4 | -2.4 | 0.925 | 1.6071 | 15 | 91 | 91 | 0 | 0 | -47.9716 | 2.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 2 | 1298 | 0.6 | 0.6 | 0.925 | 1.6071 | 15 | 85 | 85 | 0 | 0 | -45.482 | 23.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 3 | 1299 | -0.1 | -0.1 | 0.925 | 1.6071 | 15 | 94 | 94 | 0 | 0 | -40.3956 | 42.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 4 | 1300 | 0.3 | 0.3 | 0.925 | 1.6071 | 15 | 94 | 94 | 0 | 0 | -33.2309 | 59.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 5 | 1301 | -1.6 | -1.6 | 0.925 | 1.6071 | 15 | 94 | 94 | 0 | 0 | -24.8161 | 73.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 6 | 1302 | 0 | 0 | 0.925 | 1.6071 | 15 | 95 | 95 | 0 | 0 | -15.7764 | 85.5786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 7 | 1303 | 0.4 | 0.4 | 0.925 | 1.6071 | 15 | 92 | 92 | 0 | 0 | -6.5817 | 97.3931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 24 | 8 | 1304 | 1.2 | 1.2 | 0.925 | 1.6071 | 15 | 90 | 90 | 0 | 3 | 2.3711 | 109.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 9 | 1305 | 2.2 | 2.2 | 0.925 | 1.6071 | 15 | 88 | 88 | 91.778 | 53.5435 | 10.6877 | 121.4903 | 0 | 39.9435 | 86.6108 | 82.5427 | 30.1222 | 0 | 0 | 0 | 10.4565 | 21.7801 | 99.5916 | 190.5014 | 182.5766 | 80.4594 | 21.7801 | 21.7801 | 21.7801 | 53.5435 | 21.7801 | 139.5351 | 277.1123 | 265.1194 | 110.5816 | 21.7801 | 21.7801 | 21.7801 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 10 | 1306 | 3.6 | 3.6 | 0.925 | 1.6071 | 15 | 87 | 87 | 265.6515 | 112.1073 | 17.9277 | 134.8042 | 0 | 60.9824 | 222.599 | 253.8201 | 136.3568 | 0 | 0 | 0 | 65.8927 | 59.4478 | 85.1392 | 153.227 | 166.3803 | 116.8939 | 59.4478 | 59.4478 | 59.4478 | 112.1073 | 59.4478 | 146.1216 | 375.826 | 420.2004 | 253.2507 | 59.4478 | 59.4478 | 59.4478 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 11 | 1307 | 4.3 | 4.3 | 0.925 | 1.6071 | 15 | 75 | 75 | 69.9939 | 164.0677 | 23.5852 | 149.4234 | 0 | 0.22759 | 47.2507 | 66.595 | 46.9289 | 0 | 0 | 0 | 24.9323 | 75.6048 | 75.9623 | 149.8445 | 180.238 | 149.3388 | 75.6048 | 75.6048 | 75.6048 | 164.0677 | 75.6048 | 76.1899 | 197.0952 | 246.833 | 196.2676 | 75.6048 | 75.6048 | 75.6048 | 189 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 12 | 1308 | 5.2 | 5.2 | 0.925 | 1.6071 | 15 | 60 | 60 | 321.7832 | 186.2957 | 27.1329 | 165.3185 | 0 | 0 | 150.0144 | 285.6085 | 253.8969 | 73.456 | 0 | 0 | 138.7043 | 99.5593 | 99.5593 | 165.7137 | 225.5089 | 211.5246 | 131.9525 | 99.5593 | 99.5593 | 186.2957 | 99.5593 | 99.5593 | 315.7282 | 511.1174 | 465.4215 | 205.4085 | 99.5593 | 99.5593 | 325 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 13 | 1309 | 5.8 | 5.8 | 0.925 | 1.6071 | 15 | 63 | 63 | 194.9603 | 219.8663 | 28.1534 | 181.9797 | 0 | 0 | 43.9742 | 149.7753 | 167.84 | 87.5864 | 0 | 0 | 91.1337 | 107.0491 | 107.0491 | 138.009 | 212.4978 | 225.2162 | 168.7139 | 107.0491 | 107.0491 | 219.8663 | 107.0491 | 107.0491 | 181.9832 | 362.273 | 393.0562 | 256.3003 | 107.0491 | 107.0491 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 14 | 1310 | 4.9 | 4.9 | 0.925 | 1.6071 | 15 | 74 | 74 | 25.1523 | 188.3568 | 26.5111 | 198.5309 | 0 | 0 | 0 | 15.13 | 22.1632 | 16.2135 | 0.76611 | 0 | 11.6432 | 88.4703 | 88.4703 | 88.4703 | 114.0686 | 125.968 | 115.9017 | 89.7664 | 88.4703 | 188.3568 | 88.4703 | 88.4703 | 88.4703 | 129.1986 | 148.1312 | 132.1152 | 90.5325 | 88.4703 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 15 | 1311 | 4.8 | 4.8 | 0.925 | 1.6071 | 15 | 77 | 77 | 4.7998 | 111.9949 | 22.4206 | 214.1519 | 0 | 0 | 0 | 1.9144 | 4.0724 | 3.8448 | 1.365 | 0 | 2.0051 | 55.8834 | 55.8834 | 55.8834 | 55.8834 | 55.8834 | 55.8834 | 55.8834 | 55.8834 | 111.9949 | 55.8834 | 55.8834 | 55.8834 | 57.7978 | 59.9558 | 59.7282 | 57.2484 | 55.8834 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 16 | 1312 | 3.8 | 3.8 | 0.925 | 1.6071 | 15 | 88 | 88 | 1.8005 | 55.3967 | 16.3411 | 228.4499 | 0 | 0 | 0 | 0.31325 | 1.3774 | 1.6347 | 0.93439 | 0 | 0.60326 | 26.7744 | 26.7744 | 26.7744 | 26.7744 | 26.7744 | 26.7744 | 26.7744 | 26.7744 | 55.3967 | 26.7744 | 26.7744 | 26.7744 | 27.0877 | 28.1518 | 28.4091 | 27.7088 | 26.7744 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 17 | 1313 | 3.3 | 3.3 | 0.925 | 1.6071 | 15 | 91 | 91 | 0.82874 | 24.8173 | 8.8036 | 241.4917 | 0 | 0 | 0 | 0 | 0.52748 | 0.79382 | 0.59516 | 0.047856 | 0.18271 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 24.8173 | 11.7531 | 11.7531 | 11.7531 | 11.7531 | 12.2806 | 12.5469 | 12.3483 | 11.801 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 18 | 1314 | 2.8 | 2.8 | 0.925 | 1.6071 | 15 | 92 | 92 | 0.34653 | 5.9716 | 0.29939 | 253.6335 | 0 | 0 | 0 | 0 | 0.16345 | 0.32836 | 0.30093 | 0.097213 | 0.028355 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 5.9716 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.9369 | 3.1018 | 3.0744 | 2.8707 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 19 | 1315 | 2.8 | 2.8 | 0.925 | 1.6071 | 15 | 93 | 93 | 0 | 0 | -8.7452 | 265.3713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 20 | 1316 | 2.5 | 2.5 | 0.925 | 1.6071 | 15 | 94 | 94 | 0 | 0 | -17.9406 | 277.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 21 | 1317 | 1.6 | 1.6 | 0.925 | 1.6071 | 15 | 94 | 94 | 0 | 0 | -26.8795 | 290.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 22 | 1318 | 0.9 | 0.9 | 0.925 | 1.6071 | 15 | 96 | 96 | 0 | 0 | -35.0629 | 304.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 23 | 1319 | 0.9 | 0.9 | 0.925 | 1.6071 | 15 | 96 | 96 | 0 | 0 | -41.8184 | 321.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 24 | 24 | 1320 | 1 | 1 | 2.0333 | 1.5531 | 15 | 96 | 96 | 0 | 0 | -46.2791 | 340.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 1 | 1321 | 1.3 | 1.3 | 2.0333 | 1.5531 | 15 | 97 | 97 | 0 | 0 | -47.6032 | 2.5892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 2 | 1322 | 1 | 1 | 2.0333 | 1.5531 | 15 | 96 | 96 | 0 | 0 | -45.1149 | 23.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 3 | 1323 | 0.5 | 0.5 | 2.0333 | 1.5531 | 15 | 96 | 96 | 0 | 0 | -40.0453 | 42.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 4 | 1324 | 0.1 | 0.1 | 2.0333 | 1.5531 | 15 | 96 | 96 | 0 | 0 | -32.899 | 58.9534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 5 | 1325 | 0.6 | 0.6 | 2.0333 | 1.5531 | 15 | 92 | 92 | 0 | 0 | -24.4977 | 72.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 6 | 1326 | -0.8 | -0.8 | 2.0333 | 1.5531 | 15 | 93 | 93 | 0 | 0 | -15.4642 | 85.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 7 | 1327 | 0.1 | 0.1 | 2.0333 | 1.5531 | 15 | 93 | 93 | 0 | 0 | -6.2687 | 97.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 25 | 8 | 1328 | -0.3 | -0.3 | 2.0333 | 1.5531 | 15 | 93 | 93 | 0 | 6 | 2.6912 | 108.9878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 9 | 1329 | 0.4 | 0.4 | 2.0333 | 1.5531 | 15 | 95 | 95 | 29.1176 | 49.5288 | 11.0201 | 121.3207 | 0 | 12.7558 | 27.5029 | 26.1391 | 9.4635 | 0 | 0 | 0 | 3.4712 | 20.4547 | 88.871 | 167.9677 | 160.6533 | 71.2125 | 20.4547 | 20.4547 | 20.4547 | 49.5288 | 20.4547 | 101.6268 | 195.4705 | 186.7924 | 80.6759 | 20.4547 | 20.4547 | 20.4547 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 10 | 1330 | 1.2 | 1.2 | 2.0333 | 1.5531 | 15 | 90 | 90 | 139.4324 | 120.6583 | 18.2753 | 134.6655 | 0 | 32.366 | 116.9167 | 132.9792 | 71.1443 | 0 | 0 | 0 | 35.3417 | 56.9326 | 92.8349 | 186.6235 | 204.4409 | 135.85 | 56.9326 | 56.9326 | 56.9326 | 120.6583 | 56.9326 | 125.2009 | 303.5402 | 337.4201 | 206.9942 | 56.9326 | 56.9326 | 56.9326 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 11 | 1331 | 0.5 | 0.5 | 2.0333 | 1.5531 | 15 | 96 | 96 | 5.7471 | 105.921 | 23.9475 | 149.332 | 0 | 0.031857 | 3.8813 | 5.4571 | 3.8363 | 0 | 0 | 0 | 2.079 | 50.726 | 50.8329 | 63.7507 | 69.0388 | 63.5995 | 50.726 | 50.726 | 50.726 | 105.921 | 50.726 | 50.8647 | 67.632 | 74.4959 | 67.4357 | 50.726 | 50.726 | 50.726 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 12 | 1332 | 2.6 | 2.6 | 2.0333 | 1.5531 | 15 | 85 | 85 | 223.0975 | 202.5785 | 27.504 | 165.2922 | 0 | 0 | 103.9981 | 197.5472 | 175.3758 | 50.4716 | 0 | 0 | 97.4215 | 100.2681 | 100.2681 | 164.103 | 221.5242 | 207.9153 | 131.248 | 100.2681 | 100.2681 | 202.5785 | 100.2681 | 100.2681 | 268.1011 | 419.0714 | 383.291 | 181.7196 | 100.2681 | 100.2681 | 300 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 13 | 1333 | 3.5 | 3.5 | 2.0333 | 1.5531 | 15 | 74 | 74 | 193.239 | 222.5756 | 28.5226 | 182.0294 | 0 | 0 | 43.5163 | 147.9968 | 165.7828 | 86.4555 | 0 | 0 | 91.4244 | 108.1625 | 108.1625 | 139.2461 | 213.8764 | 226.581 | 169.9176 | 108.1625 | 108.1625 | 222.5756 | 108.1625 | 108.1625 | 182.7624 | 361.8732 | 392.3638 | 256.373 | 108.1625 | 108.1625 | 314 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 14 | 1334 | 3.3 | 3.3 | 2.0333 | 1.5531 | 15 | 80 | 80 | 193.2814 | 220.4339 | 26.8667 | 198.6522 | 0 | 0 | 0 | 115.755 | 169.7161 | 124.2597 | 6.0137 | 0 | 90.5661 | 107.6281 | 107.6281 | 107.6281 | 186.7779 | 223.6748 | 192.5931 | 111.7401 | 107.6281 | 220.4339 | 107.6281 | 107.6281 | 107.6281 | 302.5329 | 393.3908 | 316.8528 | 117.7538 | 107.6281 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 15 | 1335 | 0.9 | 0.9 | 2.0333 | 1.5531 | 15 | 88 | 88 | 36.6612 | 181.4793 | 22.7547 | 214.3286 | 0 | 0 | 0 | 14.5146 | 30.9863 | 29.3066 | 10.4595 | 0 | 15.5207 | 84.9585 | 84.9585 | 84.9585 | 114.6177 | 148.2759 | 144.8436 | 106.3314 | 84.9585 | 181.4793 | 84.9585 | 84.9585 | 84.9585 | 129.1323 | 179.2622 | 174.1502 | 116.7909 | 84.9585 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 16 | 1336 | 2.3 | 2.3 | 2.0333 | 1.5531 | 15 | 81 | 81 | 43.5395 | 149.1719 | 16.6517 | 228.663 | 0 | 0 | 0 | 7.435 | 33.1572 | 39.4564 | 22.6426 | 0 | 14.8281 | 71.016 | 71.016 | 71.016 | 82.0508 | 120.2273 | 129.5765 | 104.6216 | 71.016 | 149.1719 | 71.016 | 71.016 | 71.016 | 89.4858 | 153.3846 | 169.0329 | 127.2642 | 71.016 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 17 | 1337 | 1.5 | 1.5 | 2.0333 | 1.5531 | 15 | 89 | 89 | 28.5138 | 93.5598 | 9.0937 | 241.7272 | 0 | 0 | 0 | 0 | 18.0432 | 27.2622 | 20.5114 | 1.7453 | 6.4402 | 45.7388 | 45.7388 | 45.7388 | 45.7388 | 71.7735 | 85.0757 | 75.3349 | 48.2571 | 93.5598 | 45.7388 | 45.7388 | 45.7388 | 45.7388 | 89.8167 | 112.3379 | 95.8463 | 50.0024 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 18 | 1338 | 0.6 | 0.6 | 2.0333 | 1.5531 | 15 | 85 | 85 | 5.3157 | 24.5372 | 0.57468 | 253.8834 | 0 | 0 | 0 | 0 | 2.4862 | 5.0267 | 4.6227 | 1.5107 | 0.46284 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 24.5372 | 11.7914 | 11.7914 | 11.7914 | 11.7914 | 14.2776 | 16.8181 | 16.414 | 13.3021 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 19 | 1339 | 0 | 0 | 2.0333 | 1.5531 | 15 | 89 | 89 | 0 | 0 | -8.4772 | 265.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 20 | 1340 | -0.4 | -0.4 | 2.0333 | 1.5531 | 15 | 94 | 94 | 0 | 0 | -17.6716 | 277.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 21 | 1341 | -0.9 | -0.9 | 2.0333 | 1.5531 | 15 | 90 | 90 | 0 | 0 | -26.6001 | 290.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 22 | 1342 | -0.9 | -0.9 | 2.0333 | 1.5531 | 15 | 94 | 94 | 0 | 0 | -34.7635 | 304.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 23 | 1343 | -1.7 | -1.7 | 2.0333 | 1.5531 | 15 | 94 | 94 | 0 | 0 | -41.4913 | 321.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 25 | 24 | 1344 | -1.5 | -1.5 | 0.57917 | 1.1587 | 15 | 95 | 95 | 0 | 0 | -45.9239 | 341.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 1 | 1345 | -0.9 | -0.9 | 0.57917 | 1.1587 | 15 | 94 | 94 | 0 | 0 | -47.2323 | 2.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 2 | 1346 | -0.6 | -0.6 | 0.57917 | 1.1587 | 15 | 94 | 94 | 0 | 0 | -44.7448 | 23.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 3 | 1347 | -1.2 | -1.2 | 0.57917 | 1.1587 | 15 | 94 | 94 | 0 | 0 | -39.6915 | 42.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 4 | 1348 | -1.5 | -1.5 | 0.57917 | 1.1587 | 15 | 92 | 92 | 0 | 0 | -32.5634 | 58.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 5 | 1349 | -1 | -1 | 0.57917 | 1.1587 | 15 | 86 | 86 | 0 | 0 | -24.1753 | 72.6656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 6 | 1350 | -1.3 | -1.3 | 0.57917 | 1.1587 | 15 | 87 | 87 | 0 | 0 | -15.1483 | 85.1607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 7 | 1351 | -1.4 | -1.4 | 0.57917 | 1.1587 | 15 | 97 | 97 | 0 | 0 | -5.952 | 96.9903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 26 | 8 | 1352 | -0.4 | -0.4 | 0.57917 | 1.1587 | 15 | 98 | 98 | 0 | 3 | 3.0148 | 108.7993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 9 | 1353 | 0.7 | 0.7 | 0.57917 | 1.1587 | 15 | 99 | 99 | 3.9982 | 30.5021 | 11.3558 | 121.1518 | 0 | 1.7628 | 3.7796 | 3.5824 | 1.2866 | 0 | 0 | 0 | 0.49786 | 13.3297 | 39.1758 | 68.7461 | 65.8543 | 32.1943 | 13.3297 | 13.3297 | 13.3297 | 30.5021 | 13.3297 | 40.9386 | 72.5258 | 69.4367 | 33.4809 | 13.3297 | 13.3297 | 13.3297 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 10 | 1354 | 2.8 | 2.8 | 0.57917 | 1.1587 | 15 | 98 | 98 | 74.3067 | 119.7606 | 18.6262 | 134.5278 | 0 | 17.4372 | 62.3467 | 70.7344 | 37.6868 | 0 | 0 | 0 | 19.2394 | 54.5879 | 84.7517 | 162.4387 | 176.9481 | 119.7806 | 54.5879 | 54.5879 | 54.5879 | 119.7606 | 54.5879 | 102.1889 | 224.7854 | 247.6825 | 157.4674 | 54.5879 | 54.5879 | 54.5879 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 11 | 1355 | 4.3 | 4.3 | 0.57917 | 1.1587 | 15 | 87 | 87 | 734.7024 | 88.1303 | 24.3128 | 149.2421 | 0 | 5.7379 | 496.343 | 696.1971 | 488.2283 | 0 | 0 | 0 | 269.8697 | 70.714 | 71.4644 | 135.6257 | 161.7625 | 134.5644 | 70.714 | 70.714 | 70.714 | 88.1303 | 70.714 | 77.2024 | 631.9687 | 857.9596 | 622.7928 | 70.714 | 70.714 | 70.714 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 12 | 1356 | 5.3 | 5.3 | 0.57917 | 1.1587 | 15 | 84 | 84 | 634.8041 | 127.2118 | 27.8778 | 165.2685 | 0 | 0 | 295.8535 | 560.7237 | 497.1296 | 142.3236 | 0 | 0 | 280.7882 | 87.9945 | 87.9945 | 139.7135 | 186.0161 | 174.8991 | 112.8745 | 87.9945 | 87.9945 | 127.2118 | 87.9945 | 87.9945 | 435.567 | 746.7398 | 672.0286 | 255.1982 | 87.9945 | 87.9945 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 13 | 1357 | 2.1 | 2.1 | 0.57917 | 1.1587 | 15 | 85 | 85 | 52.1433 | 214.0337 | 28.8941 | 182.0825 | 0 | 0 | 11.7207 | 39.8084 | 44.5768 | 23.2328 | 0 | 0 | 24.9663 | 98.6001 | 98.6001 | 120.2755 | 172.2187 | 181.0372 | 141.5651 | 98.6001 | 98.6001 | 214.0337 | 98.6001 | 98.6001 | 131.9962 | 212.0271 | 225.614 | 164.7978 | 98.6001 | 98.6001 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 14 | 1358 | 2.6 | 2.6 | 0.57917 | 1.1587 | 15 | 89 | 89 | 2.2719 | 87.9225 | 27.224 | 198.7779 | 0 | 0 | 0 | 1.3545 | 1.9878 | 1.4567 | 0.072282 | 0 | 1.0775 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 43.1155 | 87.9225 | 43.1155 | 43.1155 | 43.1155 | 44.47 | 45.1033 | 44.5722 | 43.1878 | 43.1155 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 15 | 1359 | 3.8 | 3.8 | 0.57917 | 1.1587 | 15 | 78 | 78 | 681.4145 | 113.6825 | 23.0898 | 214.5098 | 0 | 0 | 0 | 267.7318 | 573.6792 | 543.5731 | 195.0493 | 0 | 292.3175 | 83.9685 | 83.9685 | 83.9685 | 124.917 | 171.7104 | 167.1058 | 113.8005 | 83.9685 | 113.6825 | 83.9685 | 83.9685 | 83.9685 | 392.6487 | 745.3896 | 710.6789 | 308.8498 | 83.9685 | 406 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 16 | 1360 | 2.7 | 2.7 | 0.57917 | 1.1587 | 15 | 92 | 92 | 36.6663 | 148.3095 | 16.9629 | 228.8805 | 0 | 0 | 0 | 6.141 | 27.7937 | 33.1653 | 19.1091 | 0 | 12.6905 | 70.5394 | 70.5394 | 70.5394 | 81.0479 | 118.1004 | 127.2923 | 103.2391 | 70.5394 | 148.3095 | 70.5394 | 70.5394 | 70.5394 | 87.1889 | 145.8942 | 160.4576 | 122.3482 | 70.5394 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 17 | 1361 | 3.2 | 3.2 | 0.57917 | 1.1587 | 15 | 75 | 75 | 472.4291 | 84.7344 | 9.384 | 241.9666 | 0 | 0 | 0 | 0 | 297.1679 | 450.8395 | 340.4154 | 30.5806 | 109.2656 | 53.5341 | 53.5341 | 53.5341 | 53.5341 | 114.9317 | 146.6817 | 123.867 | 59.8523 | 84.7344 | 53.5341 | 53.5341 | 53.5341 | 53.5341 | 412.0996 | 597.5211 | 464.2825 | 90.433 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 26 | 18 | 1362 | 2 | 2 | 0.57917 | 1.1587 | 15 | 75 | 75 | 311.7022 | 40.2156 | 0.85021 | 254.1369 | 0 | 0 | 0 | 0 | 144.5351 | 294.1456 | 271.4496 | 89.7421 | 28.7844 | 24.2208 | 24.2208 | 24.2208 | 24.2208 | 60.3087 | 97.6639 | 91.9971 | 46.6279 | 40.2156 | 24.2208 | 24.2208 | 24.2208 | 24.2208 | 204.8438 | 391.8095 | 363.4467 | 136.37 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 19 | 1363 | 1.1 | 1.1 | 0.57917 | 1.1587 | 15 | 80 | 80 | 0 | 0 | -8.209 | 265.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 20 | 1364 | 0.5 | 0.5 | 0.57917 | 1.1587 | 15 | 82 | 82 | 0 | 0 | -17.402 | 277.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 21 | 1365 | 0.4 | 0.4 | 0.57917 | 1.1587 | 15 | 81 | 81 | 0 | 0 | -26.3198 | 290.5954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 22 | 1366 | -0.3 | -0.3 | 0.57917 | 1.1587 | 15 | 82 | 82 | 0 | 0 | -34.4628 | 304.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 23 | 1367 | -0.4 | -0.4 | 0.57917 | 1.1587 | 15 | 86 | 86 | 0 | 0 | -41.1625 | 321.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 26 | 24 | 1368 | -0.6 | -0.6 | 0.9125 | 1.0752 | 15 | 87 | 87 | 0 | 0 | -45.5668 | 341.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 1 | 1369 | -0.4 | -0.4 | 0.9125 | 1.0752 | 15 | 94 | 94 | 0 | 0 | -46.8589 | 2.6668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 2 | 1370 | -0.2 | -0.2 | 0.9125 | 1.0752 | 15 | 91 | 91 | 0 | 0 | -44.3717 | 23.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 3 | 1371 | -1.1 | -1.1 | 0.9125 | 1.0752 | 15 | 90 | 90 | 0 | 0 | -39.3343 | 42.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 4 | 1372 | -1.8 | -1.8 | 0.9125 | 1.0752 | 15 | 88 | 88 | 0 | 0 | -32.2241 | 58.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 5 | 1373 | -2.2 | -2.2 | 0.9125 | 1.0752 | 15 | 85 | 85 | 0 | 0 | -23.8493 | 72.4585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 6 | 1374 | -2.1 | -2.1 | 0.9125 | 1.0752 | 15 | 82 | 82 | 0 | 0 | -14.8287 | 84.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 7 | 1375 | -1.6 | -1.6 | 0.9125 | 1.0752 | 15 | 82 | 82 | 0 | 0 | -5.6319 | 96.7903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 27 | 8 | 1376 | -1.8 | -1.8 | 0.9125 | 1.0752 | 15 | 84 | 84 | 0 | 3 | 3.3418 | 108.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 9 | 1377 | -1.6 | -1.6 | 0.9125 | 1.0752 | 15 | 85 | 85 | 10.8068 | 45.5967 | 11.6948 | 120.9836 | 0 | 4.795 | 10.2242 | 9.6643 | 3.4431 | 0 | 0 | 0 | 1.4033 | 17.793 | 90.3289 | 172.4602 | 163.9896 | 69.879 | 17.793 | 17.793 | 17.793 | 45.5967 | 17.793 | 95.1239 | 182.6845 | 173.6539 | 73.3221 | 17.793 | 17.793 | 17.793 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 10 | 1378 | -1.1 | -1.1 | 0.9125 | 1.0752 | 15 | 85 | 85 | 11.4683 | 93.9679 | 18.9801 | 134.391 | 0 | 2.72 | 9.6279 | 10.8959 | 5.7812 | 0 | 0 | 0 | 3.0321 | 41.9993 | 58.5318 | 100.5192 | 108.2265 | 77.1388 | 41.9993 | 41.9993 | 41.9993 | 93.9679 | 41.9993 | 61.2517 | 110.1471 | 119.1224 | 82.92 | 41.9993 | 41.9993 | 41.9993 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 11 | 1379 | -1.1 | -1.1 | 0.9125 | 1.0752 | 15 | 87 | 87 | 4.9239 | 101.1639 | 24.681 | 149.1537 | 0 | 0.049493 | 3.3273 | 4.656 | 3.2573 | 0 | 0 | 0 | 1.8361 | 49.1379 | 49.2533 | 56.8912 | 59.9874 | 56.7281 | 49.1379 | 49.1379 | 49.1379 | 101.1639 | 49.1379 | 49.3028 | 60.2185 | 64.6433 | 59.9854 | 49.1379 | 49.1379 | 49.1379 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 12 | 1380 | -0.7 | -0.7 | 0.9125 | 1.0752 | 15 | 86 | 86 | 3.6134 | 104.3813 | 28.2542 | 165.2472 | 0 | 0 | 1.6835 | 3.1836 | 2.8189 | 0.80285 | 0 | 0 | 1.6187 | 51.9865 | 51.9865 | 51.9865 | 51.9865 | 51.9865 | 51.9865 | 51.9865 | 51.9865 | 104.3813 | 51.9865 | 51.9865 | 53.67 | 55.1702 | 54.8054 | 52.7894 | 51.9865 | 51.9865 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 13 | 1381 | -0.2 | -0.2 | 0.9125 | 1.0752 | 15 | 86 | 86 | 3.7637 | 115.1765 | 29.2678 | 182.1392 | 0 | 0 | 0.84423 | 2.8639 | 3.206 | 1.67 | 0 | 0 | 1.8235 | 57.4076 | 57.4076 | 57.4076 | 57.4076 | 57.4076 | 57.4076 | 57.4076 | 57.4076 | 115.1765 | 57.4076 | 57.4076 | 58.2519 | 60.2716 | 60.6136 | 59.0776 | 57.4076 | 57.4076 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 14 | 1382 | 0.1 | 0.1 | 0.9125 | 1.0752 | 15 | 85 | 85 | 3.9677 | 117.0957 | 27.5828 | 198.9078 | 0 | 0 | 0 | 2.3544 | 3.4588 | 2.5371 | 0.1292 | 0 | 1.9043 | 58.3522 | 58.3522 | 58.3522 | 58.3522 | 58.3522 | 58.3522 | 58.3522 | 58.3522 | 117.0957 | 58.3522 | 58.3522 | 58.3522 | 60.7066 | 61.811 | 60.8893 | 58.4814 | 58.3522 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 15 | 1383 | 0.4 | 0.4 | 0.9125 | 1.0752 | 15 | 84 | 84 | 4.8381 | 116.8972 | 23.4259 | 214.6954 | 0 | 0 | 0 | 1.886 | 4.0568 | 3.8512 | 1.3896 | 0 | 2.1028 | 58.4017 | 58.4017 | 58.4017 | 58.4017 | 58.4017 | 58.4017 | 58.4017 | 58.4017 | 116.8972 | 58.4017 | 58.4017 | 58.4017 | 60.2878 | 62.4586 | 62.2529 | 59.7913 | 58.4017 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 16 | 1384 | 0.5 | 0.5 | 0.9125 | 1.0752 | 15 | 83 | 83 | 4.417 | 90.4467 | 17.2746 | 229.1022 | 0 | 0 | 0 | 0.725 | 3.3323 | 3.9876 | 2.307 | 0 | 1.5533 | 44.7614 | 44.7614 | 44.7614 | 44.7614 | 44.7614 | 44.7614 | 44.7614 | 44.7614 | 90.4467 | 44.7614 | 44.7614 | 44.7614 | 45.4864 | 48.0937 | 48.749 | 47.0684 | 44.7614 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 17 | 1385 | 0.8 | 0.8 | 0.9125 | 1.0752 | 15 | 77 | 77 | 22.578 | 94.6551 | 9.6746 | 242.2101 | 0 | 0 | 0 | 0 | 14.1153 | 21.5043 | 16.2964 | 1.5423 | 5.3449 | 46.2207 | 46.2207 | 46.2207 | 46.2207 | 71.1883 | 84.2583 | 75.0464 | 48.9488 | 94.6551 | 46.2207 | 46.2207 | 46.2207 | 46.2207 | 85.3036 | 105.7626 | 91.3428 | 50.4911 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 27 | 18 | 1386 | 0.4 | 0.4 | 0.9125 | 1.0752 | 15 | 83 | 83 | 0.43319 | 7.9577 | 1.1259 | 254.394 | 0 | 0 | 0 | 0 | 0.19909 | 0.40791 | 0.37777 | 0.12635 | 0.0423 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 7.9577 | 3.7072 | 3.7072 | 3.7072 | 3.7072 | 3.9063 | 4.1151 | 4.085 | 3.8336 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 19 | 1387 | 0 | 0 | 0.9125 | 1.0752 | 15 | 88 | 88 | 0 | 0 | -7.9404 | 266.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 20 | 1388 | -0.9 | -0.9 | 0.9125 | 1.0752 | 15 | 87 | 87 | 0 | 0 | -17.1319 | 278.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 21 | 1389 | -1.9 | -1.9 | 0.9125 | 1.0752 | 15 | 91 | 91 | 0 | 0 | -26.0388 | 290.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 22 | 1390 | -2.6 | -2.6 | 0.9125 | 1.0752 | 15 | 93 | 93 | 0 | 0 | -34.161 | 305.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 23 | 1391 | -4.1 | -4.1 | 0.9125 | 1.0752 | 15 | 93 | 93 | 0 | 0 | -40.8323 | 321.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 27 | 24 | 1392 | -3.6 | -3.6 | -1.1167 | 0.53893 | 15 | 96 | 96 | 0 | 0 | -45.2077 | 341.4352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 1 | 1393 | -3.9 | -3.9 | -1.1167 | 0.53893 | 15 | 96 | 96 | 0 | 0 | -46.4832 | 2.7106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 2 | 1394 | -4.5 | -4.5 | -1.1167 | 0.53893 | 15 | 96 | 96 | 0 | 0 | -43.9959 | 23.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 3 | 1395 | -4.9 | -4.9 | -1.1167 | 0.53893 | 15 | 96 | 96 | 0 | 0 | -38.9738 | 42.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 4 | 1396 | -5.4 | -5.4 | -1.1167 | 0.53893 | 15 | 95 | 95 | 0 | 0 | -31.8813 | 58.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 5 | 1397 | -6.5 | -6.5 | -1.1167 | 0.53893 | 15 | 95 | 95 | 0 | 0 | -23.5198 | 72.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 6 | 1398 | -6.9 | -6.9 | -1.1167 | 0.53893 | 15 | 94 | 94 | 0 | 0 | -14.5057 | 84.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 7 | 1399 | -7.4 | -7.4 | -1.1167 | 0.53893 | 15 | 93 | 93 | 0 | 0 | -5.3084 | 96.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 2 | 28 | 8 | 1400 | -7.1 | -7.1 | -1.1167 | 0.53893 | 15 | 93 | 93 | 0 | 11 | 3.672 | 108.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 11 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 5.3616 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 9 | 1401 | -3.7 | -3.7 | -1.1167 | 0.53893 | 15 | 94 | 94 | 862.6187 | 24.7093 | 12.0369 | 120.816 | 0 | 385.1233 | 816.7215 | 769.8953 | 272.0749 | 0 | 0 | 0 | 125.2907 | 23.9738 | 60.8551 | 102.1871 | 97.7028 | 50.029 | 23.9738 | 23.9738 | 23.9738 | 24.7093 | 23.9738 | 445.9784 | 918.9086 | 867.5981 | 322.1039 | 23.9738 | 23.9738 | 23.9738 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 10 | 1402 | -0.3 | -0.3 | -1.1167 | 0.53893 | 15 | 85 | 85 | 775.5055 | 59.703 | 19.3371 | 134.255 | 0 | 185.8489 | 651.3735 | 735.3324 | 388.5436 | 0 | 0 | 0 | 209.297 | 52.5109 | 69.1276 | 110.7499 | 118.2566 | 87.2504 | 52.5109 | 52.5109 | 52.5109 | 59.703 | 52.5109 | 254.9764 | 762.1234 | 853.589 | 475.7939 | 52.5109 | 52.5109 | 52.5109 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 11 | 1403 | 1.4 | 1.4 | -1.1167 | 0.53893 | 15 | 76 | 76 | 975.08 | 72.93 | 25.0521 | 149.0668 | 0 | 11.9624 | 658.9933 | 919.9948 | 642.0759 | 0 | 0 | 0 | 369.07 | 75.7234 | 76.5705 | 122.3901 | 140.8729 | 121.192 | 75.7234 | 75.7234 | 75.7234 | 72.93 | 75.7234 | 88.5329 | 781.3833 | 1060.8677 | 763.2679 | 75.7234 | 75.7234 | 75.7234 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 12 | 1404 | 1.9 | 1.9 | -1.1167 | 0.53893 | 15 | 76 | 76 | 323.2826 | 195.3401 | 28.6332 | 165.2283 | 0 | 0 | 150.5459 | 284.0869 | 251.2137 | 71.1829 | 0 | 0 | 146.6599 | 103.9174 | 103.9174 | 171.6391 | 231.7112 | 216.9235 | 135.9384 | 103.9174 | 103.9174 | 195.3401 | 103.9174 | 103.9174 | 322.185 | 515.7982 | 468.1372 | 207.1213 | 103.9174 | 103.9174 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 13 | 1405 | 2.6 | 2.6 | -1.1167 | 0.53893 | 15 | 72 | 72 | 101.5297 | 231.2291 | 29.6435 | 182.1994 | 0 | 0 | 22.7211 | 76.9961 | 86.1679 | 44.8637 | 0 | 0 | 49.7709 | 107.6405 | 107.6405 | 131.6597 | 189.0357 | 198.7315 | 155.0674 | 107.6405 | 107.6405 | 231.2291 | 107.6405 | 107.6405 | 154.3808 | 266.0319 | 284.8994 | 199.9311 | 107.6405 | 107.6405 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 14 | 1406 | 3.8 | 3.8 | -1.1167 | 0.53893 | 15 | 65 | 65 | 392.8281 | 195.2224 | 27.9431 | 199.042 | 0 | 0 | 0 | 231.9738 | 341.1631 | 250.5038 | 13.1027 | 0 | 190.7776 | 108.0723 | 108.0723 | 108.0723 | 192.7575 | 232.6185 | 199.5221 | 112.8556 | 108.0723 | 195.2224 | 108.0723 | 108.0723 | 108.0723 | 424.7312 | 573.7816 | 450.0258 | 125.9583 | 108.0723 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 15 | 1407 | 3.4 | 3.4 | -1.1167 | 0.53893 | 15 | 67 | 67 | 86.7124 | 205.821 | 23.7629 | 214.8856 | 0 | 0 | 0 | 33.53 | 72.4111 | 68.8748 | 24.9926 | 0 | 38.179 | 96.859 | 96.859 | 96.859 | 131.5337 | 171.7423 | 168.0852 | 122.7048 | 96.859 | 205.821 | 96.859 | 96.859 | 96.859 | 165.0637 | 244.1534 | 236.9601 | 147.6974 | 96.859 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 16 | 1408 | 4.2 | 4.2 | -1.1167 | 0.53893 | 15 | 61 | 61 | 534.3855 | 120.0911 | 17.5867 | 229.3282 | 0 | 0 | 0 | 85.8895 | 401.1908 | 481.4799 | 279.7246 | 0 | 190.9089 | 77.1204 | 77.1204 | 77.1204 | 95.4217 | 162.606 | 179.714 | 136.7241 | 77.1204 | 120.0911 | 77.1204 | 77.1204 | 77.1204 | 181.3113 | 563.7968 | 661.1939 | 416.4486 | 77.1204 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 17 | 1409 | 3.4 | 3.4 | -1.1167 | 0.53893 | 15 | 59 | 59 | 274.4439 | 108.5312 | 9.9654 | 242.4573 | 0 | 0 | 0 | 0 | 170.502 | 260.8704 | 198.4245 | 19.7442 | 66.4688 | 59.8997 | 59.8997 | 59.8997 | 59.8997 | 125.6338 | 160.4738 | 136.3989 | 67.5118 | 108.5312 | 59.8997 | 59.8997 | 59.8997 | 59.8997 | 296.1358 | 421.3443 | 334.8234 | 87.256 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 2 | 28 | 18 | 1410 | 0.9 | 0.9 | -1.1167 | 0.53893 | 15 | 67 | 67 | 6.9104 | 32.2884 | 1.4018 | 254.6545 | 0 | 0 | 0 | 0 | 3.1472 | 6.4927 | 6.0348 | 2.0418 | 0.71162 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 32.2884 | 15.6672 | 15.6672 | 15.6672 | 15.6672 | 18.8145 | 22.1599 | 21.702 | 17.709 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 19 | 1411 | -1.4 | -1.4 | -1.1167 | 0.53893 | 15 | 74 | 74 | 0 | 0 | -7.6716 | 266.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 20 | 1412 | -3 | -3 | -1.1167 | 0.53893 | 15 | 84 | 84 | 0 | 0 | -16.8614 | 278.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 21 | 1413 | -4.1 | -4.1 | -1.1167 | 0.53893 | 15 | 90 | 90 | 0 | 0 | -25.7569 | 291.1576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 22 | 1414 | -4.6 | -4.6 | -1.1167 | 0.53893 | 15 | 91 | 91 | 0 | 0 | -33.8581 | 305.5265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 23 | 1415 | -4.7 | -4.7 | -1.1167 | 0.53893 | 15 | 93 | 93 | 0 | 0 | -40.5005 | 322.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 2 | 28 | 24 | 1416 | -5.3 | -5.3 | -2.1708 | -0.17467 | 15 | 93 | 93 | 0 | 0 | -44.8468 | 341.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 1 | 1417 | -5.1 | -5.1 | -2.1708 | -0.17467 | 15 | 94 | 94 | 0 | 0 | -46.1052 | 2.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 2 | 1418 | -3.5 | -3.5 | -2.1708 | -0.17467 | 15 | 90 | 90 | 0 | 0 | -43.6175 | 23.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 3 | 1419 | -2.6 | -2.6 | -2.1708 | -0.17467 | 15 | 90 | 90 | 0 | 0 | -38.6103 | 42.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 4 | 1420 | -2.9 | -2.9 | -2.1708 | -0.17467 | 15 | 93 | 93 | 0 | 0 | -31.5352 | 58.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 5 | 1421 | -4.9 | -4.9 | -2.1708 | -0.17467 | 15 | 94 | 94 | 0 | 0 | -23.1868 | 72.0501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 6 | 1422 | -5.5 | -5.5 | -2.1708 | -0.17467 | 15 | 93 | 93 | 0 | 0 | -14.1792 | 84.5441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 7 | 1423 | -4.6 | -4.6 | -2.1708 | -0.17467 | 15 | 96 | 96 | 0 | 0 | -4.9817 | 96.3931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 1 | 8 | 1424 | -4.9 | -4.9 | -2.1708 | -0.17467 | 15 | 95 | 95 | 0 | 17 | 4.0054 | 108.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 17 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 8.2993 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 9 | 1425 | -1.2 | -1.2 | -2.1708 | -0.17467 | 15 | 95 | 95 | 722.5498 | 34.4082 | 12.382 | 120.6492 | 0 | 324.557 | 684.5754 | 643.5789 | 225.5825 | 0 | 0 | 0 | 101.5918 | 26.9899 | 46.0936 | 67.2845 | 64.8714 | 40.2679 | 26.9899 | 26.9899 | 26.9899 | 34.4082 | 26.9899 | 370.6506 | 751.86 | 708.4503 | 265.8504 | 26.9899 | 26.9899 | 26.9899 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 10 | 1426 | 1.1 | 1.1 | -2.1708 | -0.17467 | 15 | 85 | 85 | 844.2149 | 53.5072 | 19.6969 | 134.12 | 0 | 204.3787 | 709.3886 | 798.8483 | 420.3535 | 0 | 0 | 0 | 232.4928 | 52.3045 | 68.4409 | 108.3131 | 115.3763 | 85.4928 | 52.3045 | 52.3045 | 52.3045 | 53.5072 | 52.3045 | 272.8196 | 817.7018 | 914.2246 | 505.8463 | 52.3045 | 52.3045 | 52.3045 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 11 | 1427 | 2.7 | 2.7 | -2.1708 | -0.17467 | 15 | 70 | 70 | 700.2598 | 98.019 | 25.4259 | 148.9813 | 0 | 10.1257 | 473.291 | 659.2089 | 458.9712 | 0 | 0 | 0 | 268.981 | 74.7982 | 76.2442 | 142.3887 | 168.9396 | 140.3437 | 74.7982 | 74.7982 | 74.7982 | 98.019 | 74.7982 | 86.3699 | 615.6797 | 828.1485 | 599.3149 | 74.7982 | 74.7982 | 74.7982 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 12 | 1428 | 4 | 4 | -2.1708 | -0.17467 | 15 | 62 | 62 | 400.7026 | 182.9398 | 29.0146 | 165.2117 | 0 | 0 | 186.4888 | 351.17 | 310.1406 | 87.435 | 0 | 0 | 184.0602 | 102.7985 | 102.7985 | 167.6871 | 224.9877 | 210.7116 | 133.2214 | 102.7985 | 102.7985 | 182.9398 | 102.7985 | 102.7985 | 354.1758 | 576.1577 | 520.8522 | 220.6565 | 102.7985 | 102.7985 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 13 | 1429 | 4.2 | 4.2 | -2.1708 | -0.17467 | 15 | 52 | 52 | 211.8911 | 230.9166 | 30.0211 | 182.263 | 0 | 0 | 47.2969 | 160.1293 | 179.1601 | 93.2414 | 0 | 0 | 105.0834 | 112.949 | 112.949 | 143.9801 | 218.0086 | 230.4946 | 174.124 | 112.949 | 112.949 | 230.9166 | 112.949 | 112.949 | 191.277 | 378.1379 | 409.6547 | 267.3653 | 112.949 | 112.949 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 14 | 1430 | 4.8 | 4.8 | -2.1708 | -0.17467 | 15 | 50 | 50 | 512.2636 | 170.2902 | 28.3047 | 199.1804 | 0 | 0 | 0 | 301.0003 | 443.1929 | 325.7691 | 17.5142 | 0 | 251.7098 | 103.3396 | 103.3396 | 103.3396 | 184.6846 | 223.112 | 191.3784 | 108.0727 | 103.3396 | 170.2902 | 103.3396 | 103.3396 | 103.3396 | 485.6849 | 666.3049 | 517.1474 | 125.5869 | 103.3396 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 15 | 1431 | 5.1 | 5.1 | -2.1708 | -0.17467 | 15 | 51 | 51 | 573.3263 | 141.3152 | 24.1006 | 215.0801 | 0 | 0 | 0 | 219.8505 | 476.7574 | 454.3863 | 165.8419 | 0 | 255.6848 | 92.1385 | 92.1385 | 92.1385 | 139.633 | 195.1328 | 190.3 | 127.9655 | 92.1385 | 141.3152 | 92.1385 | 92.1385 | 92.1385 | 359.4834 | 671.8902 | 644.6863 | 293.8074 | 92.1385 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 16 | 1432 | 5.4 | 5.4 | -2.1708 | -0.17467 | 15 | 55 | 55 | 257.8966 | 164.4241 | 17.8992 | 229.5584 | 0 | 0 | 0 | 40.5552 | 192.6522 | 231.8961 | 135.2984 | 0 | 93.5759 | 86.325 | 86.325 | 86.325 | 106.9024 | 184.0751 | 203.9871 | 154.9743 | 86.325 | 164.4241 | 86.325 | 86.325 | 86.325 | 147.4576 | 376.7273 | 435.8832 | 290.2727 | 86.325 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 17 | 1433 | 4.5 | 4.5 | -2.1708 | -0.17467 | 15 | 58 | 58 | 26.6004 | 101.4116 | 10.2563 | 242.7083 | 0 | 0 | 0 | 0 | 16.4198 | 25.2328 | 19.2648 | 2.0117 | 6.5884 | 49.3465 | 49.3465 | 49.3465 | 49.3465 | 76.1449 | 90.5284 | 80.7882 | 52.6298 | 101.4116 | 49.3465 | 49.3465 | 49.3465 | 49.3465 | 92.5647 | 115.7613 | 100.053 | 54.6416 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 1 | 18 | 1434 | 4 | 4 | -2.1708 | -0.17467 | 15 | 67 | 67 | 5.29 | 30.4269 | 1.6777 | 254.9183 | 0 | 0 | 0 | 0 | 2.3868 | 4.9589 | 4.6261 | 1.5834 | 0.57308 | 14.698 | 14.698 | 14.698 | 14.698 | 14.698 | 14.698 | 14.698 | 14.698 | 30.4269 | 14.698 | 14.698 | 14.698 | 14.698 | 17.0848 | 19.6569 | 19.3241 | 16.2814 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 19 | 1435 | 3 | 3 | -2.1708 | -0.17467 | 15 | 73 | 73 | 0 | 0 | -7.4027 | 266.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 20 | 1436 | 3.1 | 3.1 | -2.1708 | -0.17467 | 15 | 74 | 74 | 0 | 0 | -16.5905 | 278.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 21 | 1437 | 3 | 3 | -2.1708 | -0.17467 | 15 | 77 | 77 | 0 | 0 | -25.4744 | 291.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 22 | 1438 | 3 | 3 | -2.1708 | -0.17467 | 15 | 82 | 82 | 0 | 0 | -33.5541 | 305.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 23 | 1439 | 2.5 | 2.5 | -2.1708 | -0.17467 | 15 | 85 | 85 | 0 | 0 | -40.1673 | 322.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 1 | 24 | 1440 | 1.9 | 1.9 | 0.7125 | -0.055592 | 15 | 85 | 85 | 0 | 0 | -44.4842 | 341.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 1 | 1441 | 1.6 | 1.6 | 0.7125 | -0.055592 | 15 | 89 | 89 | 0 | 0 | -45.7251 | 2.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 2 | 1442 | 1.4 | 1.4 | 0.7125 | -0.055592 | 15 | 90 | 90 | 0 | 0 | -43.2365 | 23.4854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 3 | 1443 | 1.3 | 1.3 | 0.7125 | -0.055592 | 15 | 94 | 94 | 0 | 0 | -38.2438 | 42.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 4 | 1444 | 1.3 | 1.3 | 0.7125 | -0.055592 | 15 | 95 | 95 | 0 | 0 | -31.1859 | 57.9947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 5 | 1445 | 0.2 | 0.2 | 0.7125 | -0.055592 | 15 | 96 | 96 | 0 | 0 | -22.8506 | 71.8488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 6 | 1446 | 1.1 | 1.1 | 0.7125 | -0.055592 | 15 | 97 | 97 | 0 | 0 | -13.8496 | 84.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 7 | 1447 | 1.6 | 1.6 | 0.7125 | -0.055592 | 15 | 97 | 97 | 0 | 0 | -4.6519 | 96.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 2 | 8 | 1448 | 1.8 | 1.8 | 0.7125 | -0.055592 | 15 | 95 | 95 | 0 | 6 | 4.3417 | 108.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 9 | 1449 | 3.5 | 3.5 | 0.7125 | -0.055592 | 15 | 91 | 91 | 7.0167 | 45.9755 | 12.7299 | 120.483 | 0 | 3.1707 | 6.6521 | 6.2369 | 2.1682 | 0 | 0 | 0 | 1.0245 | 19.3154 | 72.0411 | 129.9359 | 123.0307 | 55.3704 | 19.3154 | 19.3154 | 19.3154 | 45.9755 | 19.3154 | 75.2118 | 136.5881 | 129.2676 | 57.5386 | 19.3154 | 19.3154 | 19.3154 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 10 | 1450 | 5.4 | 5.4 | 0.7125 | -0.055592 | 15 | 80 | 80 | 59.8524 | 127.1861 | 20.0594 | 133.9858 | 0 | 14.6343 | 50.3118 | 56.5173 | 29.6158 | 0 | 0 | 0 | 16.8139 | 58.0509 | 87.0451 | 157.7311 | 170.0258 | 116.7272 | 58.0509 | 58.0509 | 58.0509 | 127.1861 | 58.0509 | 101.6794 | 208.0429 | 226.5431 | 146.343 | 58.0509 | 58.0509 | 58.0509 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 11 | 1451 | 6.7 | 6.7 | 0.7125 | -0.055592 | 15 | 71 | 71 | 229.042 | 179.7329 | 25.8022 | 148.8972 | 0 | 3.8082 | 154.8014 | 215.114 | 149.4157 | 0 | 0 | 0 | 89.2671 | 89.3991 | 91.6894 | 182.497 | 218.769 | 179.258 | 89.3991 | 89.3991 | 89.3991 | 179.7329 | 89.3991 | 95.4977 | 337.2983 | 433.883 | 328.6737 | 89.3991 | 89.3991 | 89.3991 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 12 | 1452 | 7.6 | 7.6 | 0.7125 | -0.055592 | 15 | 65 | 65 | 343.3633 | 196.3231 | 29.3983 | 165.1975 | 0 | 0 | 159.6891 | 300.0819 | 264.6909 | 74.2475 | 0 | 0 | 159.6769 | 105.6029 | 105.6029 | 173.3169 | 232.8486 | 217.8415 | 137.0865 | 105.6029 | 105.6029 | 196.3231 | 105.6029 | 105.6029 | 333.006 | 532.9305 | 482.5324 | 211.334 | 105.6029 | 105.6029 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 13 | 1453 | 7.5 | 7.5 | 0.7125 | -0.055592 | 15 | 61 | 61 | 521.1378 | 171.5668 | 30.4006 | 182.3301 | 0 | 0 | 115.9989 | 392.4166 | 438.962 | 228.3694 | 0 | 0 | 261.4332 | 104.9003 | 104.9003 | 135.8154 | 209.4839 | 221.8888 | 165.7634 | 104.9003 | 104.9003 | 171.5668 | 104.9003 | 104.9003 | 251.8143 | 601.9005 | 660.8508 | 394.1328 | 104.9003 | 104.9003 | 433 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 14 | 1454 | 7.6 | 7.6 | 0.7125 | -0.055592 | 15 | 58 | 58 | 505.3973 | 173.7715 | 28.6676 | 199.323 | 0 | 0 | 0 | 295.4479 | 435.549 | 320.5114 | 17.7226 | 0 | 251.2285 | 104.6158 | 104.6158 | 104.6158 | 186.5029 | 225.3336 | 193.4495 | 109.5278 | 104.6158 | 173.7715 | 104.6158 | 104.6158 | 104.6158 | 481.9508 | 660.8826 | 513.9609 | 127.2504 | 104.6158 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 15 | 1455 | 6.7 | 6.7 | 0.7125 | -0.055592 | 15 | 66 | 66 | 55.5305 | 202.9197 | 24.439 | 215.279 | 0 | 0 | 0 | 21.1117 | 45.9787 | 43.912 | 16.1222 | 0 | 25.0803 | 94.6525 | 94.6525 | 94.6525 | 126.9084 | 164.9017 | 161.744 | 119.2851 | 94.6525 | 202.9197 | 94.6525 | 94.6525 | 94.6525 | 148.0201 | 210.8804 | 205.656 | 135.4073 | 94.6525 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 16 | 1456 | 6.1 | 6.1 | 0.7125 | -0.055592 | 15 | 66 | 66 | 5.5532 | 105.9539 | 18.2119 | 229.7926 | 0 | 0 | 0 | 0.85365 | 4.1272 | 4.9831 | 2.9199 | 0 | 2.0461 | 52.8898 | 52.8898 | 52.8898 | 52.8898 | 52.8898 | 52.8898 | 52.8898 | 52.8898 | 105.9539 | 52.8898 | 52.8898 | 52.8898 | 53.7435 | 57.017 | 57.8729 | 55.8098 | 52.8898 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 17 | 1457 | 5.5 | 5.5 | 0.7125 | -0.055592 | 15 | 67 | 67 | 2.2273 | 46.4361 | 10.5472 | 242.9629 | 0 | 0 | 0 | 0 | 1.3658 | 2.1084 | 1.6158 | 0.17677 | 0.56392 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 46.4361 | 22.4049 | 22.4049 | 22.4049 | 22.4049 | 23.7707 | 24.5132 | 24.0207 | 22.5816 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 2 | 18 | 1458 | 5 | 5 | 0.7125 | -0.055592 | 15 | 67 | 67 | 0.9798 | 13.8886 | 1.9536 | 255.1853 | 0 | 0 | 0 | 0 | 0.43786 | 0.91629 | 0.85797 | 0.29707 | 0.11141 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 13.8886 | 6.5286 | 6.5286 | 6.5286 | 6.5286 | 6.9665 | 7.4449 | 7.3866 | 6.8257 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 19 | 1459 | 3.9 | 3.9 | 0.7125 | -0.055592 | 15 | 71 | 71 | 0 | 0 | -7.1336 | 266.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 20 | 1460 | 3.4 | 3.4 | 0.7125 | -0.055592 | 15 | 77 | 77 | 0 | 0 | -16.3192 | 278.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 21 | 1461 | 3.1 | 3.1 | 0.7125 | -0.055592 | 15 | 79 | 79 | 0 | 0 | -25.1912 | 291.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 22 | 1462 | 2.8 | 2.8 | 0.7125 | -0.055592 | 15 | 80 | 80 | 0 | 0 | -33.249 | 306.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 23 | 1463 | 1.1 | 1.1 | 0.7125 | -0.055592 | 15 | 86 | 86 | 0 | 0 | -39.8328 | 322.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 2 | 24 | 1464 | -1.4 | -1.4 | 3.5333 | 0.83893 | 15 | 90 | 90 | 0 | 0 | -44.1199 | 341.9371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 1 | 1465 | -1.9 | -1.9 | 3.5333 | 0.83893 | 15 | 93 | 93 | 0 | 0 | -45.343 | 2.8597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 2 | 1466 | -2.4 | -2.4 | 3.5333 | 0.83893 | 15 | 94 | 94 | 0 | 0 | -42.8532 | 23.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 3 | 1467 | -2.5 | -2.5 | 3.5333 | 0.83893 | 15 | 96 | 96 | 0 | 0 | -37.8744 | 41.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 4 | 1468 | -1.5 | -1.5 | 3.5333 | 0.83893 | 15 | 97 | 97 | 0 | 0 | -30.8335 | 57.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 5 | 1469 | -0.7 | -0.7 | 3.5333 | 0.83893 | 15 | 97 | 97 | 0 | 0 | -22.5113 | 71.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 6 | 1470 | -0.8 | -0.8 | 3.5333 | 0.83893 | 15 | 97 | 97 | 0 | 0 | -13.517 | 84.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 7 | 1471 | -0.4 | -0.4 | 3.5333 | 0.83893 | 15 | 98 | 98 | 0 | 0 | -4.3191 | 95.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 3 | 8 | 1472 | -0.3 | -0.3 | 3.5333 | 0.83893 | 15 | 98 | 98 | 0 | 8 | 4.6808 | 107.8677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 8 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 3.8963 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 9 | 1473 | 0.4 | 0.4 | 3.5333 | 0.83893 | 15 | 98 | 98 | 28.7468 | 62.6469 | 13.0805 | 120.3174 | 0 | 13.0662 | 27.269 | 25.4981 | 8.7907 | 0 | 0 | 0 | 4.3531 | 27.243 | 102.2327 | 183.7463 | 173.5824 | 77.6949 | 27.243 | 27.243 | 27.243 | 62.6469 | 27.243 | 115.2989 | 211.0154 | 199.0805 | 86.4856 | 27.243 | 27.243 | 27.243 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 10 | 1474 | 1.1 | 1.1 | 3.5333 | 0.83893 | 15 | 99 | 99 | 26.8011 | 117.3225 | 20.4245 | 133.8524 | 0 | 6.6168 | 22.5355 | 25.2532 | 13.1779 | 0 | 0 | 0 | 7.6775 | 51.1491 | 76.041 | 135.9254 | 146.1491 | 100.723 | 51.1491 | 51.1491 | 51.1491 | 117.3225 | 51.1491 | 82.6578 | 158.4609 | 171.4022 | 113.9009 | 51.1491 | 51.1491 | 51.1491 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 11 | 1475 | 1.4 | 1.4 | 3.5333 | 0.83893 | 15 | 98 | 98 | 24.1474 | 159.4527 | 26.1809 | 148.8145 | 0 | 0.45323 | 16.3186 | 22.6247 | 15.6776 | 0 | 0 | 0 | 9.5473 | 72.1256 | 73.4184 | 118.671 | 136.658 | 116.8428 | 72.1256 | 72.1256 | 72.1256 | 159.4527 | 72.1256 | 73.8716 | 134.9896 | 159.2828 | 132.5205 | 72.1256 | 72.1256 | 72.1256 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 12 | 1476 | 3.6 | 3.6 | 3.5333 | 0.83893 | 15 | 99 | 99 | 21.7089 | 186.7808 | 29.7841 | 165.1856 | 0 | 0 | 10.0878 | 18.9182 | 16.6665 | 4.6518 | 0 | 0 | 10.2192 | 86.2697 | 86.2697 | 111.0621 | 132.764 | 127.2302 | 97.7023 | 86.2697 | 86.2697 | 186.7808 | 86.2697 | 86.2697 | 121.1499 | 151.6822 | 143.8967 | 102.3541 | 86.2697 | 86.2697 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 13 | 1477 | 6.4 | 6.4 | 3.5333 | 0.83893 | 15 | 77 | 77 | 335.8793 | 215.5778 | 30.7818 | 182.4005 | 0 | 0 | 74.5358 | 251.9822 | 281.8208 | 146.5726 | 0 | 0 | 170.4222 | 113.9335 | 113.9335 | 147.9646 | 228.9821 | 242.6056 | 180.8548 | 113.9335 | 113.9335 | 215.5778 | 113.9335 | 113.9335 | 222.5004 | 480.9642 | 524.4264 | 327.4274 | 113.9335 | 113.9335 | 386 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 14 | 1478 | 8.1 | 8.1 | 3.5333 | 0.83893 | 15 | 65 | 65 | 572.0843 | 159.3448 | 29.0315 | 199.4696 | 0 | 0 | 0 | 332.675 | 491.0594 | 361.7878 | 20.5858 | 0 | 287.6552 | 102.3944 | 102.3944 | 102.3944 | 179.705 | 216.512 | 186.4705 | 107.1784 | 102.3944 | 159.3448 | 102.3944 | 102.3944 | 102.3944 | 512.38 | 707.5713 | 548.2583 | 127.7642 | 102.3944 | 447 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 15 | 1479 | 8.4 | 8.4 | 3.5333 | 0.83893 | 15 | 50 | 50 | 625.3996 | 132.9814 | 24.7779 | 215.4821 | 0 | 0 | 0 | 235.6735 | 515.5517 | 493.4266 | 182.259 | 0 | 286.0186 | 90.943 | 90.943 | 90.943 | 133.4776 | 183.9903 | 179.9972 | 123.8373 | 90.943 | 132.9814 | 90.943 | 90.943 | 90.943 | 369.1511 | 699.542 | 673.4238 | 306.0963 | 90.943 | 419 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 16 | 1480 | 7.9 | 7.9 | 3.5333 | 0.83893 | 15 | 64 | 64 | 392.8301 | 150.0563 | 18.5247 | 230.0308 | 0 | 0 | 0 | 58.9768 | 290.4319 | 351.756 | 207.0261 | 0 | 146.9437 | 85.1958 | 85.1958 | 85.1958 | 104.4823 | 180.1721 | 200.2261 | 152.897 | 85.1958 | 150.0563 | 85.1958 | 85.1958 | 85.1958 | 163.4591 | 470.604 | 551.9821 | 359.9231 | 85.1958 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 17 | 1481 | 6.3 | 6.3 | 3.5333 | 0.83893 | 15 | 64 | 64 | 226.5006 | 119.4053 | 10.8381 | 243.2211 | 0 | 0 | 0 | 0 | 137.9598 | 213.9375 | 164.5936 | 18.8329 | 58.5947 | 63.8617 | 63.8617 | 63.8617 | 63.8617 | 131.6127 | 168.9248 | 144.6924 | 73.1104 | 119.4053 | 63.8617 | 63.8617 | 63.8617 | 63.8617 | 269.5725 | 382.8623 | 309.2859 | 91.9434 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 18 | 1482 | 4.9 | 4.9 | 3.5333 | 0.83893 | 15 | 70 | 70 | 22.0537 | 47.3734 | 2.2295 | 255.4554 | 0 | 0 | 0 | 0 | 9.759 | 20.5742 | 19.3373 | 6.7729 | 2.6266 | 23.9636 | 23.9636 | 23.9636 | 23.9636 | 32.8266 | 42.6488 | 41.5254 | 30.1146 | 47.3734 | 23.9636 | 23.9636 | 23.9636 | 23.9636 | 42.5856 | 63.223 | 60.8627 | 36.8875 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 19 | 1483 | 2 | 2 | 3.5333 | 0.83893 | 15 | 79 | 79 | 0 | 3 | -6.8644 | 267.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 3 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 1.3929 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 20 | 1484 | 1 | 1 | 3.5333 | 0.83893 | 15 | 85 | 85 | 0 | 0 | -16.0476 | 279.2286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 21 | 1485 | -0.1 | -0.1 | 3.5333 | 0.83893 | 15 | 88 | 88 | 0 | 0 | -24.9073 | 292.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 22 | 1486 | -1.2 | -1.2 | 3.5333 | 0.83893 | 15 | 94 | 94 | 0 | 0 | -32.943 | 306.3637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 23 | 1487 | 0 | 0 | 3.5333 | 0.83893 | 15 | 91 | 91 | 0 | 0 | -39.497 | 322.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 3 | 24 | 1488 | 0.9 | 0.9 | 1.6917 | 1.0009 | 15 | 85 | 85 | 0 | 0 | -43.7541 | 342.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 1 | 1489 | 0.4 | 0.4 | 1.6917 | 1.0009 | 15 | 84 | 84 | 0 | 0 | -44.959 | 2.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 2 | 1490 | 1.3 | 1.3 | 1.6917 | 1.0009 | 15 | 82 | 82 | 0 | 0 | -42.4676 | 23.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 3 | 1491 | 1.4 | 1.4 | 1.6917 | 1.0009 | 15 | 81 | 81 | 0 | 0 | -37.5025 | 41.7465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 4 | 1492 | 1 | 1 | 1.6917 | 1.0009 | 15 | 82 | 82 | 0 | 0 | -30.4782 | 57.6299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 5 | 1493 | 1 | 1 | 1.6917 | 1.0009 | 15 | 85 | 85 | 0 | 0 | -22.169 | 71.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 6 | 1494 | 1 | 1 | 1.6917 | 1.0009 | 15 | 85 | 85 | 0 | 0 | -13.1814 | 83.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 7 | 1495 | 1.2 | 1.2 | 1.6917 | 1.0009 | 15 | 84 | 84 | 0 | 0 | -3.9835 | 95.8048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 4 | 8 | 1496 | 1.9 | 1.9 | 1.6917 | 1.0009 | 15 | 80 | 80 | 19.9995 | 0.99 | 5.0226 | 107.6836 | 0 | 12.6085 | 19.8489 | 15.4621 | 2.0178 | 0 | 0 | 0 | 5.01 | 0.99804 | 1.1962 | 1.31 | 1.241 | 1.0298 | 0.99804 | 0.99804 | 0.99804 | 0.99 | 0.99804 | 13.8046 | 21.1589 | 16.7031 | 3.0476 | 0.99804 | 0.99804 | 0.99804 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 9 | 1497 | 3.1 | 3.1 | 1.6917 | 1.0009 | 15 | 75 | 75 | 5.8074 | 46.089 | 13.4337 | 120.1525 | 0 | 2.6548 | 5.5117 | 5.14 | 1.7573 | 0 | 0 | 0 | 0.91102 | 20.0909 | 61.8207 | 106.7278 | 100.8842 | 47.7129 | 20.0909 | 20.0909 | 20.0909 | 46.089 | 20.0909 | 64.4756 | 112.2396 | 106.0241 | 49.4701 | 20.0909 | 20.0909 | 20.0909 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 10 | 1498 | 4.4 | 4.4 | 1.6917 | 1.0009 | 15 | 70 | 70 | 49.6579 | 129.4992 | 20.7921 | 133.7198 | 0 | 12.3765 | 41.764 | 46.6866 | 24.2609 | 0 | 0 | 0 | 14.5008 | 59.1671 | 87.0755 | 153.3424 | 164.4427 | 113.874 | 59.1671 | 59.1671 | 59.1671 | 129.4992 | 59.1671 | 99.452 | 195.1063 | 211.1293 | 138.1349 | 59.1671 | 59.1671 | 59.1671 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 11 | 1499 | 5.8 | 5.8 | 1.6917 | 1.0009 | 15 | 65 | 65 | 179.8144 | 188.8912 | 26.5619 | 148.7331 | 0 | 3.7558 | 121.4935 | 168.062 | 116.182 | 0 | 0 | 0 | 72.1088 | 91.2784 | 94.2589 | 187.6901 | 224.6447 | 183.4752 | 91.2784 | 91.2784 | 91.2784 | 188.8912 | 91.2784 | 98.0147 | 309.1837 | 392.7067 | 299.6572 | 91.2784 | 91.2784 | 91.2784 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 12 | 1500 | 7 | 7 | 1.6917 | 1.0009 | 15 | 60 | 60 | 197.3822 | 222.9586 | 30.172 | 165.176 | 0 | 0 | 91.6334 | 171.5017 | 150.9067 | 41.9126 | 0 | 0 | 94.0414 | 108.1433 | 108.1433 | 174.4321 | 232.2099 | 217.3112 | 138.4635 | 108.1433 | 108.1433 | 222.9586 | 108.1433 | 108.1433 | 266.0654 | 403.7116 | 368.2179 | 180.3761 | 108.1433 | 108.1433 | 317 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 13 | 1501 | 8.3 | 8.3 | 1.6917 | 1.0009 | 15 | 59 | 59 | 143.4038 | 243.4157 | 31.1645 | 182.4743 | 0 | 0 | 31.7192 | 107.1751 | 119.8493 | 62.3173 | 0 | 0 | 73.5843 | 114.5358 | 114.5358 | 146.5915 | 222.848 | 235.6566 | 177.5143 | 114.5358 | 114.5358 | 243.4157 | 114.5358 | 114.5358 | 178.3108 | 330.0231 | 355.5058 | 239.8316 | 114.5358 | 114.5358 | 317 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 14 | 1502 | 9.6 | 9.6 | 1.6917 | 1.0009 | 15 | 56 | 56 | 289.5776 | 224.735 | 29.3965 | 199.6203 | 0 | 0 | 0 | 167.4847 | 247.5562 | 182.6126 | 10.6971 | 0 | 147.265 | 114.9632 | 114.9632 | 114.9632 | 205.9455 | 249.4425 | 214.1634 | 120.7741 | 114.9632 | 224.735 | 114.9632 | 114.9632 | 114.9632 | 373.4301 | 496.9987 | 396.776 | 131.4712 | 114.9632 | 372 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 15 | 1503 | 9.4 | 9.4 | 1.6917 | 1.0009 | 15 | 53 | 53 | 168.9276 | 218.7813 | 25.1173 | 215.6894 | 0 | 0 | 0 | 63.0822 | 138.6318 | 132.9727 | 49.42 | 0 | 78.2187 | 105.9619 | 105.9619 | 105.9619 | 153.7122 | 210.8997 | 206.616 | 143.3706 | 105.9619 | 218.7813 | 105.9619 | 105.9619 | 105.9619 | 216.7945 | 349.5315 | 339.5887 | 192.7906 | 105.9619 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 16 | 1504 | 9.4 | 9.4 | 1.6917 | 1.0009 | 15 | 51 | 51 | 41.9488 | 165.0725 | 18.8376 | 230.2729 | 0 | 0 | 0 | 6.145 | 30.8488 | 37.4818 | 22.1584 | 0 | 15.9275 | 78.0472 | 78.0472 | 78.0472 | 88.1172 | 128.6002 | 139.47 | 114.359 | 78.0472 | 165.0725 | 78.0472 | 78.0472 | 78.0472 | 94.2622 | 159.449 | 176.9517 | 136.5175 | 78.0472 | 181 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 17 | 1505 | 8.9 | 8.9 | 1.6917 | 1.0009 | 15 | 51 | 51 | 7.2754 | 84.0777 | 11.1289 | 243.4827 | 0 | 0 | 0 | 0 | 4.4009 | 6.8566 | 5.2958 | 0.63279 | 1.9223 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 84.0777 | 41.8853 | 41.8853 | 41.8853 | 41.8853 | 46.2862 | 48.7419 | 47.1811 | 42.5181 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 18 | 1506 | 8.7 | 8.7 | 1.6917 | 1.0009 | 15 | 53 | 53 | 3.2714 | 27.5927 | 2.5053 | 255.7285 | 0 | 0 | 0 | 0 | 1.4331 | 3.0443 | 2.8722 | 1.0176 | 0.40735 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 27.5927 | 13.2304 | 13.2304 | 13.2304 | 13.2304 | 14.6635 | 16.2748 | 16.1026 | 14.248 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 19 | 1507 | 7 | 7 | 1.6917 | 1.0009 | 15 | 60 | 60 | 0 | 3 | -6.5952 | 267.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 3 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 20 | 1508 | 6.6 | 6.6 | 1.6917 | 1.0009 | 15 | 60 | 60 | 0 | 0 | -15.7757 | 279.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 21 | 1509 | 6 | 6 | 1.6917 | 1.0009 | 15 | 60 | 60 | 0 | 0 | -24.6228 | 292.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 22 | 1510 | 5.5 | 5.5 | 1.6917 | 1.0009 | 15 | 65 | 65 | 0 | 0 | -32.6361 | 306.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 23 | 1511 | 5.2 | 5.2 | 1.6917 | 1.0009 | 15 | 64 | 64 | 0 | 0 | -39.16 | 323.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 4 | 24 | 1512 | 4.2 | 4.2 | 4.9292 | 2.0363 | 15 | 69 | 69 | 0 | 0 | -43.3868 | 342.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 1 | 1513 | 3.6 | 3.6 | 4.9292 | 2.0363 | 15 | 72 | 72 | 0 | 0 | -44.5732 | 2.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 2 | 1514 | 3.9 | 3.9 | 4.9292 | 2.0363 | 15 | 71 | 71 | 0 | 0 | -42.08 | 23.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 3 | 1515 | 4.2 | 4.2 | 4.9292 | 2.0363 | 15 | 68 | 68 | 0 | 0 | -37.128 | 41.6104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 4 | 1516 | 3.8 | 3.8 | 4.9292 | 2.0363 | 15 | 69 | 69 | 0 | 0 | -30.1201 | 57.4515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 5 | 1517 | 3.2 | 3.2 | 4.9292 | 2.0363 | 15 | 71 | 71 | 0 | 0 | -21.8238 | 71.2567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 6 | 1518 | 3 | 3 | 4.9292 | 2.0363 | 15 | 72 | 72 | 0 | 0 | -12.843 | 83.7412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 7 | 1519 | 2.7 | 2.7 | 4.9292 | 2.0363 | 15 | 73 | 73 | 0 | 0 | -3.6453 | 95.6106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 5 | 8 | 1520 | 2.4 | 2.4 | 4.9292 | 2.0363 | 15 | 74 | 74 | 30.1103 | 4.0913 | 5.3669 | 107.5001 | 0 | 19.069 | 29.9054 | 23.2237 | 2.9378 | 0 | 0 | 0 | 3.9087 | 2.4329 | 3.2511 | 3.716 | 3.4293 | 2.5589 | 2.4329 | 2.4329 | 2.4329 | 4.0913 | 2.4329 | 22.32 | 33.6214 | 26.653 | 5.4968 | 2.4329 | 2.4329 | 2.4329 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 9 | 1521 | 3 | 3 | 4.9292 | 2.0363 | 15 | 71 | 71 | 8.9515 | 54.5469 | 13.7893 | 119.9882 | 0 | 4.1152 | 8.4998 | 7.9053 | 2.68 | 0 | 0 | 0 | 1.4531 | 23.004 | 81.5193 | 143.8645 | 135.4113 | 61.1114 | 23.004 | 23.004 | 23.004 | 54.5469 | 23.004 | 85.6345 | 152.3643 | 143.3166 | 63.7914 | 23.004 | 23.004 | 23.004 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 10 | 1522 | 3.1 | 3.1 | 4.9292 | 2.0363 | 15 | 69 | 69 | 19.6674 | 116.1475 | 21.162 | 133.5879 | 0 | 4.9474 | 16.5435 | 18.4487 | 9.5469 | 0 | 0 | 0 | 5.8525 | 51.3788 | 72.404 | 121.6849 | 129.7814 | 91.9507 | 51.3788 | 51.3788 | 51.3788 | 116.1475 | 51.3788 | 77.3514 | 138.2285 | 148.2301 | 101.4976 | 51.3788 | 51.3788 | 51.3788 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 11 | 1523 | 3.8 | 3.8 | 4.9292 | 2.0363 | 15 | 68 | 68 | 8.6395 | 135.4866 | 26.9451 | 148.653 | 0 | 0.19855 | 5.8358 | 8.0545 | 5.555 | 0 | 0 | 0 | 3.5134 | 63.6961 | 64.4549 | 85.9993 | 94.4788 | 84.9262 | 63.6961 | 63.6961 | 63.6961 | 135.4866 | 63.6961 | 64.6535 | 91.8351 | 102.5332 | 90.4812 | 63.6961 | 63.6961 | 63.6961 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 12 | 1524 | 5.1 | 5.1 | 4.9292 | 2.0363 | 15 | 64 | 64 | 11.9125 | 172.2564 | 30.5617 | 165.1686 | 0 | 0 | 5.5244 | 10.3193 | 9.0692 | 2.5066 | 0 | 0 | 5.7436 | 81.1393 | 81.1393 | 97.5194 | 111.7364 | 108.03 | 88.5715 | 81.1393 | 81.1393 | 172.2564 | 81.1393 | 81.1393 | 103.0438 | 122.0556 | 117.0993 | 91.0781 | 81.1393 | 81.1393 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 13 | 1525 | 6.8 | 6.8 | 4.9292 | 2.0363 | 15 | 58 | 58 | 70.7722 | 238.279 | 31.5488 | 182.5513 | 0 | 0 | 15.5994 | 52.6863 | 58.9103 | 30.6255 | 0 | 0 | 36.721 | 109.5629 | 109.5629 | 132.6811 | 187.6438 | 196.8678 | 154.9497 | 109.5629 | 109.5629 | 238.279 | 109.5629 | 109.5629 | 148.2805 | 240.3301 | 255.7781 | 185.5752 | 109.5629 | 109.5629 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 14 | 1526 | 7.5 | 7.5 | 4.9292 | 2.0363 | 15 | 57 | 57 | 31.1497 | 214.9802 | 29.7624 | 199.775 | 0 | 0 | 0 | 17.9164 | 26.5193 | 19.5875 | 1.1816 | 0 | 16.0198 | 99.0778 | 99.0778 | 99.0778 | 147.6256 | 170.9367 | 152.1538 | 102.2796 | 99.0778 | 214.9802 | 99.0778 | 99.0778 | 99.0778 | 165.5421 | 197.456 | 171.7413 | 103.4613 | 99.0778 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 15 | 1527 | 7.6 | 7.6 | 4.9292 | 2.0363 | 15 | 55 | 55 | 33.8258 | 198.1449 | 25.457 | 215.9008 | 0 | 0 | 0 | 12.5141 | 27.6323 | 26.5638 | 9.9346 | 0 | 15.8551 | 92.152 | 92.152 | 92.152 | 121.0088 | 155.8702 | 153.4064 | 115.0606 | 92.152 | 198.1449 | 92.152 | 92.152 | 92.152 | 133.5229 | 183.5025 | 179.9702 | 124.9953 | 92.152 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 16 | 1528 | 7.7 | 7.7 | 4.9292 | 2.0363 | 15 | 54 | 54 | 8.9706 | 129.5435 | 19.1505 | 230.5187 | 0 | 0 | 0 | 1.2809 | 6.561 | 7.9977 | 4.7495 | 0 | 3.4565 | 63.5324 | 63.5324 | 63.5324 | 64.8855 | 70.4631 | 71.9808 | 68.5495 | 63.5324 | 129.5435 | 63.5324 | 63.5324 | 63.5324 | 66.1664 | 77.0241 | 79.9785 | 73.299 | 63.5324 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 17 | 1529 | 7.1 | 7.1 | 4.9292 | 2.0363 | 15 | 56 | 56 | 2.7893 | 55.2475 | 11.4195 | 243.7476 | 0 | 0 | 0 | 0 | 1.6754 | 2.6227 | 2.0337 | 0.25341 | 0.75246 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 55.2475 | 26.8249 | 26.8249 | 26.8249 | 26.8249 | 28.5003 | 29.4477 | 28.8587 | 27.0783 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 5 | 18 | 1530 | 6.3 | 6.3 | 4.9292 | 2.0363 | 15 | 59 | 59 | 0.13799 | 5.9821 | 2.7809 | 256.0044 | 0 | 0 | 0 | 0 | 0.05983 | 0.12808 | 0.12131 | 0.043473 | 0.017932 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 5.9821 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.836 | 2.9043 | 2.8975 | 2.8197 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 19 | 1531 | 5.8 | 5.8 | 4.9292 | 2.0363 | 15 | 59 | 59 | 0 | 0 | -6.3259 | 267.8261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 20 | 1532 | 3.9 | 3.9 | 4.9292 | 2.0363 | 15 | 76 | 76 | 0 | 0 | -15.5035 | 279.8062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 21 | 1533 | 2.8 | 2.8 | 4.9292 | 2.0363 | 15 | 85 | 85 | 0 | 0 | -24.3378 | 292.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 22 | 1534 | 1.6 | 1.6 | 4.9292 | 2.0363 | 15 | 93 | 93 | 0 | 0 | -32.3282 | 306.9294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 23 | 1535 | 1.8 | 1.8 | 4.9292 | 2.0363 | 15 | 92 | 92 | 0 | 0 | -38.8218 | 323.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 5 | 24 | 1536 | 1.4 | 1.4 | 4.2542 | 2.7341 | 15 | 94 | 94 | 0 | 0 | -43.0181 | 342.4541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 1 | 1537 | 1 | 1 | 4.2542 | 2.7341 | 15 | 95 | 95 | 0 | 0 | -44.1858 | 3.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 2 | 1538 | 1.3 | 1.3 | 4.2542 | 2.7341 | 15 | 96 | 96 | 0 | 0 | -41.6903 | 23.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 3 | 1539 | 1.4 | 1.4 | 4.2542 | 2.7341 | 15 | 96 | 96 | 0 | 0 | -36.7511 | 41.4774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 4 | 1540 | 1.3 | 1.3 | 4.2542 | 2.7341 | 15 | 95 | 95 | 0 | 0 | -29.7594 | 57.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 5 | 1541 | 1.2 | 1.2 | 4.2542 | 2.7341 | 15 | 96 | 96 | 0 | 0 | -21.476 | 71.0632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 6 | 1542 | 0.9 | 0.9 | 4.2542 | 2.7341 | 15 | 95 | 95 | 0 | 0 | -12.502 | 83.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 7 | 1543 | 0.7 | 0.7 | 4.2542 | 2.7341 | 15 | 95 | 95 | 0 | 0 | -3.3045 | 95.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 6 | 8 | 1544 | 0.9 | 0.9 | 4.2542 | 2.7341 | 15 | 96 | 96 | 49.7013 | 2.7992 | 5.7137 | 107.3173 | 0 | 31.6166 | 49.397 | 38.2414 | 4.6845 | 0 | 0 | 0 | 14.2008 | 2.8207 | 3.3842 | 3.7011 | 3.5023 | 2.9041 | 2.8207 | 2.8207 | 2.8207 | 2.7992 | 2.8207 | 35.0008 | 53.0982 | 41.7437 | 7.5886 | 2.8207 | 2.8207 | 2.8207 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 9 | 1545 | 1 | 1 | 4.2542 | 2.7341 | 15 | 96 | 96 | 2.9809 | 35.4998 | 14.1471 | 119.8244 | 0 | 1.3779 | 2.8316 | 2.6265 | 0.88288 | 0 | 0 | 0 | 0.50018 | 16.8539 | 26.0895 | 35.8326 | 34.4582 | 22.7714 | 16.8539 | 16.8539 | 16.8539 | 35.4998 | 16.8539 | 27.4675 | 38.6642 | 37.0847 | 23.6542 | 16.8539 | 16.8539 | 16.8539 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 10 | 1546 | 1.6 | 1.6 | 4.2542 | 2.7341 | 15 | 95 | 95 | 3.1634 | 66.041 | 21.534 | 133.4568 | 0 | 0.803 | 2.6612 | 2.9605 | 1.5256 | 0 | 0 | 0 | 0.95898 | 32.6679 | 32.9765 | 33.6906 | 33.8056 | 33.2542 | 32.6679 | 32.6679 | 32.6679 | 66.041 | 32.6679 | 33.7795 | 36.3518 | 36.7662 | 34.7798 | 32.6679 | 32.6679 | 32.6679 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 11 | 1547 | 2.2 | 2.2 | 4.2542 | 2.7341 | 15 | 89 | 89 | 14.1791 | 152.1537 | 27.3303 | 148.574 | 0 | 0.35521 | 9.5741 | 13.1846 | 9.0718 | 0 | 0 | 0 | 5.8463 | 70.1802 | 71.4125 | 103.3958 | 115.9219 | 101.6531 | 70.1802 | 70.1802 | 70.1802 | 152.1537 | 70.1802 | 71.7677 | 112.9699 | 129.1065 | 110.7248 | 70.1802 | 70.1802 | 70.1802 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 12 | 1548 | 2.7 | 2.7 | 4.2542 | 2.7341 | 15 | 88 | 88 | 5.0327 | 133.5448 | 30.9533 | 165.1633 | 0 | 0 | 2.3311 | 4.3461 | 3.8151 | 1.0493 | 0 | 0 | 2.4552 | 65.8082 | 65.8082 | 69.0003 | 71.7593 | 71.0323 | 67.2451 | 65.8082 | 65.8082 | 133.5448 | 65.8082 | 65.8082 | 71.3314 | 76.1054 | 74.8474 | 68.2944 | 65.8082 | 65.8082 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 13 | 1549 | 3.5 | 3.5 | 4.2542 | 2.7341 | 15 | 84 | 84 | 12.8986 | 190.2334 | 31.9343 | 182.6315 | 0 | 0 | 2.8325 | 9.5639 | 10.6929 | 5.5581 | 0 | 0 | 6.7666 | 90.3471 | 90.3471 | 97.3083 | 113.8514 | 116.626 | 104.0068 | 90.3471 | 90.3471 | 190.2334 | 90.3471 | 90.3471 | 100.1408 | 123.4153 | 127.3189 | 109.5649 | 90.3471 | 90.3471 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 14 | 1550 | 4.8 | 4.8 | 4.2542 | 2.7341 | 15 | 84 | 84 | 29.512 | 215.6533 | 30.129 | 199.9337 | 0 | 0 | 0 | 16.8781 | 25.0191 | 18.5043 | 1.1499 | 0 | 15.3467 | 99.3493 | 99.3493 | 99.3493 | 147.2754 | 170.3922 | 151.8931 | 102.6146 | 99.3493 | 215.6533 | 99.3493 | 99.3493 | 99.3493 | 164.1534 | 195.4113 | 170.3974 | 103.7645 | 99.3493 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 15 | 1551 | 4.8 | 4.8 | 4.2542 | 2.7341 | 15 | 75 | 75 | 6.6858 | 146.8281 | 25.797 | 216.1162 | 0 | 0 | 0 | 2.4499 | 5.4361 | 5.2379 | 1.9714 | 0 | 3.1719 | 72.4472 | 72.4472 | 72.4472 | 75.1685 | 78.4855 | 78.2654 | 74.6371 | 72.4472 | 146.8281 | 72.4472 | 72.4472 | 72.4472 | 77.6183 | 83.9215 | 83.5033 | 76.6085 | 72.4472 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 16 | 1552 | 4.8 | 4.8 | 4.2542 | 2.7341 | 15 | 66 | 66 | 55.4633 | 175.3165 | 19.4633 | 230.7682 | 0 | 0 | 0 | 7.7117 | 40.3394 | 49.3368 | 29.4334 | 0 | 21.6835 | 82.8245 | 82.8245 | 82.8245 | 93.1465 | 136.8182 | 148.8611 | 122.2207 | 82.8245 | 175.3165 | 82.8245 | 82.8245 | 82.8245 | 100.8581 | 177.1575 | 198.1979 | 151.6541 | 82.8245 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 17 | 1553 | 4.2 | 4.2 | 4.2542 | 2.7341 | 15 | 71 | 71 | 5.8859 | 81.3795 | 11.7099 | 244.0157 | 0 | 0 | 0 | 0 | 3.5099 | 5.5215 | 4.2986 | 0.55776 | 1.6205 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 81.3795 | 40.3686 | 40.3686 | 40.3686 | 40.3686 | 43.8784 | 45.89 | 44.6672 | 40.9263 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 6 | 18 | 1554 | 3.7 | 3.7 | 4.2542 | 2.7341 | 15 | 72 | 72 | 5.3733 | 38.2725 | 3.0564 | 256.2831 | 0 | 0 | 0 | 0 | 2.3052 | 4.9744 | 4.7296 | 1.7143 | 0.72751 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 38.2725 | 18.5994 | 18.5994 | 18.5994 | 18.5994 | 20.9045 | 23.5737 | 23.329 | 20.3137 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 19 | 1555 | 2.3 | 2.3 | 4.2542 | 2.7341 | 15 | 77 | 77 | 0 | 0 | -6.0567 | 268.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 20 | 1556 | 1.5 | 1.5 | 4.2542 | 2.7341 | 15 | 79 | 79 | 0 | 0 | -15.2311 | 280.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 21 | 1557 | 0.3 | 0.3 | 4.2542 | 2.7341 | 15 | 84 | 84 | 0 | 0 | -24.0522 | 292.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 22 | 1558 | 1.2 | 1.2 | 4.2542 | 2.7341 | 15 | 83 | 83 | 0 | 0 | -32.0195 | 307.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 23 | 1559 | 0.6 | 0.6 | 4.2542 | 2.7341 | 15 | 88 | 88 | 0 | 0 | -38.4825 | 323.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 6 | 24 | 1560 | 1.5 | 1.5 | 2.0583 | 2.7521 | 15 | 88 | 88 | 0 | 0 | -42.6481 | 342.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 1 | 1561 | 2.8 | 2.8 | 2.0583 | 2.7521 | 15 | 85 | 85 | 0 | 0 | -43.7968 | 3.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 2 | 1562 | 3.2 | 3.2 | 2.0583 | 2.7521 | 15 | 87 | 87 | 0 | 0 | -41.2989 | 23.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 3 | 1563 | 2.7 | 2.7 | 2.0583 | 2.7521 | 15 | 90 | 90 | 0 | 0 | -36.372 | 41.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 4 | 1564 | 3.3 | 3.3 | 2.0583 | 2.7521 | 15 | 91 | 91 | 0 | 0 | -29.3963 | 57.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 5 | 1565 | 3.3 | 3.3 | 2.0583 | 2.7521 | 15 | 93 | 93 | 0 | 0 | -21.1257 | 70.8716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 6 | 1566 | 1.9 | 1.9 | 2.0583 | 2.7521 | 15 | 95 | 95 | 0 | 0 | -12.1585 | 83.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 7 | 1567 | 3.3 | 3.3 | 2.0583 | 2.7521 | 15 | 97 | 97 | 0 | 0 | -2.9614 | 95.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 7 | 8 | 1568 | 3.1 | 3.1 | 2.0583 | 2.7521 | 15 | 96 | 96 | 14.2259 | 7.7031 | 6.0627 | 107.1352 | 0 | 9.0892 | 14.1479 | 10.9189 | 1.2938 | 0 | 0 | 0 | 0.2969 | 3.0236 | 7.8101 | 10.474 | 8.7736 | 3.7049 | 3.0236 | 3.0236 | 3.0236 | 7.7031 | 3.0236 | 16.8993 | 24.6219 | 19.6925 | 4.9987 | 3.0236 | 3.0236 | 3.0236 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 9 | 1569 | 4.4 | 4.4 | 2.0583 | 2.7521 | 15 | 93 | 93 | 8.022 | 56.6099 | 14.5072 | 119.6612 | 0 | 3.7284 | 7.6231 | 7.0522 | 2.3503 | 0 | 0 | 0 | 1.3901 | 24.4063 | 71.7719 | 121.2492 | 113.9973 | 54.2642 | 24.4063 | 24.4063 | 24.4063 | 56.6099 | 24.4063 | 75.5003 | 128.8723 | 121.0496 | 56.6145 | 24.4063 | 24.4063 | 24.4063 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 10 | 1570 | 5.8 | 5.8 | 2.0583 | 2.7521 | 15 | 83 | 83 | 188.7372 | 144.7332 | 21.9081 | 133.3263 | 0 | 48.3341 | 158.7772 | 176.2108 | 90.4225 | 0 | 0 | 0 | 58.2668 | 70.3752 | 107.3867 | 191.9577 | 205.3074 | 139.6156 | 70.3752 | 70.3752 | 70.3752 | 144.7332 | 70.3752 | 155.7208 | 350.7349 | 381.5182 | 230.0381 | 70.3752 | 70.3752 | 70.3752 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 11 | 1571 | 6.2 | 6.2 | 2.0583 | 2.7521 | 15 | 80 | 80 | 39.8704 | 180.3355 | 27.7174 | 148.4963 | 0 | 1.0804 | 26.9095 | 36.9754 | 25.3816 | 0 | 0 | 0 | 16.6645 | 82.7875 | 85.4314 | 148.6375 | 173.2696 | 144.8985 | 82.7875 | 82.7875 | 82.7875 | 180.3355 | 82.7875 | 86.5118 | 175.547 | 210.245 | 170.28 | 82.7875 | 82.7875 | 82.7875 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 12 | 1572 | 6.9 | 6.9 | 2.0583 | 2.7521 | 15 | 74 | 74 | 234.5289 | 226.2459 | 31.3465 | 165.1601 | 0 | 0 | 108.4912 | 201.8839 | 177.0157 | 48.4542 | 0 | 0 | 115.7541 | 111.8724 | 111.8724 | 176.8849 | 232.8498 | 217.9478 | 140.9082 | 111.8724 | 111.8724 | 226.2459 | 111.8724 | 111.8724 | 285.376 | 434.7337 | 394.9635 | 189.3624 | 111.8724 | 111.8724 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 13 | 1573 | 7.6 | 7.6 | 2.0583 | 2.7521 | 15 | 69 | 69 | 119.2102 | 250.7797 | 32.3211 | 182.715 | 0 | 0 | 26.0754 | 88.0274 | 98.4141 | 51.1512 | 0 | 0 | 63.2203 | 116.9862 | 116.9862 | 141.3962 | 199.3911 | 209.1144 | 164.8703 | 116.9862 | 116.9862 | 250.7797 | 116.9862 | 116.9862 | 167.4716 | 287.4185 | 307.5285 | 216.0214 | 116.9862 | 116.9862 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 14 | 1574 | 7.5 | 7.5 | 2.0583 | 2.7521 | 15 | 71 | 71 | 4.8608 | 141.4445 | 30.4964 | 200.0961 | 0 | 0 | 0 | 2.7638 | 4.1031 | 3.0389 | 0.19457 | 0 | 2.5555 | 70.8474 | 70.8474 | 70.8474 | 71.4527 | 71.746 | 71.513 | 70.89 | 70.8474 | 141.4445 | 70.8474 | 70.8474 | 70.8474 | 74.2164 | 75.8491 | 74.5519 | 71.0846 | 70.8474 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 15 | 1575 | 8.6 | 8.6 | 2.0583 | 2.7521 | 15 | 64 | 64 | 435.554 | 182.883 | 26.1372 | 216.3355 | 0 | 0 | 0 | 158.0376 | 352.4508 | 340.403 | 128.9518 | 0 | 209.117 | 103.9484 | 103.9484 | 103.9484 | 156.1889 | 220.4535 | 216.4711 | 146.5743 | 103.9484 | 182.883 | 103.9484 | 103.9484 | 103.9484 | 314.2265 | 572.9043 | 556.8741 | 275.5261 | 103.9484 | 392 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 16 | 1576 | 5.7 | 5.7 | 2.0583 | 2.7521 | 15 | 80 | 80 | 60.0125 | 179.1998 | 19.776 | 231.0214 | 0 | 0 | 0 | 8.1163 | 43.4002 | 53.2608 | 31.922 | 0 | 23.8002 | 84.6388 | 84.6388 | 84.6388 | 94.9212 | 139.6219 | 152.1142 | 125.0804 | 84.6388 | 179.1998 | 84.6388 | 84.6388 | 84.6388 | 103.0375 | 183.022 | 205.375 | 157.0024 | 84.6388 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 17 | 1577 | 5.4 | 5.4 | 2.0583 | 2.7521 | 15 | 86 | 86 | 10.2048 | 97.1338 | 12 | 244.2869 | 0 | 0 | 0 | 0 | 6.0405 | 9.55 | 7.4651 | 1.0073 | 2.8662 | 47.8807 | 47.8807 | 47.8807 | 47.8807 | 51.1859 | 53.1062 | 51.9654 | 48.4319 | 97.1338 | 47.8807 | 47.8807 | 47.8807 | 47.8807 | 57.2265 | 62.6562 | 59.4306 | 49.4392 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 7 | 18 | 1578 | 4.5 | 4.5 | 2.0583 | 2.7521 | 15 | 87 | 87 | 3.5566 | 32.4991 | 3.3316 | 256.5644 | 0 | 0 | 0 | 0 | 1.5093 | 3.2836 | 3.1344 | 1.1491 | 0.50095 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 32.4991 | 15.6523 | 15.6523 | 15.6523 | 15.6523 | 17.1616 | 18.9359 | 18.7866 | 16.8013 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 19 | 1579 | 4.1 | 4.1 | 2.0583 | 2.7521 | 15 | 87 | 87 | 0 | 3 | -5.7876 | 268.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 3 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 1.3888 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 20 | 1580 | 3.2 | 3.2 | 2.0583 | 2.7521 | 15 | 81 | 81 | 0 | 0 | -14.9585 | 280.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 21 | 1581 | 3 | 3 | 2.0583 | 2.7521 | 15 | 78 | 78 | 0 | 0 | -23.7661 | 293.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 22 | 1582 | 1.8 | 1.8 | 2.0583 | 2.7521 | 15 | 81 | 81 | 0 | 0 | -31.7101 | 307.4996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 23 | 1583 | 1 | 1 | 2.0583 | 2.7521 | 15 | 83 | 83 | 0 | 0 | -38.1421 | 323.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 7 | 24 | 1584 | -0.1 | -0.1 | 4.1333 | 3.3359 | 15 | 85 | 85 | 0 | 0 | -42.2769 | 342.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 1 | 1585 | -1.5 | -1.5 | 4.1333 | 3.3359 | 15 | 92 | 92 | 0 | 0 | -43.4063 | 3.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 2 | 1586 | -2.2 | -2.2 | 4.1333 | 3.3359 | 15 | 93 | 93 | 0 | 0 | -40.9057 | 23.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 3 | 1587 | -1.9 | -1.9 | 4.1333 | 3.3359 | 15 | 92 | 92 | 0 | 0 | -35.9908 | 41.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 4 | 1588 | -2.3 | -2.3 | 4.1333 | 3.3359 | 15 | 90 | 90 | 0 | 0 | -29.0308 | 56.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 5 | 1589 | -2.5 | -2.5 | 4.1333 | 3.3359 | 15 | 90 | 90 | 0 | 0 | -20.773 | 70.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 6 | 1590 | -3.3 | -3.3 | 4.1333 | 3.3359 | 15 | 93 | 93 | 0 | 0 | -11.8127 | 83.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 7 | 1591 | -3.7 | -3.7 | 4.1333 | 3.3359 | 15 | 94 | 94 | 0 | 0 | -2.616 | 95.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 8 | 8 | 1592 | -2.6 | -2.6 | 4.1333 | 3.3359 | 15 | 95 | 95 | 167.0363 | 9.5059 | 6.4138 | 106.9537 | 0 | 107.1819 | 166.2187 | 127.8868 | 14.6406 | 0 | 0 | 0 | 12.4941 | 5.945 | 7.8531 | 8.9041 | 8.2217 | 6.2056 | 5.945 | 5.945 | 5.945 | 9.5059 | 5.945 | 115.035 | 175.1227 | 136.1085 | 20.8462 | 5.945 | 5.945 | 5.945 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 9 | 1593 | 0.8 | 0.8 | 4.1333 | 3.3359 | 15 | 92 | 92 | 366.5885 | 73.4649 | 14.8692 | 119.4985 | 0 | 171.2856 | 348.4621 | 321.5143 | 106.2277 | 0 | 0 | 0 | 65.5351 | 41.1459 | 67.1782 | 94.1059 | 90.0103 | 57.2906 | 41.1459 | 41.1459 | 41.1459 | 73.4649 | 41.1459 | 238.4638 | 442.568 | 411.5246 | 163.5184 | 41.1459 | 41.1459 | 41.1459 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 10 | 1594 | 3.2 | 3.2 | 4.1333 | 3.3359 | 15 | 80 | 80 | 634.8469 | 89.4689 | 22.284 | 133.1964 | 0 | 163.9899 | 534.0482 | 591.2684 | 302.1315 | 0 | 0 | 0 | 199.5311 | 63.263 | 87.9305 | 143.595 | 152.2021 | 108.7099 | 63.263 | 63.263 | 63.263 | 89.4689 | 63.263 | 251.9204 | 677.6433 | 743.4705 | 410.8414 | 63.263 | 63.263 | 63.263 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 11 | 1595 | 4.8 | 4.8 | 4.1333 | 3.3359 | 15 | 74 | 74 | 441.0332 | 160.1715 | 28.1063 | 148.4197 | 0 | 12.844 | 297.5058 | 407.8927 | 279.3416 | 0 | 0 | 0 | 186.8285 | 93.1575 | 96.9356 | 180.6695 | 213.1401 | 175.3265 | 93.1575 | 93.1575 | 93.1575 | 160.1715 | 93.1575 | 109.7796 | 478.1753 | 621.0328 | 454.6681 | 93.1575 | 93.1575 | 93.1575 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 12 | 1596 | 5.7 | 5.7 | 4.1333 | 3.3359 | 15 | 67 | 67 | 208.3592 | 231.9746 | 31.7412 | 165.159 | 0 | 0 | 96.2488 | 178.7703 | 156.5705 | 42.6539 | 0 | 0 | 104.0254 | 112.8412 | 112.8412 | 179.28 | 236.2431 | 220.919 | 142.2844 | 112.8412 | 112.8412 | 231.9746 | 112.8412 | 112.8412 | 275.5288 | 415.0133 | 377.4896 | 184.9384 | 112.8412 | 112.8412 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 13 | 1597 | 5.9 | 5.9 | 4.1333 | 3.3359 | 15 | 64 | 64 | 208.9353 | 249.0001 | 32.7091 | 182.8015 | 0 | 0 | 45.512 | 153.633 | 171.758 | 89.2694 | 0 | 0 | 111.9999 | 120.7387 | 120.7387 | 152.0744 | 226.5175 | 238.9968 | 182.2021 | 120.7387 | 120.7387 | 249.0001 | 120.7387 | 120.7387 | 197.5864 | 380.1506 | 410.7548 | 271.4715 | 120.7387 | 120.7387 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 14 | 1598 | 6.7 | 6.7 | 4.1333 | 3.3359 | 15 | 65 | 65 | 176.8 | 250.0376 | 30.8643 | 200.2624 | 0 | 0 | 0 | 99.9249 | 148.5861 | 110.2076 | 7.271 | 0 | 93.9624 | 119.5367 | 119.5367 | 119.5367 | 199.5121 | 238.4584 | 207.742 | 125.3561 | 119.5367 | 250.0376 | 119.5367 | 119.5367 | 119.5367 | 299.437 | 387.0446 | 317.9496 | 132.6271 | 119.5367 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 15 | 1599 | 6.7 | 6.7 | 4.1333 | 3.3359 | 15 | 65 | 65 | 182.9915 | 228.1013 | 26.4775 | 216.5587 | 0 | 0 | 0 | 65.7309 | 147.3565 | 142.6627 | 54.399 | 0 | 88.8987 | 110.7373 | 110.7373 | 110.7373 | 157.5978 | 215.79 | 212.4437 | 149.5192 | 110.7373 | 228.1013 | 110.7373 | 110.7373 | 110.7373 | 223.3287 | 363.1466 | 355.1065 | 203.9182 | 110.7373 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 16 | 1600 | 6.8 | 6.8 | 4.1333 | 3.3359 | 15 | 66 | 66 | 290.4105 | 177.1901 | 20.0885 | 231.278 | 0 | 0 | 0 | 38.1595 | 208.8034 | 257.1331 | 154.8377 | 0 | 116.8099 | 93.7024 | 93.7024 | 93.7024 | 111.5359 | 191.2851 | 213.8716 | 166.0646 | 93.7024 | 177.1901 | 93.7024 | 93.7024 | 93.7024 | 149.6955 | 400.0885 | 471.0047 | 320.9023 | 93.7024 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 17 | 1601 | 6.3 | 6.3 | 4.1333 | 3.3359 | 15 | 70 | 70 | 27.0914 | 117.2403 | 12.2898 | 244.5611 | 0 | 0 | 0 | 0 | 15.9158 | 25.2906 | 19.8505 | 2.7823 | 7.7597 | 56.5682 | 56.5682 | 56.5682 | 56.5682 | 85.3023 | 102.2273 | 92.4059 | 61.5913 | 117.2403 | 56.5682 | 56.5682 | 56.5682 | 56.5682 | 101.2181 | 127.518 | 112.2565 | 64.3736 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 8 | 18 | 1602 | 5.7 | 5.7 | 4.1333 | 3.3359 | 15 | 71 | 71 | 34.5411 | 61.9459 | 3.6065 | 256.8481 | 0 | 0 | 0 | 0 | 14.4971 | 31.8017 | 30.4773 | 11.2997 | 5.0541 | 30.9861 | 30.9861 | 30.9861 | 30.9861 | 43.0876 | 57.5327 | 56.4271 | 40.4186 | 61.9459 | 30.9861 | 30.9861 | 30.9861 | 30.9861 | 57.5847 | 89.3343 | 86.9044 | 51.7184 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 19 | 1603 | 5.4 | 5.4 | 4.1333 | 3.3359 | 15 | 72 | 72 | 0 | 3 | -5.5185 | 268.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 3 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 1.3881 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 20 | 1604 | 5.1 | 5.1 | 4.1333 | 3.3359 | 15 | 78 | 78 | 0 | 0 | -14.6857 | 280.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 21 | 1605 | 4.7 | 4.7 | 4.1333 | 3.3359 | 15 | 77 | 77 | 0 | 0 | -23.4796 | 293.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 22 | 1606 | 4.3 | 4.3 | 4.1333 | 3.3359 | 15 | 80 | 80 | 0 | 0 | -31.3998 | 307.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 23 | 1607 | 4.1 | 4.1 | 4.1333 | 3.3359 | 15 | 80 | 80 | 0 | 0 | -37.8008 | 324.2237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 8 | 24 | 1608 | 3.7 | 3.7 | 2.4958 | 3.2501 | 15 | 83 | 83 | 0 | 0 | -41.9046 | 342.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 1 | 1609 | 3 | 3 | 2.4958 | 3.2501 | 15 | 83 | 83 | 0 | 0 | -43.0145 | 3.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 2 | 1610 | 1.4 | 1.4 | 2.4958 | 3.2501 | 15 | 79 | 79 | 0 | 0 | -40.5109 | 23.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 3 | 1611 | 0 | 0 | 2.4958 | 3.2501 | 15 | 83 | 83 | 0 | 0 | -35.6077 | 41.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 4 | 1612 | 0.9 | 0.9 | 2.4958 | 3.2501 | 15 | 79 | 79 | 0 | 0 | -28.6632 | 56.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 5 | 1613 | 1 | 1 | 2.4958 | 3.2501 | 15 | 77 | 77 | 0 | 0 | -20.418 | 70.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 6 | 1614 | 1.2 | 1.2 | 2.4958 | 3.2501 | 15 | 74 | 74 | 0 | 0 | -11.4647 | 82.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 7 | 1615 | 0.4 | 0.4 | 2.4958 | 3.2501 | 15 | 78 | 78 | 0 | 0 | -2.2685 | 94.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 9 | 8 | 1616 | 0.3 | 0.3 | 2.4958 | 3.2501 | 15 | 80 | 80 | 117.5576 | 10.0741 | 6.7668 | 106.7728 | 0 | 75.7514 | 117.0461 | 89.7768 | 9.9174 | 0 | 0 | 0 | 17.9259 | 6.7634 | 8.792 | 9.8979 | 9.1676 | 7.029 | 6.7634 | 6.7634 | 6.7634 | 10.0741 | 6.7634 | 84.5434 | 126.9439 | 98.9443 | 16.9464 | 6.7634 | 6.7634 | 6.7634 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 9 | 1617 | 1.2 | 1.2 | 2.4958 | 3.2501 | 15 | 79 | 79 | 462.421 | 67.7902 | 15.233 | 119.3363 | 0 | 217.1871 | 439.6637 | 404.5914 | 132.5149 | 0 | 0 | 0 | 85.2098 | 41.2827 | 75.2878 | 110.121 | 104.6297 | 62.0306 | 41.2827 | 41.2827 | 41.2827 | 67.7902 | 41.2827 | 292.4748 | 549.7848 | 509.2211 | 194.5455 | 41.2827 | 41.2827 | 41.2827 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 10 | 1618 | 2.3 | 2.3 | 2.4958 | 3.2501 | 15 | 72 | 72 | 841.447 | 61.8394 | 22.6617 | 133.0671 | 0 | 219.201 | 707.7664 | 781.7318 | 397.7693 | 0 | 0 | 0 | 269.1606 | 60.243 | 77.8177 | 116.9888 | 122.9191 | 92.1345 | 60.243 | 60.243 | 60.243 | 61.8394 | 60.243 | 297.0187 | 824.7552 | 904.6509 | 489.9039 | 60.243 | 60.243 | 60.243 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 11 | 1619 | 2.6 | 2.6 | 2.4958 | 3.2501 | 15 | 65 | 65 | 509.353 | 148.3539 | 28.4969 | 148.3441 | 0 | 15.8533 | 343.3814 | 469.7613 | 320.9615 | 0 | 0 | 0 | 218.6461 | 91.6686 | 95.6097 | 177.0323 | 208.45 | 171.4588 | 91.6686 | 91.6686 | 91.6686 | 148.3539 | 91.6686 | 111.463 | 520.4137 | 678.2113 | 492.4202 | 91.6686 | 91.6686 | 91.6686 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 12 | 1620 | 3.5 | 3.5 | 2.4958 | 3.2501 | 15 | 62 | 62 | 622.6273 | 146.6025 | 32.1374 | 165.1598 | 0 | 0 | 287.1753 | 532.4184 | 465.778 | 126.2911 | 0 | 0 | 314.3975 | 98.8585 | 98.8585 | 153.3519 | 199.8884 | 187.2429 | 122.8231 | 98.8585 | 98.8585 | 146.6025 | 98.8585 | 98.8585 | 440.5272 | 732.3068 | 653.0209 | 249.1142 | 98.8585 | 98.8585 | 461 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 13 | 1621 | 3.8 | 3.8 | 2.4958 | 3.2501 | 15 | 59 | 59 | 214.4303 | 250.8288 | 33.098 | 182.8911 | 0 | 0 | 46.5054 | 156.994 | 175.5177 | 91.2254 | 0 | 0 | 116.1712 | 121.8895 | 121.8895 | 153.1158 | 227.3039 | 239.7417 | 183.1432 | 121.8895 | 121.8895 | 250.8288 | 121.8895 | 121.8895 | 199.6212 | 384.2979 | 415.2593 | 274.3687 | 121.8895 | 121.8895 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 14 | 1622 | 3.6 | 3.6 | 2.4958 | 3.2501 | 15 | 61 | 61 | 8.2376 | 176.575 | 31.2327 | 200.4324 | 0 | 0 | 0 | 4.6274 | 6.8922 | 5.1196 | 0.34807 | 0 | 4.425 | 85.8876 | 85.8876 | 85.8876 | 95.0055 | 99.468 | 95.9754 | 86.5735 | 85.8876 | 176.575 | 85.8876 | 85.8876 | 85.8876 | 99.6328 | 106.3602 | 101.095 | 86.9216 | 85.8876 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 15 | 1623 | 3.6 | 3.6 | 2.4958 | 3.2501 | 15 | 61 | 61 | 11.0169 | 172.5853 | 26.8178 | 216.7857 | 0 | 0 | 0 | 3.9166 | 8.8275 | 8.5674 | 3.2886 | 0 | 5.4147 | 83.5434 | 83.5434 | 83.5434 | 90.3279 | 98.835 | 98.3844 | 89.2401 | 83.5434 | 172.5853 | 83.5434 | 83.5434 | 83.5434 | 94.2445 | 107.6625 | 106.9518 | 92.5287 | 83.5434 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 16 | 1624 | 3.5 | 3.5 | 2.4958 | 3.2501 | 15 | 63 | 63 | 7.0195 | 128.1371 | 20.4007 | 231.538 | 0 | 0 | 0 | 0.89505 | 5.0171 | 6.2002 | 3.7513 | 0 | 2.8629 | 63.3904 | 63.3904 | 63.3904 | 64.0648 | 67.1712 | 68.0627 | 66.2173 | 63.3904 | 128.1371 | 63.3904 | 63.3904 | 63.3904 | 64.9599 | 72.1883 | 74.263 | 69.9686 | 63.3904 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 17 | 1625 | 3.4 | 3.4 | 2.4958 | 3.2501 | 15 | 62 | 62 | 1.9018 | 49.4447 | 12.5792 | 244.8381 | 0 | 0 | 0 | 0 | 1.1087 | 1.771 | 1.3958 | 0.20296 | 0.55532 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 49.4447 | 23.8495 | 23.8495 | 23.8495 | 23.8495 | 24.9583 | 25.6205 | 25.2453 | 24.0525 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 9 | 18 | 1626 | 3.3 | 3.3 | 2.4958 | 3.2501 | 15 | 62 | 62 | 3.6478 | 35.4463 | 3.8811 | 257.1343 | 0 | 0 | 0 | 0 | 1.5137 | 3.349 | 3.2224 | 1.2082 | 0.55374 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 35.4463 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 18.6239 | 20.4591 | 20.3326 | 18.3184 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 19 | 1627 | 3 | 3 | 2.4958 | 3.2501 | 15 | 65 | 65 | 0 | 3 | -5.2496 | 268.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 3 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 20 | 1628 | 2.5 | 2.5 | 2.4958 | 3.2501 | 15 | 72 | 72 | 0 | 0 | -14.4129 | 280.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 21 | 1629 | 2.3 | 2.3 | 2.4958 | 3.2501 | 15 | 78 | 78 | 0 | 0 | -23.1926 | 293.7827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 22 | 1630 | 2 | 2 | 2.4958 | 3.2501 | 15 | 75 | 75 | 0 | 0 | -31.0889 | 308.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 23 | 1631 | 1.5 | 1.5 | 2.4958 | 3.2501 | 15 | 78 | 78 | 0 | 0 | -37.4586 | 324.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 9 | 24 | 1632 | 1.2 | 1.2 | 2.1458 | 2.9396 | 15 | 82 | 82 | 0 | 0 | -41.5313 | 343.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 1 | 1633 | 0.9 | 0.9 | 2.1458 | 2.9396 | 15 | 83 | 83 | 0 | 0 | -42.6214 | 3.2919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 2 | 1634 | 0.8 | 0.8 | 2.1458 | 2.9396 | 15 | 83 | 83 | 0 | 0 | -40.1147 | 23.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 3 | 1635 | 0.6 | 0.6 | 2.1458 | 2.9396 | 15 | 83 | 83 | 0 | 0 | -35.2228 | 40.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 4 | 1636 | 0.3 | 0.3 | 2.1458 | 2.9396 | 15 | 85 | 85 | 0 | 0 | -28.2936 | 56.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 5 | 1637 | 0.2 | 0.2 | 2.1458 | 2.9396 | 15 | 86 | 86 | 0 | 0 | -20.061 | 70.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 6 | 1638 | -0.1 | -0.1 | 2.1458 | 2.9396 | 15 | 84 | 84 | 0 | 0 | -11.1147 | 82.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 7 | 1639 | -0.2 | -0.2 | 2.1458 | 2.9396 | 15 | 84 | 84 | 0 | 0 | -1.9191 | 94.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 10 | 8 | 1640 | 0.1 | 0.1 | 2.1458 | 2.9396 | 15 | 86 | 86 | 1.698 | 5.937 | 7.1217 | 106.5925 | 0 | 1.0987 | 1.6915 | 1.2934 | 0.13768 | 0 | 0 | 0 | 0.062983 | 2.6417 | 4.391 | 5.3348 | 4.7011 | 2.8609 | 2.6417 | 2.6417 | 2.6417 | 5.937 | 2.6417 | 5.4897 | 7.0263 | 5.9945 | 2.9986 | 2.6417 | 2.6417 | 2.6417 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 9 | 1641 | 0.8 | 0.8 | 2.1458 | 2.9396 | 15 | 82 | 82 | 5.0615 | 52.0395 | 15.5986 | 119.1745 | 0 | 2.3894 | 4.8133 | 4.4177 | 1.4342 | 0 | 0 | 0 | 0.96054 | 23.8185 | 45.5644 | 67.6249 | 64.0242 | 36.8715 | 23.8185 | 23.8185 | 23.8185 | 52.0395 | 23.8185 | 47.9537 | 72.4382 | 68.4418 | 38.3058 | 23.8185 | 23.8185 | 23.8185 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 10 | 1642 | 0.8 | 0.8 | 2.1458 | 2.9396 | 15 | 86 | 86 | 3.1759 | 70.9664 | 23.0411 | 132.9384 | 0 | 0.83421 | 2.6709 | 2.943 | 1.4912 | 0 | 0 | 0 | 1.0336 | 35.2287 | 35.2724 | 35.3686 | 35.3828 | 35.3068 | 35.2287 | 35.2287 | 35.2287 | 70.9664 | 35.2287 | 36.1066 | 38.0395 | 38.3259 | 36.7979 | 35.2287 | 35.2287 | 35.2287 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 11 | 1643 | 1.4 | 1.4 | 2.1458 | 2.9396 | 15 | 84 | 84 | 1.7786 | 71.2265 | 28.8889 | 148.2695 | 0 | 0.058879 | 1.1982 | 1.6356 | 1.1149 | 0 | 0 | 0 | 0.77352 | 34.7875 | 34.7875 | 34.7875 | 34.7875 | 34.7875 | 34.7875 | 34.7875 | 34.7875 | 71.2265 | 34.7875 | 34.8464 | 35.9857 | 36.4231 | 35.9024 | 34.7875 | 34.7875 | 34.7875 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 12 | 1644 | 1.6 | 1.6 | 2.1458 | 2.9396 | 15 | 88 | 88 | 3.0663 | 109.4342 | 32.5348 | 165.1626 | 0 | 0 | 1.412 | 2.6131 | 2.2835 | 0.61624 | 0 | 0 | 1.5658 | 54.3334 | 54.3334 | 54.3334 | 54.3334 | 54.3334 | 54.3334 | 54.3334 | 54.3334 | 109.4342 | 54.3334 | 54.3334 | 55.7454 | 56.9465 | 56.6169 | 54.9496 | 54.3334 | 54.3334 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 13 | 1645 | 1.9 | 1.9 | 2.1458 | 2.9396 | 15 | 86 | 86 | 1.715 | 88.0611 | 33.4879 | 182.9837 | 0 | 0 | 0.37024 | 1.2501 | 1.3976 | 0.72646 | 0 | 0 | 0.93889 | 43.0814 | 43.0814 | 43.0814 | 43.0814 | 43.0814 | 43.0814 | 43.0814 | 43.0814 | 88.0611 | 43.0814 | 43.0814 | 43.4517 | 44.3315 | 44.4791 | 43.8079 | 43.0814 | 43.0814 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 14 | 1646 | 2.2 | 2.2 | 2.1458 | 2.9396 | 15 | 85 | 85 | 1.0483 | 68.4309 | 31.6015 | 200.6061 | 0 | 0 | 0 | 0.58521 | 0.87311 | 0.64956 | 0.045509 | 0 | 0.56911 | 33.1315 | 33.1315 | 33.1315 | 33.1315 | 33.1315 | 33.1315 | 33.1315 | 33.1315 | 68.4309 | 33.1315 | 33.1315 | 33.1315 | 33.7167 | 34.0046 | 33.7811 | 33.177 | 33.1315 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 15 | 1647 | 2.3 | 2.3 | 2.1458 | 2.9396 | 15 | 86 | 86 | 0.9769 | 60.5143 | 27.158 | 217.0163 | 0 | 0 | 0 | 0.34364 | 0.77881 | 0.75776 | 0.29283 | 0 | 0.48568 | 29.1918 | 29.1918 | 29.1918 | 29.1918 | 29.1918 | 29.1918 | 29.1918 | 29.1918 | 60.5143 | 29.1918 | 29.1918 | 29.1918 | 29.5355 | 29.9706 | 29.9496 | 29.4847 | 29.1918 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 16 | 1648 | 2.2 | 2.2 | 2.1458 | 2.9396 | 15 | 86 | 86 | 0.66954 | 41.7232 | 20.7125 | 231.8012 | 0 | 0 | 0 | 0.082741 | 0.47566 | 0.58995 | 0.35865 | 0 | 0.27684 | 19.9293 | 19.9293 | 19.9293 | 19.9293 | 19.9293 | 19.9293 | 19.9293 | 19.9293 | 41.7232 | 19.9293 | 19.9293 | 19.9293 | 20.012 | 20.4049 | 20.5192 | 20.2879 | 19.9293 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 17 | 1649 | 2.4 | 2.4 | 2.1458 | 2.9396 | 15 | 84 | 84 | 0.26459 | 18.9213 | 12.8681 | 245.1179 | 0 | 0 | 0 | 0 | 0.15304 | 0.24575 | 0.19449 | 0.029309 | 0.07873 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 18.9213 | 8.8996 | 8.8996 | 8.8996 | 8.8996 | 9.0526 | 9.1453 | 9.0941 | 8.9289 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 18 | 1650 | 2.2 | 2.2 | 2.1458 | 2.9396 | 15 | 85 | 85 | 0.3174 | 10.9501 | 4.1554 | 257.4227 | 0 | 0 | 0 | 0 | 0.13019 | 0.29055 | 0.2807 | 0.10643 | 0.049922 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 10.9501 | 5.1156 | 5.1156 | 5.1156 | 5.1156 | 5.2458 | 5.4061 | 5.3963 | 5.222 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 19 | 1651 | 2.2 | 2.2 | 2.1458 | 2.9396 | 15 | 85 | 85 | 0 | 0 | -4.9809 | 269.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 20 | 1652 | 2.1 | 2.1 | 2.1458 | 2.9396 | 15 | 87 | 87 | 0 | 0 | -14.1399 | 281.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 21 | 1653 | 2 | 2 | 2.1458 | 2.9396 | 15 | 88 | 88 | 0 | 0 | -22.9053 | 294.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 22 | 1654 | 1.8 | 1.8 | 2.1458 | 2.9396 | 15 | 87 | 87 | 0 | 0 | -30.7773 | 308.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 23 | 1655 | 1.7 | 1.7 | 2.1458 | 2.9396 | 15 | 88 | 88 | 0 | 0 | -37.1156 | 324.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 10 | 24 | 1656 | 1.5 | 1.5 | 1.3208 | 2.5492 | 15 | 90 | 90 | 0 | 0 | -41.157 | 343.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 1 | 1657 | 1.4 | 1.4 | 1.3208 | 2.5492 | 15 | 90 | 90 | 0 | 0 | -42.2272 | 3.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 2 | 1658 | 1.1 | 1.1 | 1.3208 | 2.5492 | 15 | 92 | 92 | 0 | 0 | -39.7172 | 23.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 3 | 1659 | 0.9 | 0.9 | 1.3208 | 2.5492 | 15 | 92 | 92 | 0 | 0 | -34.8363 | 40.8552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 4 | 1660 | 1 | 1 | 1.3208 | 2.5492 | 15 | 92 | 92 | 0 | 0 | -27.9222 | 56.4322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 5 | 1661 | 0.9 | 0.9 | 1.3208 | 2.5492 | 15 | 92 | 92 | 0 | 0 | -19.702 | 70.1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 6 | 1662 | 0.9 | 0.9 | 1.3208 | 2.5492 | 15 | 92 | 92 | 0 | 0 | -10.7628 | 82.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 7 | 1663 | 0.7 | 0.7 | 1.3208 | 2.5492 | 15 | 88 | 88 | 0 | 0 | -1.568 | 94.4648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 11 | 8 | 1664 | 0.8 | 0.8 | 1.3208 | 2.5492 | 15 | 86 | 86 | 7.6147 | 13.6762 | 7.4783 | 106.4128 | 0 | 4.9471 | 7.5887 | 5.7851 | 0.59256 | 0 | 0 | 0 | 0.3238 | 5.0639 | 12.7249 | 16.8159 | 14.0227 | 5.9815 | 5.0639 | 5.0639 | 5.0639 | 13.6762 | 5.0639 | 17.672 | 24.4046 | 19.8077 | 6.5741 | 5.0639 | 5.0639 | 5.0639 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 9 | 1665 | 1 | 1 | 1.3208 | 2.5492 | 15 | 86 | 86 | 8.8411 | 65.2735 | 15.9658 | 119.0131 | 0 | 4.1944 | 8.4087 | 7.6973 | 2.4769 | 0 | 0 | 0 | 1.7265 | 28.5639 | 69.6446 | 110.9193 | 103.9514 | 52.8224 | 28.5639 | 28.5639 | 28.5639 | 65.2735 | 28.5639 | 73.839 | 119.328 | 111.6486 | 55.2993 | 28.5639 | 28.5639 | 28.5639 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 10 | 1666 | 1.4 | 1.4 | 1.3208 | 2.5492 | 15 | 85 | 85 | 14.9437 | 123.0531 | 23.4219 | 132.8101 | 0 | 3.957 | 12.5643 | 13.8116 | 6.9682 | 0 | 0 | 0 | 4.9469 | 55.5607 | 72.511 | 109.3814 | 114.7244 | 85.4101 | 55.5607 | 55.5607 | 55.5607 | 123.0531 | 55.5607 | 76.468 | 121.9457 | 128.536 | 92.3783 | 55.5607 | 55.5607 | 55.5607 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 11 | 1667 | 2.6 | 2.6 | 1.3208 | 2.5492 | 15 | 81 | 81 | 52.4107 | 195.9111 | 29.2823 | 148.1959 | 0 | 1.8377 | 35.2809 | 48.0571 | 32.6821 | 0 | 0 | 0 | 23.0889 | 89.8019 | 93.4424 | 159.6949 | 185.005 | 154.5464 | 89.8019 | 89.8019 | 89.8019 | 195.9111 | 89.8019 | 95.2801 | 194.9758 | 233.0621 | 187.2285 | 89.8019 | 89.8019 | 89.8019 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 12 | 1668 | 3.5 | 3.5 | 1.3208 | 2.5492 | 15 | 75 | 75 | 110.2241 | 243.09 | 32.9334 | 165.1672 | 0 | 0 | 50.6672 | 93.6011 | 81.7048 | 21.9469 | 0 | 0 | 56.91 | 112.7565 | 112.7565 | 165.5072 | 210.2066 | 197.8211 | 135.6059 | 112.7565 | 112.7565 | 243.09 | 112.7565 | 112.7565 | 216.1744 | 303.8077 | 279.5259 | 157.5527 | 112.7565 | 112.7565 | 300 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 13 | 1669 | 4.5 | 4.5 | 1.3208 | 2.5492 | 15 | 69 | 69 | 422.3622 | 213.3635 | 33.8785 | 183.0792 | 0 | 0 | 90.7488 | 306.4784 | 342.6771 | 178.1402 | 0 | 0 | 233.6365 | 117.6121 | 117.6121 | 151.4056 | 231.7402 | 245.22 | 183.9489 | 117.6121 | 117.6121 | 213.3635 | 117.6121 | 117.6121 | 242.1544 | 538.2186 | 587.8971 | 362.089 | 117.6121 | 117.6121 | 447 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 14 | 1670 | 5.1 | 5.1 | 1.3208 | 2.5492 | 15 | 62 | 62 | 130.7392 | 259.2805 | 31.9706 | 200.7833 | 0 | 0 | 0 | 72.5175 | 108.3857 | 80.7631 | 5.8305 | 0 | 71.7195 | 120.7975 | 120.7975 | 120.7975 | 201.2302 | 241.0134 | 210.3757 | 127.2644 | 120.7975 | 259.2805 | 120.7975 | 120.7975 | 120.7975 | 273.7477 | 349.3991 | 291.1388 | 133.0949 | 120.7975 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 15 | 1671 | 5.3 | 5.3 | 1.3208 | 2.5492 | 15 | 56 | 56 | 72.2441 | 230.673 | 27.4981 | 217.2505 | 0 | 0 | 0 | 25.1389 | 57.2982 | 55.893 | 21.7465 | 0 | 36.327 | 107.0983 | 107.0983 | 107.0983 | 139.9186 | 181.9045 | 180.07 | 135.4896 | 107.0983 | 230.673 | 107.0983 | 107.0983 | 107.0983 | 165.0574 | 239.2027 | 235.963 | 157.2361 | 107.0983 | 267 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 16 | 1672 | 5.1 | 5.1 | 1.3208 | 2.5492 | 15 | 56 | 56 | 66.8716 | 190.9735 | 21.0238 | 232.0676 | 0 | 0 | 0 | 7.9985 | 47.216 | 58.7751 | 35.9045 | 0 | 28.0265 | 89.9733 | 89.9733 | 89.9733 | 99.5753 | 146.6554 | 160.5318 | 133.0761 | 89.9733 | 190.9735 | 89.9733 | 89.9733 | 89.9733 | 107.5738 | 193.8714 | 219.307 | 168.9806 | 89.9733 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 17 | 1673 | 4.7 | 4.7 | 1.3208 | 2.5492 | 15 | 60 | 60 | 8.5225 | 100.4167 | 13.1566 | 245.4003 | 0 | 0 | 0 | 0 | 4.8903 | 7.8947 | 6.2745 | 0.9788 | 2.5833 | 49.6628 | 49.6628 | 49.6628 | 49.6628 | 52.0085 | 53.4497 | 52.6725 | 50.1323 | 100.4167 | 49.6628 | 49.6628 | 49.6628 | 49.6628 | 56.8988 | 61.3443 | 58.947 | 51.1111 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 18 | 1674 | 3.9 | 3.9 | 1.3208 | 2.5492 | 15 | 62 | 62 | 29.1823 | 67.2498 | 4.4292 | 257.7132 | 0 | 0 | 0 | 0 | 11.829 | 26.634 | 25.8372 | 9.9053 | 4.7502 | 33.4503 | 33.4503 | 33.4503 | 33.4503 | 45.8826 | 61.4428 | 60.6053 | 43.8608 | 67.2498 | 33.4503 | 33.4503 | 33.4503 | 33.4503 | 57.7117 | 88.0768 | 86.4424 | 53.766 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 19 | 1675 | 1.7 | 1.7 | 1.3208 | 2.5492 | 15 | 71 | 71 | 27.231 | 1.434 | -4.7123 | 269.5724 | 0 | 0 | 0 | 0 | 5.7776 | 22.8433 | 26.5278 | 14.6726 | 6.566 | 1.6105 | 1.6105 | 1.6105 | 1.6105 | 2.9551 | 6.9267 | 7.7841 | 5.0251 | 1.434 | 1.6105 | 1.6105 | 1.6105 | 1.6105 | 8.7327 | 29.77 | 34.3119 | 19.6977 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 20 | 1676 | 0.6 | 0.6 | 1.3208 | 2.5492 | 15 | 78 | 78 | 0 | 0 | -13.8668 | 281.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 21 | 1677 | 0.8 | 0.8 | 1.3208 | 2.5492 | 15 | 78 | 78 | 0 | 0 | -22.6176 | 294.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 22 | 1678 | 1 | 1 | 1.3208 | 2.5492 | 15 | 82 | 82 | 0 | 0 | -30.4651 | 308.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 23 | 1679 | 1 | 1 | 1.3208 | 2.5492 | 15 | 84 | 84 | 0 | 0 | -36.7717 | 324.9804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 11 | 24 | 1680 | 1.6 | 1.6 | 2.1458 | 2.3315 | 15 | 84 | 84 | 0 | 0 | -40.7818 | 343.5155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 1 | 1681 | 0.9 | 0.9 | 2.1458 | 2.3315 | 15 | 86 | 86 | 0 | 0 | -41.832 | 3.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 2 | 1682 | 1 | 1 | 2.1458 | 2.3315 | 15 | 86 | 86 | 0 | 0 | -39.3185 | 23.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 3 | 1683 | 0.1 | 0.1 | 2.1458 | 2.3315 | 15 | 88 | 88 | 0 | 0 | -34.4483 | 40.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 4 | 1684 | 0.3 | 0.3 | 2.1458 | 2.3315 | 15 | 90 | 90 | 0 | 0 | -27.549 | 56.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 5 | 1685 | 0.9 | 0.9 | 2.1458 | 2.3315 | 15 | 88 | 88 | 0 | 0 | -19.3413 | 69.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 6 | 1686 | 0.4 | 0.4 | 2.1458 | 2.3315 | 15 | 89 | 89 | 0 | 0 | -10.4091 | 82.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 7 | 1687 | 0.2 | 0.2 | 2.1458 | 2.3315 | 15 | 89 | 89 | 0 | 0 | -1.2152 | 94.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 12 | 8 | 1688 | 0.8 | 0.8 | 2.1458 | 2.3315 | 15 | 85 | 85 | 10.0961 | 16.5158 | 7.8364 | 106.2336 | 0 | 6.5853 | 10.0658 | 7.6499 | 0.75277 | 0 | 0 | 0 | 0.48425 | 6.1174 | 15.3975 | 20.3022 | 16.8977 | 7.1782 | 6.1174 | 6.1174 | 6.1174 | 16.5158 | 6.1174 | 21.9828 | 30.368 | 24.5476 | 7.931 | 6.1174 | 6.1174 | 6.1174 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 9 | 1689 | 1.8 | 1.8 | 2.1458 | 2.3315 | 15 | 78 | 78 | 10.6074 | 69.8701 | 16.3343 | 118.8521 | 0 | 5.057 | 10.0894 | 9.2115 | 2.9377 | 0 | 0 | 0 | 2.1299 | 30.384 | 74.9459 | 119.2903 | 111.5546 | 56.2703 | 30.384 | 30.384 | 30.384 | 69.8701 | 30.384 | 80.003 | 129.3797 | 120.7661 | 59.208 | 30.384 | 30.384 | 30.384 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 10 | 1690 | 3.1 | 3.1 | 2.1458 | 2.3315 | 15 | 72 | 72 | 247.8652 | 152.5661 | 23.804 | 132.6823 | 0 | 66.1534 | 208.3346 | 228.4762 | 114.7796 | 0 | 0 | 0 | 83.4339 | 79.37 | 113.5238 | 186.9295 | 197.3282 | 138.6286 | 79.37 | 79.37 | 79.37 | 152.5661 | 79.37 | 179.6772 | 395.2641 | 425.8044 | 253.4082 | 79.37 | 79.37 | 79.37 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 11 | 1691 | 3.9 | 3.9 | 2.1458 | 2.3315 | 15 | 71 | 71 | 327.4539 | 189.9019 | 29.677 | 148.1232 | 0 | 12.1161 | 220.2417 | 299.3527 | 203.107 | 0 | 0 | 0 | 146.0981 | 101.6066 | 106.8961 | 197.7582 | 232.2959 | 190.2776 | 101.6066 | 101.6066 | 101.6066 | 189.9019 | 101.6066 | 119.0122 | 417.9999 | 531.6486 | 393.3846 | 101.6066 | 101.6066 | 101.6066 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 12 | 1692 | 4.7 | 4.7 | 2.1458 | 2.3315 | 15 | 67 | 67 | 105.0424 | 245.1706 | 33.3331 | 165.1737 | 0 | 0 | 48.1961 | 88.8806 | 77.5001 | 20.721 | 0 | 0 | 54.8294 | 113.4412 | 113.4412 | 166.0547 | 210.4682 | 198.0446 | 136.0614 | 113.4412 | 113.4412 | 245.1706 | 113.4412 | 113.4412 | 214.2508 | 299.3488 | 275.5447 | 156.7825 | 113.4412 | 113.4412 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 13 | 1693 | 5.9 | 5.9 | 2.1458 | 2.3315 | 15 | 62 | 62 | 101.7776 | 262.122 | 34.2698 | 183.1776 | 0 | 0 | 21.7594 | 73.5125 | 82.203 | 42.7401 | 0 | 0 | 56.878 | 121.0505 | 121.0505 | 145.1553 | 202.4866 | 212.1137 | 168.3973 | 121.0505 | 121.0505 | 262.122 | 121.0505 | 121.0505 | 166.9147 | 275.9991 | 294.3167 | 211.1374 | 121.0505 | 121.0505 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 14 | 1694 | 6.2 | 6.2 | 2.1458 | 2.3315 | 15 | 60 | 60 | 102.7101 | 260.0734 | 32.3399 | 200.9641 | 0 | 0 | 0 | 56.5994 | 84.7485 | 63.2531 | 4.7049 | 0 | 56.9266 | 120.6101 | 120.6101 | 120.6101 | 180.0802 | 209.657 | 187.0714 | 125.5536 | 120.6101 | 260.0734 | 120.6101 | 120.6101 | 120.6101 | 236.6796 | 294.4055 | 250.3245 | 130.2585 | 120.6101 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 15 | 1695 | 6.1 | 6.1 | 2.1458 | 2.3315 | 15 | 59 | 59 | 34.9571 | 215.2246 | 27.8378 | 217.4881 | 0 | 0 | 0 | 12.0299 | 27.5799 | 26.974 | 10.5671 | 0 | 17.7754 | 99.4698 | 99.4698 | 99.4698 | 127.894 | 164.6356 | 163.2039 | 124.4377 | 99.4698 | 215.2246 | 99.4698 | 99.4698 | 99.4698 | 139.9239 | 192.2154 | 190.1779 | 135.0048 | 99.4698 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 16 | 1696 | 6.1 | 6.1 | 2.1458 | 2.3315 | 15 | 61 | 61 | 6.9769 | 133.0367 | 21.3347 | 232.337 | 0 | 0 | 0 | 0.80654 | 4.8953 | 6.1165 | 3.7547 | 0 | 2.9633 | 65.8032 | 65.8032 | 65.8032 | 66.4557 | 69.7638 | 70.7518 | 68.841 | 65.8032 | 133.0367 | 65.8032 | 65.8032 | 65.8032 | 67.2623 | 74.6591 | 76.8683 | 72.5957 | 65.8032 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 17 | 1697 | 6.3 | 6.3 | 2.1458 | 2.3315 | 15 | 62 | 62 | 2.1381 | 55.34 | 13.4445 | 245.6852 | 0 | 0 | 0 | 0 | 1.2169 | 1.9752 | 1.5765 | 0.25433 | 0.65997 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 55.34 | 26.7897 | 26.7897 | 26.7897 | 26.7897 | 28.0065 | 28.7649 | 28.3662 | 27.044 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 12 | 18 | 1698 | 6.1 | 6.1 | 2.1458 | 2.3315 | 15 | 63 | 63 | 0.82819 | 18.8606 | 4.7027 | 258.0056 | 0 | 0 | 0 | 0 | 0.33166 | 0.75357 | 0.73404 | 0.28453 | 0.13936 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 18.8606 | 8.8978 | 8.8978 | 8.8978 | 8.8978 | 9.2294 | 9.6513 | 9.6318 | 9.1823 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 19 | 1699 | 4.1 | 4.1 | 2.1458 | 2.3315 | 15 | 85 | 85 | 3.4224 | 2.9553 | -4.444 | 269.8696 | 0 | 0 | 0 | 0 | 0.70883 | 2.8604 | 3.3364 | 1.858 | 0.044731 | 1.66 | 1.66 | 1.66 | 1.66 | 2.2369 | 3.9881 | 4.3755 | 3.1722 | 2.9553 | 1.66 | 1.66 | 1.66 | 1.66 | 2.9457 | 6.8485 | 7.7119 | 5.0302 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 20 | 1700 | 3.9 | 3.9 | 2.1458 | 2.3315 | 15 | 90 | 90 | 0 | 0 | -13.5937 | 281.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 21 | 1701 | 3.9 | 3.9 | 2.1458 | 2.3315 | 15 | 91 | 91 | 0 | 0 | -22.3295 | 294.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 22 | 1702 | 3.9 | 3.9 | 2.1458 | 2.3315 | 15 | 90 | 90 | 0 | 0 | -30.1523 | 308.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 23 | 1703 | 4 | 4 | 2.1458 | 2.3315 | 15 | 91 | 91 | 0 | 0 | -36.4272 | 325.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 12 | 24 | 1704 | 4.5 | 4.5 | 3.2958 | 2.5073 | 15 | 90 | 90 | 0 | 0 | -40.4058 | 343.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 1 | 1705 | 4.9 | 4.9 | 3.2958 | 2.5073 | 15 | 90 | 90 | 0 | 0 | -41.4359 | 3.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 2 | 1706 | 5.4 | 5.4 | 3.2958 | 2.5073 | 15 | 91 | 91 | 0 | 0 | -38.9188 | 22.9654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 3 | 1707 | 5.8 | 5.8 | 3.2958 | 2.5073 | 15 | 94 | 94 | 0 | 0 | -34.0589 | 40.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 4 | 1708 | 6.4 | 6.4 | 3.2958 | 2.5073 | 15 | 95 | 95 | 0 | 0 | -27.1742 | 56.1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 5 | 1709 | 6.7 | 6.7 | 3.2958 | 2.5073 | 15 | 96 | 96 | 0 | 0 | -18.979 | 69.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 6 | 1710 | 7.5 | 7.5 | 3.2958 | 2.5073 | 15 | 95 | 95 | 0 | 0 | -10.0539 | 82.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 7 | 1711 | 7.7 | 7.7 | 3.2958 | 2.5073 | 15 | 94 | 94 | 0 | 0 | -0.86085 | 94.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 13 | 8 | 1712 | 8.3 | 8.3 | 3.2958 | 2.5073 | 15 | 90 | 90 | 0.20504 | 2.989 | 8.1958 | 106.0549 | 0 | 0.13426 | 0.2045 | 0.15494 | 0.014622 | 0 | 0 | 0 | 0.010952 | 1.4074 | 1.8715 | 2.1143 | 1.943 | 1.4579 | 1.4074 | 1.4074 | 1.4074 | 2.989 | 1.4074 | 2.0058 | 2.3188 | 2.0979 | 1.4726 | 1.4074 | 1.4074 | 1.4074 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 9 | 1713 | 8.1 | 8.1 | 3.2958 | 2.5073 | 15 | 80 | 80 | 6.3925 | 62.6812 | 16.7042 | 118.6913 | 0 | 3.0622 | 6.0805 | 5.5369 | 1.7499 | 0 | 0 | 0 | 1.3188 | 28.331 | 55.4257 | 82.1315 | 77.3218 | 43.8139 | 28.331 | 28.331 | 28.331 | 62.6812 | 28.331 | 58.4879 | 88.212 | 82.8587 | 45.5638 | 28.331 | 28.331 | 28.331 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 10 | 1714 | 8.5 | 8.5 | 3.2958 | 2.5073 | 15 | 76 | 76 | 5.223 | 95.2128 | 24.1874 | 132.5548 | 0 | 1.4048 | 4.3884 | 4.8014 | 2.4017 | 0 | 0 | 0 | 1.7872 | 45.6532 | 50.4304 | 60.5764 | 61.9806 | 53.8205 | 45.6532 | 45.6532 | 45.6532 | 95.2128 | 45.6532 | 51.8352 | 64.9648 | 66.782 | 56.2222 | 45.6532 | 45.6532 | 45.6532 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 11 | 1715 | 8.7 | 8.7 | 3.2958 | 2.5073 | 15 | 73 | 73 | 2.3552 | 84.936 | 30.0727 | 148.0512 | 0 | 0.091662 | 1.5826 | 2.1465 | 1.453 | 0 | 0 | 0 | 1.064 | 41.8122 | 41.8122 | 41.8122 | 41.8122 | 41.8122 | 41.8122 | 41.8122 | 41.8122 | 84.936 | 41.8122 | 41.9039 | 43.3949 | 43.9587 | 43.2652 | 41.8122 | 41.8122 | 41.8122 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 12 | 1716 | 8.7 | 8.7 | 3.2958 | 2.5073 | 15 | 72 | 72 | 1.0481 | 66.447 | 33.7337 | 165.1818 | 0 | 0 | 0.47994 | 0.88356 | 0.7696 | 0.20482 | 0 | 0 | 0.55298 | 32.1709 | 32.1709 | 32.1709 | 32.1709 | 32.1709 | 32.1709 | 32.1709 | 32.1709 | 66.447 | 32.1709 | 32.1709 | 32.6509 | 33.0545 | 32.9405 | 32.3757 | 32.1709 | 32.1709 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 13 | 1717 | 9.4 | 9.4 | 3.2958 | 2.5073 | 15 | 72 | 72 | 1.919 | 95.9167 | 34.6617 | 183.2787 | 0 | 0 | 0.40817 | 1.3796 | 1.5429 | 0.80235 | 0 | 0 | 1.0833 | 47.0841 | 47.0841 | 47.0841 | 47.0841 | 47.0841 | 47.0841 | 47.0841 | 47.0841 | 95.9167 | 47.0841 | 47.0841 | 47.4922 | 48.4637 | 48.6269 | 47.8864 | 47.0841 | 47.0841 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 14 | 1718 | 9.6 | 9.6 | 3.2958 | 2.5073 | 15 | 70 | 70 | 7.1918 | 176.9733 | 32.7092 | 201.1482 | 0 | 0 | 0 | 3.9368 | 5.9058 | 4.4152 | 0.33832 | 0 | 4.0267 | 86.6462 | 86.6462 | 86.6462 | 93.7015 | 97.2303 | 94.559 | 87.2525 | 86.6462 | 176.9733 | 86.6462 | 86.6462 | 86.6462 | 97.6383 | 103.136 | 98.9742 | 87.5909 | 86.6462 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 15 | 1719 | 9.5 | 9.5 | 3.2958 | 2.5073 | 15 | 71 | 71 | 2.0812 | 90.93 | 28.1773 | 217.7292 | 0 | 0 | 0 | 0.70812 | 1.6332 | 1.6016 | 0.63178 | 0 | 1.07 | 44.5569 | 44.5569 | 44.5569 | 44.5569 | 44.5569 | 44.5569 | 44.5569 | 44.5569 | 90.93 | 44.5569 | 44.5569 | 44.5569 | 45.265 | 46.1901 | 46.1585 | 45.1887 | 44.5569 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 16 | 1720 | 9.3 | 9.3 | 3.2958 | 2.5073 | 15 | 75 | 75 | 6.0232 | 128.4081 | 21.645 | 232.6094 | 0 | 0 | 0 | 0.67195 | 4.1992 | 5.2667 | 3.249 | 0 | 2.5919 | 63.9272 | 63.9272 | 63.9272 | 64.2265 | 65.7975 | 66.2729 | 65.3742 | 63.9272 | 128.4081 | 63.9272 | 63.9272 | 63.9272 | 64.8984 | 69.9967 | 71.5396 | 68.6232 | 63.9272 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 17 | 1721 | 9.8 | 9.8 | 3.2958 | 2.5073 | 15 | 73 | 73 | 5.5713 | 90.2493 | 13.7319 | 245.9724 | 0 | 0 | 0 | 0 | 3.1446 | 5.1328 | 4.1143 | 0.68572 | 1.7507 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 90.2493 | 44.8479 | 44.8479 | 44.8479 | 44.8479 | 47.9925 | 49.9807 | 48.9623 | 45.5336 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 13 | 18 | 1722 | 9.9 | 9.9 | 3.2958 | 2.5073 | 15 | 71 | 71 | 4.7547 | 46.1738 | 4.9756 | 258.3 | 0 | 0 | 0 | 0 | 1.8807 | 4.3129 | 4.2186 | 1.6532 | 0.82624 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 46.1738 | 22.5092 | 22.5092 | 22.5092 | 22.5092 | 24.3899 | 26.8221 | 26.7278 | 24.1624 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 19 | 1723 | 8.3 | 8.3 | 3.2958 | 2.5073 | 15 | 74 | 74 | 25.815 | 5.2248 | -4.1759 | 270.1682 | 0 | 0 | 0 | 0 | 5.2152 | 21.4951 | 25.1834 | 14.1196 | 11.7752 | 4.1853 | 4.1853 | 4.1853 | 4.1853 | 8.6179 | 22.4546 | 25.5894 | 16.186 | 5.2248 | 4.1853 | 4.1853 | 4.1853 | 4.1853 | 13.8331 | 43.9497 | 50.7728 | 30.3056 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 20 | 1724 | 6.9 | 6.9 | 3.2958 | 2.5073 | 15 | 81 | 81 | 0 | 0 | -13.3206 | 282.1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 21 | 1725 | 6.6 | 6.6 | 3.2958 | 2.5073 | 15 | 82 | 82 | 0 | 0 | -22.0412 | 294.9807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 22 | 1726 | 6.3 | 6.3 | 3.2958 | 2.5073 | 15 | 82 | 82 | 0 | 0 | -29.839 | 309.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 23 | 1727 | 5.7 | 5.7 | 3.2958 | 2.5073 | 15 | 85 | 85 | 0 | 0 | -36.082 | 325.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 13 | 24 | 1728 | 4.9 | 4.9 | 7.6208 | 3.8524 | 15 | 86 | 86 | 0 | 0 | -40.0291 | 343.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 1 | 1729 | 6.6 | 6.6 | 7.6208 | 3.8524 | 15 | 82 | 82 | 0 | 0 | -41.039 | 3.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 2 | 1730 | 5.4 | 5.4 | 7.6208 | 3.8524 | 15 | 86 | 86 | 0 | 0 | -38.5181 | 22.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 3 | 1731 | 5.5 | 5.5 | 7.6208 | 3.8524 | 15 | 89 | 89 | 0 | 0 | -33.6683 | 40.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 4 | 1732 | 5.2 | 5.2 | 7.6208 | 3.8524 | 15 | 88 | 88 | 0 | 0 | -26.7981 | 55.9532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 5 | 1733 | 5.3 | 5.3 | 7.6208 | 3.8524 | 15 | 86 | 86 | 0 | 0 | -18.6152 | 69.5801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 6 | 1734 | 5.2 | 5.2 | 7.6208 | 3.8524 | 15 | 87 | 87 | 0 | 0 | -9.6973 | 82.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 7 | 1735 | 5.5 | 5.5 | 7.6208 | 3.8524 | 15 | 86 | 86 | 0 | 0 | -0.50521 | 93.9035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 14 | 8 | 1736 | 6.1 | 6.1 | 7.6208 | 3.8524 | 15 | 83 | 83 | 69.8542 | 26.888 | 8.5565 | 105.8767 | 0 | 45.9154 | 69.6894 | 52.6403 | 4.7552 | 0 | 0 | 0 | 4.112 | 10.704 | 27.6502 | 36.4246 | 30.1322 | 12.459 | 10.704 | 10.704 | 10.704 | 26.888 | 10.704 | 73.5656 | 106.114 | 82.7725 | 17.2142 | 10.704 | 10.704 | 10.704 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 9 | 1737 | 7.6 | 7.6 | 7.6208 | 3.8524 | 15 | 79 | 79 | 388.711 | 84.6658 | 17.0751 | 118.5309 | 0 | 187.0763 | 369.7212 | 335.7884 | 105.1554 | 0 | 0 | 0 | 82.3342 | 48.6776 | 86.1219 | 122.6792 | 115.8874 | 69.725 | 48.6776 | 48.6776 | 48.6776 | 84.6658 | 48.6776 | 273.1982 | 492.4004 | 451.6758 | 174.8803 | 48.6776 | 48.6776 | 48.6776 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 10 | 1738 | 8.4 | 8.4 | 7.6208 | 3.8524 | 15 | 78 | 78 | 36.9897 | 148.1373 | 24.5718 | 132.4276 | 0 | 10.0243 | 31.0652 | 33.9085 | 16.8887 | 0 | 0 | 0 | 12.8627 | 68.0263 | 94.6442 | 150.5151 | 158.0652 | 112.8717 | 68.0263 | 68.0263 | 68.0263 | 148.1373 | 68.0263 | 104.6685 | 181.5803 | 191.9737 | 129.7604 | 68.0263 | 68.0263 | 68.0263 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 11 | 1739 | 9.8 | 9.8 | 7.6208 | 3.8524 | 15 | 76 | 76 | 27.7147 | 187.3238 | 30.4695 | 147.98 | 0 | 1.1312 | 18.6045 | 25.1795 | 17.0047 | 0 | 0 | 0 | 12.6762 | 85.2458 | 87.9813 | 130.2345 | 146.134 | 126.3659 | 85.2458 | 85.2458 | 85.2458 | 187.3238 | 85.2458 | 89.1126 | 148.8391 | 171.3135 | 143.3706 | 85.2458 | 85.2458 | 85.2458 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 12 | 1740 | 11 | 11 | 7.6208 | 3.8524 | 15 | 71 | 71 | 137.4646 | 251.6968 | 34.1351 | 165.1915 | 0 | 0 | 62.8203 | 115.4533 | 100.4554 | 26.612 | 0 | 0 | 73.3032 | 117.363 | 117.363 | 186.3067 | 244.0702 | 227.6103 | 146.5691 | 117.363 | 117.363 | 251.6968 | 117.363 | 117.363 | 249.127 | 359.5235 | 328.0657 | 173.1811 | 117.363 | 117.363 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 13 | 1741 | 12.9 | 12.9 | 7.6208 | 3.8524 | 15 | 65 | 65 | 110.4167 | 268.0455 | 35.0541 | 183.3825 | 0 | 0 | 23.3592 | 78.9961 | 88.3581 | 45.9612 | 0 | 0 | 62.9545 | 124.0136 | 124.0136 | 148.1997 | 205.8059 | 215.4994 | 171.6017 | 124.0136 | 124.0136 | 268.0455 | 124.0136 | 124.0136 | 171.5589 | 284.802 | 303.8575 | 217.5629 | 124.0136 | 124.0136 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 14 | 1742 | 13.2 | 13.2 | 7.6208 | 3.8524 | 15 | 57 | 57 | 184.7959 | 264.4885 | 33.0786 | 201.3356 | 0 | 0 | 0 | 100.4705 | 151.0123 | 113.0931 | 8.9255 | 0 | 104.5115 | 126.1054 | 126.1054 | 126.1054 | 205.2477 | 245.0603 | 215.1907 | 133.1362 | 126.1054 | 264.4885 | 126.1054 | 126.1054 | 126.1054 | 305.7182 | 396.0726 | 328.2839 | 142.0617 | 126.1054 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 15 | 1743 | 12.9 | 12.9 | 7.6208 | 3.8524 | 15 | 58 | 58 | 86.1003 | 241.2487 | 28.5164 | 217.9735 | 0 | 0 | 0 | 28.9576 | 67.201 | 66.0789 | 26.2487 | 0 | 44.7513 | 112.1448 | 112.1448 | 112.1448 | 145.2438 | 188.9565 | 187.674 | 142.1475 | 112.1448 | 241.2487 | 112.1448 | 112.1448 | 112.1448 | 174.2014 | 256.1575 | 253.7529 | 168.3962 | 112.1448 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 16 | 1744 | 12.9 | 12.9 | 7.6208 | 3.8524 | 15 | 57 | 57 | 189.1727 | 203.5355 | 21.9547 | 232.8845 | 0 | 0 | 0 | 20.3338 | 131.0324 | 164.974 | 102.276 | 0 | 82.4645 | 100.4526 | 100.4526 | 100.4526 | 113.2381 | 182.8428 | 204.1845 | 164.7615 | 100.4526 | 203.5355 | 100.4526 | 100.4526 | 100.4526 | 133.5719 | 313.8752 | 369.1585 | 267.0375 | 100.4526 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 17 | 1745 | 11.9 | 11.9 | 7.6208 | 3.8524 | 15 | 60 | 60 | 5.3825 | 90.2788 | 14.0186 | 246.2619 | 0 | 0 | 0 | 0 | 3.0124 | 4.9449 | 3.9808 | 0.6848 | 1.7212 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 90.2788 | 44.8333 | 44.8333 | 44.8333 | 44.8333 | 47.8456 | 49.7782 | 48.8141 | 45.5181 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 14 | 18 | 1746 | 11.7 | 11.7 | 7.6208 | 3.8524 | 15 | 61 | 61 | 5.6841 | 51.981 | 5.2481 | 258.5961 | 0 | 0 | 0 | 0 | 2.22 | 5.1394 | 5.0482 | 1.9999 | 1.019 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 51.981 | 25.4895 | 25.4895 | 25.4895 | 25.4895 | 27.7095 | 30.629 | 30.5378 | 27.4894 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 19 | 1747 | 11.6 | 11.6 | 7.6208 | 3.8524 | 15 | 61 | 61 | 8.0451 | 7.8074 | -3.9081 | 270.4681 | 0 | 0 | 0 | 0 | 1.584 | 6.6731 | 7.8532 | 4.433 | 0.19263 | 4.3193 | 4.3193 | 4.3193 | 4.3193 | 5.9188 | 11.0576 | 12.2492 | 8.7956 | 7.8074 | 4.3193 | 4.3193 | 4.3193 | 4.3193 | 7.5028 | 17.7308 | 20.1024 | 13.2285 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 20 | 1748 | 11.5 | 11.5 | 7.6208 | 3.8524 | 15 | 62 | 62 | 0 | 0 | -13.0475 | 282.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 21 | 1749 | 11.1 | 11.1 | 7.6208 | 3.8524 | 15 | 66 | 66 | 0 | 0 | -21.7526 | 295.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 22 | 1750 | 10.7 | 10.7 | 7.6208 | 3.8524 | 15 | 71 | 71 | 0 | 0 | -29.5253 | 309.5139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 23 | 1751 | 11.1 | 11.1 | 7.6208 | 3.8524 | 15 | 70 | 70 | 0 | 0 | -35.7362 | 325.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 14 | 24 | 1752 | 11 | 11 | 9.3375 | 5.3042 | 15 | 72 | 72 | 0 | 0 | -39.6518 | 344.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 1 | 1753 | 11.1 | 11.1 | 9.3375 | 5.3042 | 15 | 72 | 72 | 0 | 0 | -40.6415 | 3.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 2 | 1754 | 11 | 11 | 9.3375 | 5.3042 | 15 | 74 | 74 | 0 | 0 | -38.1167 | 22.9012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 3 | 1755 | 11 | 11 | 9.3375 | 5.3042 | 15 | 76 | 76 | 0 | 0 | -33.2766 | 40.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 4 | 1756 | 11 | 11 | 9.3375 | 5.3042 | 15 | 76 | 76 | 0 | 0 | -26.4207 | 55.7977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 5 | 1757 | 10.9 | 10.9 | 9.3375 | 5.3042 | 15 | 78 | 78 | 0 | 0 | -18.2501 | 69.4023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 6 | 1758 | 10.7 | 10.7 | 9.3375 | 5.3042 | 15 | 79 | 79 | 0 | 0 | -9.3393 | 81.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 7 | 1759 | 10.4 | 10.4 | 9.3375 | 5.3042 | 15 | 84 | 84 | 0 | 0 | -0.14838 | 93.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 15 | 8 | 1760 | 10.3 | 10.3 | 9.3375 | 5.3042 | 15 | 86 | 86 | 0.56612 | 5.9636 | 8.9183 | 105.6989 | 0 | 0.37351 | 0.56493 | 0.42542 | 0.03671 | 0 | 0 | 0 | 0.036415 | 2.8063 | 3.7437 | 4.2241 | 3.874 | 2.8985 | 2.8063 | 2.8063 | 2.8063 | 5.9636 | 2.8063 | 4.1172 | 4.789 | 4.2994 | 2.9352 | 2.8063 | 2.8063 | 2.8063 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 9 | 1761 | 10.8 | 10.8 | 9.3375 | 5.3042 | 15 | 85 | 85 | 7.8205 | 70.3005 | 17.4471 | 118.3707 | 0 | 3.7811 | 7.4377 | 6.7375 | 2.0905 | 0 | 0 | 0 | 1.6995 | 31.5174 | 62.48 | 92.4239 | 86.6896 | 48.6362 | 31.5174 | 31.5174 | 31.5174 | 70.3005 | 31.5174 | 66.2611 | 99.8616 | 93.4271 | 50.7267 | 31.5174 | 31.5174 | 31.5174 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 10 | 1762 | 11.3 | 11.3 | 9.3375 | 5.3042 | 15 | 81 | 81 | 10.0742 | 121.4409 | 24.9571 | 132.3007 | 0 | 2.7504 | 8.4564 | 9.2088 | 4.5668 | 0 | 0 | 0 | 3.5591 | 56.0358 | 68.372 | 93.9651 | 97.3397 | 76.519 | 56.0358 | 56.0358 | 56.0358 | 121.4409 | 56.0358 | 71.1224 | 102.4215 | 106.5485 | 81.0858 | 56.0358 | 56.0358 | 56.0358 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 11 | 1763 | 12.2 | 12.2 | 9.3375 | 5.3042 | 15 | 74 | 74 | 36.766 | 196.9785 | 30.8671 | 147.9094 | 0 | 1.5698 | 24.6538 | 33.296 | 22.4338 | 0 | 0 | 0 | 17.0215 | 90.2377 | 94.3488 | 154.8008 | 177.4327 | 148.987 | 90.2377 | 90.2377 | 90.2377 | 196.9785 | 90.2377 | 95.9186 | 179.4547 | 210.7287 | 171.4208 | 90.2377 | 90.2377 | 90.2377 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 12 | 1764 | 11.8 | 11.8 | 9.3375 | 5.3042 | 15 | 73 | 73 | 19.2232 | 208.6413 | 34.5372 | 165.2028 | 0 | 0 | 8.766 | 16.0834 | 13.9793 | 3.6864 | 0 | 0 | 10.3587 | 97.2774 | 97.2774 | 118.7612 | 136.6948 | 131.5381 | 106.312 | 97.2774 | 97.2774 | 208.6413 | 97.2774 | 97.2774 | 127.5273 | 152.7782 | 145.5175 | 109.9984 | 97.2774 | 97.2774 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 13 | 1765 | 12.3 | 12.3 | 9.3375 | 5.3042 | 15 | 77 | 77 | 4.5943 | 150.3547 | 35.4468 | 183.489 | 0 | 0 | 0.96658 | 3.2708 | 3.6591 | 1.9039 | 0 | 0 | 2.6453 | 75.3239 | 75.3239 | 75.6419 | 76.3998 | 76.5275 | 75.9502 | 75.3239 | 75.3239 | 150.3547 | 75.3239 | 75.3239 | 76.6084 | 79.6706 | 80.1866 | 77.854 | 75.3239 | 75.3239 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 14 | 1766 | 13.2 | 13.2 | 9.3375 | 5.3042 | 15 | 72 | 72 | 4.6687 | 150.3334 | 33.4478 | 201.5263 | 0 | 0 | 0 | 2.5207 | 3.7963 | 2.8481 | 0.23146 | 0 | 2.6666 | 75.5877 | 75.5877 | 75.5877 | 75.746 | 75.8261 | 75.7665 | 75.6022 | 75.5877 | 150.3334 | 75.5877 | 75.5877 | 75.5877 | 78.2667 | 79.6224 | 78.6146 | 75.8337 | 75.5877 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 15 | 1767 | 13 | 13 | 9.3375 | 5.3042 | 15 | 69 | 69 | 5.094 | 144.3238 | 28.855 | 218.2209 | 0 | 0 | 0 | 1.693 | 3.9539 | 3.8986 | 1.5596 | 0 | 2.6762 | 72.4002 | 72.4002 | 72.4002 | 72.6554 | 72.9961 | 72.9877 | 72.6352 | 72.4002 | 144.3238 | 72.4002 | 72.4002 | 72.4002 | 74.3484 | 76.95 | 76.8864 | 74.1948 | 72.4002 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 16 | 1768 | 13.3 | 13.3 | 9.3375 | 5.3042 | 15 | 70 | 70 | 84.7115 | 204.5998 | 22.2638 | 233.1624 | 0 | 0 | 0 | 8.758 | 58.2892 | 73.6753 | 45.9035 | 0 | 37.4002 | 96.4775 | 96.4775 | 96.4775 | 105.3577 | 155.5799 | 171.1808 | 143.0215 | 96.4775 | 204.5998 | 96.4775 | 96.4775 | 96.4775 | 114.1157 | 213.8691 | 244.8561 | 188.925 | 96.4775 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 17 | 1769 | 13 | 13 | 9.3375 | 5.3042 | 15 | 71 | 71 | 14.6165 | 120.2449 | 14.3046 | 246.5536 | 0 | 0 | 0 | 0 | 8.11 | 13.3898 | 10.826 | 1.9205 | 4.7551 | 58.4791 | 58.4791 | 58.4791 | 58.4791 | 66.3272 | 71.4366 | 68.9556 | 60.3376 | 120.2449 | 58.4791 | 58.4791 | 58.4791 | 58.4791 | 74.4372 | 84.8263 | 79.7816 | 62.2581 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 15 | 18 | 1770 | 12.9 | 12.9 | 9.3375 | 5.3042 | 15 | 72 | 72 | 5.3539 | 52.0108 | 5.52 | 258.8937 | 0 | 0 | 0 | 0 | 2.0642 | 4.8251 | 4.7595 | 1.9059 | 0.9892 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 52.0108 | 25.4801 | 25.4801 | 25.4801 | 25.4801 | 27.5443 | 30.3052 | 30.2396 | 27.386 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 19 | 1771 | 12.6 | 12.6 | 9.3375 | 5.3042 | 15 | 74 | 74 | 12.9183 | 10.6203 | -3.6406 | 270.7691 | 0 | 0 | 0 | 0 | 2.4769 | 10.6734 | 12.6176 | 7.1706 | 0.37968 | 5.8356 | 5.8356 | 5.8356 | 5.8356 | 7.9936 | 15.1351 | 16.829 | 12.0831 | 10.6203 | 5.8356 | 5.8356 | 5.8356 | 5.8356 | 10.4706 | 25.8085 | 29.4466 | 19.2536 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 20 | 1772 | 12.2 | 12.2 | 9.3375 | 5.3042 | 15 | 74 | 74 | 0 | 0 | -12.7745 | 282.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 21 | 1773 | 12.4 | 12.4 | 9.3375 | 5.3042 | 15 | 72 | 72 | 0 | 0 | -21.4638 | 295.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 22 | 1774 | 12.6 | 12.6 | 9.3375 | 5.3042 | 15 | 73 | 73 | 0 | 0 | -29.2111 | 309.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 23 | 1775 | 12.8 | 12.8 | 9.3375 | 5.3042 | 15 | 72 | 72 | 0 | 0 | -35.3898 | 325.9881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 15 | 24 | 1776 | 12.9 | 12.9 | 11.9042 | 7.1785 | 15 | 73 | 73 | 0 | 0 | -39.274 | 344.2303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 1 | 1777 | 13 | 13 | 11.9042 | 7.1785 | 15 | 74 | 74 | 0 | 0 | -40.2433 | 3.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 2 | 1778 | 12.4 | 12.4 | 11.9042 | 7.1785 | 15 | 78 | 78 | 0 | 0 | -37.7146 | 22.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 3 | 1779 | 12.6 | 12.6 | 11.9042 | 7.1785 | 15 | 79 | 79 | 0 | 0 | -32.8841 | 40.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 4 | 1780 | 12.4 | 12.4 | 11.9042 | 7.1785 | 15 | 81 | 81 | 0 | 0 | -26.0422 | 55.6441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 5 | 1781 | 12.1 | 12.1 | 11.9042 | 7.1785 | 15 | 84 | 84 | 0 | 0 | -17.8838 | 69.2261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 6 | 1782 | 11.8 | 11.8 | 11.9042 | 7.1785 | 15 | 86 | 86 | 0 | 0 | -8.9803 | 81.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 7 | 1783 | 11.8 | 11.8 | 11.9042 | 7.1785 | 15 | 86 | 86 | 0 | 0 | 0.20948 | 93.5331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 16 | 8 | 1784 | 11.7 | 11.7 | 11.9042 | 7.1785 | 15 | 88 | 88 | 0.48126 | 5.9664 | 9.281 | 105.5215 | 0 | 0.31868 | 0.48034 | 0.36062 | 0.029657 | 0 | 0 | 0 | 0.033584 | 2.8883 | 2.8883 | 2.8883 | 2.8883 | 2.8883 | 2.8883 | 2.8883 | 2.8883 | 5.9664 | 2.8883 | 3.2069 | 3.3686 | 3.2489 | 2.9179 | 2.8883 | 2.8883 | 2.8883 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 9 | 1785 | 11.6 | 11.6 | 11.9042 | 7.1785 | 15 | 88 | 88 | 0.8195 | 24.8174 | 17.8199 | 118.2107 | 0 | 0.39799 | 0.77928 | 0.70407 | 0.21643 | 0 | 0 | 0 | 0.1826 | 11.8999 | 11.8999 | 11.8999 | 11.8999 | 11.8999 | 11.8999 | 11.8999 | 11.8999 | 24.8174 | 11.8999 | 12.2979 | 12.6792 | 12.604 | 12.1164 | 11.8999 | 11.8999 | 11.8999 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 10 | 1786 | 11.8 | 11.8 | 11.9042 | 7.1785 | 15 | 89 | 89 | 1.4202 | 52.4904 | 25.3432 | 132.1739 | 0 | 0.39056 | 1.1915 | 1.2945 | 0.63916 | 0 | 0 | 0 | 0.50962 | 25.4691 | 25.4691 | 25.4691 | 25.4691 | 25.4691 | 25.4691 | 25.4691 | 25.4691 | 52.4904 | 25.4691 | 25.8597 | 26.6606 | 26.7636 | 26.1083 | 25.4691 | 25.4691 | 25.4691 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 11 | 1787 | 12.3 | 12.3 | 11.9042 | 7.1785 | 15 | 88 | 88 | 1.6681 | 74.2184 | 31.2654 | 147.8395 | 0 | 0.074329 | 1.1173 | 1.5057 | 1.0121 | 0 | 0 | 0 | 0.78156 | 36.2272 | 36.2272 | 36.2272 | 36.2272 | 36.2272 | 36.2272 | 36.2272 | 36.2272 | 74.2184 | 36.2272 | 36.3015 | 37.3444 | 37.7329 | 37.2393 | 36.2272 | 36.2272 | 36.2272 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 12 | 1788 | 12.6 | 12.6 | 11.9042 | 7.1785 | 15 | 87 | 87 | 1.8588 | 90.988 | 34.9399 | 165.2156 | 0 | 0 | 0.84573 | 1.5491 | 1.3451 | 0.35307 | 0 | 0 | 1.012 | 44.6219 | 44.6219 | 44.6219 | 44.6219 | 44.6219 | 44.6219 | 44.6219 | 44.6219 | 90.988 | 44.6219 | 44.6219 | 45.4677 | 46.171 | 45.967 | 44.975 | 44.6219 | 44.6219 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 13 | 1789 | 13.5 | 13.5 | 11.9042 | 7.1785 | 15 | 84 | 84 | 3.8836 | 139.7421 | 35.8397 | 183.5979 | 0 | 0 | 0.8124 | 2.7511 | 3.0782 | 1.6022 | 0 | 0 | 2.2579 | 70.0216 | 70.0216 | 70.0216 | 70.0216 | 70.0216 | 70.0216 | 70.0216 | 70.0216 | 139.7421 | 70.0216 | 70.0216 | 70.834 | 72.7727 | 73.0998 | 71.6238 | 70.0216 | 70.0216 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 14 | 1790 | 14.7 | 14.7 | 11.9042 | 7.1785 | 15 | 80 | 80 | 15.7533 | 215.9139 | 33.8169 | 201.7201 | 0 | 0 | 0 | 8.4456 | 12.7454 | 9.579 | 0.80141 | 0 | 9.0861 | 102.9184 | 102.9184 | 102.9184 | 120.129 | 128.8909 | 122.4385 | 104.5515 | 102.9184 | 215.9139 | 102.9184 | 102.9184 | 102.9184 | 128.5746 | 141.6363 | 132.0175 | 105.3529 | 102.9184 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 15 | 1791 | 14.7 | 14.7 | 11.9042 | 7.1785 | 15 | 81 | 81 | 4.6564 | 139.5277 | 29.193 | 218.4714 | 0 | 0 | 0 | 1.529 | 3.5939 | 3.5536 | 1.4317 | 0 | 2.4723 | 70.0051 | 70.0051 | 70.0051 | 70.0051 | 70.0051 | 70.0051 | 70.0051 | 70.0051 | 139.5277 | 70.0051 | 70.0051 | 70.0051 | 71.5341 | 73.599 | 73.5587 | 71.4368 | 70.0051 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 16 | 1792 | 15.6 | 15.6 | 11.9042 | 7.1785 | 15 | 75 | 75 | 12.8284 | 161.2649 | 22.5721 | 233.4428 | 0 | 0 | 0 | 1.2733 | 8.7679 | 11.1263 | 6.9671 | 0 | 5.7351 | 78.085 | 78.085 | 78.085 | 79.9317 | 90.8012 | 94.2218 | 88.1896 | 78.085 | 161.2649 | 78.085 | 78.085 | 78.085 | 81.205 | 99.5691 | 105.3481 | 95.1567 | 78.085 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 17 | 1793 | 15.7 | 15.7 | 11.9042 | 7.1785 | 15 | 76 | 76 | 52.2137 | 146.7248 | 14.5899 | 246.8472 | 0 | 0 | 0 | 0 | 28.7175 | 47.6915 | 38.7285 | 7.0789 | 17.2752 | 70.1378 | 70.1378 | 70.1378 | 70.1378 | 105.2636 | 128.4717 | 117.5085 | 78.7963 | 146.7248 | 70.1378 | 70.1378 | 70.1378 | 70.1378 | 133.981 | 176.1631 | 156.237 | 85.8751 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 16 | 18 | 1794 | 15 | 15 | 11.9042 | 7.1785 | 15 | 75 | 75 | 20.1211 | 74.1718 | 5.7913 | 259.1928 | 0 | 0 | 0 | 0 | 7.6562 | 18.0738 | 17.904 | 7.2463 | 3.8282 | 36.6494 | 36.6494 | 36.6494 | 36.6494 | 48.8054 | 65.3456 | 65.076 | 48.1545 | 74.1718 | 36.6494 | 36.6494 | 36.6494 | 36.6494 | 56.4616 | 83.4194 | 82.9799 | 55.4007 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 19 | 1795 | 14.5 | 14.5 | 11.9042 | 7.1785 | 15 | 77 | 77 | 18.2116 | 13.3655 | -3.3735 | 271.0711 | 0 | 0 | 0 | 0 | 3.3973 | 14.9869 | 17.7973 | 10.1823 | 0.63451 | 7.3011 | 7.3011 | 7.3011 | 7.3011 | 9.9725 | 19.0855 | 21.2954 | 15.3076 | 13.3655 | 7.3011 | 7.3011 | 7.3011 | 7.3011 | 13.3698 | 34.0724 | 39.0928 | 25.49 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 20 | 1796 | 13.2 | 13.2 | 11.9042 | 7.1785 | 15 | 82 | 82 | 0 | 0 | -12.5015 | 283.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 21 | 1797 | 11.8 | 11.8 | 11.9042 | 7.1785 | 15 | 88 | 88 | 0 | 0 | -21.1748 | 295.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 22 | 1798 | 11.1 | 11.1 | 11.9042 | 7.1785 | 15 | 86 | 86 | 0 | 0 | -28.8964 | 310.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 23 | 1799 | 10.5 | 10.5 | 11.9042 | 7.1785 | 15 | 87 | 87 | 0 | 0 | -35.043 | 326.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 16 | 24 | 1800 | 9.6 | 9.6 | 12.75 | 8.9243 | 15 | 90 | 90 | 0 | 0 | -38.8957 | 344.4085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 1 | 1801 | 9 | 9 | 12.75 | 8.9243 | 15 | 92 | 92 | 0 | 0 | -39.8446 | 3.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 2 | 1802 | 7.7 | 7.7 | 12.75 | 8.9243 | 15 | 93 | 93 | 0 | 0 | -37.3119 | 22.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 3 | 1803 | 8.9 | 8.9 | 12.75 | 8.9243 | 15 | 91 | 91 | 0 | 0 | -32.4907 | 40.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 4 | 1804 | 7.5 | 7.5 | 12.75 | 8.9243 | 15 | 93 | 93 | 0 | 0 | -25.6628 | 55.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 5 | 1805 | 6.7 | 6.7 | 12.75 | 8.9243 | 15 | 95 | 95 | 0 | 0 | -17.5165 | 69.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 6 | 1806 | 6.2 | 6.2 | 12.75 | 8.9243 | 15 | 95 | 95 | 0 | 0 | -8.6202 | 81.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 7 | 1807 | 6.2 | 6.2 | 12.75 | 8.9243 | 15 | 96 | 96 | 0 | 0 | 0.56822 | 93.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 17 | 8 | 1808 | 7.9 | 7.9 | 12.75 | 8.9243 | 15 | 93 | 93 | 154.0134 | 35.4113 | 9.6445 | 105.3444 | 0 | 102.3512 | 153.7429 | 115.074 | 8.9963 | 0 | 0 | 0 | 11.5887 | 15.4498 | 15.4498 | 15.4498 | 15.4498 | 15.4498 | 15.4498 | 15.4498 | 15.4498 | 35.4113 | 15.4498 | 117.8011 | 169.1927 | 130.5238 | 24.4462 | 15.4498 | 15.4498 | 15.4498 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 9 | 1809 | 10.8 | 10.8 | 12.75 | 8.9243 | 15 | 82 | 82 | 275.0785 | 101.1951 | 18.1934 | 118.0508 | 0 | 134.181 | 261.5233 | 235.6688 | 71.7627 | 0 | 0 | 0 | 62.8049 | 54.1982 | 106.4709 | 156.0794 | 146.0073 | 82.1547 | 54.1982 | 54.1982 | 54.1982 | 101.1951 | 54.1982 | 240.6519 | 417.6027 | 381.6761 | 153.9174 | 54.1982 | 54.1982 | 54.1982 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 10 | 1810 | 14.2 | 14.2 | 12.75 | 8.9243 | 15 | 70 | 70 | 438.7433 | 137.1422 | 25.73 | 132.0473 | 0 | 121.5101 | 367.8475 | 398.7049 | 196.0063 | 0 | 0 | 0 | 159.8578 | 80.8056 | 113.3542 | 179.3399 | 187.6056 | 133.3093 | 80.8056 | 80.8056 | 80.8056 | 137.1422 | 80.8056 | 234.8643 | 547.1875 | 586.3105 | 329.3156 | 80.8056 | 80.8056 | 80.8056 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 11 | 1811 | 16 | 16 | 12.75 | 8.9243 | 15 | 62 | 62 | 595.2224 | 142.8115 | 31.6643 | 147.77 | 0 | 27.6211 | 398.1826 | 535.4942 | 359.1206 | 0 | 0 | 0 | 282.1885 | 95.6255 | 101.4171 | 179.1164 | 207.9079 | 170.9259 | 95.6255 | 95.6255 | 95.6255 | 142.8115 | 95.6255 | 129.0382 | 577.2991 | 743.4022 | 530.0465 | 95.6255 | 95.6255 | 95.6255 | 425 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 12 | 1812 | 17.4 | 17.4 | 12.75 | 8.9243 | 15 | 59 | 59 | 609.221 | 161.9118 | 35.343 | 165.2298 | 0 | 0 | 276.5428 | 505.7057 | 438.6331 | 114.6152 | 0 | 0 | 335.0882 | 107.9623 | 107.9623 | 168.7065 | 219.0435 | 204.3106 | 133.1382 | 107.9623 | 107.9623 | 161.9118 | 107.9623 | 107.9623 | 445.2493 | 724.7492 | 642.9437 | 247.7533 | 107.9623 | 107.9623 | 497 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 13 | 1813 | 18.1 | 18.1 | 12.75 | 8.9243 | 15 | 53 | 53 | 601.2861 | 175.0675 | 36.2328 | 183.7093 | 0 | 0 | 125.0422 | 423.7738 | 474.2644 | 246.9374 | 0 | 0 | 352.9325 | 112.8047 | 112.8047 | 139.7714 | 204.1959 | 215.0847 | 166.0593 | 112.8047 | 112.8047 | 175.0675 | 112.8047 | 112.8047 | 264.8136 | 627.9697 | 689.3491 | 412.9967 | 112.8047 | 112.8047 | 528 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 14 | 1814 | 18.1 | 18.1 | 12.75 | 8.9243 | 15 | 54 | 54 | 568.0891 | 183.1705 | 34.1856 | 201.917 | 0 | 0 | 0 | 302.3787 | 457.2735 | 344.3037 | 29.6455 | 0 | 330.8295 | 115.039 | 115.039 | 115.039 | 192.0695 | 231.5287 | 202.7498 | 122.5911 | 115.039 | 183.1705 | 115.039 | 115.039 | 115.039 | 494.4481 | 688.8022 | 547.0535 | 152.2366 | 115.039 | 514 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 15 | 1815 | 18.2 | 18.2 | 12.75 | 8.9243 | 15 | 53 | 53 | 504.4781 | 185.337 | 29.5304 | 218.7249 | 0 | 0 | 0 | 163.6146 | 387.154 | 383.9039 | 155.7681 | 0 | 270.663 | 110.3416 | 110.3416 | 110.3416 | 157.5788 | 222.1169 | 221.1786 | 155.3135 | 110.3416 | 185.337 | 110.3416 | 110.3416 | 110.3416 | 321.1934 | 609.271 | 605.0825 | 311.0816 | 110.3416 | 456 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 16 | 1816 | 17.6 | 17.6 | 12.75 | 8.9243 | 15 | 56 | 56 | 363.8996 | 185.2948 | 22.8796 | 233.7256 | 0 | 0 | 0 | 34.6083 | 247.0195 | 314.73 | 198.0759 | 0 | 164.7052 | 101.4257 | 101.4257 | 101.4257 | 114.54 | 195.0302 | 220.6882 | 176.4838 | 101.4257 | 185.2948 | 101.4257 | 101.4257 | 101.4257 | 149.1483 | 442.0497 | 535.4181 | 374.5597 | 101.4257 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 17 | 1817 | 16.6 | 16.6 | 12.75 | 8.9243 | 15 | 59 | 59 | 177.0341 | 157.4503 | 14.8745 | 247.1426 | 0 | 0 | 0 | 0 | 96.502 | 161.218 | 131.4947 | 24.7436 | 59.5497 | 79.1718 | 79.1718 | 79.1718 | 79.1718 | 134.1339 | 170.9925 | 154.0638 | 93.2643 | 157.4503 | 79.1718 | 79.1718 | 79.1718 | 79.1718 | 230.6359 | 332.2105 | 285.5585 | 118.0079 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 18 | 1818 | 14.9 | 14.9 | 12.75 | 8.9243 | 15 | 62 | 62 | 11.9786 | 69.6553 | 6.0621 | 259.4933 | 0 | 0 | 0 | 0 | 4.497 | 10.7233 | 10.6681 | 4.3636 | 2.3447 | 34.549 | 34.549 | 34.549 | 34.549 | 35.2526 | 36.2268 | 36.2182 | 35.2317 | 69.6553 | 34.549 | 34.549 | 34.549 | 34.549 | 39.7496 | 46.9501 | 46.8862 | 39.5953 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 19 | 1819 | 11.3 | 11.3 | 12.75 | 8.9243 | 15 | 76 | 76 | 2.5677 | 7.8965 | -3.1067 | 271.374 | 0 | 0 | 0 | 0 | 0.4656 | 2.1044 | 2.5105 | 1.446 | 0.10346 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 7.8965 | 4.2299 | 4.2299 | 4.2299 | 4.2299 | 4.6955 | 6.3343 | 6.7404 | 5.6758 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 20 | 1820 | 9.7 | 9.7 | 12.75 | 8.9243 | 15 | 84 | 84 | 0 | 0 | -12.2286 | 283.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 21 | 1821 | 8.6 | 8.6 | 12.75 | 8.9243 | 15 | 90 | 90 | 0 | 0 | -20.8856 | 296.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 22 | 1822 | 7.7 | 7.7 | 12.75 | 8.9243 | 15 | 93 | 93 | 0 | 0 | -28.5815 | 310.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 23 | 1823 | 7.2 | 7.2 | 12.75 | 8.9243 | 15 | 95 | 95 | 0 | 0 | -34.6958 | 326.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 17 | 24 | 1824 | 6.2 | 6.2 | 11.3625 | 9.9579 | 15 | 97 | 97 | 0 | 0 | -38.517 | 344.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 1 | 1825 | 6.4 | 6.4 | 11.3625 | 9.9579 | 15 | 97 | 97 | 0 | 0 | -39.4456 | 3.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 2 | 1826 | 6.3 | 6.3 | 11.3625 | 9.9579 | 15 | 97 | 97 | 0 | 0 | -36.9088 | 22.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 3 | 1827 | 5.4 | 5.4 | 11.3625 | 9.9579 | 15 | 98 | 98 | 0 | 0 | -32.0967 | 40.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 4 | 1828 | 4.2 | 4.2 | 11.3625 | 9.9579 | 15 | 98 | 98 | 0 | 0 | -25.2826 | 55.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 5 | 1829 | 3.8 | 3.8 | 11.3625 | 9.9579 | 15 | 98 | 98 | 0 | 0 | -17.1484 | 68.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 6 | 1830 | 4 | 4 | 11.3625 | 9.9579 | 15 | 99 | 99 | 0 | 0 | -8.2594 | 81.2749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 7 | 1831 | 4.8 | 4.8 | 11.3625 | 9.9579 | 15 | 99 | 99 | 0 | 0 | 0.9277 | 93.1653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 18 | 8 | 1832 | 6.8 | 6.8 | 11.3625 | 9.9579 | 15 | 99 | 99 | 14.6859 | 29.8148 | 10.0086 | 105.1677 | 0 | 9.794 | 14.6616 | 10.9407 | 0.81081 | 0 | 0 | 0 | 1.1852 | 12.2727 | 73.6639 | 104.1754 | 80.8515 | 17.3551 | 12.2727 | 12.2727 | 12.2727 | 29.8148 | 12.2727 | 83.4579 | 118.837 | 91.7922 | 18.1659 | 12.2727 | 12.2727 | 12.2727 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 9 | 1833 | 8 | 8 | 11.3625 | 9.9579 | 15 | 98 | 98 | 4.4362 | 59.9628 | 18.5674 | 117.891 | 0 | 2.1733 | 4.2165 | 3.7898 | 1.1431 | 0 | 0 | 0 | 1.0372 | 28.4774 | 38.7128 | 48.3359 | 46.3261 | 33.8608 | 28.4774 | 28.4774 | 28.4774 | 59.9628 | 28.4774 | 40.8861 | 52.5524 | 50.1159 | 35.0039 | 28.4774 | 28.4774 | 28.4774 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 10 | 1834 | 9.6 | 9.6 | 11.3625 | 9.9579 | 15 | 89 | 89 | 17.3265 | 140.5915 | 26.1172 | 131.9207 | 0 | 4.832 | 14.5168 | 15.6978 | 7.6833 | 0 | 0 | 0 | 6.4085 | 63.7715 | 81.1249 | 115.9062 | 120.1478 | 91.3649 | 63.7715 | 63.7715 | 63.7715 | 140.5915 | 63.7715 | 85.9569 | 130.423 | 135.8456 | 99.0482 | 63.7715 | 63.7715 | 63.7715 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 11 | 1835 | 11.2 | 11.2 | 11.3625 | 9.9579 | 15 | 85 | 85 | 9.9532 | 164.2262 | 32.0636 | 147.701 | 0 | 0.48008 | 6.6497 | 8.9241 | 5.9708 | 0 | 0 | 0 | 4.7738 | 77.4437 | 79.0501 | 99.6941 | 107.3042 | 97.4224 | 77.4437 | 77.4437 | 77.4437 | 164.2262 | 77.4437 | 79.5302 | 106.3438 | 116.2282 | 103.3932 | 77.4437 | 77.4437 | 77.4437 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 12 | 1836 | 12.8 | 12.8 | 11.3625 | 9.9579 | 15 | 79 | 79 | 15.9154 | 208.1578 | 35.7464 | 165.2453 | 0 | 0 | 7.2069 | 13.1576 | 11.4007 | 2.9654 | 0 | 0 | 8.8422 | 97.7248 | 97.7248 | 116.3952 | 131.811 | 127.2596 | 105.4071 | 97.7248 | 97.7248 | 208.1578 | 97.7248 | 97.7248 | 123.6021 | 144.9686 | 138.6603 | 108.3725 | 97.7248 | 97.7248 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 13 | 1837 | 14.3 | 14.3 | 11.3625 | 9.9579 | 15 | 71 | 71 | 95.8142 | 276.2285 | 36.6259 | 183.8231 | 0 | 0 | 19.805 | 67.1784 | 75.1995 | 39.1698 | 0 | 0 | 56.7715 | 126.763 | 126.763 | 150.5131 | 207.3232 | 216.9421 | 173.7354 | 126.763 | 126.763 | 276.2285 | 126.763 | 126.763 | 170.3181 | 274.5015 | 292.1417 | 212.9052 | 126.763 | 126.763 | 333 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 14 | 1838 | 14.2 | 14.2 | 11.3625 | 9.9579 | 15 | 78 | 78 | 47.7866 | 257.9059 | 34.554 | 202.1167 | 0 | 0 | 0 | 25.2498 | 38.2657 | 28.8661 | 2.5571 | 0 | 28.0941 | 117.4663 | 117.4663 | 117.4663 | 170.1335 | 197.2828 | 177.6766 | 122.8 | 117.4663 | 257.9059 | 117.4663 | 117.4663 | 117.4663 | 195.3833 | 235.5484 | 206.5427 | 125.3571 | 117.4663 | 286 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 15 | 1839 | 13.1 | 13.1 | 11.3625 | 9.9579 | 15 | 88 | 88 | 0.69555 | 55.623 | 29.8671 | 218.9811 | 0 | 0 | 0 | 0.22276 | 0.5307 | 0.52777 | 0.21568 | 0 | 0.37703 | 26.7576 | 26.7576 | 26.7576 | 26.7576 | 26.7576 | 26.7576 | 26.7576 | 26.7576 | 55.623 | 26.7576 | 26.7576 | 26.7576 | 26.9804 | 27.2883 | 27.2854 | 26.9733 | 26.7576 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 16 | 1840 | 13.5 | 13.5 | 11.3625 | 9.9579 | 15 | 92 | 92 | 2.4595 | 87.8732 | 23.1863 | 234.0107 | 0 | 0 | 0 | 0.22364 | 1.6579 | 2.121 | 1.3417 | 0 | 1.1268 | 43.0834 | 43.0834 | 43.0834 | 43.0834 | 43.0834 | 43.0834 | 43.0834 | 43.0834 | 87.8732 | 43.0834 | 43.0834 | 43.0834 | 43.307 | 44.7413 | 45.2045 | 44.4251 | 43.0834 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 17 | 1841 | 13.3 | 13.3 | 11.3625 | 9.9579 | 15 | 90 | 90 | 9.4647 | 115.7642 | 15.1583 | 247.4398 | 0 | 0 | 0 | 0 | 5.1126 | 8.5929 | 7.0396 | 1.3626 | 3.2358 | 56.8823 | 56.8823 | 56.8823 | 56.8823 | 61.1548 | 64.0633 | 62.7653 | 58.021 | 115.7642 | 56.8823 | 56.8823 | 56.8823 | 56.8823 | 66.2674 | 72.6562 | 69.8049 | 59.3836 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 18 | 1842 | 13.1 | 13.1 | 11.3625 | 9.9579 | 15 | 89 | 89 | 5.9891 | 59.7949 | 6.3323 | 259.7949 | 0 | 0 | 0 | 0 | 2.2178 | 5.343 | 5.3384 | 2.2066 | 1.2051 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 59.7949 | 29.4621 | 29.4621 | 29.4621 | 29.4621 | 31.6799 | 34.8051 | 34.8005 | 31.6687 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 19 | 1843 | 13.3 | 13.3 | 11.3625 | 9.9579 | 15 | 87 | 87 | 1.9931 | 7.9088 | -2.8403 | 271.6776 | 0 | 0 | 0 | 0 | 0.35097 | 1.6267 | 1.9496 | 1.1304 | 0.091176 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 7.9088 | 3.7035 | 3.7035 | 3.7035 | 3.7035 | 4.0544 | 5.3302 | 5.6531 | 4.8339 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 20 | 1844 | 11.6 | 11.6 | 11.3625 | 9.9579 | 15 | 77 | 77 | 0 | 0 | -11.9558 | 283.6995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 21 | 1845 | 9.8 | 9.8 | 11.3625 | 9.9579 | 15 | 86 | 86 | 0 | 0 | -20.5963 | 296.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 22 | 1846 | 9.3 | 9.3 | 11.3625 | 9.9579 | 15 | 82 | 82 | 0 | 0 | -28.2662 | 310.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 23 | 1847 | 9.5 | 9.5 | 11.3625 | 9.9579 | 15 | 79 | 79 | 0 | 0 | -34.3482 | 326.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 18 | 24 | 1848 | 8.7 | 8.7 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -38.1381 | 344.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 1 | 1849 | 8.9 | 8.9 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -39.0463 | 3.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 2 | 1850 | 8.7 | 8.7 | 9.4583 | 10.2186 | 15 | 89 | 89 | 0 | 0 | -36.5055 | 22.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 3 | 1851 | 8.1 | 8.1 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -31.7022 | 39.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 4 | 1852 | 7.8 | 7.8 | 9.4583 | 10.2186 | 15 | 91 | 91 | 0 | 0 | -24.9017 | 55.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 5 | 1853 | 7.5 | 7.5 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -16.7795 | 68.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 6 | 1854 | 7.9 | 7.9 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -7.8979 | 81.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 7 | 1855 | 8.3 | 8.3 | 9.4583 | 10.2186 | 15 | 88 | 88 | 0 | 0 | 1.2878 | 92.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 19 | 8 | 1856 | 8.4 | 8.4 | 9.4583 | 10.2186 | 15 | 85 | 85 | 3.1709 | 18.7268 | 10.3732 | 104.9912 | 0 | 2.1219 | 3.1658 | 2.3552 | 0.16494 | 0 | 0 | 0 | 0.27321 | 8.2046 | 31.5012 | 42.9618 | 34.0621 | 10.0154 | 8.2046 | 8.2046 | 8.2046 | 18.7268 | 8.2046 | 33.6231 | 46.1276 | 36.4173 | 10.1803 | 8.2046 | 8.2046 | 8.2046 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 9 | 1857 | 9.2 | 9.2 | 9.4583 | 10.2186 | 15 | 83 | 83 | 16.4028 | 90.0752 | 18.9419 | 117.7312 | 0 | 8.0695 | 15.5856 | 13.9718 | 4.1736 | 0 | 0 | 0 | 3.9248 | 39.4148 | 83.8577 | 125.2527 | 116.365 | 62.4009 | 39.4148 | 39.4148 | 39.4148 | 90.0752 | 39.4148 | 91.9272 | 140.8383 | 130.3368 | 66.5744 | 39.4148 | 39.4148 | 39.4148 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 10 | 1858 | 9.8 | 9.8 | 9.4583 | 10.2186 | 15 | 80 | 80 | 16.1558 | 140.9358 | 26.5048 | 131.7941 | 0 | 4.5362 | 13.5258 | 14.5921 | 7.1106 | 0 | 0 | 0 | 6.0642 | 64.1636 | 80.6829 | 113.4195 | 117.3026 | 90.0577 | 64.1636 | 64.1636 | 64.1636 | 140.9358 | 64.1636 | 85.2191 | 126.9453 | 131.8948 | 97.1683 | 64.1636 | 64.1636 | 64.1636 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 11 | 1859 | 10.5 | 10.5 | 9.4583 | 10.2186 | 15 | 75 | 75 | 24.1595 | 194.2795 | 32.4633 | 147.6323 | 0 | 1.2091 | 16.1189 | 21.5864 | 14.4089 | 0 | 0 | 0 | 11.7205 | 89.0679 | 92.0804 | 129.2285 | 142.8511 | 124.9682 | 89.0679 | 89.0679 | 89.0679 | 194.2795 | 89.0679 | 93.2895 | 145.3473 | 164.4375 | 139.3771 | 89.0679 | 89.0679 | 89.0679 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 12 | 1860 | 11.8 | 11.8 | 9.4583 | 10.2186 | 15 | 69 | 69 | 142.4314 | 264.0824 | 36.15 | 165.262 | 0 | 0 | 64.3355 | 117.2655 | 101.5029 | 26.2813 | 0 | 0 | 79.9176 | 122.8317 | 122.8317 | 192.2001 | 249.2706 | 232.275 | 151.1689 | 122.8317 | 122.8317 | 264.0824 | 122.8317 | 122.8317 | 256.5356 | 366.5361 | 333.7779 | 177.4502 | 122.8317 | 122.8317 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 13 | 1861 | 11.4 | 11.4 | 9.4583 | 10.2186 | 15 | 67 | 67 | 5.0846 | 163.9592 | 37.0189 | 183.9392 | 0 | 0 | 1.0445 | 3.5462 | 3.9706 | 2.0691 | 0 | 0 | 3.0408 | 81.6549 | 81.6549 | 82.5884 | 84.8243 | 85.2036 | 83.5041 | 81.6549 | 81.6549 | 163.9592 | 81.6549 | 81.6549 | 83.6329 | 88.3705 | 89.1742 | 85.5732 | 81.6549 | 81.6549 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 14 | 1862 | 9.6 | 9.6 | 9.4583 | 10.2186 | 15 | 85 | 85 | 0.4629 | 49.7253 | 34.922 | 202.3194 | 0 | 0 | 0 | 0.24277 | 0.36872 | 0.27868 | 0.02539 | 0 | 0.2747 | 23.8552 | 23.8552 | 23.8552 | 23.8552 | 23.8552 | 23.8552 | 23.8552 | 23.8552 | 49.7253 | 23.8552 | 23.8552 | 23.8552 | 24.098 | 24.2239 | 24.1339 | 23.8806 | 23.8552 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 15 | 1863 | 9.9 | 9.9 | 9.4583 | 10.2186 | 15 | 87 | 87 | 0.54367 | 49.7023 | 30.203 | 219.2401 | 0 | 0 | 0 | 0.17189 | 0.41237 | 0.4113 | 0.16929 | 0 | 0.2977 | 23.8392 | 23.8392 | 23.8392 | 23.8392 | 23.8392 | 23.8392 | 23.8392 | 23.8392 | 49.7023 | 23.8392 | 23.8392 | 23.8392 | 24.0111 | 24.2516 | 24.2505 | 24.0085 | 23.8392 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 16 | 1864 | 10.1 | 10.1 | 9.4583 | 10.2186 | 15 | 89 | 89 | 0.67006 | 46.6893 | 23.4921 | 234.298 | 0 | 0 | 0 | 0.058119 | 0.44852 | 0.57618 | 0.36632 | 0 | 0.31067 | 22.3602 | 22.3602 | 22.3602 | 22.3602 | 22.3602 | 22.3602 | 22.3602 | 22.3602 | 46.6893 | 22.3602 | 22.3602 | 22.3602 | 22.4183 | 22.8087 | 22.9363 | 22.7265 | 22.3602 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 17 | 1865 | 10.2 | 10.2 | 9.4583 | 10.2186 | 15 | 92 | 92 | 0.42367 | 27.8528 | 15.4412 | 247.7385 | 0 | 0 | 0 | 0 | 0.22675 | 0.38345 | 0.31553 | 0.062778 | 0.14717 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 27.8528 | 13.1897 | 13.1897 | 13.1897 | 13.1897 | 13.4165 | 13.5732 | 13.5053 | 13.2525 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 19 | 18 | 1866 | 10.4 | 10.4 | 9.4583 | 10.2186 | 15 | 94 | 94 | 0.18468 | 10.9618 | 6.6018 | 260.0976 | 0 | 0 | 0 | 0 | 0.067438 | 0.16418 | 0.16475 | 0.068808 | 0.038173 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 10.9618 | 5.1186 | 5.1186 | 5.1186 | 5.1186 | 5.186 | 5.2827 | 5.2833 | 5.1874 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 19 | 1867 | 10.4 | 10.4 | 9.4583 | 10.2186 | 15 | 95 | 95 | 0 | 0 | -2.5742 | 271.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 20 | 1868 | 10 | 10 | 9.4583 | 10.2186 | 15 | 91 | 91 | 0 | 0 | -11.6831 | 284.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 21 | 1869 | 9.4 | 9.4 | 9.4583 | 10.2186 | 15 | 90 | 90 | 0 | 0 | -20.3069 | 296.7865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 22 | 1870 | 9 | 9 | 9.4583 | 10.2186 | 15 | 85 | 85 | 0 | 0 | -27.9507 | 310.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 23 | 1871 | 8.6 | 8.6 | 9.4583 | 10.2186 | 15 | 82 | 82 | 0 | 0 | -34.0004 | 326.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 19 | 24 | 1872 | 8.7 | 8.7 | 9.3583 | 10.317 | 15 | 75 | 75 | 0 | 0 | -37.759 | 344.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 1 | 1873 | 8.3 | 8.3 | 9.3583 | 10.317 | 15 | 73 | 73 | 0 | 0 | -38.6468 | 4.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 2 | 1874 | 7.5 | 7.5 | 9.3583 | 10.317 | 15 | 77 | 77 | 0 | 0 | -36.102 | 22.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 3 | 1875 | 7.5 | 7.5 | 9.3583 | 10.317 | 15 | 80 | 80 | 0 | 0 | -31.3074 | 39.8841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 4 | 1876 | 7.4 | 7.4 | 9.3583 | 10.317 | 15 | 85 | 85 | 0 | 0 | -24.5203 | 55.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 5 | 1877 | 6.9 | 6.9 | 9.3583 | 10.317 | 15 | 85 | 85 | 0 | 0 | -16.4101 | 68.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 6 | 1878 | 7.4 | 7.4 | 9.3583 | 10.317 | 15 | 87 | 87 | 0 | 0 | -7.5358 | 80.9123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 7 | 1879 | 7.5 | 7.5 | 9.3583 | 10.317 | 15 | 91 | 91 | 0 | 0 | 1.6483 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 20 | 8 | 1880 | 7.6 | 7.6 | 9.3583 | 10.317 | 15 | 95 | 95 | 0.27985 | 5.9744 | 10.7381 | 104.815 | 0 | 0.1879 | 0.2794 | 0.20723 | 0.013665 | 0 | 0 | 0 | 0.025638 | 2.8355 | 2.8355 | 2.8355 | 2.8355 | 2.8355 | 2.8355 | 2.8355 | 2.8355 | 5.9744 | 2.8355 | 3.0234 | 3.1149 | 3.0428 | 2.8492 | 2.8355 | 2.8355 | 2.8355 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 9 | 1881 | 8.9 | 8.9 | 9.3583 | 10.317 | 15 | 96 | 96 | 0.13179 | 10.9677 | 19.3166 | 117.5714 | 0 | 0.065105 | 0.12518 | 0.11193 | 0.033109 | 0 | 0 | 0 | 0.032256 | 5.1279 | 5.1279 | 5.1279 | 5.1279 | 5.1279 | 5.1279 | 5.1279 | 5.1279 | 10.9677 | 5.1279 | 5.193 | 5.2531 | 5.2398 | 5.161 | 5.1279 | 5.1279 | 5.1279 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 10 | 1882 | 10.6 | 10.6 | 9.3583 | 10.317 | 15 | 94 | 94 | 0.21772 | 21.9171 | 26.8926 | 131.6674 | 0 | 0.06154 | 0.18213 | 0.19603 | 0.0951 | 0 | 0 | 0 | 0.082916 | 10.3347 | 10.3347 | 10.3347 | 10.3347 | 10.3347 | 10.3347 | 10.3347 | 10.3347 | 21.9171 | 10.3347 | 10.3962 | 10.5168 | 10.5307 | 10.4298 | 10.3347 | 10.3347 | 10.3347 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 11 | 1883 | 11.7 | 11.7 | 9.3583 | 10.317 | 15 | 88 | 88 | 1.7783 | 80.1275 | 32.8631 | 147.5638 | 0 | 0.092198 | 1.1848 | 1.5833 | 1.0544 | 0 | 0 | 0 | 0.87249 | 39.1994 | 39.1994 | 39.1994 | 39.1994 | 39.1994 | 39.1994 | 39.1994 | 39.1994 | 80.1275 | 39.1994 | 39.2916 | 40.3842 | 40.7827 | 40.2538 | 39.1994 | 39.1994 | 39.1994 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 12 | 1884 | 11.8 | 11.8 | 9.3583 | 10.317 | 15 | 89 | 89 | 2.2835 | 104.7062 | 36.5537 | 165.2798 | 0 | 0 | 1.0288 | 1.8722 | 1.6189 | 0.41724 | 0 | 0 | 1.2938 | 51.6644 | 51.6644 | 51.6644 | 51.6644 | 51.6644 | 51.6644 | 51.6644 | 51.6644 | 104.7062 | 51.6644 | 51.6644 | 52.6932 | 53.5366 | 53.2833 | 52.0816 | 51.6644 | 51.6644 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 13 | 1885 | 11.9 | 11.9 | 9.3583 | 10.317 | 15 | 89 | 89 | 0.31595 | 41.8093 | 37.4117 | 184.0574 | 0 | 0 | 0.064491 | 0.21918 | 0.24547 | 0.12797 | 0 | 0 | 0.19069 | 19.9799 | 19.9799 | 19.9799 | 19.9799 | 19.9799 | 19.9799 | 19.9799 | 19.9799 | 41.8093 | 19.9799 | 19.9799 | 20.0443 | 20.199 | 20.2253 | 20.1078 | 19.9799 | 19.9799 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 14 | 1886 | 11.4 | 11.4 | 9.3583 | 10.317 | 15 | 95 | 95 | 0.27663 | 38.8343 | 35.2893 | 202.5247 | 0 | 0 | 0 | 0.14399 | 0.21918 | 0.16598 | 0.015547 | 0 | 0.16569 | 18.5363 | 18.5363 | 18.5363 | 18.5363 | 18.5363 | 18.5363 | 18.5363 | 18.5363 | 38.8343 | 18.5363 | 18.5363 | 18.5363 | 18.6803 | 18.7555 | 18.7023 | 18.5519 | 18.5363 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 15 | 1887 | 12.1 | 12.1 | 9.3583 | 10.317 | 15 | 91 | 91 | 0.32441 | 38.8206 | 30.5381 | 219.5016 | 0 | 0 | 0 | 0.10123 | 0.2446 | 0.24468 | 0.10144 | 0 | 0.17942 | 18.5203 | 18.5203 | 18.5203 | 18.5203 | 18.5203 | 18.5203 | 18.5203 | 18.5203 | 38.8206 | 18.5203 | 18.5203 | 18.5203 | 18.6216 | 18.7649 | 18.765 | 18.6218 | 18.5203 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 16 | 1888 | 12 | 12 | 9.3583 | 10.317 | 15 | 91 | 91 | 0.38419 | 35.8198 | 23.7969 | 234.5874 | 0 | 0 | 0 | 0.031707 | 0.25533 | 0.32938 | 0.21049 | 0 | 0.18024 | 17.0489 | 17.0489 | 17.0489 | 17.0489 | 17.0489 | 17.0489 | 17.0489 | 17.0489 | 35.8198 | 17.0489 | 17.0489 | 17.0489 | 17.0806 | 17.3043 | 17.3783 | 17.2594 | 17.0489 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 17 | 1889 | 11.9 | 11.9 | 9.3583 | 10.317 | 15 | 92 | 92 | 0.033539 | 7.9882 | 15.7233 | 248.0387 | 0 | 0 | 0 | 0 | 0.017782 | 0.030259 | 0.02501 | 0.005111 | 0.011834 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 7.9882 | 3.7286 | 3.7286 | 3.7286 | 3.7286 | 3.7464 | 3.7589 | 3.7536 | 3.7337 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 20 | 18 | 1890 | 12.1 | 12.1 | 9.3583 | 10.317 | 15 | 88 | 88 | 0.092769 | 7.9803 | 6.8706 | 260.4013 | 0 | 0 | 0 | 0 | 0.033396 | 0.082176 | 0.082818 | 0.034947 | 0.019682 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 7.9803 | 3.7142 | 3.7142 | 3.7142 | 3.7142 | 3.7476 | 3.7964 | 3.7971 | 3.7492 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 19 | 1891 | 12.4 | 12.4 | 9.3583 | 10.317 | 15 | 83 | 83 | 0.18299 | 2.9896 | -2.3086 | 272.2865 | 0 | 0 | 0 | 0 | 0.030294 | 0.14809 | 0.17913 | 0.10524 | 0.010366 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 2.9896 | 1.3809 | 1.3809 | 1.3809 | 1.3809 | 1.4112 | 1.529 | 1.56 | 1.4861 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 20 | 1892 | 12.1 | 12.1 | 9.3583 | 10.317 | 15 | 81 | 81 | 0 | 0 | -11.4106 | 284.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 21 | 1893 | 11.7 | 11.7 | 9.3583 | 10.317 | 15 | 81 | 81 | 0 | 0 | -20.0174 | 297.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 22 | 1894 | 11.1 | 11.1 | 9.3583 | 10.317 | 15 | 79 | 79 | 0 | 0 | -27.635 | 311.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 23 | 1895 | 10.5 | 10.5 | 9.3583 | 10.317 | 15 | 75 | 75 | 0 | 0 | -33.6524 | 327.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 20 | 24 | 1896 | 10.3 | 10.3 | 10.1083 | 10.3921 | 15 | 67 | 67 | 0 | 0 | -37.3797 | 345.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 1 | 1897 | 9.5 | 9.5 | 10.1083 | 10.3921 | 15 | 68 | 68 | 0 | 0 | -38.2473 | 4.1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 2 | 1898 | 8.7 | 8.7 | 10.1083 | 10.3921 | 15 | 72 | 72 | 0 | 0 | -35.6984 | 22.7454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 3 | 1899 | 8.3 | 8.3 | 10.1083 | 10.3921 | 15 | 71 | 71 | 0 | 0 | -30.9123 | 39.7855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 4 | 1900 | 8.1 | 8.1 | 10.1083 | 10.3921 | 15 | 71 | 71 | 0 | 0 | -24.1385 | 54.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 5 | 1901 | 7.7 | 7.7 | 10.1083 | 10.3921 | 15 | 71 | 71 | 0 | 0 | -16.0403 | 68.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 6 | 1902 | 7.7 | 7.7 | 10.1083 | 10.3921 | 15 | 71 | 71 | 0 | 0 | -7.1734 | 80.7323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 7 | 1903 | 7.3 | 7.3 | 10.1083 | 10.3921 | 15 | 74 | 74 | 0 | 3 | 2.009 | 92.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 21 | 8 | 1904 | 7.9 | 7.9 | 10.1083 | 10.3921 | 15 | 73 | 73 | 127.5665 | 45.6185 | 11.1033 | 104.6389 | 0 | 85.9356 | 127.355 | 94.1716 | 5.8237 | 0 | 0 | 0 | 12.3815 | 21.3191 | 33.539 | 39.4287 | 34.7101 | 22.1472 | 21.3191 | 21.3191 | 21.3191 | 45.6185 | 21.3191 | 119.4746 | 166.7838 | 128.8817 | 27.9709 | 21.3191 | 21.3191 | 21.3191 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 9 | 1905 | 9.1 | 9.1 | 10.1083 | 10.3921 | 15 | 67 | 67 | 603.3545 | 74.0438 | 19.6914 | 117.4115 | 0 | 299.2557 | 572.8411 | 510.8639 | 149.6296 | 0 | 0 | 0 | 150.9562 | 50.8831 | 93.9717 | 133.3641 | 124.4403 | 72.4276 | 50.8831 | 50.8831 | 50.8831 | 74.0438 | 50.8831 | 393.2274 | 706.2052 | 635.3042 | 222.0572 | 50.8831 | 50.8831 | 50.8831 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 10 | 1906 | 8.9 | 8.9 | 10.1083 | 10.3921 | 15 | 66 | 66 | 190.1149 | 179.5601 | 27.2805 | 131.5406 | 0 | 54.0892 | 158.9 | 170.6293 | 82.4063 | 0 | 0 | 0 | 73.4399 | 87.3641 | 127.4616 | 205.1602 | 213.8554 | 148.4537 | 87.3641 | 87.3641 | 87.3641 | 179.5601 | 87.3641 | 181.5508 | 364.0602 | 384.4847 | 230.86 | 87.3641 | 87.3641 | 87.3641 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 11 | 1907 | 9.9 | 9.9 | 10.1083 | 10.3921 | 15 | 63 | 63 | 226.7636 | 226.5072 | 33.263 | 147.4956 | 0 | 12.1611 | 150.8509 | 201.1743 | 133.6525 | 0 | 0 | 0 | 112.4928 | 111.3219 | 118.9974 | 206.5308 | 238.2921 | 195.676 | 111.3219 | 111.3219 | 111.3219 | 226.5072 | 111.3219 | 131.1585 | 357.3817 | 439.4664 | 329.3285 | 111.3219 | 111.3219 | 111.3219 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 12 | 1908 | 10.7 | 10.7 | 10.1083 | 10.3921 | 15 | 59 | 59 | 264.0516 | 254.9478 | 36.9574 | 165.2986 | 0 | 0 | 118.6446 | 215.5599 | 186.2031 | 47.771 | 0 | 0 | 151.0522 | 126.1673 | 126.1673 | 202.6968 | 265.2102 | 246.2741 | 156.9811 | 126.1673 | 126.1673 | 254.9478 | 126.1673 | 126.1673 | 321.3414 | 480.77 | 432.4772 | 204.7522 | 126.1673 | 126.1673 | 406 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 13 | 1909 | 9.9 | 9.9 | 10.1083 | 10.3921 | 15 | 66 | 66 | 14.4986 | 224.1702 | 37.8043 | 184.1776 | 0 | 0 | 2.9402 | 10.0031 | 11.2063 | 5.845 | 0 | 0 | 8.8298 | 106.5602 | 106.5602 | 113.4578 | 130.0271 | 132.8497 | 120.2724 | 106.5602 | 106.5602 | 224.1702 | 106.5602 | 106.5602 | 116.398 | 140.0302 | 144.0561 | 126.1174 | 106.5602 | 106.5602 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 14 | 1910 | 10.4 | 10.4 | 10.1083 | 10.3921 | 15 | 61 | 61 | 22.5803 | 239.3525 | 35.6561 | 202.7326 | 0 | 0 | 0 | 11.6629 | 17.7935 | 13.5009 | 1.2997 | 0 | 13.6475 | 113.1478 | 113.1478 | 113.1478 | 134.3598 | 145.5099 | 137.7027 | 115.5116 | 113.1478 | 239.3525 | 113.1478 | 113.1478 | 113.1478 | 146.0226 | 163.3034 | 151.2037 | 116.8113 | 113.1478 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 15 | 1911 | 11.3 | 11.3 | 10.1083 | 10.3921 | 15 | 57 | 57 | 77.8897 | 256.4954 | 30.8723 | 219.7656 | 0 | 0 | 0 | 23.9816 | 58.3714 | 58.5681 | 24.4564 | 0 | 43.5046 | 118.2324 | 118.2324 | 118.2324 | 149.4844 | 194.3001 | 194.5564 | 150.1031 | 118.2324 | 256.4954 | 118.2324 | 118.2324 | 118.2324 | 173.4659 | 252.6715 | 253.1245 | 174.5595 | 118.2324 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 16 | 1912 | 11.1 | 11.1 | 10.1083 | 10.3921 | 15 | 63 | 63 | 116.5868 | 222.6691 | 24.1008 | 234.8786 | 0 | 0 | 0 | 9.1293 | 76.9191 | 99.6507 | 64.0083 | 0 | 55.3309 | 105.2683 | 105.2683 | 105.2683 | 115.1795 | 188.7753 | 213.4539 | 174.7587 | 105.2683 | 222.6691 | 105.2683 | 105.2683 | 105.2683 | 124.3088 | 265.6944 | 313.1046 | 238.767 | 105.2683 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 17 | 1913 | 10.2 | 10.2 | 10.1083 | 10.3921 | 15 | 71 | 71 | 258.7703 | 160.2831 | 16.0045 | 248.3403 | 0 | 0 | 0 | 0 | 135.8957 | 232.7107 | 193.2069 | 40.5251 | 92.7169 | 84.4465 | 84.4465 | 84.4465 | 84.4465 | 151.7714 | 199.7351 | 180.1643 | 104.5233 | 160.2831 | 84.4465 | 84.4465 | 84.4465 | 84.4465 | 287.6671 | 432.4458 | 373.3712 | 145.0485 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 21 | 18 | 1914 | 9.7 | 9.7 | 10.1083 | 10.3921 | 15 | 69 | 69 | 7.8486 | 70.2921 | 7.1387 | 260.7057 | 0 | 0 | 0 | 0 | 2.7846 | 6.927 | 7.0117 | 2.989 | 1.7079 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 70.2921 | 34.9278 | 34.9278 | 34.9278 | 34.9278 | 37.7124 | 41.8548 | 41.9395 | 37.9168 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 19 | 1915 | 8.4 | 8.4 | 10.1083 | 10.3921 | 15 | 75 | 75 | 0.60956 | 5.9622 | -2.0435 | 272.5914 | 0 | 0 | 0 | 0 | 0.097684 | 0.49114 | 0.59689 | 0.35299 | 0.037848 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 5.9622 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.871 | 3.2645 | 3.3703 | 3.1264 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 20 | 1916 | 7.2 | 7.2 | 10.1083 | 10.3921 | 15 | 75 | 75 | 0 | 0 | -11.1383 | 284.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 21 | 1917 | 7.9 | 7.9 | 10.1083 | 10.3921 | 15 | 81 | 81 | 0 | 0 | -19.7279 | 297.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 22 | 1918 | 6.8 | 6.8 | 10.1083 | 10.3921 | 15 | 83 | 83 | 0 | 0 | -27.3192 | 311.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 23 | 1919 | 6.5 | 6.5 | 10.1083 | 10.3921 | 15 | 79 | 79 | 0 | 0 | -33.3042 | 327.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 21 | 24 | 1920 | 5.8 | 5.8 | 8.7083 | 9.9711 | 15 | 83 | 83 | 0 | 0 | -37.0005 | 345.2901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 1 | 1921 | 5.6 | 5.6 | 8.7083 | 9.9711 | 15 | 83 | 83 | 0 | 0 | -37.8479 | 4.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 2 | 1922 | 5 | 5 | 8.7083 | 9.9711 | 15 | 91 | 91 | 0 | 0 | -35.295 | 22.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 3 | 1923 | 6.9 | 6.9 | 8.7083 | 9.9711 | 15 | 82 | 82 | 0 | 0 | -30.5172 | 39.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 4 | 1924 | 6.5 | 6.5 | 8.7083 | 9.9711 | 15 | 82 | 82 | 0 | 0 | -23.7565 | 54.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 5 | 1925 | 7.2 | 7.2 | 8.7083 | 9.9711 | 15 | 76 | 76 | 0 | 0 | -15.6702 | 68.1981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 6 | 1926 | 6.5 | 6.5 | 8.7083 | 9.9711 | 15 | 76 | 76 | 0 | 0 | -6.8108 | 80.5532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 7 | 1927 | 3.5 | 3.5 | 8.7083 | 9.9711 | 15 | 91 | 91 | 0 | 0 | 2.37 | 92.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 22 | 8 | 1928 | 3.5 | 3.5 | 8.7083 | 9.9711 | 15 | 94 | 94 | 0.22382 | 5.9771 | 11.4684 | 104.463 | 0 | 0.15126 | 0.22342 | 0.16471 | 0.0095082 | 0 | 0 | 0 | 0.02294 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | 2.8194 | 5.9771 | 2.8194 | 2.9706 | 3.0428 | 2.9841 | 2.8289 | 2.8194 | 2.8194 | 2.8194 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 9 | 1929 | 5.1 | 5.1 | 8.7083 | 9.9711 | 15 | 94 | 94 | 0.1959 | 13.9499 | 20.0662 | 117.2515 | 0 | 0.09755 | 0.18591 | 0.16536 | 0.047951 | 0 | 0 | 0 | 0.050079 | 6.5471 | 6.5471 | 6.5471 | 6.5471 | 6.5471 | 6.5471 | 6.5471 | 6.5471 | 13.9499 | 6.5471 | 6.6447 | 6.733 | 6.7125 | 6.5951 | 6.5471 | 6.5471 | 6.5471 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 10 | 1930 | 7.1 | 7.1 | 8.7083 | 9.9711 | 15 | 88 | 88 | 5.8266 | 114.7175 | 27.6683 | 131.4136 | 0 | 1.6684 | 4.8655 | 5.2124 | 2.506 | 0 | 0 | 0 | 2.2825 | 54.9596 | 60.5426 | 71.2412 | 72.4023 | 63.3457 | 54.9596 | 54.9596 | 54.9596 | 114.7175 | 54.9596 | 62.2109 | 76.1067 | 77.6147 | 65.8518 | 54.9596 | 54.9596 | 54.9596 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 11 | 1931 | 7.8 | 7.8 | 8.7083 | 9.9711 | 15 | 78 | 78 | 21.6034 | 197.1656 | 33.6628 | 147.4274 | 0 | 1.1968 | 14.3489 | 19.0956 | 12.6563 | 0 | 0 | 0 | 10.8344 | 90.86 | 93.9329 | 127.7009 | 139.888 | 123.3552 | 90.86 | 90.86 | 90.86 | 197.1656 | 90.86 | 95.1297 | 142.0498 | 158.9836 | 136.0115 | 90.86 | 90.86 | 90.86 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 12 | 1932 | 7.9 | 7.9 | 8.7083 | 9.9711 | 15 | 75 | 75 | 38.812 | 246.5864 | 37.361 | 165.3184 | 0 | 0 | 17.3913 | 31.5469 | 27.2227 | 6.9519 | 0 | 0 | 22.4136 | 111.9565 | 111.9565 | 157.0649 | 193.7806 | 182.5649 | 129.9877 | 111.9565 | 111.9565 | 246.5864 | 111.9565 | 111.9565 | 174.4562 | 225.3275 | 209.7876 | 136.9396 | 111.9565 | 111.9565 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 13 | 1933 | 9.3 | 9.3 | 8.7083 | 9.9711 | 15 | 69 | 69 | 106.9085 | 287.3105 | 38.1965 | 184.2999 | 0 | 0 | 21.5365 | 73.3523 | 82.1994 | 42.8952 | 0 | 0 | 65.6895 | 132.0045 | 132.0045 | 155.7279 | 212.8055 | 222.5509 | 179.2555 | 132.0045 | 132.0045 | 287.3105 | 132.0045 | 132.0045 | 177.2643 | 286.1578 | 304.7503 | 222.1507 | 132.0045 | 132.0045 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 14 | 1934 | 9.1 | 9.1 | 8.7083 | 9.9711 | 15 | 65 | 65 | 547.9963 | 196.8125 | 36.0221 | 202.9431 | 0 | 0 | 0 | 280.8381 | 429.4552 | 326.5032 | 32.2901 | 0 | 334.1875 | 120.1264 | 120.1264 | 120.1264 | 197.899 | 239.0556 | 210.5451 | 129.0685 | 120.1264 | 196.8125 | 120.1264 | 120.1264 | 120.1264 | 478.7371 | 668.5108 | 537.0483 | 161.3586 | 120.1264 | 531 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 15 | 1935 | 8.2 | 8.2 | 8.7083 | 9.9711 | 15 | 70 | 70 | 26.7318 | 228.9239 | 31.2055 | 220.0319 | 0 | 0 | 0 | 8.119 | 19.9101 | 20.038 | 8.428 | 0 | 15.0761 | 108.3703 | 108.3703 | 108.3703 | 120.6837 | 138.566 | 138.76 | 121.1522 | 108.3703 | 228.9239 | 108.3703 | 108.3703 | 108.3703 | 128.8027 | 158.476 | 158.7981 | 129.5802 | 108.3703 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 16 | 1936 | 8.4 | 8.4 | 8.7083 | 9.9711 | 15 | 67 | 67 | 169.7465 | 224.5176 | 24.4037 | 235.1717 | 0 | 0 | 0 | 12.5734 | 111.1675 | 144.6412 | 93.3861 | 0 | 81.4824 | 108.6193 | 108.6193 | 108.6193 | 118.0267 | 191.7946 | 216.8395 | 178.4905 | 108.6193 | 224.5176 | 108.6193 | 108.6193 | 108.6193 | 130.6001 | 302.9621 | 361.4807 | 271.8766 | 108.6193 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 17 | 1937 | 8.5 | 8.5 | 8.7083 | 9.9711 | 15 | 64 | 64 | 232.5609 | 165.4101 | 16.2848 | 248.643 | 0 | 0 | 0 | 0 | 120.9535 | 208.4547 | 173.8459 | 37.4006 | 84.5899 | 85.7117 | 85.7117 | 85.7117 | 85.7117 | 153.6661 | 202.8261 | 183.3822 | 106.7242 | 165.4101 | 85.7117 | 85.7117 | 85.7117 | 85.7117 | 274.6196 | 411.2809 | 357.2281 | 144.1247 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 22 | 18 | 1938 | 7.5 | 7.5 | 8.7083 | 9.9711 | 15 | 72 | 72 | 75.6054 | 102.1369 | 7.4062 | 261.0108 | 0 | 0 | 0 | 0 | 26.4292 | 66.4806 | 67.5885 | 29.104 | 16.8631 | 50.9249 | 50.9249 | 50.9249 | 50.9249 | 77.6738 | 118.2097 | 119.3311 | 80.381 | 102.1369 | 50.9249 | 50.9249 | 50.9249 | 50.9249 | 104.103 | 184.6903 | 186.9196 | 109.485 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 19 | 1939 | 6.4 | 6.4 | 8.7083 | 9.9711 | 15 | 78 | 78 | 2.8073 | 13.8104 | -1.7788 | 272.8966 | 0 | 0 | 0 | 0 | 0.43497 | 2.2519 | 2.7497 | 1.6367 | 0.18957 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 13.8104 | 6.5384 | 6.5384 | 6.5384 | 6.5384 | 6.9734 | 8.7903 | 9.288 | 8.1751 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 20 | 1940 | 5.6 | 5.6 | 8.7083 | 9.9711 | 15 | 83 | 83 | 0 | 0 | -10.8662 | 284.9165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 21 | 1941 | 5.5 | 5.5 | 8.7083 | 9.9711 | 15 | 85 | 85 | 0 | 0 | -19.4384 | 297.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 22 | 1942 | 4.3 | 4.3 | 8.7083 | 9.9711 | 15 | 92 | 92 | 0 | 0 | -27.0032 | 311.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 23 | 1943 | 2.3 | 2.3 | 8.7083 | 9.9711 | 15 | 95 | 95 | 0 | 0 | -32.9559 | 327.7225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 22 | 24 | 1944 | 1.4 | 1.4 | 6.2125 | 8.8593 | 15 | 96 | 96 | 0 | 0 | -36.6213 | 345.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 1 | 1945 | 0.3 | 0.3 | 6.2125 | 8.8593 | 15 | 97 | 97 | 0 | 0 | -37.4486 | 4.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 2 | 1946 | -0.5 | -0.5 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 0 | -34.8918 | 22.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 3 | 1947 | -0.6 | -0.6 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 0 | -30.1221 | 39.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 4 | 1948 | -0.5 | -0.5 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 0 | -23.3745 | 54.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 5 | 1949 | -1 | -1 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 0 | -15.3 | 68.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 6 | 1950 | -1.2 | -1.2 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 0 | -6.4481 | 80.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 7 | 1951 | -1 | -1 | 6.2125 | 8.8593 | 15 | 98 | 98 | 0 | 3 | 2.7309 | 92.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 23 | 8 | 1952 | 0.2 | 0.2 | 6.2125 | 8.8593 | 15 | 99 | 99 | 6.2155 | 32.3292 | 11.8335 | 104.2872 | 0 | 4.2138 | 6.2036 | 4.5595 | 0.24439 | 0 | 0 | 0 | 0.67082 | 13.5405 | 69.6426 | 96.1347 | 74.2442 | 16.7943 | 13.5405 | 13.5405 | 13.5405 | 32.3292 | 13.5405 | 73.8564 | 102.3383 | 78.8036 | 17.0387 | 13.5405 | 13.5405 | 13.5405 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 9 | 1953 | 3.5 | 3.5 | 6.2125 | 8.8593 | 15 | 99 | 99 | 19.4761 | 100.9158 | 20.4407 | 117.0913 | 0 | 9.7357 | 18.4726 | 16.3885 | 4.7042 | 0 | 0 | 0 | 5.0842 | 44.3903 | 87.9602 | 127.0602 | 117.7332 | 65.443 | 44.3903 | 44.3903 | 44.3903 | 100.9158 | 44.3903 | 97.6959 | 145.5328 | 134.1217 | 70.1472 | 44.3903 | 44.3903 | 44.3903 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 10 | 1954 | 5.9 | 5.9 | 6.2125 | 8.8593 | 15 | 96 | 96 | 74.2598 | 181.5085 | 28.0559 | 131.2863 | 0 | 21.3972 | 61.9494 | 66.2125 | 31.6892 | 0 | 0 | 0 | 29.4915 | 83.576 | 115.3752 | 175.6416 | 181.9772 | 130.6707 | 83.576 | 83.576 | 83.576 | 181.5085 | 83.576 | 136.7724 | 237.591 | 248.1897 | 162.3599 | 83.576 | 83.576 | 83.576 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 11 | 1955 | 7.3 | 7.3 | 6.2125 | 8.8593 | 15 | 72 | 72 | 336.9801 | 212.1779 | 34.0625 | 147.3592 | 0 | 19.2617 | 223.459 | 296.757 | 196.2188 | 0 | 0 | 0 | 170.8221 | 112.6264 | 121.2928 | 213.1664 | 246.145 | 200.9103 | 112.6264 | 112.6264 | 112.6264 | 212.1779 | 112.6264 | 140.5545 | 436.6254 | 542.902 | 397.1291 | 112.6264 | 112.6264 | 112.6264 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 12 | 1956 | 8.5 | 8.5 | 6.2125 | 8.8593 | 15 | 67 | 67 | 316.1559 | 248.7146 | 37.7642 | 165.3389 | 0 | 0 | 141.2676 | 255.8424 | 220.5481 | 56.0598 | 0 | 0 | 184.2854 | 127.0687 | 127.0687 | 201.9185 | 262.6253 | 243.9249 | 156.7717 | 127.0687 | 127.0687 | 248.7146 | 127.0687 | 127.0687 | 343.1862 | 518.4677 | 464.473 | 212.8314 | 127.0687 | 127.0687 | 433 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 13 | 1957 | 6.8 | 6.8 | 6.2125 | 8.8593 | 15 | 79 | 79 | 237.3488 | 280.8798 | 38.5882 | 184.424 | 0 | 0 | 47.49 | 161.9372 | 181.5238 | 94.7762 | 0 | 0 | 147.1202 | 136.4223 | 136.4223 | 166.5491 | 239.1524 | 251.5778 | 196.5467 | 136.4223 | 136.4223 | 280.8798 | 136.4223 | 136.4223 | 214.0392 | 401.0896 | 433.1016 | 291.3229 | 136.4223 | 136.4223 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 14 | 1958 | 7.7 | 7.7 | 6.2125 | 8.8593 | 15 | 70 | 70 | 237.7646 | 278.7184 | 36.3874 | 203.156 | 0 | 0 | 0 | 120.8862 | 185.2946 | 141.16 | 14.3357 | 0 | 146.2816 | 135.6891 | 135.6891 | 135.6891 | 210.4888 | 250.3423 | 223.0335 | 144.5595 | 135.6891 | 278.7184 | 135.6891 | 135.6891 | 135.6891 | 331.375 | 435.637 | 364.1935 | 158.8953 | 135.6891 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 15 | 1959 | 8.4 | 8.4 | 6.2125 | 8.8593 | 15 | 58 | 58 | 313.4366 | 243.5357 | 31.5376 | 220.3004 | 0 | 0 | 0 | 93.8851 | 231.9963 | 234.2073 | 99.2228 | 0 | 178.4643 | 124.1104 | 124.1104 | 124.1104 | 173.5034 | 246.164 | 247.3272 | 176.3116 | 124.1104 | 243.5357 | 124.1104 | 124.1104 | 124.1104 | 267.3885 | 478.1603 | 481.5344 | 275.5344 | 124.1104 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 16 | 1960 | 9.7 | 9.7 | 6.2125 | 8.8593 | 15 | 53 | 53 | 582.2208 | 148.3721 | 24.7054 | 235.4664 | 0 | 0 | 0 | 40.6567 | 378.4529 | 494.5566 | 320.9557 | 0 | 282.6279 | 96.2646 | 96.2646 | 96.2646 | 104.5478 | 173.3691 | 197.0236 | 161.6548 | 96.2646 | 148.3721 | 96.2646 | 96.2646 | 96.2646 | 145.2045 | 551.822 | 691.5801 | 482.6105 | 96.2646 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 17 | 1961 | 8.4 | 8.4 | 6.2125 | 8.8593 | 15 | 63 | 63 | 551.6855 | 118.3481 | 16.5641 | 248.9467 | 0 | 0 | 0 | 0 | 284.1191 | 492.8501 | 412.8762 | 91.045 | 203.6519 | 76.7704 | 76.7704 | 76.7704 | 76.7704 | 131.7603 | 172.1592 | 156.6806 | 94.3917 | 118.3481 | 76.7704 | 76.7704 | 76.7704 | 76.7704 | 415.8794 | 665.0093 | 569.5568 | 185.4367 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 23 | 18 | 1962 | 6.1 | 6.1 | 6.2125 | 8.8593 | 15 | 75 | 75 | 24.3634 | 91.4339 | 7.6728 | 261.3164 | 0 | 0 | 0 | 0 | 8.389 | 21.3422 | 21.7935 | 9.4784 | 5.5661 | 44.6563 | 44.6563 | 44.6563 | 44.6563 | 58.4835 | 79.8337 | 80.5774 | 60.2791 | 91.4339 | 44.6563 | 44.6563 | 44.6563 | 44.6563 | 66.8725 | 101.1759 | 102.3709 | 69.7575 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 19 | 1963 | 5.7 | 5.7 | 6.2125 | 8.8593 | 15 | 78 | 78 | 2.4063 | 13.8244 | -1.5146 | 273.2018 | 0 | 0 | 0 | 0 | 0.36004 | 1.9215 | 2.3574 | 1.4123 | 0.17556 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 13.8244 | 6.5391 | 6.5391 | 6.5391 | 6.5391 | 6.8992 | 8.4607 | 8.8965 | 7.9515 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 20 | 1964 | 5.1 | 5.1 | 6.2125 | 8.8593 | 15 | 81 | 81 | 0 | 0 | -10.5943 | 285.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 21 | 1965 | 3.6 | 3.6 | 6.2125 | 8.8593 | 15 | 90 | 90 | 0 | 0 | -19.1489 | 297.9831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 22 | 1966 | 2.3 | 2.3 | 6.2125 | 8.8593 | 15 | 94 | 94 | 0 | 0 | -26.6871 | 312.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 23 | 1967 | 1.6 | 1.6 | 6.2125 | 8.8593 | 15 | 96 | 96 | 0 | 0 | -32.6076 | 327.9651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 23 | 24 | 1968 | 1.5 | 1.5 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 0 | -36.2422 | 345.6359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 1 | 1969 | 1.3 | 1.3 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 0 | -37.0495 | 4.3326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 2 | 1970 | 1.2 | 1.2 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 0 | -34.4889 | 22.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 3 | 1971 | 0.5 | 0.5 | 3.6583 | 7.3055 | 15 | 99 | 99 | 0 | 0 | -29.7273 | 39.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 4 | 1972 | 0.4 | 0.4 | 3.6583 | 7.3055 | 15 | 99 | 99 | 0 | 0 | -22.9925 | 54.4765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 5 | 1973 | -0.7 | -0.7 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 0 | -14.9299 | 67.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 6 | 1974 | -1 | -1 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 0 | -6.0855 | 80.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 7 | 1975 | -0.8 | -0.8 | 3.6583 | 7.3055 | 15 | 98 | 98 | 0 | 3 | 3.0916 | 92.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 24 | 8 | 1976 | 1.8 | 1.8 | 3.6583 | 7.3055 | 15 | 99 | 99 | 167.8194 | 52.9786 | 12.1982 | 104.1115 | 0 | 114.1243 | 167.4653 | 122.7073 | 6.0691 | 0 | 0 | 0 | 19.0214 | 25.9459 | 55.2812 | 68.9923 | 57.4874 | 27.5059 | 25.9459 | 25.9459 | 25.9459 | 52.9786 | 25.9459 | 169.4055 | 236.4575 | 180.1947 | 33.575 | 25.9459 | 25.9459 | 25.9459 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 9 | 1977 | 4.7 | 4.7 | 3.6583 | 7.3055 | 15 | 99 | 99 | 232.65 | 121.0102 | 20.815 | 116.9309 | 0 | 116.7387 | 220.5352 | 195.1451 | 55.4417 | 0 | 0 | 0 | 61.9898 | 63.1885 | 120.8318 | 172.0844 | 159.5473 | 90.5646 | 63.1885 | 63.1885 | 63.1885 | 121.0102 | 63.1885 | 237.5704 | 392.6195 | 354.6924 | 146.0063 | 63.1885 | 63.1885 | 63.1885 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 10 | 1978 | 6 | 6 | 3.6583 | 7.3055 | 15 | 99 | 99 | 23.0772 | 159.7108 | 28.4431 | 131.1586 | 0 | 6.6906 | 19.2318 | 20.5072 | 9.7699 | 0 | 0 | 0 | 9.2892 | 72.3276 | 91.7421 | 128.1338 | 131.835 | 100.6775 | 72.3276 | 72.3276 | 72.3276 | 159.7108 | 72.3276 | 98.4327 | 147.3656 | 152.3422 | 110.4474 | 72.3276 | 72.3276 | 72.3276 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 11 | 1979 | 6.1 | 6.1 | 3.6583 | 7.3055 | 15 | 83 | 83 | 7.7995 | 165.0044 | 34.4617 | 147.291 | 0 | 0.45945 | 5.1633 | 6.8426 | 4.5136 | 0 | 0 | 0 | 3.9956 | 78.9279 | 80.351 | 94.9207 | 100.1221 | 92.9082 | 78.9279 | 78.9279 | 78.9279 | 165.0044 | 78.9279 | 80.8104 | 100.0841 | 106.9647 | 97.4217 | 78.9279 | 78.9279 | 78.9279 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 12 | 1980 | 7 | 7 | 3.6583 | 7.3055 | 15 | 77 | 77 | 3.6508 | 136.8524 | 38.1671 | 165.3603 | 0 | 0 | 1.6266 | 2.9411 | 2.5327 | 0.64077 | 0 | 0 | 2.1476 | 68.5263 | 68.5263 | 68.5263 | 68.5263 | 68.5263 | 68.5263 | 68.5263 | 68.5263 | 136.8524 | 68.5263 | 68.5263 | 70.1529 | 71.4674 | 71.0591 | 69.1671 | 68.5263 | 68.5263 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 13 | 1981 | 7.1 | 7.1 | 3.6583 | 7.3055 | 15 | 72 | 72 | 3.373 | 139.8912 | 38.9793 | 184.5499 | 0 | 0 | 0.67024 | 2.2882 | 2.5658 | 1.3404 | 0 | 0 | 2.1088 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 139.8912 | 69.93 | 69.93 | 70.6002 | 72.2182 | 72.4958 | 71.2704 | 69.93 | 69.93 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 14 | 1982 | 6.3 | 6.3 | 3.6583 | 7.3055 | 15 | 78 | 78 | 1.6977 | 98.9464 | 36.7517 | 203.3711 | 0 | 0 | 0 | 0.85625 | 1.3156 | 1.0043 | 0.10469 | 0 | 1.0536 | 48.5523 | 48.5523 | 48.5523 | 48.5523 | 48.5523 | 48.5523 | 48.5523 | 48.5523 | 98.9464 | 48.5523 | 48.5523 | 48.5523 | 49.4086 | 49.868 | 49.5567 | 48.657 | 48.5523 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 15 | 1983 | 8 | 8 | 3.6583 | 7.3055 | 15 | 65 | 65 | 20.6388 | 224.1379 | 31.8687 | 220.571 | 0 | 0 | 0 | 6.0953 | 15.1798 | 15.3722 | 6.5598 | 0 | 11.8621 | 106.6966 | 106.6966 | 106.6966 | 116.9912 | 132.3345 | 132.6595 | 117.7757 | 106.6966 | 224.1379 | 106.6966 | 106.6966 | 106.6966 | 123.0864 | 147.5143 | 148.0317 | 124.3355 | 106.6966 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 16 | 1984 | 8.7 | 8.7 | 3.6583 | 7.3055 | 15 | 59 | 59 | 173.0144 | 229.083 | 25.0061 | 235.7625 | 0 | 0 | 0 | 11.3469 | 111.6114 | 146.4954 | 95.5644 | 0 | 84.917 | 110.7433 | 110.7433 | 110.7433 | 119.1744 | 193.6737 | 219.5936 | 181.7504 | 110.7433 | 229.083 | 110.7433 | 110.7433 | 110.7433 | 130.5213 | 305.2851 | 366.089 | 277.3148 | 110.7433 | 314 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 17 | 1985 | 7.3 | 7.3 | 3.6583 | 7.3055 | 15 | 67 | 67 | 22.1706 | 147.6963 | 16.8424 | 249.2514 | 0 | 0 | 0 | 0 | 11.3045 | 19.739 | 16.6107 | 3.752 | 8.3037 | 70.8763 | 70.8763 | 70.8763 | 70.8763 | 83.609 | 93.1091 | 89.5855 | 75.1023 | 147.6963 | 70.8763 | 70.8763 | 70.8763 | 70.8763 | 94.9135 | 112.8481 | 106.1962 | 78.8544 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 18 | 1986 | 7.2 | 7.2 | 3.6583 | 7.3055 | 15 | 66 | 66 | 42.8304 | 100.9835 | 7.9388 | 261.6223 | 0 | 0 | 0 | 0 | 14.5226 | 37.3757 | 38.3346 | 16.8376 | 10.0165 | 49.1922 | 49.1922 | 49.1922 | 49.1922 | 65.3338 | 90.7345 | 91.8003 | 67.9068 | 100.9835 | 49.1922 | 49.1922 | 49.1922 | 49.1922 | 79.8564 | 128.1102 | 130.1348 | 84.7444 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 19 | 1987 | 6.6 | 6.6 | 3.6583 | 7.3055 | 15 | 63 | 63 | 77.5037 | 35.9252 | -1.2508 | 273.507 | 0 | 0 | 0 | 0 | 11.1839 | 61.6072 | 75.9419 | 45.7908 | 6.0748 | 19.6323 | 19.6323 | 19.6323 | 19.6323 | 29.3668 | 73.2557 | 85.7327 | 59.489 | 35.9252 | 19.6323 | 19.6323 | 19.6323 | 19.6323 | 40.5507 | 134.8629 | 161.6745 | 105.2798 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 20 | 1988 | 5 | 5 | 3.6583 | 7.3055 | 15 | 71 | 71 | 0 | 0 | -10.3227 | 285.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 21 | 1989 | 2 | 2 | 3.6583 | 7.3055 | 15 | 83 | 83 | 0 | 0 | -18.8595 | 298.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 22 | 1990 | 2.6 | 2.6 | 3.6583 | 7.3055 | 15 | 88 | 88 | 0 | 0 | -26.3711 | 312.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 23 | 1991 | 1.9 | 1.9 | 3.6583 | 7.3055 | 15 | 90 | 90 | 0 | 0 | -32.2594 | 328.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 24 | 24 | 1992 | 0.5 | 0.5 | 3.7375 | 6.1811 | 15 | 94 | 94 | 0 | 0 | -35.8634 | 345.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 1 | 1993 | 0.1 | 0.1 | 3.7375 | 6.1811 | 15 | 97 | 97 | 0 | 0 | -36.6509 | 4.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 2 | 1994 | -1.2 | -1.2 | 3.7375 | 6.1811 | 15 | 96 | 96 | 0 | 0 | -34.0864 | 22.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 3 | 1995 | -1.2 | -1.2 | 3.7375 | 6.1811 | 15 | 98 | 98 | 0 | 0 | -29.3327 | 39.4053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 4 | 1996 | -0.5 | -0.5 | 3.7375 | 6.1811 | 15 | 98 | 98 | 0 | 0 | -22.6108 | 54.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 5 | 1997 | -0.5 | -0.5 | 3.7375 | 6.1811 | 15 | 98 | 98 | 0 | 0 | -14.56 | 67.7007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 6 | 1998 | -0.4 | -0.4 | 3.7375 | 6.1811 | 15 | 98 | 98 | 0 | 0 | -5.7231 | 80.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 7 | 1999 | 0.2 | 0.2 | 3.7375 | 6.1811 | 15 | 98 | 98 | 0 | 3 | 3.452 | 91.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 25 | 8 | 2000 | 1.6 | 1.6 | 3.7375 | 6.1811 | 15 | 98 | 98 | 23.4663 | 47.2134 | 12.5626 | 103.9358 | 0 | 16.0061 | 23.4109 | 17.1018 | 0.77477 | 0 | 0 | 0 | 2.7866 | 20.6981 | 101.3049 | 138.5951 | 106.8228 | 24.5998 | 20.6981 | 20.6981 | 20.6981 | 47.2134 | 20.6981 | 117.3111 | 162.006 | 123.9246 | 25.3746 | 20.6981 | 20.6981 | 20.6981 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 9 | 2001 | 3.4 | 3.4 | 3.7375 | 6.1811 | 15 | 88 | 88 | 5.8091 | 79.4209 | 21.1888 | 116.7702 | 0 | 2.9257 | 5.5031 | 4.8569 | 1.3655 | 0 | 0 | 0 | 1.5791 | 37.2965 | 51.9425 | 64.8448 | 61.6097 | 44.1323 | 37.2965 | 37.2965 | 37.2965 | 79.4209 | 37.2965 | 54.8682 | 70.3479 | 66.4666 | 45.4979 | 37.2965 | 37.2965 | 37.2965 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 10 | 2002 | 4.4 | 4.4 | 3.7375 | 6.1811 | 15 | 69 | 69 | 20.3882 | 158.6839 | 28.8299 | 131.0305 | 0 | 5.9468 | 16.9724 | 18.0557 | 8.5623 | 0 | 0 | 0 | 8.3161 | 72.2067 | 90.2793 | 123.7862 | 127.0786 | 98.2277 | 72.2067 | 72.2067 | 72.2067 | 158.6839 | 72.2067 | 96.2261 | 140.7586 | 145.1343 | 106.79 | 72.2067 | 72.2067 | 72.2067 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 11 | 2003 | 6.1 | 6.1 | 3.7375 | 6.1811 | 15 | 62 | 62 | 203.5241 | 238.6475 | 34.8605 | 147.2225 | 0 | 12.3428 | 134.5013 | 177.8707 | 117.0459 | 0 | 0 | 0 | 105.3525 | 115.3565 | 124.2697 | 212.4842 | 243.8026 | 199.8791 | 115.3565 | 115.3565 | 115.3565 | 238.6475 | 115.3565 | 136.6124 | 346.9854 | 421.6733 | 316.925 | 115.3565 | 115.3565 | 115.3565 | 344 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 12 | 2004 | 6 | 6 | 3.7375 | 6.1811 | 15 | 60 | 60 | 61.4733 | 266.5096 | 38.5695 | 165.3822 | 0 | 0 | 27.308 | 49.2983 | 42.4103 | 10.6789 | 0 | 0 | 36.4904 | 120.9094 | 120.9094 | 170.2943 | 210.0624 | 197.6059 | 140.2216 | 120.9094 | 120.9094 | 266.5096 | 120.9094 | 120.9094 | 197.6022 | 259.3606 | 240.0161 | 150.9005 | 120.9094 | 120.9094 | 303 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 13 | 2005 | 7.5 | 7.5 | 3.7375 | 6.1811 | 15 | 55 | 55 | 509.7542 | 214.5772 | 39.3698 | 184.6774 | 0 | 0 | 100.5826 | 343.8195 | 385.6516 | 201.5742 | 0 | 0 | 321.4228 | 125.4487 | 125.4487 | 157.0899 | 233.607 | 246.7665 | 188.8597 | 125.4487 | 125.4487 | 214.5772 | 125.4487 | 125.4487 | 257.6725 | 577.4266 | 632.4181 | 390.4339 | 125.4487 | 125.4487 | 536 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 14 | 2006 | 6.5 | 6.5 | 3.7375 | 6.1811 | 15 | 53 | 53 | 396.214 | 245.996 | 37.1151 | 203.5884 | 0 | 0 | 0 | 198.2041 | 305.2803 | 233.5275 | 24.9774 | 0 | 248.004 | 131.2049 | 131.2049 | 131.2049 | 214.1072 | 258.8938 | 228.8819 | 141.6521 | 131.2049 | 245.996 | 131.2049 | 131.2049 | 131.2049 | 412.3113 | 564.1741 | 462.4093 | 166.6295 | 131.2049 | 494 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 15 | 2007 | 6.5 | 6.5 | 3.7375 | 6.1811 | 15 | 54 | 54 | 62.385 | 260.8114 | 32.1987 | 220.8435 | 0 | 0 | 0 | 18.161 | 45.5906 | 46.3139 | 19.9071 | 0 | 36.1886 | 119.3776 | 119.3776 | 119.3776 | 148.6598 | 192.8863 | 194.0525 | 151.4751 | 119.3776 | 260.8114 | 119.3776 | 119.3776 | 119.3776 | 166.8208 | 238.477 | 240.3663 | 171.3821 | 119.3776 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 16 | 2008 | 7.4 | 7.4 | 3.7375 | 6.1811 | 15 | 51 | 51 | 312.0543 | 212.1724 | 25.3055 | 236.0601 | 0 | 0 | 0 | 19.1396 | 199.7628 | 263.3676 | 172.6953 | 0 | 154.8276 | 110.6049 | 110.6049 | 110.6049 | 119.8269 | 206.8559 | 237.5025 | 193.8141 | 110.6049 | 212.1724 | 110.6049 | 110.6049 | 110.6049 | 138.9665 | 406.6187 | 500.8701 | 366.5094 | 110.6049 | 367 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 17 | 2009 | 7.7 | 7.7 | 3.7375 | 6.1811 | 15 | 52 | 52 | 425.6417 | 144.2996 | 17.1197 | 249.5568 | 0 | 0 | 0 | 0 | 214.8415 | 377.6506 | 319.2371 | 73.8188 | 161.7004 | 84.1824 | 84.1824 | 84.1824 | 84.1824 | 147.4095 | 195.3237 | 178.1328 | 105.907 | 144.2996 | 84.1824 | 84.1824 | 84.1824 | 84.1824 | 362.251 | 572.9743 | 497.3699 | 179.7259 | 306 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 18 | 2010 | 6.5 | 6.5 | 3.7375 | 6.1811 | 15 | 58 | 58 | 145.4451 | 112.2023 | 8.2039 | 261.9286 | 0 | 0 | 0 | 0 | 48.5501 | 126.4281 | 130.2463 | 57.768 | 34.7977 | 57.0642 | 57.0642 | 57.0642 | 57.0642 | 84.7919 | 129.2692 | 131.4498 | 90.0563 | 112.2023 | 57.0642 | 57.0642 | 57.0642 | 57.0642 | 133.3419 | 255.6973 | 261.6961 | 147.8243 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 19 | 2011 | 5.3 | 5.3 | 3.7375 | 6.1811 | 15 | 62 | 62 | 38.9218 | 35.7387 | -0.98764 | 273.8119 | 0 | 0 | 0 | 0 | 5.409 | 30.7952 | 38.1419 | 23.1457 | 3.2613 | 18.7596 | 18.7596 | 18.7596 | 18.7596 | 23.8601 | 47.7981 | 54.7258 | 40.585 | 35.7387 | 18.7596 | 18.7596 | 18.7596 | 18.7596 | 29.2691 | 78.5933 | 92.8677 | 63.7307 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 20 | 2012 | 3.8 | 3.8 | 3.7375 | 6.1811 | 15 | 68 | 68 | 0 | 0 | -10.0513 | 285.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 21 | 2013 | 4.2 | 4.2 | 3.7375 | 6.1811 | 15 | 73 | 73 | 0 | 0 | -18.5702 | 298.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 22 | 2014 | 3.3 | 3.3 | 3.7375 | 6.1811 | 15 | 78 | 78 | 0 | 0 | -26.055 | 312.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 23 | 2015 | 2.4 | 2.4 | 3.7375 | 6.1811 | 15 | 81 | 81 | 0 | 0 | -31.9113 | 328.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 25 | 24 | 2016 | 1.4 | 1.4 | 3.3542 | 5.2718 | 15 | 85 | 85 | 0 | 0 | -35.4849 | 345.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 1 | 2017 | 0.8 | 0.8 | 3.3542 | 5.2718 | 15 | 87 | 87 | 0 | 0 | -36.2527 | 4.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 2 | 2018 | -1.1 | -1.1 | 3.3542 | 5.2718 | 15 | 89 | 89 | 0 | 0 | -33.6846 | 22.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 3 | 2019 | -2.4 | -2.4 | 3.3542 | 5.2718 | 15 | 94 | 94 | 0 | 0 | -28.9387 | 39.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 4 | 2020 | -2.2 | -2.2 | 3.3542 | 5.2718 | 15 | 95 | 95 | 0 | 0 | -22.2295 | 54.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 5 | 2021 | -2.5 | -2.5 | 3.3542 | 5.2718 | 15 | 97 | 97 | 0 | 0 | -14.1904 | 67.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 6 | 2022 | -3 | -3 | 3.3542 | 5.2718 | 15 | 97 | 97 | 0 | 0 | -5.3611 | 79.8448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 7 | 2023 | -2.7 | -2.7 | 3.3542 | 5.2718 | 15 | 97 | 97 | 0 | 8 | 3.812 | 91.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 8 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 26 | 8 | 2024 | 1.1 | 1.1 | 3.3542 | 5.2718 | 15 | 98 | 98 | 596.4937 | 36.9512 | 12.9264 | 103.7601 | 0 | 408.0623 | 594.9072 | 433.2635 | 17.82 | 0 | 0 | 0 | 74.0488 | 24.6053 | 44.6753 | 53.865 | 45.9148 | 25.4817 | 24.6053 | 24.6053 | 24.6053 | 36.9512 | 24.6053 | 452.7376 | 648.7722 | 479.1783 | 43.3017 | 24.6053 | 24.6053 | 24.6053 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 9 | 2025 | 4.4 | 4.4 | 3.3542 | 5.2718 | 15 | 81 | 81 | 667.8631 | 72.8739 | 21.5619 | 116.6091 | 0 | 337.5911 | 632.2563 | 556.5543 | 154.8303 | 0 | 0 | 0 | 185.1261 | 54.6172 | 100.1661 | 139.9232 | 129.7093 | 75.5074 | 54.6172 | 54.6172 | 54.6172 | 72.8739 | 54.6172 | 437.7572 | 772.1795 | 686.2635 | 230.3377 | 54.6172 | 54.6172 | 54.6172 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 10 | 2026 | 6.2 | 6.2 | 3.3542 | 5.2718 | 15 | 55 | 55 | 772.3017 | 88.8704 | 29.216 | 130.9019 | 0 | 226.6085 | 642.181 | 681.5726 | 321.7082 | 0 | 0 | 0 | 319.1296 | 76.1238 | 103.604 | 153.9993 | 158.7762 | 115.1364 | 76.1238 | 76.1238 | 76.1238 | 88.8704 | 76.1238 | 330.2124 | 796.1803 | 840.3488 | 436.8447 | 76.1238 | 76.1238 | 76.1238 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 11 | 2027 | 5.7 | 5.7 | 3.3542 | 5.2718 | 15 | 65 | 65 | 29.9637 | 215.3304 | 35.2588 | 147.1538 | 0 | 1.8689 | 19.7664 | 26.085 | 17.1234 | 0 | 0 | 0 | 15.6696 | 98.7097 | 102.6905 | 140.8125 | 154.2712 | 135.1827 | 98.7097 | 98.7097 | 98.7097 | 215.3304 | 98.7097 | 104.5595 | 160.5789 | 180.3562 | 152.3061 | 98.7097 | 98.7097 | 98.7097 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 12 | 2028 | 3.3 | 3.3 | 3.3542 | 5.2718 | 15 | 89 | 89 | 1.7172 | 95.9716 | 38.9713 | 165.4047 | 0 | 0 | 0.76053 | 1.3708 | 1.178 | 0.29521 | 0 | 0 | 1.0284 | 47.0888 | 47.0888 | 47.0888 | 47.0888 | 47.0888 | 47.0888 | 47.0888 | 47.0888 | 95.9716 | 47.0888 | 47.0888 | 47.8493 | 48.4595 | 48.2668 | 47.384 | 47.0888 | 47.0888 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 13 | 2029 | 5.8 | 5.8 | 3.3542 | 5.2718 | 15 | 79 | 79 | 11.9849 | 225.3795 | 39.7595 | 184.8065 | 0 | 0 | 2.348 | 8.0364 | 9.0171 | 4.7158 | 0 | 0 | 7.6205 | 107.93 | 107.93 | 113.6087 | 127.366 | 129.738 | 119.3352 | 107.93 | 107.93 | 225.3795 | 107.93 | 107.93 | 115.9567 | 135.4024 | 138.7552 | 124.051 | 107.93 | 107.93 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 14 | 2030 | 7.6 | 7.6 | 3.3542 | 5.2718 | 15 | 65 | 65 | 576.5605 | 194.0595 | 37.4775 | 203.8077 | 0 | 0 | 0 | 286.0434 | 441.6643 | 338.5642 | 37.1378 | 0 | 363.9405 | 121.5743 | 121.5743 | 121.5743 | 196.1954 | 236.7927 | 209.8967 | 131.2626 | 121.5743 | 194.0595 | 121.5743 | 121.5743 | 121.5743 | 482.2389 | 678.4571 | 548.4609 | 168.4004 | 121.5743 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 15 | 2031 | 6.9 | 6.9 | 3.3542 | 5.2718 | 15 | 72 | 72 | 134.1368 | 274.4782 | 32.5274 | 221.1178 | 0 | 0 | 0 | 38.4815 | 97.3916 | 99.251 | 42.9705 | 0 | 78.5218 | 127.2493 | 127.2493 | 127.2493 | 169.3663 | 233.8419 | 235.877 | 174.2794 | 127.2493 | 274.4782 | 127.2493 | 127.2493 | 127.2493 | 207.8479 | 331.2335 | 335.128 | 217.2499 | 127.2493 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 16 | 2032 | 7.2 | 7.2 | 3.3542 | 5.2718 | 15 | 61 | 61 | 61.6374 | 225.0906 | 25.6038 | 236.3588 | 0 | 0 | 0 | 3.5186 | 39.151 | 51.8494 | 34.1751 | 0 | 30.9094 | 104.4641 | 104.4641 | 104.4641 | 109.5586 | 161.1511 | 179.5371 | 153.9464 | 104.4641 | 225.0906 | 104.4641 | 104.4641 | 104.4641 | 113.0772 | 200.3022 | 231.3865 | 188.1214 | 104.4641 | 256 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 17 | 2033 | 7 | 7 | 3.3542 | 5.2718 | 15 | 55 | 55 | 62.1547 | 173.0558 | 17.396 | 249.8628 | 0 | 0 | 0 | 0 | 31.0519 | 54.9535 | 46.6641 | 11.0395 | 23.9442 | 81.9827 | 81.9827 | 81.9827 | 81.9827 | 118.874 | 147.2704 | 137.4222 | 95.0982 | 173.0558 | 81.9827 | 81.9827 | 81.9827 | 81.9827 | 149.9259 | 202.2239 | 184.0862 | 106.1377 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 26 | 18 | 2034 | 6.5 | 6.5 | 3.3542 | 5.2718 | 15 | 59 | 59 | 120.4132 | 114.5451 | 8.4682 | 262.2349 | 0 | 0 | 0 | 0 | 39.5585 | 104.2559 | 107.8816 | 48.3118 | 29.4549 | 57.5551 | 57.5551 | 57.5551 | 57.5551 | 85.206 | 130.4287 | 132.9631 | 91.3244 | 114.5451 | 57.5551 | 57.5551 | 57.5551 | 57.5551 | 124.7645 | 234.6846 | 240.8447 | 139.6362 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 19 | 2035 | 5.6 | 5.6 | 3.3542 | 5.2718 | 15 | 66 | 66 | 5.1434 | 24.5413 | -0.72499 | 274.1165 | 0 | 0 | 0 | 0 | 0.68736 | 4.0503 | 5.0407 | 3.0783 | 0.45873 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 24.5413 | 11.8288 | 11.8288 | 11.8288 | 11.8288 | 12.5162 | 15.8792 | 16.8695 | 14.9071 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 20 | 2036 | 3.6 | 3.6 | 3.3542 | 5.2718 | 15 | 76 | 76 | 0 | 0 | -9.7803 | 286.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 21 | 2037 | 2.2 | 2.2 | 3.3542 | 5.2718 | 15 | 84 | 84 | 0 | 0 | -18.281 | 298.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 22 | 2038 | 2.2 | 2.2 | 3.3542 | 5.2718 | 15 | 85 | 85 | 0 | 0 | -25.7391 | 312.9169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 23 | 2039 | 1.1 | 1.1 | 3.3542 | 5.2718 | 15 | 92 | 92 | 0 | 0 | -31.5633 | 328.6823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 26 | 24 | 2040 | 1.3 | 1.3 | 2.6917 | 4.3594 | 15 | 93 | 93 | 0 | 0 | -35.1068 | 346.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 1 | 2041 | 1.2 | 1.2 | 2.6917 | 4.3594 | 15 | 92 | 92 | 0 | 0 | -35.8551 | 4.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 2 | 2042 | -0.5 | -0.5 | 2.6917 | 4.3594 | 15 | 94 | 94 | 0 | 0 | -33.2834 | 22.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 3 | 2043 | -1.8 | -1.8 | 2.6917 | 4.3594 | 15 | 95 | 95 | 0 | 0 | -28.5452 | 39.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 4 | 2044 | -2.5 | -2.5 | 2.6917 | 4.3594 | 15 | 96 | 96 | 0 | 0 | -21.8486 | 54.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 5 | 2045 | -3.2 | -3.2 | 2.6917 | 4.3594 | 15 | 97 | 97 | 0 | 0 | -13.8213 | 67.3743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 6 | 2046 | -3.4 | -3.4 | 2.6917 | 4.3594 | 15 | 97 | 97 | 0 | 0 | -4.9996 | 79.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 7 | 2047 | -2.7 | -2.7 | 2.6917 | 4.3594 | 15 | 97 | 97 | 0 | 11 | 4.1713 | 91.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 11 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 27 | 8 | 2048 | 0.5 | 0.5 | 2.6917 | 4.3594 | 15 | 95 | 95 | 479.9865 | 45.8345 | 13.2896 | 103.5843 | 0 | 329.3055 | 478.5429 | 347.4564 | 12.8346 | 0 | 0 | 0 | 62.1655 | 26.5758 | 44.4581 | 52.5622 | 45.4438 | 27.2728 | 26.5758 | 26.5758 | 26.5758 | 45.8345 | 26.5758 | 373.7636 | 531.1051 | 392.9001 | 40.1074 | 26.5758 | 26.5758 | 26.5758 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 9 | 2049 | 3 | 3 | 2.6917 | 4.3594 | 15 | 85 | 85 | 709.0925 | 68.6614 | 21.9344 | 116.4477 | 0 | 359.7116 | 670.798 | 588.94 | 162.089 | 0 | 0 | 0 | 200.3386 | 54.5408 | 99.6517 | 138.6646 | 128.3989 | 74.8681 | 54.5408 | 54.5408 | 54.5408 | 68.6614 | 54.5408 | 459.3633 | 809.4626 | 717.339 | 236.9571 | 54.5408 | 54.5408 | 54.5408 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 10 | 2050 | 6.4 | 6.4 | 2.6917 | 4.3594 | 15 | 72 | 72 | 796.1464 | 85.7951 | 29.6014 | 130.7727 | 0 | 234.9736 | 661.2232 | 700.1373 | 328.9204 | 0 | 0 | 0 | 333.2049 | 76.2311 | 103.2181 | 152.1735 | 156.6428 | 114.008 | 76.2311 | 76.2311 | 76.2311 | 85.7951 | 76.2311 | 338.1917 | 813.3967 | 856.7801 | 442.9284 | 76.2311 | 76.2311 | 76.2311 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 11 | 2051 | 6.5 | 6.5 | 2.6917 | 4.3594 | 15 | 65 | 65 | 607.104 | 154.309 | 35.6563 | 147.0847 | 0 | 38.9108 | 399.7568 | 526.4307 | 344.7286 | 0 | 0 | 0 | 320.691 | 103.717 | 112.039 | 189.2141 | 216.3062 | 177.4451 | 103.717 | 103.717 | 103.717 | 154.309 | 103.717 | 150.9498 | 588.9709 | 742.7369 | 522.1737 | 103.717 | 103.717 | 103.717 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 12 | 2052 | 7.2 | 7.2 | 2.6917 | 4.3594 | 15 | 63 | 63 | 167.2848 | 281.9338 | 39.3724 | 165.4275 | 0 | 0 | 73.8608 | 132.9115 | 114.1045 | 28.4566 | 0 | 0 | 101.0662 | 131.744 | 131.744 | 201.1402 | 256.6216 | 238.9513 | 158.4805 | 131.744 | 131.744 | 281.9338 | 131.744 | 131.744 | 275.001 | 389.5331 | 353.0558 | 186.9371 | 131.744 | 131.744 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 13 | 2053 | 7.6 | 7.6 | 2.6917 | 4.3594 | 15 | 59 | 59 | 31.5736 | 265.7585 | 40.1483 | 184.937 | 0 | 0 | 6.1411 | 21.046 | 23.6225 | 12.3612 | 0 | 0 | 20.2415 | 120.0225 | 120.0225 | 139.1725 | 185.6514 | 193.6857 | 158.5691 | 120.0225 | 120.0225 | 265.7585 | 120.0225 | 120.0225 | 145.3136 | 206.6974 | 217.3082 | 170.9303 | 120.0225 | 120.0225 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 14 | 2054 | 8.2 | 8.2 | 2.6917 | 4.3594 | 15 | 53 | 53 | 61.8445 | 285.6372 | 37.8387 | 204.029 | 0 | 0 | 0 | 30.4261 | 47.0972 | 36.1795 | 4.0683 | 0 | 39.3628 | 129.3616 | 129.3616 | 129.3616 | 183.0956 | 212.5377 | 193.2564 | 136.5463 | 129.3616 | 285.6372 | 129.3616 | 129.3616 | 129.3616 | 213.5217 | 259.635 | 229.4359 | 140.6146 | 129.3616 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 15 | 2055 | 8.2 | 8.2 | 2.6917 | 4.3594 | 15 | 58 | 58 | 8.6175 | 194.9101 | 32.8548 | 221.3938 | 0 | 0 | 0 | 2.4357 | 6.2159 | 6.3548 | 2.7712 | 0 | 5.0899 | 95.2016 | 95.2016 | 95.2016 | 99.5927 | 106.4074 | 106.658 | 100.1976 | 95.2016 | 194.9101 | 95.2016 | 95.2016 | 95.2016 | 102.0284 | 112.6233 | 113.0128 | 102.9688 | 95.2016 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 16 | 2056 | 8.4 | 8.4 | 2.6917 | 4.3594 | 15 | 55 | 55 | 5.143 | 139.3938 | 25.9009 | 236.6587 | 0 | 0 | 0 | 0.27174 | 3.241 | 4.3118 | 2.8567 | 0 | 2.6062 | 70.0226 | 70.0226 | 70.0226 | 70.0276 | 70.0821 | 70.1018 | 70.0751 | 70.0226 | 139.3938 | 70.0226 | 70.0226 | 70.0226 | 70.2994 | 73.3232 | 74.4135 | 72.9318 | 70.0226 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 17 | 2057 | 8.2 | 8.2 | 2.6917 | 4.3594 | 15 | 57 | 57 | 123.2633 | 182.8601 | 17.6712 | 250.1694 | 0 | 0 | 0 | 0 | 60.9434 | 108.594 | 92.6318 | 22.4071 | 48.1399 | 88.5018 | 88.5018 | 88.5018 | 88.5018 | 143.6026 | 186.685 | 172.2531 | 108.7608 | 182.8601 | 88.5018 | 88.5018 | 88.5018 | 88.5018 | 204.5459 | 295.279 | 264.8848 | 131.1678 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 27 | 18 | 2058 | 7.9 | 7.9 | 2.6917 | 4.3594 | 15 | 59 | 59 | 12.2511 | 88.9377 | 8.7317 | 262.5412 | 0 | 0 | 0 | 0 | 3.96 | 10.5647 | 10.9808 | 4.9645 | 3.0623 | 43.6318 | 43.6318 | 43.6318 | 43.6318 | 46.0914 | 50.1938 | 50.4522 | 46.7154 | 88.9377 | 43.6318 | 43.6318 | 43.6318 | 43.6318 | 50.0514 | 60.7585 | 61.433 | 51.6798 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 19 | 2059 | 5.8 | 5.8 | 2.6917 | 4.3594 | 15 | 73 | 73 | 30.8623 | 39.0813 | -0.4629 | 274.4207 | 0 | 0 | 0 | 0 | 3.9599 | 24.1876 | 30.2465 | 18.5875 | 2.9187 | 19.8776 | 19.8776 | 19.8776 | 19.8776 | 22.3608 | 35.0454 | 38.8448 | 31.5336 | 39.0813 | 19.8776 | 19.8776 | 19.8776 | 19.8776 | 26.3207 | 59.233 | 69.0914 | 50.121 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 20 | 2060 | 4 | 4 | 2.6917 | 4.3594 | 15 | 81 | 81 | 0 | 0 | -9.5096 | 286.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 21 | 2061 | 1.9 | 1.9 | 2.6917 | 4.3594 | 15 | 88 | 88 | 0 | 0 | -17.992 | 299.1637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 22 | 2062 | 0.9 | 0.9 | 2.6917 | 4.3594 | 15 | 93 | 93 | 0 | 0 | -25.4233 | 313.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 23 | 2063 | 1.3 | 1.3 | 2.6917 | 4.3594 | 15 | 95 | 95 | 0 | 0 | -31.2157 | 328.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 27 | 24 | 2064 | 2.3 | 2.3 | 3.1417 | 3.7487 | 15 | 94 | 94 | 0 | 0 | -34.7292 | 346.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 1 | 2065 | 2.9 | 2.9 | 3.1417 | 3.7487 | 15 | 92 | 92 | 0 | 0 | -35.4581 | 4.6322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 2 | 2066 | 3.3 | 3.3 | 3.1417 | 3.7487 | 15 | 92 | 92 | 0 | 0 | -32.8831 | 22.6054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 3 | 2067 | 3.7 | 3.7 | 3.1417 | 3.7487 | 15 | 89 | 89 | 0 | 0 | -28.1525 | 39.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 4 | 2068 | 4.2 | 4.2 | 3.1417 | 3.7487 | 15 | 86 | 86 | 0 | 0 | -21.4684 | 53.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 5 | 2069 | 4.4 | 4.4 | 3.1417 | 3.7487 | 15 | 85 | 85 | 0 | 0 | -13.4528 | 67.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 6 | 2070 | 4.4 | 4.4 | 3.1417 | 3.7487 | 15 | 81 | 81 | 0 | 0 | -4.6388 | 79.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 7 | 2071 | 4.7 | 4.7 | 3.1417 | 3.7487 | 15 | 77 | 77 | 0 | 3 | 4.5299 | 91.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 28 | 8 | 2072 | 5.6 | 5.6 | 3.1417 | 3.7487 | 15 | 71 | 71 | 3.9233 | 32.4708 | 13.6519 | 103.4085 | 0 | 2.6993 | 3.91 | 2.8303 | 0.092633 | 0 | 0 | 0 | 0.52915 | 15.0476 | 38.0388 | 48.351 | 39.1546 | 15.8366 | 15.0476 | 15.0476 | 15.0476 | 32.4708 | 15.0476 | 40.738 | 52.261 | 41.9848 | 15.9292 | 15.0476 | 15.0476 | 15.0476 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 9 | 2073 | 6.5 | 6.5 | 3.1417 | 3.7487 | 15 | 67 | 67 | 9.5539 | 97.25 | 22.3059 | 116.2858 | 0 | 4.8635 | 9.0309 | 7.9081 | 2.1529 | 0 | 0 | 0 | 2.75 | 44.5566 | 69.1892 | 90.2962 | 84.6096 | 55.4605 | 44.5566 | 44.5566 | 44.5566 | 97.25 | 44.5566 | 74.0527 | 99.3272 | 92.5177 | 57.6133 | 44.5566 | 44.5566 | 44.5566 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 10 | 2074 | 7.7 | 7.7 | 3.1417 | 3.7487 | 15 | 64 | 64 | 18.005 | 161.3696 | 29.9858 | 130.6429 | 0 | 5.3446 | 14.9352 | 15.777 | 7.3769 | 0 | 0 | 0 | 7.6304 | 73.9431 | 90.4888 | 120.1794 | 122.7854 | 96.7802 | 73.9431 | 73.9431 | 73.9431 | 161.3696 | 73.9431 | 95.8333 | 135.1146 | 138.5624 | 104.1571 | 73.9431 | 73.9431 | 73.9431 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 11 | 2075 | 9.1 | 9.1 | 3.1417 | 3.7487 | 15 | 61 | 61 | 64.9019 | 240.3766 | 36.0529 | 147.0151 | 0 | 4.2708 | 42.6548 | 56.0523 | 36.615 | 0 | 0 | 0 | 34.6234 | 109.6531 | 116.8955 | 181.9876 | 204.7071 | 171.7452 | 109.6531 | 109.6531 | 109.6531 | 240.3766 | 109.6531 | 121.1663 | 224.6424 | 260.7593 | 208.3602 | 109.6531 | 109.6531 | 109.6531 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 12 | 2076 | 10.3 | 10.3 | 3.1417 | 3.7487 | 15 | 57 | 57 | 275.7574 | 267.9597 | 39.7726 | 165.4507 | 0 | 0 | 121.3739 | 218.0585 | 187.0075 | 46.4099 | 0 | 0 | 168.0403 | 132.0398 | 132.0398 | 209.5488 | 271.2914 | 251.4622 | 161.677 | 132.0398 | 132.0398 | 267.9597 | 132.0398 | 132.0398 | 330.9227 | 489.3499 | 438.4697 | 208.087 | 132.0398 | 132.0398 | 436 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 13 | 2077 | 11.6 | 11.6 | 3.1417 | 3.7487 | 15 | 54 | 54 | 504.5229 | 220.9273 | 40.5361 | 185.0688 | 0 | 0 | 97.4129 | 334.2839 | 375.3359 | 196.5212 | 0 | 0 | 326.0727 | 127.8991 | 127.8991 | 159.5008 | 236.3441 | 249.6618 | 191.6525 | 127.8991 | 127.8991 | 220.9273 | 127.8991 | 127.8991 | 256.9137 | 570.628 | 624.9977 | 388.1737 | 127.8991 | 127.8991 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 14 | 2078 | 11.4 | 11.4 | 3.1417 | 3.7487 | 15 | 49 | 49 | 858.9192 | 117.8388 | 38.1988 | 204.252 | 0 | 0 | 0 | 418.9956 | 650.223 | 500.5586 | 57.6737 | 0 | 551.1612 | 111.6039 | 111.6039 | 111.6039 | 149.091 | 169.7787 | 156.3884 | 116.7639 | 111.6039 | 117.8388 | 111.6039 | 111.6039 | 111.6039 | 568.0866 | 820.0017 | 656.9469 | 174.4376 | 111.6039 | 669 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 15 | 2079 | 11.6 | 11.6 | 3.1417 | 3.7487 | 15 | 49 | 49 | 680.0222 | 152.7932 | 33.1809 | 221.6713 | 0 | 0 | 0 | 189.3188 | 487.2463 | 499.7516 | 219.5091 | 0 | 405.2068 | 109.5346 | 109.5346 | 109.5346 | 142.8534 | 195.2866 | 197.4875 | 148.1667 | 109.5346 | 152.7932 | 109.5346 | 109.5346 | 109.5346 | 332.1722 | 682.533 | 697.2391 | 367.6759 | 109.5346 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 16 | 2080 | 11.4 | 11.4 | 3.1417 | 3.7487 | 15 | 49 | 49 | 537.3358 | 166.8839 | 26.1966 | 236.9595 | 0 | 0 | 0 | 26.1126 | 335.9289 | 448.9626 | 299.0001 | 0 | 275.1161 | 103.6262 | 103.6262 | 103.6262 | 110.2344 | 188.6373 | 217.2419 | 179.292 | 103.6262 | 166.8839 | 103.6262 | 103.6262 | 103.6262 | 136.347 | 524.5662 | 666.2044 | 478.292 | 103.6262 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 17 | 2081 | 10.9 | 10.9 | 3.1417 | 3.7487 | 15 | 47 | 47 | 405.2178 | 153.6047 | 17.9453 | 250.4762 | 0 | 0 | 0 | 0 | 198.244 | 355.7035 | 304.7968 | 75.3442 | 160.3953 | 87.7715 | 87.7715 | 87.7715 | 87.7715 | 151.0957 | 201.3924 | 185.1314 | 111.8384 | 153.6047 | 87.7715 | 87.7715 | 87.7715 | 87.7715 | 349.3397 | 557.0959 | 489.9283 | 187.1826 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 28 | 18 | 2082 | 9.9 | 9.9 | 3.1417 | 3.7487 | 15 | 50 | 50 | 163.9109 | 119.1568 | 8.9944 | 262.8474 | 0 | 0 | 0 | 0 | 52.1137 | 140.7741 | 146.9709 | 67.0742 | 41.8432 | 60.8055 | 60.8055 | 60.8055 | 60.8055 | 88.2387 | 134.9105 | 138.1725 | 96.114 | 119.1568 | 60.8055 | 60.8055 | 60.8055 | 60.8055 | 140.3525 | 275.6846 | 285.1435 | 163.1882 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 19 | 2083 | 8.4 | 8.4 | 3.1417 | 3.7487 | 15 | 60 | 60 | 16.1914 | 37.3819 | -0.20139 | 274.7242 | 0 | 0 | 0 | 0 | 1.9913 | 12.6283 | 15.8679 | 9.8122 | 1.6181 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 21.0424 | 31.9544 | 35.2777 | 29.0656 | 37.3819 | 18.9997 | 18.9997 | 18.9997 | 18.9997 | 23.0337 | 44.5827 | 51.1456 | 38.8778 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 20 | 2084 | 5.6 | 5.6 | 3.1417 | 3.7487 | 15 | 70 | 70 | 0 | 0 | -9.2392 | 286.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 21 | 2085 | 3.4 | 3.4 | 3.1417 | 3.7487 | 15 | 80 | 80 | 0 | 0 | -17.7032 | 299.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 22 | 2086 | 2.3 | 2.3 | 3.1417 | 3.7487 | 15 | 87 | 87 | 0 | 0 | -25.1077 | 313.4646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 23 | 2087 | 2 | 2 | 3.1417 | 3.7487 | 15 | 87 | 87 | 0 | 0 | -30.8684 | 329.1505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 28 | 24 | 2088 | 0.7 | 0.7 | 6.5 | 4.2475 | 15 | 92 | 92 | 0 | 0 | -34.3521 | 346.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 1 | 2089 | 0.1 | 0.1 | 6.5 | 4.2475 | 15 | 94 | 94 | 0 | 0 | -35.062 | 4.7055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 2 | 2090 | -0.1 | -0.1 | 6.5 | 4.2475 | 15 | 95 | 95 | 0 | 0 | -32.4837 | 22.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 3 | 2091 | 1.2 | 1.2 | 6.5 | 4.2475 | 15 | 96 | 96 | 0 | 0 | -27.7607 | 39.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 4 | 2092 | 3 | 3 | 6.5 | 4.2475 | 15 | 96 | 96 | 0 | 0 | -21.089 | 53.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 5 | 2093 | 3.5 | 3.5 | 6.5 | 4.2475 | 15 | 94 | 94 | 0 | 0 | -13.0851 | 67.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 6 | 2094 | 3.9 | 3.9 | 6.5 | 4.2475 | 15 | 90 | 90 | 0 | 0 | -4.2788 | 79.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 7 | 2095 | 3.5 | 3.5 | 6.5 | 4.2475 | 15 | 92 | 92 | 0 | 6 | 4.8876 | 91.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 29 | 8 | 2096 | 5.1 | 5.1 | 6.5 | 4.2475 | 15 | 89 | 89 | 18.1842 | 53.4504 | 14.0132 | 103.2325 | 0 | 12.5453 | 18.1143 | 13.0722 | 0.37256 | 0 | 0 | 0 | 2.5496 | 24.1841 | 103.2415 | 138.3359 | 106.5617 | 26.5318 | 24.1841 | 24.1841 | 24.1841 | 53.4504 | 24.1841 | 115.7868 | 156.4502 | 119.6339 | 26.9044 | 24.1841 | 24.1841 | 24.1841 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 9 | 2097 | 6.9 | 6.9 | 6.5 | 4.2475 | 15 | 85 | 85 | 18.1275 | 111.6864 | 22.6763 | 116.1235 | 0 | 9.2596 | 17.121 | 14.9532 | 4.0259 | 0 | 0 | 0 | 5.3136 | 49.9503 | 86.7706 | 118.0309 | 109.4105 | 65.9591 | 49.9503 | 49.9503 | 49.9503 | 111.6864 | 49.9503 | 96.0302 | 135.1519 | 124.3637 | 69.9851 | 49.9503 | 49.9503 | 49.9503 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 10 | 2098 | 8.8 | 8.8 | 6.5 | 4.2475 | 15 | 81 | 81 | 55.3938 | 190.2341 | 30.3692 | 130.5123 | 0 | 16.5362 | 45.8905 | 48.3628 | 22.5048 | 0 | 0 | 0 | 23.7659 | 87.2865 | 118.269 | 173.268 | 177.9002 | 129.452 | 87.2865 | 87.2865 | 87.2865 | 190.2341 | 87.2865 | 134.8052 | 219.1585 | 226.2629 | 151.9569 | 87.2865 | 87.2865 | 87.2865 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 11 | 2099 | 11 | 11 | 6.5 | 4.2475 | 15 | 69 | 69 | 247.8003 | 241.5158 | 36.4486 | 146.945 | 0 | 16.7286 | 162.5437 | 213.143 | 138.886 | 0 | 0 | 0 | 133.4842 | 119.624 | 129.3021 | 213.6615 | 242.935 | 199.9746 | 119.624 | 119.624 | 119.624 | 241.5158 | 119.624 | 146.0307 | 376.2052 | 456.078 | 338.8606 | 119.624 | 119.624 | 119.624 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 12 | 2100 | 12 | 12 | 6.5 | 4.2475 | 15 | 58 | 58 | 424.9877 | 232.8207 | 40.1719 | 165.4741 | 0 | 0 | 186.4632 | 334.4537 | 286.5258 | 70.7549 | 0 | 0 | 261.1793 | 126.6446 | 126.6446 | 199.7363 | 257.747 | 238.9598 | 154.3798 | 126.6446 | 126.6446 | 232.8207 | 126.6446 | 126.6446 | 386.1995 | 592.2008 | 525.4855 | 225.1347 | 126.6446 | 126.6446 | 494 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 13 | 2101 | 12.4 | 12.4 | 6.5 | 4.2475 | 15 | 50 | 50 | 10.8216 | 225.9501 | 40.9229 | 185.2018 | 0 | 0 | 2.074 | 7.1266 | 8.0046 | 4.1936 | 0 | 0 | 7.0499 | 108.6632 | 108.6632 | 113.7072 | 125.9952 | 128.1304 | 118.862 | 108.6632 | 108.6632 | 225.9501 | 108.6632 | 108.6632 | 115.7812 | 133.1218 | 136.135 | 123.0556 | 108.6632 | 108.6632 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 14 | 2102 | 12.8 | 12.8 | 6.5 | 4.2475 | 15 | 49 | 49 | 73.474 | 294.4725 | 38.5575 | 204.4767 | 0 | 0 | 0 | 35.5352 | 55.2877 | 42.6534 | 5.0333 | 0 | 47.5275 | 133.4878 | 133.4878 | 133.4878 | 188.2011 | 218.6138 | 199.1609 | 141.2376 | 133.4878 | 294.4725 | 133.4878 | 133.4878 | 133.4878 | 223.7363 | 273.9015 | 241.8143 | 146.2709 | 133.4878 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 15 | 2103 | 13.4 | 13.4 | 6.5 | 4.2475 | 15 | 49 | 49 | 146.0388 | 281.2224 | 33.5057 | 221.9502 | 0 | 0 | 0 | 40.0371 | 103.9366 | 106.9515 | 47.3157 | 0 | 87.7776 | 130.6299 | 130.6299 | 130.6299 | 171.5047 | 236.7413 | 239.8192 | 178.9356 | 130.6299 | 281.2224 | 130.6299 | 130.6299 | 130.6299 | 211.5417 | 340.6779 | 346.7708 | 226.2512 | 130.6299 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 16 | 2104 | 13.3 | 13.3 | 6.5 | 4.2475 | 15 | 51 | 51 | 11.9049 | 182.8427 | 26.4911 | 237.2611 | 0 | 0 | 0 | 0.52813 | 7.3827 | 9.9126 | 6.6358 | 0 | 6.1573 | 88.5641 | 88.5641 | 88.5641 | 89.4348 | 100.7357 | 104.9066 | 99.5043 | 88.5641 | 182.8427 | 88.5641 | 88.5641 | 88.5641 | 89.963 | 108.1184 | 114.8192 | 106.1401 | 88.5641 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 17 | 2105 | 13.1 | 13.1 | 6.5 | 4.2475 | 15 | 49 | 49 | 38.5656 | 170.5324 | 18.2183 | 250.7833 | 0 | 0 | 0 | 0 | 18.6668 | 33.729 | 29.0332 | 7.3301 | 15.4676 | 80.3527 | 80.3527 | 80.3527 | 80.3527 | 113.7789 | 140.7503 | 132.3416 | 93.4785 | 170.5324 | 80.3527 | 80.3527 | 80.3527 | 80.3527 | 132.4457 | 174.4793 | 161.3748 | 100.8086 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 29 | 18 | 2106 | 12.6 | 12.6 | 6.5 | 4.2475 | 15 | 52 | 52 | 5.0063 | 70.6955 | 9.2562 | 263.1532 | 0 | 0 | 0 | 0 | 1.5652 | 4.2819 | 4.4904 | 2.0684 | 1.3045 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 70.6955 | 34.8886 | 34.8886 | 34.8886 | 34.8886 | 36.4538 | 39.1705 | 39.379 | 36.957 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 19 | 2107 | 11 | 11 | 6.5 | 4.2475 | 15 | 66 | 66 | 5.6844 | 30.4015 | 0.059518 | 275.0269 | 0 | 0 | 0 | 0 | 0.66884 | 4.4118 | 5.5704 | 3.4659 | 0.5985 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 30.4015 | 14.7555 | 14.7555 | 14.7555 | 14.7555 | 15.4243 | 19.1673 | 20.3259 | 18.2214 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 20 | 2108 | 9.6 | 9.6 | 6.5 | 4.2475 | 15 | 70 | 70 | 0 | 0 | -8.9693 | 287.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 21 | 2109 | 8.3 | 8.3 | 6.5 | 4.2475 | 15 | 74 | 74 | 0 | 0 | -17.4146 | 299.7455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 22 | 2110 | 7.2 | 7.2 | 6.5 | 4.2475 | 15 | 82 | 82 | 0 | 0 | -24.7923 | 313.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 23 | 2111 | 7.3 | 7.3 | 6.5 | 4.2475 | 15 | 85 | 85 | 0 | 0 | -30.5214 | 329.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 29 | 24 | 2112 | 6.8 | 6.8 | 7.7792 | 5.1065 | 15 | 88 | 88 | 0 | 0 | -33.9758 | 346.6376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 1 | 2113 | 5.9 | 5.9 | 7.7792 | 5.1065 | 15 | 91 | 91 | 0 | 0 | -34.6667 | 4.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 2 | 2114 | 5.2 | 5.2 | 7.7792 | 5.1065 | 15 | 93 | 93 | 0 | 0 | -32.0854 | 22.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 3 | 2115 | 4.9 | 4.9 | 7.7792 | 5.1065 | 15 | 94 | 94 | 0 | 0 | -27.3698 | 38.9547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 4 | 2116 | 4.7 | 4.7 | 7.7792 | 5.1065 | 15 | 93 | 93 | 0 | 0 | -20.7106 | 53.6572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 5 | 2117 | 4.1 | 4.1 | 7.7792 | 5.1065 | 15 | 91 | 91 | 0 | 0 | -12.7183 | 66.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 6 | 2118 | 3.8 | 3.8 | 7.7792 | 5.1065 | 15 | 90 | 90 | 0 | 0 | -3.9197 | 79.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 7 | 2119 | 4.7 | 4.7 | 7.7792 | 5.1065 | 15 | 84 | 84 | 0 | 11 | 5.2443 | 90.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 11 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 5.3619 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 30 | 8 | 2120 | 6.2 | 6.2 | 7.7792 | 5.1065 | 15 | 79 | 79 | 318.4695 | 61.6534 | 14.3733 | 103.0563 | 0 | 220.3034 | 317.0882 | 228.127 | 5.5321 | 0 | 0 | 0 | 46.3466 | 33.7582 | 67.0824 | 81.7226 | 68.2658 | 34.595 | 33.7582 | 33.7582 | 33.7582 | 61.6534 | 33.7582 | 287.3859 | 398.8107 | 296.3928 | 40.1271 | 33.7582 | 33.7582 | 33.7582 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 9 | 2121 | 9.4 | 9.4 | 7.7792 | 5.1065 | 15 | 63 | 63 | 560.9717 | 93.6145 | 23.0456 | 115.9605 | 0 | 287.5121 | 529.3647 | 461.1227 | 122.7612 | 0 | 0 | 0 | 167.3855 | 62.9445 | 115.1885 | 159.1356 | 146.7353 | 85.2515 | 62.9445 | 62.9445 | 62.9445 | 93.6145 | 62.9445 | 402.7005 | 688.5003 | 607.858 | 208.0127 | 62.9445 | 62.9445 | 62.9445 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 10 | 2122 | 11.5 | 11.5 | 7.7792 | 5.1065 | 15 | 53 | 53 | 713.2781 | 104.265 | 30.7515 | 130.381 | 0 | 214.1152 | 590.125 | 620.4475 | 287.3203 | 0 | 0 | 0 | 309.735 | 81.6291 | 111.8749 | 164.9899 | 169.2732 | 122.2158 | 81.6291 | 81.6291 | 81.6291 | 104.265 | 81.6291 | 325.9901 | 755.1148 | 789.7208 | 409.5362 | 81.6291 | 81.6291 | 81.6291 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 11 | 2123 | 12.8 | 12.8 | 7.7792 | 5.1065 | 15 | 48 | 48 | 805.1922 | 109.1026 | 36.8431 | 146.8742 | 0 | 55.7245 | 527.1155 | 689.7294 | 448.3092 | 0 | 0 | 0 | 437.8974 | 96.3374 | 103.1746 | 161.0126 | 180.9648 | 151.3434 | 96.3374 | 96.3374 | 96.3374 | 109.1026 | 96.3374 | 158.8991 | 688.1281 | 870.6942 | 599.6525 | 96.3374 | 96.3374 | 96.3374 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 12 | 2124 | 14.1 | 14.1 | 7.7792 | 5.1065 | 15 | 41 | 41 | 824.7362 | 119.9149 | 40.5701 | 165.4976 | 0 | 0 | 360.6868 | 645.8967 | 552.7491 | 135.8086 | 0 | 0 | 511.0851 | 109.0387 | 109.0387 | 143.6826 | 171.077 | 162.1302 | 122.0831 | 109.0387 | 109.0387 | 119.9149 | 109.0387 | 109.0387 | 504.3694 | 816.9737 | 714.8793 | 257.8916 | 109.0387 | 109.0387 | 631 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 13 | 2125 | 15.2 | 15.2 | 7.7792 | 5.1065 | 15 | 36 | 36 | 832.6133 | 125.3125 | 41.3085 | 185.3359 | 0 | 0 | 158.3819 | 544.9613 | 612.3097 | 320.9754 | 0 | 0 | 546.6875 | 114.104 | 114.104 | 129.3614 | 166.6017 | 173.0896 | 145.0245 | 114.104 | 114.104 | 125.3125 | 114.104 | 114.104 | 287.7433 | 711.563 | 785.3993 | 465.9999 | 114.104 | 114.104 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 14 | 2126 | 15.5 | 15.5 | 7.7792 | 5.1065 | 15 | 37 | 37 | 825.0137 | 126.1013 | 38.915 | 204.703 | 0 | 0 | 0 | 395.5604 | 617.0373 | 477.0622 | 57.6305 | 0 | 537.8987 | 113.3903 | 113.3903 | 113.3903 | 151.8965 | 173.4563 | 159.8303 | 119.0004 | 113.3903 | 126.1013 | 113.3903 | 113.3903 | 113.3903 | 547.4569 | 790.4937 | 636.8925 | 176.6309 | 113.3903 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 15 | 2127 | 16 | 16 | 7.7792 | 5.1065 | 15 | 36 | 36 | 778.5317 | 128.0546 | 33.829 | 222.2304 | 0 | 0 | 0 | 210.1302 | 550.3242 | 568.1458 | 253.1553 | 0 | 471.9454 | 106.4822 | 106.4822 | 106.4822 | 135.0698 | 181.3522 | 183.7767 | 140.9232 | 106.4822 | 128.0546 | 106.4822 | 106.4822 | 106.4822 | 345.2 | 731.6764 | 751.9225 | 394.0785 | 106.4822 | 600 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 16 | 2128 | 16.2 | 16.2 | 7.7792 | 5.1065 | 15 | 37 | 37 | 669.6033 | 136.21 | 26.7842 | 237.5633 | 0 | 0 | 0 | 26.8776 | 411.868 | 555.5917 | 373.8573 | 0 | 349.79 | 98.1649 | 98.1649 | 98.1649 | 102.6755 | 167.2839 | 191.4034 | 160.905 | 98.1649 | 136.21 | 98.1649 | 98.1649 | 98.1649 | 129.5531 | 579.1519 | 746.9951 | 534.7623 | 98.1649 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 17 | 2129 | 15.8 | 15.8 | 7.7792 | 5.1065 | 15 | 38 | 38 | 520.7145 | 135.4387 | 18.4901 | 251.0905 | 0 | 0 | 0 | 0 | 249.3288 | 453.717 | 392.324 | 101.1129 | 211.5613 | 85.3332 | 85.3332 | 85.3332 | 85.3332 | 142.9888 | 190.2521 | 176.0554 | 108.7149 | 135.4387 | 85.3332 | 85.3332 | 85.3332 | 85.3332 | 392.3175 | 643.9691 | 568.3794 | 209.8277 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2004 | 3 | 30 | 18 | 2130 | 15.3 | 15.3 | 7.7792 | 5.1065 | 15 | 39 | 39 | 253.2501 | 118.6742 | 9.5172 | 263.4587 | 0 | 0 | 0 | 0 | 77.8351 | 215.703 | 227.215 | 105.6275 | 67.3258 | 64.3196 | 64.3196 | 64.3196 | 64.3196 | 98.2109 | 158.2417 | 163.2543 | 110.3123 | 118.6742 | 64.3196 | 64.3196 | 64.3196 | 64.3196 | 176.046 | 373.9447 | 390.4693 | 215.9398 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 19 | 2131 | 13.8 | 13.8 | 7.7792 | 5.1065 | 15 | 46 | 46 | 33.9668 | 46.2426 | 0.3198 | 275.3289 | 0 | 0 | 0 | 0 | 3.8162 | 26.2319 | 33.2812 | 20.8349 | 3.7574 | 23.3297 | 23.3297 | 23.3297 | 23.3297 | 26.0459 | 41.9999 | 47.0171 | 38.1587 | 46.2426 | 23.3297 | 23.3297 | 23.3297 | 23.3297 | 29.8621 | 68.2317 | 80.2984 | 58.9935 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 20 | 2132 | 12.4 | 12.4 | 7.7792 | 5.1065 | 15 | 52 | 52 | 0 | 0 | -8.6997 | 287.3233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 21 | 2133 | 11.6 | 11.6 | 7.7792 | 5.1065 | 15 | 57 | 57 | 0 | 0 | -17.1264 | 300.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 22 | 2134 | 10.5 | 10.5 | 7.7792 | 5.1065 | 15 | 62 | 62 | 0 | 0 | -24.4772 | 314.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 23 | 2135 | 9.8 | 9.8 | 7.7792 | 5.1065 | 15 | 64 | 64 | 0 | 0 | -30.175 | 329.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 30 | 24 | 2136 | 9.3 | 9.3 | 10.3625 | 6.5492 | 15 | 65 | 65 | 0 | 0 | -33.6002 | 346.7982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 1 | 2137 | 8.3 | 8.3 | 10.3625 | 6.5492 | 15 | 67 | 67 | 0 | 0 | -34.2725 | 4.8491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 2 | 2138 | 7.4 | 7.4 | 10.3625 | 6.5492 | 15 | 69 | 69 | 0 | 0 | -31.6882 | 22.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 3 | 2139 | 6.5 | 6.5 | 10.3625 | 6.5492 | 15 | 71 | 71 | 0 | 0 | -26.9801 | 38.8669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 4 | 2140 | 6.2 | 6.2 | 10.3625 | 6.5492 | 15 | 71 | 71 | 0 | 0 | -20.3332 | 53.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 5 | 2141 | 5.5 | 5.5 | 10.3625 | 6.5492 | 15 | 73 | 73 | 0 | 0 | -12.3525 | 66.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 6 | 2142 | 4.9 | 4.9 | 10.3625 | 6.5492 | 15 | 75 | 75 | 0 | 0 | -3.5618 | 78.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 7 | 2143 | 6.3 | 6.3 | 10.3625 | 6.5492 | 15 | 69 | 69 | 0 | 19 | 5.5997 | 90.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 19 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 9.2814 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2004 | 3 | 31 | 8 | 2144 | 9.2 | 9.2 | 10.3625 | 6.5492 | 15 | 60 | 60 | 513.4904 | 37.7031 | 14.7322 | 102.8799 | 0 | 356.1453 | 510.9875 | 366.5002 | 7.322 | 0 | 0 | 0 | 104.2969 | 29.3619 | 83.6011 | 107.1828 | 85.1781 | 30.477 | 29.3619 | 29.3619 | 29.3619 | 37.7031 | 29.3619 | 439.7464 | 618.1703 | 451.6783 | 37.799 | 29.3619 | 29.3619 | 29.3619 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 9 | 2145 | 10.9 | 10.9 | 10.3625 | 6.5492 | 15 | 53 | 53 | 673.6029 | 78.4843 | 23.4135 | 115.797 | 0 | 346.3777 | 635.0671 | 551.7428 | 145.2151 | 0 | 0 | 0 | 204.5157 | 59.3261 | 106.6939 | 146.1728 | 134.778 | 79.1846 | 59.3261 | 59.3261 | 59.3261 | 78.4843 | 59.3261 | 453.0716 | 781.2399 | 686.5208 | 224.3996 | 59.3261 | 59.3261 | 59.3261 | 283 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 10 | 2146 | 12.5 | 12.5 | 10.3625 | 6.5492 | 15 | 50 | 50 | 763.6227 | 95.4541 | 31.1324 | 130.2488 | 0 | 230.4862 | 630.911 | 661.7566 | 304.9542 | 0 | 0 | 0 | 335.5459 | 80.5963 | 109.5353 | 159.8112 | 163.6841 | 118.8852 | 80.5963 | 80.5963 | 80.5963 | 95.4541 | 80.5963 | 340.0216 | 790.7222 | 825.4407 | 423.8394 | 80.5963 | 80.5963 | 80.5963 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 11 | 2147 | 14.7 | 14.7 | 10.3625 | 6.5492 | 15 | 45 | 45 | 671.1749 | 142.5466 | 37.2364 | 146.8027 | 0 | 47.5858 | 438.4914 | 572.5347 | 371.1949 | 0 | 0 | 0 | 368.4534 | 102.6221 | 110.8417 | 178.3637 | 201.5173 | 166.7394 | 102.6221 | 102.6221 | 102.6221 | 142.5466 | 102.6221 | 158.4275 | 616.8552 | 774.052 | 537.9343 | 102.6221 | 102.6221 | 102.6221 | 511 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 12 | 2148 | 15.2 | 15.2 | 10.3625 | 6.5492 | 15 | 39 | 39 | 831.93 | 119.2186 | 40.9672 | 165.521 | 0 | 0 | 362.645 | 648.3337 | 554.2374 | 135.4762 | 0 | 0 | 519.7814 | 109.5673 | 109.5673 | 143.8881 | 170.9258 | 162.0205 | 122.3888 | 109.5673 | 109.5673 | 119.2186 | 109.5673 | 109.5673 | 506.5331 | 819.2595 | 716.2578 | 257.865 | 109.5673 | 109.5673 | 639 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 13 | 2149 | 16.2 | 16.2 | 10.3625 | 6.5492 | 15 | 39 | 39 | 834.7937 | 125.6403 | 41.6928 | 185.4709 | 0 | 0 | 157.6011 | 543.0026 | 610.3205 | 320.1209 | 0 | 0 | 552.3597 | 114.7173 | 114.7173 | 129.8594 | 166.8882 | 173.356 | 145.4741 | 114.7173 | 114.7173 | 125.6403 | 114.7173 | 114.7173 | 287.4605 | 709.8908 | 783.6765 | 465.595 | 114.7173 | 114.7173 | 678 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 14 | 2150 | 16.8 | 16.8 | 10.3625 | 6.5492 | 15 | 38 | 38 | 785.8851 | 136.6192 | 39.271 | 204.9306 | 0 | 0 | 0 | 373.5042 | 584.1641 | 452.6286 | 55.9494 | 0 | 516.3808 | 115.1934 | 115.1934 | 115.1934 | 155.4478 | 178.1517 | 163.9754 | 121.2233 | 115.1934 | 136.6192 | 115.1934 | 115.1934 | 115.1934 | 528.952 | 762.3158 | 616.604 | 177.1727 | 115.1934 | 653 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 15 | 2151 | 17.4 | 17.4 | 10.3625 | 6.5492 | 15 | 39 | 39 | 723.5725 | 143.6808 | 34.1508 | 222.5117 | 0 | 0 | 0 | 192.2241 | 507.9653 | 526.1473 | 236.1194 | 0 | 442.3192 | 109.5921 | 109.5921 | 109.5921 | 140.0466 | 190.0704 | 192.951 | 147.0011 | 109.5921 | 143.6808 | 109.5921 | 109.5921 | 109.5921 | 332.2707 | 698.0357 | 719.0983 | 383.1205 | 109.5921 | 586 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 16 | 2152 | 17.3 | 17.3 | 10.3625 | 6.5492 | 15 | 42 | 42 | 336.1924 | 219.6525 | 27.0759 | 237.8661 | 0 | 0 | 0 | 12.0792 | 205.0873 | 277.958 | 188.0047 | 0 | 177.3475 | 115.359 | 115.359 | 115.359 | 120.8684 | 208.9011 | 242.1381 | 201.1096 | 115.359 | 219.6525 | 115.359 | 115.359 | 115.359 | 132.9476 | 413.9884 | 520.0961 | 389.1143 | 115.359 | 397 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 17 | 2153 | 17.4 | 17.4 | 10.3625 | 6.5492 | 15 | 43 | 43 | 168.9567 | 191.4788 | 18.7608 | 251.3976 | 0 | 0 | 0 | 0 | 80.0189 | 146.6628 | 127.3936 | 33.4989 | 69.5212 | 94.1516 | 94.1516 | 94.1516 | 94.1516 | 148.3797 | 193.5437 | 180.4851 | 116.8535 | 191.4788 | 94.1516 | 94.1516 | 94.1516 | 94.1516 | 228.3987 | 340.2064 | 307.8787 | 150.3525 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 18 | 2154 | 16.5 | 16.5 | 10.3625 | 6.5492 | 15 | 40 | 40 | 311.9286 | 115.4393 | 9.7772 | 263.7636 | 0 | 0 | 0 | 0 | 94.2181 | 264.559 | 279.9249 | 131.3145 | 84.5607 | 64.6643 | 64.6643 | 64.6643 | 64.6643 | 97.2535 | 156.1729 | 161.4878 | 110.0848 | 115.4393 | 64.6643 | 64.6643 | 64.6643 | 64.6643 | 191.4716 | 420.7319 | 441.4126 | 241.3993 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 19 | 2155 | 13.2 | 13.2 | 10.3625 | 6.5492 | 15 | 50 | 50 | 19.6753 | 44.7191 | 0.57945 | 275.6298 | 0 | 0 | 0 | 0 | 2.1063 | 15.1187 | 19.2748 | 12.1399 | 2.2809 | 22.5361 | 22.5361 | 22.5361 | 22.5361 | 24.8309 | 39.0075 | 43.5354 | 35.7622 | 44.7191 | 22.5361 | 22.5361 | 22.5361 | 22.5361 | 26.9372 | 54.1262 | 62.8102 | 47.9022 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 20 | 2156 | 13.3 | 13.3 | 10.3625 | 6.5492 | 15 | 51 | 51 | 0 | 0 | -8.4306 | 287.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 21 | 2157 | 11.8 | 11.8 | 10.3625 | 6.5492 | 15 | 54 | 54 | 0 | 0 | -16.8384 | 300.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 22 | 2158 | 9.8 | 9.8 | 10.3625 | 6.5492 | 15 | 59 | 59 | 0 | 0 | -24.1625 | 314.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 23 | 2159 | 9.5 | 9.5 | 10.3625 | 6.5492 | 15 | 62 | 62 | 0 | 0 | -29.8291 | 329.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2004 | 3 | 31 | 24 | 2160 | 9.1 | 9.1 | 11.4958 | 8.0101 | 15 | 65 | 65 | 0 | 0 | -33.2254 | 346.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 1 | 2161 | 8.9 | 8.9 | 11.4958 | 8.0101 | 15 | 76 | 76 | 0 | 0 | -33.8793 | 4.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 2 | 2162 | 9.3 | 9.3 | 11.4958 | 8.0101 | 15 | 80 | 80 | 0 | 0 | -31.2924 | 22.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 3 | 2163 | 9.6 | 9.6 | 11.4958 | 8.0101 | 15 | 84 | 84 | 0 | 0 | -26.5917 | 38.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 4 | 2164 | 8.6 | 8.6 | 11.4958 | 8.0101 | 15 | 85 | 85 | 0 | 0 | -19.957 | 53.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 5 | 2165 | 6 | 6 | 11.4958 | 8.0101 | 15 | 90 | 90 | 0 | 0 | -11.988 | 66.5735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 6 | 2166 | 6 | 6 | 11.4958 | 8.0101 | 15 | 94 | 94 | 0 | 0 | -3.2051 | 78.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 7 | 2167 | 5.5 | 5.5 | 11.4958 | 8.0101 | 15 | 95 | 95 | 0 | 8 | 5.9539 | 90.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 8 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 3.8964 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 1 | 8 | 2168 | 9.2 | 9.2 | 11.4958 | 8.0101 | 15 | 95 | 95 | 200.0717 | 71.7693 | 15.0897 | 102.7032 | 0 | 139.1222 | 198.98 | 142.278 | 2.2315 | 0 | 0 | 0 | 31.2307 | 37.0009 | 101.7635 | 129.6278 | 103.2325 | 38.0397 | 37.0009 | 37.0009 | 37.0009 | 71.7693 | 37.0009 | 240.8857 | 328.6078 | 245.5105 | 40.2711 | 37.0009 | 37.0009 | 37.0009 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 9 | 2169 | 10.3 | 10.3 | 11.4958 | 8.0101 | 15 | 91 | 91 | 26.7282 | 124.746 | 23.78 | 115.6329 | 0 | 13.7886 | 25.1749 | 21.8141 | 5.6749 | 0 | 0 | 0 | 8.254 | 55.4252 | 97.8551 | 132.8928 | 122.5511 | 72.8879 | 55.4252 | 55.4252 | 55.4252 | 124.746 | 55.4252 | 111.6437 | 158.0677 | 144.3652 | 78.5628 | 55.4252 | 55.4252 | 55.4252 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 10 | 2170 | 11.2 | 11.2 | 11.4958 | 8.0101 | 15 | 83 | 83 | 80.0798 | 203.4006 | 31.5119 | 130.1157 | 0 | 24.3014 | 66.069 | 69.1343 | 31.7017 | 0 | 0 | 0 | 35.5994 | 93.7165 | 127.1399 | 184.5858 | 188.8017 | 137.318 | 93.7165 | 93.7165 | 93.7165 | 203.4006 | 93.7165 | 151.4413 | 250.6548 | 257.936 | 169.0196 | 93.7165 | 93.7165 | 93.7165 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 11 | 2171 | 13.1 | 13.1 | 11.4958 | 8.0101 | 15 | 74 | 74 | 507.3342 | 187.9104 | 37.6284 | 146.7304 | 0 | 36.8262 | 330.7663 | 430.9479 | 278.6861 | 0 | 0 | 0 | 281.0896 | 112.7826 | 123.3499 | 207.6955 | 236.4424 | 192.7512 | 112.7826 | 112.7826 | 112.7826 | 187.9104 | 112.7826 | 160.1761 | 538.4617 | 667.3904 | 471.4373 | 112.7826 | 112.7826 | 112.7826 | 469 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 12 | 2172 | 14.9 | 14.9 | 11.4958 | 8.0101 | 15 | 64 | 64 | 799.6964 | 127.3193 | 41.3629 | 165.5443 | 0 | 0 | 347.4424 | 620.1219 | 529.5423 | 128.764 | 0 | 0 | 503.6807 | 109.5553 | 109.5553 | 155.5989 | 191.7348 | 179.7311 | 126.6193 | 109.5553 | 109.5553 | 127.3193 | 109.5553 | 109.5553 | 503.0414 | 811.8566 | 709.2734 | 255.3834 | 109.5553 | 109.5553 | 631 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 13 | 2173 | 15.9 | 15.9 | 11.4958 | 8.0101 | 15 | 58 | 58 | 830.379 | 127.3816 | 42.0758 | 185.6068 | 0 | 0 | 155.5784 | 536.7501 | 603.5008 | 316.7289 | 0 | 0 | 553.6184 | 115.4387 | 115.4387 | 130.5833 | 167.6881 | 174.1858 | 146.2703 | 115.4387 | 115.4387 | 127.3816 | 115.4387 | 115.4387 | 286.1617 | 704.4381 | 777.6866 | 462.9993 | 115.4387 | 115.4387 | 681 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 14 | 2174 | 17 | 17 | 11.4958 | 8.0101 | 15 | 53 | 53 | 851.4097 | 122.2778 | 39.6255 | 205.1595 | 0 | 0 | 0 | 401.0702 | 628.9427 | 488.3891 | 61.7438 | 0 | 563.7222 | 114.3029 | 114.3029 | 114.3029 | 151.1887 | 172.1458 | 159.2193 | 119.9814 | 114.3029 | 122.2778 | 114.3029 | 114.3029 | 114.3029 | 552.259 | 801.0885 | 647.6084 | 181.7251 | 114.3029 | 686 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 15 | 2175 | 17 | 17 | 11.4958 | 8.0101 | 15 | 51 | 51 | 449.5007 | 225.9481 | 34.4711 | 222.7939 | 0 | 0 | 0 | 117.5076 | 313.3722 | 325.6676 | 147.1913 | 0 | 277.0519 | 124.8558 | 124.8558 | 124.8558 | 168.1823 | 240.4 | 244.9334 | 179.127 | 124.8558 | 225.9481 | 124.8558 | 124.8558 | 124.8558 | 285.6899 | 553.7722 | 570.601 | 326.3183 | 124.8558 | 503 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 16 | 2176 | 16.8 | 16.8 | 11.4958 | 8.0101 | 15 | 50 | 50 | 475.4921 | 188.7473 | 27.3662 | 238.1692 | 0 | 0 | 0 | 15.0897 | 287.6514 | 391.7108 | 266.3114 | 0 | 253.2527 | 109.7724 | 109.7724 | 109.7724 | 114.4326 | 198.6093 | 230.7465 | 192.0187 | 109.7724 | 188.7473 | 109.7724 | 109.7724 | 109.7724 | 129.5223 | 486.2607 | 622.4573 | 458.3301 | 109.7724 | 442 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 17 | 2177 | 16.9 | 16.9 | 11.4958 | 8.0101 | 15 | 53 | 53 | 209.6052 | 190.6741 | 19.0303 | 251.7045 | 0 | 0 | 0 | 0 | 98.1765 | 181.2523 | 158.1528 | 42.4097 | 87.3259 | 95.688 | 95.688 | 95.688 | 95.688 | 148.5663 | 193.3113 | 180.8699 | 118.53 | 190.6741 | 95.688 | 95.688 | 95.688 | 95.688 | 246.7429 | 374.5636 | 339.0227 | 160.9397 | 278 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 18 | 2178 | 16.4 | 16.4 | 11.4958 | 8.0101 | 15 | 54 | 54 | 180.8638 | 128.0266 | 10.0363 | 264.0678 | 0 | 0 | 0 | 0 | 53.6733 | 152.7416 | 162.336 | 76.8361 | 49.9734 | 65.4655 | 65.4655 | 65.4655 | 65.4655 | 92.2171 | 141.5943 | 146.3762 | 103.7618 | 128.0266 | 65.4655 | 65.4655 | 65.4655 | 65.4655 | 145.8905 | 294.3359 | 308.7122 | 180.5979 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 19 | 2179 | 14.5 | 14.5 | 11.4958 | 8.0101 | 15 | 60 | 60 | 28.8484 | 49.5031 | 0.83843 | 275.9296 | 0 | 0 | 0 | 0 | 2.9359 | 22.0552 | 28.2548 | 17.9031 | 3.4969 | 24.8533 | 24.8533 | 24.8533 | 24.8533 | 27.4569 | 44.4117 | 49.9095 | 40.7297 | 49.5031 | 24.8533 | 24.8533 | 24.8533 | 24.8533 | 30.3928 | 66.4669 | 78.1643 | 58.6329 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 20 | 2180 | 11.1 | 11.1 | 11.4958 | 8.0101 | 15 | 72 | 72 | 0 | 0 | -8.1619 | 287.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 21 | 2181 | 9.4 | 9.4 | 11.4958 | 8.0101 | 15 | 83 | 83 | 0 | 0 | -16.5508 | 300.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 22 | 2182 | 9.7 | 9.7 | 11.4958 | 8.0101 | 15 | 83 | 83 | 0 | 0 | -23.8482 | 314.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 23 | 2183 | 9.1 | 9.1 | 11.4958 | 8.0101 | 15 | 83 | 83 | 0 | 0 | -29.4838 | 330.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 1 | 24 | 2184 | 8.4 | 8.4 | 11.45 | 9.167 | 15 | 84 | 84 | 0 | 0 | -32.8516 | 347.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 1 | 2185 | 8.4 | 8.4 | 11.45 | 9.167 | 15 | 85 | 85 | 0 | 0 | -33.4873 | 4.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 2 | 2186 | 8 | 8 | 11.45 | 9.167 | 15 | 87 | 87 | 0 | 0 | -30.898 | 22.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 3 | 2187 | 9.1 | 9.1 | 11.45 | 9.167 | 15 | 83 | 83 | 0 | 0 | -26.2047 | 38.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 4 | 2188 | 9.3 | 9.3 | 11.45 | 9.167 | 15 | 74 | 74 | 0 | 0 | -19.5822 | 53.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 5 | 2189 | 8.8 | 8.8 | 11.45 | 9.167 | 15 | 75 | 75 | 0 | 0 | -11.6248 | 66.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 6 | 2190 | 8 | 8 | 11.45 | 9.167 | 15 | 76 | 76 | 0 | 0 | -2.8498 | 78.6288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 7 | 2191 | 8.6 | 8.6 | 11.45 | 9.167 | 15 | 73 | 73 | 2.8318 | 1.32 | 6.3066 | 90.4642 | 0.55763 | 2.3549 | 2.7728 | 1.5663 | 0 | 0 | 0 | 0 | 6.68 | 1.4376 | 2.2561 | 2.4464 | 1.897 | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 1.32 | 1.9952 | 4.6111 | 5.2192 | 3.4633 | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 2 | 8 | 2192 | 10.7 | 10.7 | 11.45 | 9.167 | 15 | 65 | 65 | 237.9111 | 72.6142 | 15.4456 | 102.5263 | 0 | 165.8503 | 236.4636 | 168.5596 | 1.9158 | 0 | 0 | 0 | 38.3858 | 38.3345 | 104.6267 | 132.8515 | 105.7096 | 39.1002 | 38.3345 | 38.3345 | 38.3345 | 72.6142 | 38.3345 | 270.477 | 369.3151 | 274.2692 | 41.016 | 38.3345 | 38.3345 | 38.3345 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 9 | 2193 | 12.4 | 12.4 | 11.45 | 9.167 | 15 | 60 | 60 | 497.0375 | 107.9394 | 24.1449 | 115.4681 | 0 | 257.2273 | 467.6823 | 404.1754 | 103.908 | 0 | 0 | 0 | 156.0606 | 68.0098 | 123.2072 | 168.3679 | 154.7402 | 90.307 | 68.0098 | 68.0098 | 68.0098 | 107.9394 | 68.0098 | 380.4345 | 636.0503 | 558.9156 | 194.215 | 68.0098 | 68.0098 | 68.0098 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 10 | 2194 | 14.7 | 14.7 | 11.45 | 9.167 | 15 | 53 | 53 | 665.8259 | 117.614 | 31.8898 | 129.9816 | 0 | 203.1317 | 548.5341 | 572.6127 | 261.2625 | 0 | 0 | 0 | 299.386 | 85.9534 | 118.3583 | 173.459 | 177.3002 | 127.6317 | 85.9534 | 85.9534 | 85.9534 | 117.614 | 85.9534 | 321.49 | 721.9931 | 749.9129 | 388.8942 | 85.9534 | 85.9534 | 85.9534 | 417 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 11 | 2195 | 17.1 | 17.1 | 11.45 | 9.167 | 15 | 46 | 46 | 744.4379 | 125.7891 | 38.0189 | 146.6571 | 0 | 55.2911 | 484.3294 | 629.654 | 406.1359 | 0 | 0 | 0 | 416.2109 | 100.8557 | 108.8474 | 170.8597 | 191.8646 | 159.5577 | 100.8557 | 100.8557 | 100.8557 | 125.7891 | 100.8557 | 164.1385 | 655.189 | 821.5186 | 565.6936 | 100.8557 | 100.8557 | 100.8557 | 542 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 12 | 2196 | 18.6 | 18.6 | 11.45 | 9.167 | 15 | 42 | 42 | 807.7582 | 126.1995 | 41.7573 | 165.5673 | 0 | 0 | 349.7734 | 623.233 | 531.6112 | 128.5788 | 0 | 0 | 512.8005 | 111.4865 | 111.4865 | 146.7489 | 174.3178 | 165.0809 | 124.4492 | 111.4865 | 111.4865 | 126.1995 | 111.4865 | 111.4865 | 496.5223 | 797.5508 | 696.6921 | 253.028 | 111.4865 | 111.4865 | 639 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 13 | 2197 | 19.3 | 19.3 | 11.45 | 9.167 | 15 | 41 | 41 | 719.5536 | 158.6818 | 42.4574 | 185.7434 | 0 | 0 | 133.7852 | 462.174 | 519.8276 | 272.9733 | 0 | 0 | 483.3182 | 118.9104 | 118.9104 | 141.5878 | 197.2519 | 207.0246 | 165.1811 | 118.9104 | 118.9104 | 158.6818 | 118.9104 | 118.9104 | 275.373 | 659.4259 | 726.8522 | 438.1544 | 118.9104 | 118.9104 | 642 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 14 | 2198 | 20.2 | 20.2 | 11.45 | 9.167 | 15 | 34 | 34 | 774.2603 | 141.4966 | 39.9785 | 205.3895 | 0 | 0 | 0 | 361.4733 | 568.3657 | 442.3172 | 57.1653 | 0 | 516.5034 | 115.5723 | 115.5723 | 115.5723 | 168.1017 | 198.1673 | 179.8499 | 123.8796 | 115.5723 | 141.4966 | 115.5723 | 115.5723 | 115.5723 | 529.575 | 766.533 | 622.1671 | 181.0448 | 115.5723 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 15 | 2199 | 20.3 | 20.3 | 11.45 | 9.167 | 15 | 35 | 35 | 728.7491 | 144.1806 | 34.7898 | 223.077 | 0 | 0 | 0 | 187.4223 | 504.4935 | 526.0392 | 239.4383 | 0 | 452.8194 | 110.7032 | 110.7032 | 110.7032 | 140.196 | 190.0905 | 193.4809 | 148.3813 | 110.7032 | 144.1806 | 110.7032 | 110.7032 | 110.7032 | 327.6184 | 694.584 | 719.5201 | 387.8196 | 110.7032 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 16 | 2200 | 20.4 | 20.4 | 11.45 | 9.167 | 15 | 33 | 33 | 620.1915 | 152.5454 | 27.655 | 238.4726 | 0 | 0 | 0 | 17.0915 | 372.0355 | 509.0461 | 347.8644 | 0 | 333.4546 | 102.6368 | 102.6368 | 102.6368 | 105.9415 | 174.5703 | 201.0615 | 169.8968 | 102.6368 | 152.5454 | 102.6368 | 102.6368 | 102.6368 | 123.033 | 546.6058 | 710.1076 | 517.7612 | 102.6368 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 17 | 2201 | 20 | 20 | 11.45 | 9.167 | 15 | 33 | 33 | 380.4029 | 167.572 | 19.2985 | 252.0111 | 0 | 0 | 0 | 0 | 176.1907 | 327.6728 | 287.2087 | 78.5015 | 160.428 | 93.222 | 93.222 | 93.222 | 93.222 | 156.0109 | 209.9944 | 195.5743 | 121.1975 | 167.572 | 93.222 | 93.222 | 93.222 | 93.222 | 332.2017 | 537.6673 | 482.7829 | 199.6991 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 2 | 18 | 2202 | 19 | 19 | 11.45 | 9.167 | 15 | 33 | 33 | 92.5708 | 129.9425 | 10.2945 | 264.3711 | 0 | 0 | 0 | 0 | 26.9825 | 77.8389 | 83.0983 | 39.6798 | 26.0575 | 63.9089 | 63.9089 | 63.9089 | 63.9089 | 90.3798 | 140.272 | 145.4317 | 102.8364 | 129.9425 | 63.9089 | 63.9089 | 63.9089 | 63.9089 | 117.3624 | 218.1109 | 228.53 | 142.5162 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 19 | 2203 | 17.2 | 17.2 | 11.45 | 9.167 | 15 | 38 | 38 | 8.0881 | 40.977 | 1.0967 | 276.2281 | 0 | 0 | 0 | 0 | 0.78055 | 6.1519 | 7.9195 | 5.048 | 1.023 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 40.977 | 20.1437 | 20.1437 | 20.1437 | 20.1437 | 20.9243 | 26.2956 | 28.0633 | 25.1918 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 20 | 2204 | 14.4 | 14.4 | 11.45 | 9.167 | 15 | 46 | 46 | 0 | 0 | -7.8937 | 288.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 21 | 2205 | 13.2 | 13.2 | 11.45 | 9.167 | 15 | 52 | 52 | 0 | 0 | -16.2636 | 300.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 22 | 2206 | 13.3 | 13.3 | 11.45 | 9.167 | 15 | 53 | 53 | 0 | 0 | -23.5343 | 314.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 23 | 2207 | 12.5 | 12.5 | 11.45 | 9.167 | 15 | 55 | 55 | 0 | 0 | -29.1392 | 330.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 2 | 24 | 2208 | 12.7 | 12.7 | 14.0083 | 10.7729 | 15 | 55 | 55 | 0 | 0 | -32.4788 | 347.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 1 | 2209 | 12.5 | 12.5 | 14.0083 | 10.7729 | 15 | 55 | 55 | 0 | 0 | -33.0967 | 5.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 2 | 2210 | 11.9 | 11.9 | 14.0083 | 10.7729 | 15 | 58 | 58 | 0 | 0 | -30.5051 | 22.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 3 | 2211 | 12.1 | 12.1 | 14.0083 | 10.7729 | 15 | 57 | 57 | 0 | 0 | -25.8191 | 38.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 4 | 2212 | 11.7 | 11.7 | 14.0083 | 10.7729 | 15 | 58 | 58 | 0 | 0 | -19.2088 | 53.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 5 | 2213 | 11.7 | 11.7 | 14.0083 | 10.7729 | 15 | 57 | 57 | 0 | 0 | -11.2631 | 66.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 6 | 2214 | 11.2 | 11.2 | 14.0083 | 10.7729 | 15 | 57 | 57 | 0 | 0 | -2.4961 | 78.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 7 | 2215 | 10.2 | 10.2 | 14.0083 | 10.7729 | 15 | 61 | 61 | 3.1286 | 2.31 | 6.6576 | 90.2859 | 0.62545 | 2.6077 | 3.0624 | 1.7232 | 0 | 0 | 0 | 0 | 11.69 | 2.4729 | 3.9728 | 4.3168 | 3.3035 | 1.9996 | 1.9996 | 1.9996 | 1.9996 | 2.31 | 3.0983 | 6.5805 | 7.3792 | 5.0267 | 1.9996 | 1.9996 | 1.9996 | 1.9996 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 3 | 8 | 2216 | 11.5 | 11.5 | 14.0083 | 10.7729 | 15 | 57 | 57 | 364.7677 | 67.2421 | 15.7999 | 102.3491 | 0 | 254.9088 | 362.3035 | 257.4657 | 1.808 | 0 | 0 | 0 | 60.7579 | 38.4562 | 86.7696 | 107.1243 | 87.2542 | 38.7988 | 38.4562 | 38.4562 | 38.4562 | 67.2421 | 38.4562 | 341.6783 | 469.4278 | 344.7199 | 40.6068 | 38.4562 | 38.4562 | 38.4562 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 9 | 2217 | 13.5 | 13.5 | 14.0083 | 10.7729 | 15 | 52 | 52 | 624.1991 | 89.808 | 24.508 | 115.3025 | 0 | 324.044 | 586.7194 | 505.7025 | 128.452 | 0 | 0 | 0 | 199.192 | 63.5415 | 113.0561 | 153.1935 | 140.8139 | 83.1693 | 63.5415 | 63.5415 | 63.5415 | 89.808 | 63.5415 | 437.1001 | 739.9129 | 646.5165 | 211.6213 | 63.5415 | 63.5415 | 63.5415 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 10 | 2218 | 15.5 | 15.5 | 14.0083 | 10.7729 | 15 | 47 | 47 | 769.0696 | 97.3005 | 32.2659 | 129.8465 | 0 | 235.8628 | 632.6445 | 658.8316 | 299.0841 | 0 | 0 | 0 | 349.6995 | 82.7951 | 112.2543 | 161.8123 | 165.083 | 120.1507 | 82.7951 | 82.7951 | 82.7951 | 97.3005 | 82.7951 | 348.1172 | 794.4568 | 823.9146 | 419.2347 | 82.7951 | 82.7951 | 82.7951 | 447 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 11 | 2219 | 16.6 | 16.6 | 14.0083 | 10.7729 | 15 | 44 | 44 | 788.5754 | 116.1706 | 38.4077 | 146.5828 | 0 | 59.8955 | 511.9475 | 664.1076 | 427.2424 | 0 | 0 | 0 | 444.8294 | 99.8006 | 107.5495 | 166.0332 | 185.7188 | 155.0746 | 99.8006 | 99.8006 | 99.8006 | 116.1706 | 99.8006 | 167.445 | 677.9807 | 849.8263 | 582.3171 | 99.8006 | 99.8006 | 99.8006 | 561 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 12 | 2220 | 17.8 | 17.8 | 14.0083 | 10.7729 | 15 | 41 | 41 | 836.8671 | 120.5714 | 42.1501 | 165.59 | 0 | 0 | 361.1571 | 642.4226 | 547.3657 | 131.6694 | 0 | 0 | 535.4286 | 111.4683 | 111.4683 | 145.4874 | 171.9812 | 163.0273 | 123.8709 | 111.4683 | 111.4683 | 120.5714 | 111.4683 | 111.4683 | 506.6445 | 814.4038 | 710.393 | 255.5403 | 111.4683 | 111.4683 | 656 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 13 | 2221 | 18.2 | 18.2 | 14.0083 | 10.7729 | 15 | 41 | 41 | 833.0546 | 128.3309 | 42.8375 | 185.8806 | 0 | 0 | 153.6997 | 531.6642 | 598.187 | 314.2999 | 0 | 0 | 563.6691 | 116.6404 | 116.6404 | 131.5807 | 168.3206 | 174.7869 | 147.1918 | 116.6404 | 116.6404 | 128.3309 | 116.6404 | 116.6404 | 285.2805 | 699.9848 | 772.9739 | 461.4917 | 116.6404 | 116.6404 | 692 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 14 | 2222 | 18.7 | 18.7 | 14.0083 | 10.7729 | 15 | 40 | 40 | 811.912 | 132.3687 | 40.3298 | 205.6206 | 0 | 0 | 0 | 375.6378 | 592.2303 | 461.9023 | 60.9982 | 0 | 545.6313 | 116.2458 | 116.2458 | 116.2458 | 154.4337 | 176.4529 | 163.2035 | 122.447 | 116.2458 | 132.3687 | 116.2458 | 116.2458 | 116.2458 | 530.0715 | 768.6832 | 625.1058 | 183.4452 | 116.2458 | 678 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 15 | 2223 | 19.2 | 19.2 | 14.0083 | 10.7729 | 15 | 38 | 38 | 814.6952 | 122.7325 | 35.1068 | 223.3607 | 0 | 0 | 0 | 206.0843 | 560.003 | 585.8796 | 268.5559 | 0 | 510.2675 | 109.4695 | 109.4695 | 109.4695 | 129.4747 | 163.8306 | 166.3425 | 135.539 | 109.4695 | 122.7325 | 109.4695 | 109.4695 | 109.4695 | 335.559 | 723.8336 | 752.2221 | 404.0948 | 109.4695 | 633 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 16 | 2224 | 19.3 | 19.3 | 14.0083 | 10.7729 | 15 | 35 | 35 | 767.5411 | 116.4759 | 27.9423 | 238.776 | 0 | 0 | 0 | 17.9624 | 456.5197 | 627.6539 | 431.117 | 0 | 416.5241 | 96.7815 | 96.7815 | 96.7815 | 99.137 | 156.6479 | 179.0899 | 153.3167 | 96.7815 | 116.4759 | 96.7815 | 96.7815 | 96.7815 | 117.0995 | 613.1676 | 806.7438 | 584.4337 | 96.7815 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 17 | 2225 | 19.2 | 19.2 | 14.0083 | 10.7729 | 15 | 35 | 35 | 635.5107 | 117.7607 | 19.5656 | 252.3171 | 0 | 0 | 0 | 0 | 291.0329 | 545.2727 | 480.0992 | 133.6901 | 271.2393 | 83.3256 | 83.3256 | 83.3256 | 83.3256 | 131.4684 | 173.5249 | 162.7439 | 105.4407 | 117.7607 | 83.3256 | 83.3256 | 83.3256 | 83.3256 | 422.5013 | 718.7976 | 642.843 | 239.1308 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 3 | 18 | 2226 | 18.8 | 18.8 | 14.0083 | 10.7729 | 15 | 33 | 33 | 444.7079 | 105.5291 | 10.5517 | 264.6735 | 0 | 0 | 0 | 0 | 127.2795 | 372.2997 | 399.2317 | 192.2992 | 127.4709 | 64.5 | 64.5 | 64.5 | 64.5 | 95.1207 | 154.0673 | 160.5465 | 110.763 | 105.5291 | 64.5 | 64.5 | 64.5 | 64.5 | 222.4002 | 526.367 | 559.7783 | 303.0623 | 233 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 19 | 2227 | 17 | 17 | 14.0083 | 10.7729 | 15 | 37 | 37 | 165.1279 | 61.2489 | 1.3543 | 276.5253 | 0 | 0 | 0 | 0 | 15.0697 | 124.9488 | 161.6346 | 103.6371 | 21.7511 | 33.4814 | 33.4814 | 33.4814 | 33.4814 | 41.2565 | 97.9479 | 116.8757 | 86.9522 | 61.2489 | 33.4814 | 33.4814 | 33.4814 | 33.4814 | 56.3261 | 222.8967 | 278.5103 | 190.5893 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 20 | 2228 | 15.4 | 15.4 | 14.0083 | 10.7729 | 15 | 42 | 42 | 0 | 0 | -7.6261 | 288.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 21 | 2229 | 14.5 | 14.5 | 14.0083 | 10.7729 | 15 | 46 | 46 | 0 | 0 | -15.9769 | 301.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 22 | 2230 | 13.9 | 13.9 | 14.0083 | 10.7729 | 15 | 47 | 47 | 0 | 0 | -23.221 | 315.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 23 | 2231 | 12.8 | 12.8 | 14.0083 | 10.7729 | 15 | 49 | 49 | 0 | 0 | -28.7953 | 330.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 3 | 24 | 2232 | 11.6 | 11.6 | 14.7833 | 12.207 | 15 | 54 | 54 | 0 | 0 | -32.1072 | 347.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 1 | 2233 | 11.1 | 11.1 | 14.7833 | 12.207 | 15 | 56 | 56 | 0 | 0 | -32.7074 | 5.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 2 | 2234 | 10.1 | 10.1 | 14.7833 | 12.207 | 15 | 60 | 60 | 0 | 0 | -30.1139 | 22.4755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 3 | 2235 | 9.5 | 9.5 | 14.7833 | 12.207 | 15 | 62 | 62 | 0 | 0 | -25.4353 | 38.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 4 | 2236 | 9.3 | 9.3 | 14.7833 | 12.207 | 15 | 61 | 61 | 0 | 0 | -18.8371 | 52.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 5 | 2237 | 8.4 | 8.4 | 14.7833 | 12.207 | 15 | 62 | 62 | 0 | 0 | -10.903 | 66.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 6 | 2238 | 7.8 | 7.8 | 14.7833 | 12.207 | 15 | 63 | 63 | 0 | 0 | -2.144 | 78.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 7 | 2239 | 7.6 | 7.6 | 14.7833 | 12.207 | 15 | 62 | 62 | 9.4353 | 2.805 | 7.007 | 90.1077 | 1.9144 | 7.8819 | 9.2323 | 5.1746 | 0 | 0 | 0 | 0 | 14.195 | 3.0693 | 4.8007 | 5.1925 | 4.0152 | 2.5138 | 2.5138 | 2.5138 | 2.5138 | 2.805 | 4.9836 | 12.6826 | 14.4249 | 9.1898 | 2.5138 | 2.5138 | 2.5138 | 2.5138 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 4 | 8 | 2240 | 8.4 | 8.4 | 14.7833 | 12.207 | 15 | 60 | 60 | 229.3432 | 77.6083 | 16.1523 | 102.1715 | 0 | 160.6561 | 227.6299 | 161.2612 | 0.4279 | 0 | 0 | 0 | 39.3917 | 40.8816 | 109.1501 | 137.6096 | 109.4072 | 41.0634 | 40.8816 | 40.8816 | 40.8816 | 77.6083 | 40.8816 | 269.8062 | 365.2396 | 270.6684 | 41.4913 | 40.8816 | 40.8816 | 40.8816 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 9 | 2241 | 10.3 | 10.3 | 14.7833 | 12.207 | 15 | 55 | 55 | 615.0848 | 92.5796 | 24.8693 | 115.1362 | 0 | 320.2909 | 577.524 | 496.4514 | 124.5643 | 0 | 0 | 0 | 199.4204 | 64.732 | 114.8108 | 155.0303 | 142.3543 | 84.2082 | 64.732 | 64.732 | 64.732 | 92.5796 | 64.732 | 435.1017 | 732.5543 | 638.8057 | 208.7725 | 64.732 | 64.732 | 64.732 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 10 | 2242 | 12.1 | 12.1 | 14.7833 | 12.207 | 15 | 52 | 52 | 762.2808 | 99.562 | 32.6403 | 129.7102 | 0 | 234.9933 | 626.1005 | 650.4465 | 293.7698 | 0 | 0 | 0 | 350.438 | 83.8141 | 113.7398 | 163.5461 | 166.6465 | 121.2248 | 83.8141 | 83.8141 | 83.8141 | 99.562 | 83.8141 | 348.733 | 789.6466 | 817.0931 | 414.9946 | 83.8141 | 83.8141 | 83.8141 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 11 | 2243 | 13.7 | 13.7 | 14.7833 | 12.207 | 15 | 49 | 49 | 814.8384 | 111.3197 | 38.7949 | 146.5074 | 0 | 63.2588 | 527.8485 | 683.2316 | 438.387 | 0 | 0 | 0 | 463.6803 | 101.3108 | 107.3068 | 151.3426 | 166.0705 | 142.8631 | 101.3108 | 101.3108 | 101.3108 | 111.3197 | 101.3108 | 170.5656 | 679.1911 | 849.3022 | 581.2501 | 101.3108 | 101.3108 | 101.3108 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 12 | 2244 | 15.1 | 15.1 | 14.7833 | 12.207 | 15 | 48 | 48 | 803.8711 | 128.736 | 42.5414 | 165.6122 | 0 | 0 | 345.7393 | 613.9386 | 522.5011 | 124.9895 | 0 | 0 | 518.264 | 112.8782 | 112.8782 | 148.235 | 175.6623 | 166.3115 | 125.6602 | 112.8782 | 112.8782 | 128.736 | 112.8782 | 112.8782 | 493.9743 | 789.6009 | 688.8125 | 250.6496 | 112.8782 | 112.8782 | 647 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 13 | 2245 | 16.2 | 16.2 | 14.7833 | 12.207 | 15 | 42 | 42 | 815.644 | 133.1246 | 43.2159 | 186.0182 | 0 | 0 | 149.3284 | 517.2046 | 582.1093 | 306.0223 | 0 | 0 | 555.8754 | 117.6156 | 117.6156 | 132.799 | 170.204 | 176.8034 | 148.7314 | 117.6156 | 117.6156 | 133.1246 | 117.6156 | 117.6156 | 282.1275 | 687.4086 | 758.9127 | 454.7537 | 117.6156 | 117.6156 | 689 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 14 | 2246 | 17.3 | 17.3 | 14.7833 | 12.207 | 15 | 39 | 39 | 849.6373 | 124.861 | 40.6794 | 205.8525 | 0 | 0 | 0 | 389.5206 | 615.785 | 481.3309 | 64.9197 | 0 | 575.139 | 116.2031 | 116.2031 | 116.2031 | 152.4579 | 173.5175 | 161.0031 | 122.2455 | 116.2031 | 124.861 | 116.2031 | 116.2031 | 116.2031 | 541.9784 | 789.3024 | 642.334 | 187.1652 | 116.2031 | 700 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 15 | 2247 | 18.3 | 18.3 | 14.7833 | 12.207 | 15 | 38 | 38 | 742.8779 | 142.0613 | 35.4222 | 223.645 | 0 | 0 | 0 | 184.7879 | 506.9924 | 532.2076 | 245.6628 | 0 | 468.9387 | 111.3623 | 111.3623 | 111.3623 | 139.5401 | 188.6721 | 192.5171 | 148.8227 | 111.3623 | 142.0613 | 111.3623 | 111.3623 | 111.3623 | 324.328 | 695.6645 | 724.7247 | 394.4855 | 111.3623 | 611 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 16 | 2248 | 18.1 | 18.1 | 14.7833 | 12.207 | 15 | 36 | 36 | 368.987 | 219.9284 | 28.2282 | 239.0794 | 0 | 0 | 0 | 7.1103 | 217.5873 | 300.6046 | 207.5318 | 0 | 202.0716 | 117.6492 | 117.6492 | 117.6492 | 120.5977 | 207.878 | 242.3035 | 203.7082 | 117.6492 | 219.9284 | 117.6492 | 117.6492 | 117.6492 | 127.708 | 425.4653 | 542.9081 | 411.2401 | 117.6492 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 17 | 2249 | 17.2 | 17.2 | 14.7833 | 12.207 | 15 | 35 | 35 | 286.151 | 187.4287 | 19.8314 | 252.6226 | 0 | 0 | 0 | 0 | 129.5514 | 244.5455 | 216.2882 | 61.3322 | 123.5713 | 98.1822 | 98.1822 | 98.1822 | 98.1822 | 161.2605 | 217.251 | 203.4926 | 128.0448 | 187.4287 | 98.1822 | 98.1822 | 98.1822 | 98.1822 | 290.8119 | 461.7966 | 419.7808 | 189.377 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 4 | 18 | 2250 | 15.3 | 15.3 | 14.7833 | 12.207 | 15 | 38 | 38 | 83.4092 | 133.6647 | 10.8079 | 264.9749 | 0 | 0 | 0 | 0 | 23.434 | 69.5195 | 74.8815 | 36.3788 | 24.3353 | 64.7302 | 64.7302 | 64.7302 | 64.7302 | 82.9119 | 118.6682 | 122.8283 | 92.9554 | 133.6647 | 64.7302 | 64.7302 | 64.7302 | 64.7302 | 106.3459 | 188.1877 | 197.7098 | 129.3342 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 19 | 2251 | 14.3 | 14.3 | 14.7833 | 12.207 | 15 | 43 | 43 | 188.7961 | 63.147 | 1.6112 | 276.8209 | 0 | 0 | 0 | 0 | 16.2438 | 142.113 | 184.7344 | 119.1409 | 25.853 | 34.7959 | 34.7959 | 34.7959 | 34.7959 | 42.2027 | 99.5963 | 119.0307 | 89.1215 | 63.147 | 34.7959 | 34.7959 | 34.7959 | 34.7959 | 58.4464 | 241.7093 | 303.7651 | 208.2623 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 20 | 2252 | 12.6 | 12.6 | 14.7833 | 12.207 | 15 | 47 | 47 | 0 | 3 | -7.359 | 288.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 3 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 1.3969 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 21 | 2253 | 11.8 | 11.8 | 14.7833 | 12.207 | 15 | 47 | 47 | 0 | 0 | -15.6907 | 301.4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 22 | 2254 | 10.5 | 10.5 | 14.7833 | 12.207 | 15 | 49 | 49 | 0 | 0 | -22.9083 | 315.3107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 23 | 2255 | 9.7 | 9.7 | 14.7833 | 12.207 | 15 | 49 | 49 | 0 | 0 | -28.4524 | 330.7134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 4 | 24 | 2256 | 8.6 | 8.6 | 12.2208 | 12.4843 | 15 | 49 | 49 | 0 | 0 | -31.7367 | 347.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 1 | 2257 | 7.8 | 7.8 | 12.2208 | 12.4843 | 15 | 49 | 49 | 0 | 0 | -32.3197 | 5.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 2 | 2258 | 7.3 | 7.3 | 12.2208 | 12.4843 | 15 | 50 | 50 | 0 | 0 | -29.7244 | 22.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 3 | 2259 | 6.7 | 6.7 | 12.2208 | 12.4843 | 15 | 52 | 52 | 0 | 0 | -25.0532 | 38.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 4 | 2260 | 6.1 | 6.1 | 12.2208 | 12.4843 | 15 | 53 | 53 | 0 | 0 | -18.4671 | 52.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 5 | 2261 | 5.2 | 5.2 | 12.2208 | 12.4843 | 15 | 55 | 55 | 0 | 0 | -10.5446 | 65.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 6 | 2262 | 4.7 | 4.7 | 12.2208 | 12.4843 | 15 | 55 | 55 | 0 | 0 | -1.7937 | 78.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 7 | 2263 | 4.7 | 4.7 | 12.2208 | 12.4843 | 15 | 57 | 57 | 25.4621 | 3.63 | 7.3544 | 89.9295 | 5.2416 | 21.3161 | 24.904 | 13.9034 | 0 | 0 | 0 | 0 | 18.37 | 3.8863 | 4.6104 | 4.7721 | 4.2765 | 3.6502 | 3.6502 | 3.6502 | 3.6502 | 3.63 | 9.1279 | 25.9266 | 29.6761 | 18.1799 | 3.6502 | 3.6502 | 3.6502 | 3.6502 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 5 | 8 | 2264 | 5.8 | 5.8 | 12.2208 | 12.4843 | 15 | 53 | 53 | 512.4834 | 59.3302 | 16.5027 | 101.9935 | 0.62538 | 359.8413 | 508.267 | 358.9568 | 0 | 0 | 0 | 0 | 90.6698 | 37.1166 | 86.4707 | 106.8635 | 86.3492 | 37.0307 | 37.0307 | 37.0307 | 37.0307 | 59.3302 | 37.742 | 446.312 | 615.1305 | 445.306 | 37.0307 | 37.0307 | 37.0307 | 37.0307 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 9 | 2265 | 7.7 | 7.7 | 12.2208 | 12.4843 | 15 | 48 | 48 | 734 | 75.3083 | 25.2285 | 114.9691 | 0 | 383.3639 | 688.4013 | 590.1826 | 146.243 | 0 | 0 | 0 | 241.6917 | 62.0874 | 109.0732 | 146.4591 | 134.4212 | 80.0112 | 62.0874 | 62.0874 | 62.0874 | 75.3083 | 62.0874 | 492.437 | 834.8604 | 724.6039 | 226.2542 | 62.0874 | 62.0874 | 62.0874 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 10 | 2266 | 10.2 | 10.2 | 12.2208 | 12.4843 | 15 | 41 | 41 | 851.308 | 85.3973 | 33.0126 | 129.5728 | 0 | 263.7819 | 698.1284 | 723.5208 | 325.0845 | 0 | 0 | 0 | 395.6027 | 83.9583 | 105.5514 | 141.1069 | 143.1855 | 110.5696 | 83.9583 | 83.9583 | 83.9583 | 85.3973 | 83.9583 | 369.3333 | 839.2353 | 866.7063 | 435.6541 | 83.9583 | 83.9583 | 83.9583 | 481 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 11 | 2267 | 11.9 | 11.9 | 12.2208 | 12.4843 | 15 | 38 | 38 | 858.1055 | 104.4877 | 39.1801 | 146.4307 | 0 | 68.0577 | 554.6525 | 716.3393 | 458.4043 | 0 | 0 | 0 | 492.5123 | 101.348 | 107.2102 | 149.1231 | 163.05 | 140.8328 | 101.348 | 101.348 | 101.348 | 104.4877 | 101.348 | 175.2679 | 703.7756 | 879.3894 | 599.2371 | 101.348 | 101.348 | 101.348 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 12 | 2268 | 12.7 | 12.7 | 12.2208 | 12.4843 | 15 | 33 | 33 | 868.6058 | 116.7795 | 42.9309 | 165.6338 | 0 | 0 | 372.3041 | 659.9566 | 561.0155 | 133.4391 | 0 | 0 | 564.2205 | 112.6895 | 112.6895 | 145.5978 | 171.0238 | 162.2783 | 124.4843 | 112.6895 | 112.6895 | 116.7795 | 112.6895 | 112.6895 | 517.902 | 830.9804 | 723.2937 | 257.9234 | 112.6895 | 112.6895 | 681 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 13 | 2269 | 13.2 | 13.2 | 12.2208 | 12.4843 | 15 | 33 | 33 | 878.0686 | 122.3338 | 43.5926 | 186.1562 | 0 | 0 | 159.5159 | 553.1786 | 622.7968 | 327.589 | 0 | 0 | 602.6662 | 118.018 | 118.018 | 132.1877 | 167.1564 | 173.3405 | 147.1175 | 118.018 | 118.018 | 122.3338 | 118.018 | 118.018 | 291.7036 | 720.335 | 796.1373 | 474.7065 | 118.018 | 118.018 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 14 | 2270 | 14 | 14 | 12.2208 | 12.4843 | 15 | 33 | 33 | 872.6274 | 122.0751 | 41.0273 | 206.0851 | 0 | 0 | 0 | 396.396 | 628.365 | 492.2463 | 67.7764 | 0 | 594.9249 | 116.9982 | 116.9982 | 116.9982 | 152.2796 | 172.9261 | 160.8108 | 123.0306 | 116.9982 | 122.0751 | 116.9982 | 116.9982 | 116.9982 | 548.6756 | 801.2912 | 653.0572 | 190.807 | 116.9982 | 717 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 15 | 2271 | 14.8 | 14.8 | 12.2208 | 12.4843 | 15 | 30 | 30 | 850.3926 | 117.0535 | 35.7358 | 223.9297 | 0 | 0 | 0 | 207.9617 | 576.1881 | 606.8914 | 282.0858 | 0 | 540.9465 | 110.1308 | 110.1308 | 110.1308 | 128.7646 | 161.7584 | 164.5094 | 135.4063 | 110.1308 | 117.0535 | 110.1308 | 110.1308 | 110.1308 | 336.7263 | 737.9465 | 771.4008 | 417.4921 | 110.1308 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 16 | 2272 | 14.5 | 14.5 | 12.2208 | 12.4843 | 15 | 31 | 31 | 808.6055 | 109.1978 | 28.5124 | 239.3826 | 0 | 0 | 0 | 12.2604 | 472.7049 | 656.2453 | 455.3661 | 0 | 446.8022 | 98.399 | 98.399 | 98.399 | 99.5323 | 142.0958 | 159.0622 | 140.493 | 98.399 | 109.1978 | 98.399 | 98.399 | 98.399 | 111.7927 | 614.8007 | 815.3076 | 595.8591 | 98.399 | 556 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 17 | 2273 | 13.6 | 13.6 | 12.2208 | 12.4843 | 15 | 37 | 37 | 693.4205 | 108.0907 | 20.0958 | 252.9273 | 0 | 0 | 0 | 0 | 310.3273 | 590.2211 | 524.3713 | 151.3519 | 302.9093 | 82.5326 | 82.5326 | 82.5326 | 82.5326 | 127.067 | 167.234 | 157.784 | 104.2528 | 108.0907 | 82.5326 | 82.5326 | 82.5326 | 82.5326 | 437.3944 | 757.455 | 682.1553 | 255.6047 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 5 | 18 | 2274 | 12.8 | 12.8 | 12.2208 | 12.4843 | 15 | 39 | 39 | 540.8296 | 95.4586 | 11.0631 | 265.275 | 0 | 0 | 0 | 0 | 149.1129 | 448.7544 | 485.5217 | 237.8769 | 160.5414 | 62.8206 | 62.8206 | 62.8206 | 62.8206 | 89.7562 | 143.8831 | 150.5247 | 105.7904 | 95.4586 | 62.8206 | 62.8206 | 62.8206 | 62.8206 | 238.869 | 592.6375 | 636.0463 | 343.6673 | 256 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 19 | 2275 | 11.6 | 11.6 | 12.2208 | 12.4843 | 15 | 42 | 42 | 231.5682 | 64.0892 | 1.8672 | 277.115 | 0 | 0 | 0 | 0 | 18.7205 | 173.3917 | 226.4924 | 146.9169 | 32.9108 | 35.9933 | 35.9933 | 35.9933 | 35.9933 | 43.2424 | 103.1355 | 123.6977 | 92.8837 | 64.0892 | 35.9933 | 35.9933 | 35.9933 | 35.9933 | 61.9629 | 276.5273 | 350.1901 | 239.8007 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 20 | 2276 | 9.9 | 9.9 | 12.2208 | 12.4843 | 15 | 46 | 46 | 0 | 6 | -7.0925 | 289.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 6 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 21 | 2277 | 8.9 | 8.9 | 12.2208 | 12.4843 | 15 | 46 | 46 | 0 | 0 | -15.405 | 301.7201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 22 | 2278 | 7.9 | 7.9 | 12.2208 | 12.4843 | 15 | 46 | 46 | 0 | 0 | -22.5962 | 315.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 23 | 2279 | 7 | 7 | 12.2208 | 12.4843 | 15 | 45 | 45 | 0 | 0 | -28.1103 | 330.9257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 5 | 24 | 2280 | 6 | 6 | 9.375 | 11.8755 | 15 | 48 | 48 | 0 | 0 | -31.3675 | 347.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 1 | 2281 | 5.3 | 5.3 | 9.375 | 11.8755 | 15 | 53 | 53 | 0 | 0 | -31.9336 | 5.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 2 | 2282 | 4.4 | 4.4 | 9.375 | 11.8755 | 15 | 55 | 55 | 0 | 0 | -29.3368 | 22.4358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 3 | 2283 | 3.5 | 3.5 | 9.375 | 11.8755 | 15 | 57 | 57 | 0 | 0 | -24.673 | 38.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 4 | 2284 | 2.3 | 2.3 | 9.375 | 11.8755 | 15 | 63 | 63 | 0 | 0 | -18.099 | 52.7406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 5 | 2285 | 1.3 | 1.3 | 9.375 | 11.8755 | 15 | 67 | 67 | 0 | 0 | -10.1882 | 65.7894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 6 | 2286 | 0.3 | 0.3 | 9.375 | 11.8755 | 15 | 69 | 69 | 0 | 0 | -1.4453 | 77.9435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 7 | 2287 | 0.1 | 0.1 | 9.375 | 11.8755 | 15 | 67 | 67 | 78.0638 | 8.413 | 7.6998 | 89.7513 | 16.3005 | 65.4909 | 76.3176 | 42.4385 | 0 | 0 | 0 | 0 | 10.587 | 5.7725 | 7.4336 | 7.7992 | 6.6552 | 5.2221 | 5.2221 | 5.2221 | 5.2221 | 8.413 | 22.073 | 72.9245 | 84.1168 | 49.0937 | 5.2221 | 5.2221 | 5.2221 | 5.2221 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 6 | 8 | 2288 | 0.9 | 0.9 | 9.375 | 11.8755 | 15 | 64 | 64 | 436.4483 | 67.5423 | 16.8511 | 101.8152 | 1.8774 | 307.1576 | 432.5091 | 304.5025 | 0 | 0 | 0 | 0 | 79.4577 | 41.4346 | 98.2615 | 121.5953 | 97.7673 | 41.0851 | 41.0851 | 41.0851 | 41.0851 | 67.5423 | 43.312 | 405.4192 | 554.1044 | 402.2698 | 41.0851 | 41.0851 | 41.0851 | 41.0851 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 9 | 2289 | 2.5 | 2.5 | 9.375 | 11.8755 | 15 | 57 | 57 | 735.4484 | 76.1342 | 25.5856 | 114.8011 | 0 | 385.257 | 688.9566 | 589.0748 | 144.1209 | 0 | 0 | 0 | 245.8658 | 62.9029 | 110.1004 | 147.3063 | 135.0699 | 80.5591 | 62.9029 | 62.9029 | 62.9029 | 76.1342 | 62.9029 | 495.3574 | 836.2629 | 724.1447 | 224.68 | 62.9029 | 62.9029 | 62.9029 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 10 | 2290 | 4.8 | 4.8 | 9.375 | 11.8755 | 15 | 45 | 45 | 842.4553 | 87.3544 | 33.3828 | 129.4341 | 0 | 262.3589 | 689.7639 | 713.1145 | 318.7323 | 0 | 0 | 0 | 395.6456 | 84.8033 | 106.72 | 142.4242 | 144.3748 | 111.4293 | 84.8033 | 84.8033 | 84.8033 | 87.3544 | 84.8033 | 369.0789 | 832.188 | 857.4893 | 430.1616 | 84.8033 | 84.8033 | 84.8033 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 11 | 2291 | 6.6 | 6.6 | 9.375 | 11.8755 | 15 | 41 | 41 | 883.2944 | 102.7376 | 39.5634 | 146.3528 | 0 | 71.537 | 569.6606 | 734.0848 | 468.492 | 0 | 0 | 0 | 511.2624 | 102.4475 | 108.3485 | 149.4381 | 163.0012 | 141.0928 | 102.4475 | 102.4475 | 102.4475 | 102.7376 | 102.4475 | 179.8855 | 719.0987 | 897.086 | 609.5848 | 102.4475 | 102.4475 | 102.4475 | 614 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 12 | 2292 | 8.2 | 8.2 | 9.375 | 11.8755 | 15 | 38 | 38 | 901.2417 | 116.2455 | 43.3186 | 165.6546 | 0 | 0 | 384.965 | 681.1912 | 578.3847 | 136.7684 | 0 | 0 | 589.7545 | 114.9547 | 114.9547 | 147.574 | 172.6742 | 163.9631 | 126.5435 | 114.9547 | 114.9547 | 116.2455 | 114.9547 | 114.9547 | 532.539 | 853.8654 | 742.3478 | 263.3119 | 114.9547 | 114.9547 | 706 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 13 | 2293 | 8.8 | 8.8 | 9.375 | 11.8755 | 15 | 38 | 38 | 899.0887 | 122.6041 | 43.9676 | 186.2944 | 0 | 0 | 162.0719 | 562.7214 | 633.7364 | 333.5172 | 0 | 0 | 621.3959 | 119.9086 | 119.9086 | 133.9668 | 168.7194 | 174.8793 | 148.8381 | 119.9086 | 119.9086 | 122.6041 | 119.9086 | 119.9086 | 296.0387 | 731.4408 | 808.6157 | 482.3553 | 119.9086 | 119.9086 | 744 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 14 | 2294 | 10.2 | 10.2 | 9.375 | 11.8755 | 15 | 36 | 36 | 882.8338 | 121.8895 | 41.3733 | 206.3183 | 0 | 0 | 0 | 397.3306 | 631.5742 | 495.8502 | 69.6639 | 0 | 606.1105 | 117.955 | 117.955 | 117.955 | 152.8143 | 173.3654 | 161.4578 | 124.0669 | 117.955 | 121.8895 | 117.955 | 117.955 | 117.955 | 550.1449 | 804.9396 | 657.3081 | 193.7308 | 117.955 | 728 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 15 | 2295 | 10.8 | 10.8 | 9.375 | 11.8755 | 15 | 34 | 34 | 893.2312 | 113.4996 | 36.0477 | 224.2146 | 0 | 0 | 0 | 214.7033 | 600.8176 | 634.9811 | 297.1813 | 0 | 572.5004 | 111.7768 | 111.7768 | 111.7768 | 129.6516 | 161.7971 | 164.6414 | 136.5182 | 111.7768 | 113.4996 | 111.7768 | 111.7768 | 111.7768 | 344.3549 | 762.6147 | 799.6224 | 433.6995 | 111.7768 | 686 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 16 | 2296 | 10.7 | 10.7 | 9.375 | 11.8755 | 15 | 36 | 36 | 872.3234 | 99.7383 | 28.7951 | 239.6854 | 0 | 0 | 0 | 9.6678 | 505.5098 | 705.231 | 491.8375 | 0 | 486.2617 | 98.337 | 98.337 | 98.337 | 99.1122 | 138.8684 | 154.8819 | 137.7722 | 98.337 | 99.7383 | 98.337 | 98.337 | 98.337 | 108.7799 | 644.3782 | 860.113 | 629.6097 | 98.337 | 586 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 17 | 2297 | 10.5 | 10.5 | 9.375 | 11.8755 | 15 | 37 | 37 | 807.121 | 87.4252 | 20.359 | 253.2311 | 0 | 0 | 0 | 0 | 357.0171 | 684.2121 | 610.6048 | 179.3136 | 356.5748 | 80.8116 | 80.8116 | 80.8116 | 80.8116 | 110.9096 | 138.4935 | 132.2881 | 95.9285 | 87.4252 | 80.8116 | 80.8116 | 80.8116 | 80.8116 | 467.9268 | 822.7056 | 742.893 | 275.2421 | 444 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 6 | 18 | 2298 | 10.3 | 10.3 | 9.375 | 11.8755 | 15 | 39 | 39 | 674.8894 | 77.2567 | 11.3173 | 265.5738 | 0 | 0 | 0 | 0 | 182.5503 | 557.4646 | 605.8237 | 299.2995 | 203.7433 | 59.4889 | 59.4889 | 59.4889 | 59.4889 | 83.1034 | 131.602 | 137.8577 | 98.206 | 77.2567 | 59.4889 | 59.4889 | 59.4889 | 59.4889 | 265.6537 | 689.0666 | 743.6814 | 397.5055 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 19 | 2299 | 9.4 | 9.4 | 9.375 | 11.8755 | 15 | 41 | 41 | 341.1714 | 60.7532 | 2.1226 | 277.4073 | 0 | 0 | 0 | 0 | 25.8179 | 254.1042 | 333.5397 | 217.5921 | 50.2468 | 36.2417 | 36.2417 | 36.2417 | 36.2417 | 42.8628 | 101.4078 | 121.7794 | 92.0442 | 60.7532 | 36.2417 | 36.2417 | 36.2417 | 36.2417 | 68.6808 | 355.512 | 455.3191 | 309.6363 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 20 | 2300 | 8 | 8 | 9.375 | 11.8755 | 15 | 44 | 44 | 0 | 8 | -6.8266 | 289.3567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 8 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 3.8206 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 21 | 2301 | 6.9 | 6.9 | 9.375 | 11.8755 | 15 | 57 | 57 | 0 | 0 | -15.1199 | 301.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 22 | 2302 | 5.8 | 5.8 | 9.375 | 11.8755 | 15 | 65 | 65 | 0 | 0 | -22.2848 | 315.8144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 23 | 2303 | 4.6 | 4.6 | 9.375 | 11.8755 | 15 | 67 | 67 | 0 | 0 | -27.7692 | 331.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 6 | 24 | 2304 | 3 | 3 | 5.8 | 10.3583 | 15 | 70 | 70 | 0 | 0 | -30.9997 | 347.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 1 | 2305 | 2.9 | 2.9 | 5.8 | 10.3583 | 15 | 72 | 72 | 0 | 0 | -31.5492 | 5.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 2 | 2306 | 2.2 | 2.2 | 5.8 | 10.3583 | 15 | 75 | 75 | 0 | 0 | -28.9512 | 22.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 3 | 2307 | 1.8 | 1.8 | 5.8 | 10.3583 | 15 | 78 | 78 | 0 | 0 | -24.2948 | 38.2654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 4 | 2308 | -0.1 | -0.1 | 5.8 | 10.3583 | 15 | 81 | 81 | 0 | 0 | -17.7329 | 52.6119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 5 | 2309 | 0 | 0 | 5.8 | 10.3583 | 15 | 87 | 87 | 0 | 0 | -9.8337 | 65.6342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 6 | 2310 | -0.8 | -0.8 | 5.8 | 10.3583 | 15 | 87 | 87 | 0 | 0 | -1.099 | 77.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 7 | 2311 | 1.5 | 1.5 | 5.8 | 10.3583 | 15 | 89 | 89 | 114.2298 | 6.0076 | 8.0431 | 89.5731 | 24.1879 | 96.0294 | 111.6181 | 61.8224 | 0 | 0 | 0 | 0 | 21.9924 | 5.5865 | 6.7754 | 7.0334 | 6.2093 | 5.1862 | 5.1862 | 5.1862 | 5.1862 | 6.0076 | 29.7744 | 102.8047 | 118.6514 | 68.0317 | 5.1862 | 5.1862 | 5.1862 | 5.1862 | 28 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 7 | 8 | 2312 | 4.2 | 4.2 | 5.8 | 10.3583 | 15 | 85 | 85 | 506.7788 | 63.1535 | 17.1972 | 101.6364 | 3.7392 | 357.4558 | 501.7797 | 352.1679 | 0 | 0 | 0 | 0 | 94.8465 | 39.8401 | 90.9379 | 111.7869 | 90.174 | 39.2999 | 39.2999 | 39.2999 | 39.2999 | 63.1535 | 43.5792 | 448.3938 | 613.5667 | 442.3419 | 39.2999 | 39.2999 | 39.2999 | 39.2999 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 9 | 2313 | 6.2 | 6.2 | 5.8 | 10.3583 | 15 | 77 | 77 | 726.3204 | 78.5623 | 25.9404 | 114.6323 | 0 | 381.5824 | 679.5883 | 579.5007 | 139.9494 | 0 | 0 | 0 | 246.4377 | 64.0306 | 111.8841 | 149.2565 | 136.7047 | 81.5814 | 64.0306 | 64.0306 | 64.0306 | 78.5623 | 64.0306 | 493.4665 | 828.8448 | 716.2054 | 221.5307 | 64.0306 | 64.0306 | 64.0306 | 325 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 10 | 2314 | 7.7 | 7.7 | 5.8 | 10.3583 | 15 | 67 | 67 | 836.6963 | 88.9673 | 33.7508 | 129.2941 | 0 | 261.8677 | 683.9314 | 705.3575 | 313.5946 | 0 | 0 | 0 | 397.0327 | 85.629 | 107.8161 | 143.5762 | 145.3916 | 112.1988 | 85.629 | 85.629 | 85.629 | 88.9673 | 85.629 | 369.6838 | 827.5076 | 850.749 | 425.7934 | 85.629 | 85.629 | 85.629 | 486 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 11 | 2315 | 9 | 9 | 5.8 | 10.3583 | 15 | 57 | 57 | 827.2724 | 111.1831 | 39.9446 | 146.2735 | 0 | 68.3873 | 532.3275 | 684.4374 | 435.6132 | 0 | 0 | 0 | 482.8169 | 103.0444 | 109.3757 | 152.3276 | 166.41 | 143.3737 | 103.0444 | 103.0444 | 103.0444 | 111.1831 | 103.0444 | 177.7631 | 684.655 | 850.8474 | 578.9869 | 103.0444 | 103.0444 | 103.0444 | 594 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 12 | 2316 | 10.4 | 10.4 | 5.8 | 10.3583 | 15 | 52 | 52 | 889.5393 | 116.6706 | 43.7043 | 165.6747 | 0 | 0 | 378.6551 | 668.8209 | 567.2005 | 133.3217 | 0 | 0 | 586.3294 | 114.7091 | 114.7091 | 147.2315 | 172.1537 | 163.4256 | 126.16 | 114.7091 | 114.7091 | 116.6706 | 114.7091 | 114.7091 | 525.8867 | 840.9746 | 730.6261 | 259.4818 | 114.7091 | 114.7091 | 703 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 13 | 2317 | 11.3 | 11.3 | 5.8 | 10.3583 | 15 | 48 | 48 | 889.276 | 123.1774 | 44.3406 | 186.4327 | 0 | 0 | 159.0638 | 552.9191 | 622.8819 | 327.9689 | 0 | 0 | 618.8226 | 119.787 | 119.787 | 133.7604 | 168.3596 | 174.5057 | 148.5983 | 119.787 | 119.787 | 123.1774 | 119.787 | 119.787 | 292.8242 | 721.2787 | 797.3875 | 476.5671 | 119.787 | 119.787 | 742 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 14 | 2318 | 12.7 | 12.7 | 5.8 | 10.3583 | 15 | 43 | 43 | 882.9599 | 122.6215 | 41.7175 | 206.5519 | 0 | 0 | 0 | 393.6928 | 627.515 | 493.7473 | 70.7492 | 0 | 610.3785 | 118.5813 | 118.5813 | 118.5813 | 153.2131 | 173.7816 | 162.0145 | 124.8049 | 118.5813 | 122.6215 | 118.5813 | 118.5813 | 118.5813 | 546.9059 | 801.2965 | 655.7618 | 195.5541 | 118.5813 | 733 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 15 | 2319 | 12.4 | 12.4 | 5.8 | 10.3583 | 15 | 48 | 48 | 704.8059 | 155.9073 | 36.3577 | 224.4996 | 0 | 0 | 0 | 166.4791 | 470.6047 | 499.0564 | 235.1677 | 0 | 455.0927 | 115.0291 | 115.0291 | 115.0291 | 143.4756 | 195.4419 | 200.3035 | 155.2125 | 115.0291 | 155.9073 | 115.0291 | 115.0291 | 115.0291 | 309.9547 | 666.0466 | 699.3599 | 390.3801 | 115.0291 | 611 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 16 | 2320 | 12.9 | 12.9 | 5.8 | 10.3583 | 15 | 44 | 44 | 804.5141 | 111.6544 | 29.0762 | 239.9877 | 0 | 0 | 0 | 5.6584 | 462.1184 | 647.8756 | 454.1161 | 0 | 452.3456 | 99.8631 | 99.8631 | 99.8631 | 100.3946 | 143.2759 | 160.7265 | 142.5242 | 99.8631 | 111.6544 | 99.8631 | 99.8631 | 99.8631 | 106.0531 | 605.3943 | 808.6022 | 596.6403 | 99.8631 | 564 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 17 | 2321 | 12.6 | 12.6 | 5.8 | 10.3583 | 15 | 44 | 44 | 739.0583 | 100.8658 | 20.6209 | 253.5339 | 0 | 0 | 0 | 0 | 323.0785 | 623.9444 | 559.3121 | 167.0424 | 330.1342 | 82.1919 | 82.1919 | 82.1919 | 82.1919 | 123.5936 | 162.1488 | 153.8663 | 103.5979 | 100.8658 | 82.1919 | 82.1919 | 82.1919 | 82.1919 | 446.6721 | 786.0932 | 713.1784 | 270.6403 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 18 | 2322 | 11.4 | 11.4 | 5.8 | 10.3583 | 15 | 56 | 56 | 569.7083 | 94.1548 | 11.5705 | 265.8711 | 0 | 0 | 0 | 0 | 151.1369 | 468.4416 | 511.3396 | 254.7017 | 174.8452 | 63.7739 | 63.7739 | 63.7739 | 63.7739 | 89.4549 | 143.3709 | 150.6601 | 107.0525 | 94.1548 | 63.7739 | 63.7739 | 63.7739 | 63.7739 | 240.5918 | 611.8126 | 661.9997 | 361.7542 | 269 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 19 | 2323 | 10 | 10 | 5.8 | 10.3583 | 15 | 63 | 63 | 270.0068 | 66.8503 | 2.3771 | 277.6978 | 0 | 0 | 0 | 0 | 19.0455 | 200.0255 | 263.8333 | 173.0911 | 41.1497 | 38.1336 | 38.1336 | 38.1336 | 38.1336 | 44.5318 | 105.3305 | 126.7661 | 96.2821 | 66.8503 | 38.1336 | 38.1336 | 38.1336 | 38.1336 | 63.5773 | 305.356 | 390.5995 | 269.3732 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 20 | 2324 | 8.5 | 8.5 | 5.8 | 10.3583 | 15 | 71 | 71 | 0 | 6 | -6.5614 | 289.6391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 6 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 2.8289 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 21 | 2325 | 7.2 | 7.2 | 5.8 | 10.3583 | 15 | 82 | 82 | 0 | 0 | -14.8354 | 302.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 22 | 2326 | 7.2 | 7.2 | 5.8 | 10.3583 | 15 | 83 | 83 | 0 | 0 | -21.9742 | 316.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 23 | 2327 | 6.4 | 6.4 | 5.8 | 10.3583 | 15 | 82 | 82 | 0 | 0 | -27.4292 | 331.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 7 | 24 | 2328 | 5.3 | 5.3 | 6.7875 | 9.3602 | 15 | 86 | 86 | 0 | 0 | -30.6334 | 348.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 1 | 2329 | 4.8 | 4.8 | 6.7875 | 9.3602 | 15 | 86 | 86 | 0 | 0 | -31.1666 | 5.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 2 | 2330 | 4 | 4 | 6.7875 | 9.3602 | 15 | 87 | 87 | 0 | 0 | -28.5677 | 22.3939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 3 | 2331 | 3.5 | 3.5 | 6.7875 | 9.3602 | 15 | 88 | 88 | 0 | 0 | -23.9188 | 38.1805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 4 | 2332 | 3 | 3 | 6.7875 | 9.3602 | 15 | 87 | 87 | 0 | 0 | -17.3689 | 52.4838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 5 | 2333 | 1.9 | 1.9 | 6.7875 | 9.3602 | 15 | 88 | 88 | 0 | 0 | -9.4814 | 65.4794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 6 | 2334 | 1 | 1 | 6.7875 | 9.3602 | 15 | 88 | 88 | 0 | 0 | -0.75488 | 77.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 7 | 2335 | 1.7 | 1.7 | 6.7875 | 9.3602 | 15 | 87 | 87 | 108.5885 | 7.164 | 8.3841 | 89.3948 | 23.311 | 91.4701 | 106.0472 | 58.5033 | 0 | 0 | 0 | 0 | 25.836 | 6.6204 | 8.0325 | 8.3345 | 7.3495 | 6.1375 | 6.1375 | 6.1375 | 6.1375 | 7.164 | 29.9314 | 99.5026 | 114.3817 | 65.8528 | 6.1375 | 6.1375 | 6.1375 | 6.1375 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 8 | 8 | 2336 | 4.3 | 4.3 | 6.7875 | 9.3602 | 15 | 76 | 76 | 494.6103 | 65.9247 | 17.5409 | 101.4572 | 5.1688 | 349.6402 | 489.297 | 342.3303 | 0 | 0 | 0 | 0 | 95.0753 | 41.2974 | 92.5424 | 113.3183 | 91.4549 | 40.5285 | 40.5285 | 40.5285 | 40.5285 | 65.9247 | 46.4662 | 442.1825 | 602.6153 | 433.7853 | 40.5285 | 40.5285 | 40.5285 | 40.5285 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 9 | 2337 | 8.3 | 8.3 | 6.7875 | 9.3602 | 15 | 55 | 55 | 744.0712 | 76.857 | 26.2928 | 114.4625 | 0 | 392.0267 | 695.336 | 591.3269 | 140.9265 | 0 | 0 | 0 | 256.143 | 64.3238 | 111.6726 | 148.3061 | 135.744 | 81.3448 | 64.3238 | 64.3238 | 64.3238 | 76.857 | 64.3238 | 503.6993 | 843.6421 | 727.0708 | 222.2713 | 64.3238 | 64.3238 | 64.3238 | 333 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 10 | 2338 | 10.3 | 10.3 | 6.7875 | 9.3602 | 15 | 41 | 41 | 831.0944 | 90.5986 | 34.1164 | 129.1527 | 0 | 261.3997 | 678.2241 | 697.754 | 308.5491 | 0 | 0 | 0 | 398.4014 | 86.456 | 108.917 | 144.7329 | 146.411 | 112.9683 | 86.456 | 86.456 | 86.456 | 90.5986 | 86.456 | 370.3167 | 822.957 | 844.165 | 421.5174 | 86.456 | 86.456 | 86.456 | 489 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 11 | 2339 | 11.7 | 11.7 | 6.7875 | 9.3602 | 15 | 37 | 37 | 856.7057 | 106.925 | 40.3235 | 146.1927 | 0 | 72.2578 | 550.0117 | 705.5763 | 447.8238 | 0 | 0 | 0 | 504.075 | 103.3789 | 109.6574 | 151.1696 | 164.6867 | 142.2905 | 103.3789 | 103.3789 | 103.3789 | 106.925 | 103.3789 | 181.9151 | 701.1813 | 870.263 | 590.1143 | 103.3789 | 103.3789 | 103.3789 | 611 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 12 | 2340 | 12.6 | 12.6 | 6.7875 | 9.3602 | 15 | 39 | 39 | 881.6262 | 117.7374 | 44.088 | 165.6938 | 0 | 0 | 373.9878 | 659.3699 | 558.5021 | 130.4713 | 0 | 0 | 585.2626 | 114.9556 | 114.9556 | 147.5093 | 172.3503 | 163.5703 | 126.3124 | 114.9556 | 114.9556 | 117.7374 | 114.9556 | 114.9556 | 521.4971 | 831.7203 | 722.0724 | 256.7837 | 114.9556 | 114.9556 | 703 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 13 | 2341 | 13.1 | 13.1 | 6.7875 | 9.3602 | 15 | 38 | 38 | 881.8278 | 124.2344 | 44.7117 | 186.5709 | 0 | 0 | 156.5139 | 544.6587 | 613.7498 | 323.3146 | 0 | 0 | 617.7656 | 120.0051 | 120.0051 | 133.9345 | 168.4784 | 174.6274 | 148.7793 | 120.0051 | 120.0051 | 124.2344 | 120.0051 | 120.0051 | 290.4484 | 713.1372 | 788.3772 | 472.094 | 120.0051 | 120.0051 | 742 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 14 | 2342 | 13.6 | 13.6 | 6.7875 | 9.3602 | 15 | 37 | 37 | 849.5545 | 127.7365 | 42.0597 | 206.7859 | 0 | 0 | 0 | 375.2529 | 599.7749 | 472.9569 | 69.0871 | 0 | 591.2635 | 118.5762 | 118.5762 | 118.5762 | 153.8694 | 174.986 | 163.0586 | 125.074 | 118.5762 | 127.7365 | 118.5762 | 118.5762 | 118.5762 | 529.1223 | 774.7609 | 636.0155 | 194.1611 | 118.5762 | 719 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 15 | 2343 | 13.4 | 13.4 | 6.7875 | 9.3602 | 15 | 35 | 35 | 867.6482 | 116.6686 | 36.6659 | 224.7845 | 0 | 0 | 0 | 201.3519 | 575.0605 | 611.9064 | 290.3059 | 0 | 564.3314 | 112.0937 | 112.0937 | 112.0937 | 129.6393 | 162.2037 | 165.4144 | 137.3906 | 112.0937 | 116.6686 | 112.0937 | 112.0937 | 112.0937 | 330.9912 | 737.2642 | 777.3208 | 427.6965 | 112.0937 | 681 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 16 | 2344 | 13.9 | 13.9 | 6.7875 | 9.3602 | 15 | 35 | 35 | 813.8953 | 110.4909 | 29.3557 | 240.2894 | 0 | 0 | 0 | 2.455 | 463.3679 | 652.8461 | 459.896 | 0 | 461.5091 | 100.2536 | 100.2536 | 100.2536 | 100.4795 | 142.8843 | 160.3167 | 142.5649 | 100.2536 | 110.4909 | 100.2536 | 100.2536 | 100.2536 | 102.9345 | 606.2522 | 813.1628 | 602.4609 | 100.2536 | 572 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 17 | 2345 | 13.3 | 13.3 | 6.7875 | 9.3602 | 15 | 36 | 36 | 410.7649 | 172.5144 | 20.8814 | 253.8355 | 0 | 0 | 0 | 0 | 177.4415 | 345.3482 | 310.9547 | 94.4081 | 185.4856 | 97.4673 | 97.4673 | 97.4673 | 97.4673 | 157.0834 | 213.4961 | 201.9406 | 129.1862 | 172.5144 | 97.4673 | 97.4673 | 97.4673 | 97.4673 | 334.5249 | 558.8443 | 512.8954 | 223.5943 | 358 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 18 | 2346 | 12.6 | 12.6 | 6.7875 | 9.3602 | 15 | 42 | 42 | 493.2661 | 107.1621 | 11.8226 | 266.1668 | 0 | 0 | 0 | 0 | 128.3041 | 403.7245 | 442.6486 | 222.2752 | 153.8379 | 67.8204 | 67.8204 | 67.8204 | 67.8204 | 95.6771 | 155.4749 | 163.9259 | 116.0796 | 107.1621 | 67.8204 | 67.8204 | 67.8204 | 67.8204 | 223.9812 | 559.1995 | 606.5745 | 338.3548 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 19 | 2347 | 11.4 | 11.4 | 6.7875 | 9.3602 | 15 | 51 | 51 | 237.2515 | 70.634 | 2.6307 | 277.9863 | 0 | 0 | 0 | 0 | 15.5241 | 174.8132 | 231.6991 | 152.8588 | 37.366 | 39.4867 | 39.4867 | 39.4867 | 39.4867 | 45.3425 | 105.427 | 126.8847 | 97.1457 | 70.634 | 39.4867 | 39.4867 | 39.4867 | 39.4867 | 60.8666 | 280.2403 | 358.5838 | 250.0046 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 20 | 2348 | 9.6 | 9.6 | 6.7875 | 9.3602 | 15 | 62 | 62 | 0 | 8 | -6.2969 | 289.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 8 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 3.8017 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 21 | 2349 | 9.1 | 9.1 | 6.7875 | 9.3602 | 15 | 68 | 68 | 0 | 0 | -14.5516 | 302.5303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 22 | 2350 | 8.4 | 8.4 | 6.7875 | 9.3602 | 15 | 65 | 65 | 0 | 0 | -21.6644 | 316.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 23 | 2351 | 7.7 | 7.7 | 6.7875 | 9.3602 | 15 | 70 | 70 | 0 | 0 | -27.0904 | 331.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 8 | 24 | 2352 | 6.2 | 6.2 | 8.3083 | 8.9555 | 15 | 76 | 76 | 0 | 0 | -30.2687 | 348.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 1 | 2353 | 3.4 | 3.4 | 8.3083 | 8.9555 | 15 | 82 | 82 | 0 | 0 | -30.786 | 5.4318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 2 | 2354 | 2.9 | 2.9 | 8.3083 | 8.9555 | 15 | 88 | 88 | 0 | 0 | -28.1865 | 22.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 3 | 2355 | 2 | 2 | 8.3083 | 8.9555 | 15 | 90 | 90 | 0 | 0 | -23.545 | 38.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 4 | 2356 | 1.1 | 1.1 | 8.3083 | 8.9555 | 15 | 92 | 92 | 0 | 0 | -17.0072 | 52.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 5 | 2357 | 0.4 | 0.4 | 8.3083 | 8.9555 | 15 | 93 | 93 | 0 | 0 | -9.1314 | 65.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 6 | 2358 | -0.8 | -0.8 | 8.3083 | 8.9555 | 15 | 94 | 94 | 0 | 0 | -0.41311 | 77.4325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 7 | 2359 | 1.2 | 1.2 | 8.3083 | 8.9555 | 15 | 96 | 96 | 166.1459 | 9.9674 | 8.7227 | 89.2164 | 36.1508 | 140.2275 | 162.1608 | 89.1026 | 0 | 0 | 0 | 0 | 26.0326 | 8.1984 | 10.1494 | 10.5605 | 9.191 | 7.5207 | 7.5207 | 7.5207 | 7.5207 | 9.9674 | 44.3492 | 150.3769 | 172.7214 | 98.2936 | 7.5207 | 7.5207 | 7.5207 | 7.5207 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 9 | 8 | 2360 | 5.3 | 5.3 | 8.3083 | 8.9555 | 15 | 95 | 95 | 591.9662 | 58.232 | 17.8822 | 101.2775 | 8.002 | 419.3615 | 585.0648 | 408.045 | 0 | 0 | 0 | 0 | 116.768 | 41.2956 | 97.803 | 120.5653 | 96.2485 | 40.1964 | 40.1964 | 40.1964 | 40.1964 | 58.232 | 49.2976 | 517.1646 | 705.63 | 504.2935 | 40.1964 | 40.1964 | 40.1964 | 40.1964 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 9 | 2361 | 5.9 | 5.9 | 8.3083 | 8.9555 | 15 | 95 | 95 | 95.0608 | 160.8092 | 26.6427 | 114.2918 | 0 | 50.2255 | 88.7216 | 75.2458 | 17.6921 | 0 | 0 | 0 | 33.1908 | 74.8963 | 132.279 | 176.261 | 160.8649 | 95.1096 | 74.8963 | 74.8963 | 74.8963 | 160.8092 | 74.8963 | 182.5045 | 264.9826 | 236.1107 | 112.8016 | 74.8963 | 74.8963 | 74.8963 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 10 | 2362 | 7.5 | 7.5 | 8.3083 | 8.9555 | 15 | 88 | 88 | 110.5866 | 224.4574 | 34.4795 | 129.01 | 0 | 34.9523 | 90.0931 | 92.4586 | 40.6631 | 0 | 0 | 0 | 53.5426 | 104.3069 | 140.2022 | 196.8309 | 199.2602 | 146.0672 | 104.3069 | 104.3069 | 104.3069 | 224.4574 | 104.3069 | 175.1545 | 286.924 | 291.7188 | 186.7303 | 104.3069 | 104.3069 | 104.3069 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 11 | 2363 | 8.3 | 8.3 | 8.3083 | 8.9555 | 15 | 77 | 77 | 45.5944 | 255.958 | 40.7001 | 146.1103 | 0 | 3.9221 | 29.2047 | 37.3796 | 23.658 | 0 | 0 | 0 | 27.042 | 115.867 | 124.9434 | 183.4511 | 202.369 | 170.6151 | 115.867 | 115.867 | 115.867 | 255.958 | 115.867 | 128.8656 | 212.6559 | 239.7486 | 194.2731 | 115.867 | 115.867 | 115.867 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 12 | 2364 | 9.3 | 9.3 | 8.3083 | 8.9555 | 15 | 72 | 72 | 133.1785 | 310.9705 | 44.4696 | 165.7118 | 0 | 0 | 56.2988 | 99.0747 | 83.8141 | 19.4562 | 0 | 0 | 89.0295 | 141.0132 | 141.0132 | 210.907 | 264.0125 | 245.0667 | 165.1678 | 141.0132 | 141.0132 | 310.9705 | 141.0132 | 141.0132 | 267.2058 | 363.0872 | 328.8807 | 184.624 | 141.0132 | 141.0132 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 13 | 2365 | 9.4 | 9.4 | 8.3083 | 8.9555 | 15 | 70 | 70 | 47.3191 | 305.6318 | 45.0807 | 186.7089 | 0 | 0 | 8.3339 | 29.0319 | 32.7234 | 17.246 | 0 | 0 | 33.3682 | 136.5215 | 136.5215 | 156.4117 | 205.811 | 214.6214 | 177.6819 | 136.5215 | 136.5215 | 305.6318 | 136.5215 | 136.5215 | 164.7456 | 234.8429 | 247.3448 | 194.9279 | 136.5215 | 136.5215 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 14 | 2366 | 8.9 | 8.9 | 8.3083 | 8.9555 | 15 | 70 | 70 | 6.2902 | 209.5931 | 42.3998 | 207.0199 | 0 | 0 | 0 | 2.7523 | 4.4112 | 3.4861 | 0.51888 | 0 | 4.4069 | 103.76 | 103.76 | 103.76 | 108.2119 | 110.8953 | 109.3989 | 104.5994 | 103.76 | 209.5931 | 103.76 | 103.76 | 103.76 | 110.9642 | 115.3064 | 112.885 | 105.1182 | 103.76 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 15 | 2367 | 9.7 | 9.7 | 8.3083 | 8.9555 | 15 | 65 | 65 | 21.4089 | 254.9755 | 36.9722 | 225.0693 | 0 | 0 | 0 | 4.8802 | 14.084 | 15.0375 | 7.1823 | 0 | 14.0245 | 121.3511 | 121.3511 | 121.3511 | 129.9093 | 146.0495 | 147.7217 | 133.9464 | 121.3511 | 254.9755 | 121.3511 | 121.3511 | 121.3511 | 134.7895 | 160.1334 | 162.7592 | 141.1287 | 121.3511 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 16 | 2368 | 10.1 | 10.1 | 8.3083 | 8.9555 | 15 | 57 | 57 | 216.0163 | 259.4892 | 29.6334 | 240.5903 | 0 | 0 | 0 | 0 | 121.8859 | 172.5814 | 122.181 | 0.20867 | 123.5108 | 126.2042 | 126.2042 | 126.2042 | 126.2042 | 203.9638 | 236.306 | 204.1521 | 126.3374 | 259.4892 | 126.2042 | 126.2042 | 126.2042 | 126.2042 | 325.8497 | 408.8873 | 326.333 | 126.546 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 17 | 2369 | 9.5 | 9.5 | 8.3083 | 8.9555 | 15 | 63 | 63 | 4.7151 | 119.8481 | 21.1405 | 254.1358 | 0 | 0 | 0 | 0 | 2.0125 | 3.9476 | 3.5703 | 1.1015 | 2.1519 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 119.8481 | 59.8876 | 59.8876 | 59.8876 | 59.8876 | 61.9001 | 63.8353 | 63.4579 | 60.9891 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 9 | 18 | 2370 | 7.8 | 7.8 | 8.3083 | 8.9555 | 15 | 76 | 76 | 3.6979 | 73.8285 | 12.0736 | 266.4609 | 0 | 0 | 0 | 0 | 0.94283 | 3.0126 | 3.3177 | 1.6793 | 1.1715 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 73.8285 | 36.2971 | 36.2971 | 36.2971 | 36.2971 | 37.2399 | 39.3098 | 39.6148 | 37.9764 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 19 | 2371 | 7.5 | 7.5 | 8.3083 | 8.9555 | 15 | 80 | 80 | 3.2362 | 35.4739 | 2.8835 | 278.2727 | 0 | 0 | 0 | 0 | 0.19535 | 2.3716 | 3.1586 | 2.0953 | 0.52606 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 35.4739 | 17.1583 | 17.1583 | 17.1583 | 17.1583 | 17.3537 | 19.5299 | 20.3169 | 19.2537 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 20 | 2372 | 6.5 | 6.5 | 8.3083 | 8.9555 | 15 | 86 | 86 | 0 | 0 | -6.0331 | 290.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 21 | 2373 | 6.1 | 6.1 | 8.3083 | 8.9555 | 15 | 89 | 89 | 0 | 0 | -14.2685 | 302.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 22 | 2374 | 5.9 | 5.9 | 8.3083 | 8.9555 | 15 | 83 | 83 | 0 | 0 | -21.3555 | 316.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 23 | 2375 | 5.1 | 5.1 | 8.3083 | 8.9555 | 15 | 83 | 83 | 0 | 0 | -26.7528 | 331.7444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 9 | 24 | 2376 | 5.1 | 5.1 | 5.7542 | 7.828 | 15 | 75 | 75 | 0 | 0 | -29.9056 | 348.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 1 | 2377 | 4.5 | 4.5 | 5.7542 | 7.828 | 15 | 71 | 71 | 0 | 0 | -30.4074 | 5.4886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 2 | 2378 | 4.1 | 4.1 | 5.7542 | 7.828 | 15 | 70 | 70 | 0 | 0 | -27.8075 | 22.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 3 | 2379 | 3.5 | 3.5 | 5.7542 | 7.828 | 15 | 71 | 71 | 0 | 0 | -23.1736 | 38.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 4 | 2380 | 2.9 | 2.9 | 5.7542 | 7.828 | 15 | 73 | 73 | 0 | 0 | -16.6478 | 52.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 5 | 2381 | 2.4 | 2.4 | 5.7542 | 7.828 | 15 | 76 | 76 | 0 | 0 | -8.7838 | 65.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 6 | 2382 | 1.9 | 1.9 | 5.7542 | 7.828 | 15 | 76 | 76 | 0 | 0 | -0.073787 | 77.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 7 | 2383 | 2 | 2 | 5.7542 | 7.828 | 15 | 76 | 76 | 140.0682 | 19.2807 | 9.0587 | 89.038 | 30.8827 | 118.4431 | 136.6211 | 74.7683 | 0 | 0 | 0 | 0 | 11.7193 | 11.8166 | 15.5204 | 16.2893 | 13.673 | 10.5103 | 10.5103 | 10.5103 | 10.5103 | 19.2807 | 42.6993 | 133.9635 | 152.9104 | 88.4413 | 10.5103 | 10.5103 | 10.5103 | 10.5103 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 10 | 8 | 2384 | 3.3 | 3.3 | 5.7542 | 7.828 | 15 | 72 | 72 | 261.6033 | 89.0907 | 18.2208 | 101.0973 | 4.3375 | 185.7156 | 258.3041 | 179.5815 | 0 | 0 | 0 | 0 | 52.9093 | 49.7437 | 121.2429 | 149.8573 | 118.8248 | 48.0339 | 48.0339 | 48.0339 | 48.0339 | 89.0907 | 54.0812 | 306.9586 | 408.1613 | 298.4063 | 48.0339 | 48.0339 | 48.0339 | 48.0339 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 9 | 2385 | 5.7 | 5.7 | 5.7542 | 7.828 | 15 | 66 | 66 | 482.2469 | 123.2751 | 26.9898 | 114.1202 | 0 | 255.502 | 449.5013 | 380.1888 | 88.1669 | 0 | 0 | 0 | 170.7249 | 76.1938 | 136.3515 | 182.0285 | 165.7089 | 96.9526 | 76.1938 | 76.1938 | 76.1938 | 123.2751 | 76.1938 | 391.8535 | 631.5298 | 545.8977 | 185.1195 | 76.1938 | 76.1938 | 76.1938 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 10 | 2386 | 7.6 | 7.6 | 5.7542 | 7.828 | 15 | 57 | 57 | 569.4978 | 149.5606 | 34.84 | 128.8658 | 0 | 180.8677 | 463.1649 | 474.1464 | 207.3794 | 0 | 0 | 0 | 278.4394 | 97.7976 | 138.2067 | 201.2769 | 203.7304 | 144.1299 | 97.7976 | 97.7976 | 97.7976 | 149.5606 | 97.7976 | 319.0744 | 664.4418 | 677.8768 | 351.5092 | 97.7976 | 97.7976 | 97.7976 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 11 | 2387 | 9.1 | 9.1 | 5.7542 | 7.828 | 15 | 52 | 52 | 621.061 | 167.7541 | 41.0742 | 146.0263 | 0 | 54.469 | 396.8897 | 506.8178 | 319.859 | 0 | 0 | 0 | 371.2459 | 111.8756 | 122.9226 | 192.3704 | 214.6654 | 176.7475 | 111.8756 | 111.8756 | 111.8756 | 167.7541 | 111.8756 | 177.3916 | 589.2601 | 721.4833 | 496.6065 | 111.8756 | 111.8756 | 111.8756 | 539 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 12 | 2388 | 11 | 11 | 5.7542 | 7.828 | 15 | 44 | 44 | 786.0612 | 137.9054 | 44.8489 | 165.7287 | 0 | 0 | 331.1404 | 581.6399 | 491.4227 | 113.3368 | 0 | 0 | 529.0946 | 115.6598 | 115.6598 | 162.2968 | 197.5766 | 184.8706 | 131.6219 | 115.6598 | 115.6598 | 137.9054 | 115.6598 | 115.6598 | 493.4372 | 779.2165 | 676.2933 | 244.9586 | 115.6598 | 115.6598 | 667 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 13 | 2389 | 11.3 | 11.3 | 5.7542 | 7.828 | 15 | 46 | 46 | 694.4345 | 174.1291 | 45.4476 | 186.8466 | 0 | 0 | 121.367 | 423.2078 | 477.1391 | 251.5689 | 0 | 0 | 492.8709 | 124.7914 | 124.7914 | 147.3912 | 203.597 | 213.6396 | 171.6361 | 124.7914 | 124.7914 | 174.1291 | 124.7914 | 124.7914 | 268.7582 | 626.8048 | 690.7787 | 423.205 | 124.7914 | 124.7914 | 667 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 14 | 2390 | 11.8 | 11.8 | 5.7542 | 7.828 | 15 | 43 | 43 | 361.4848 | 284.0921 | 42.7379 | 207.254 | 0 | 0 | 0 | 156.6686 | 251.7952 | 199.4235 | 30.2323 | 0 | 254.9079 | 143.5569 | 143.5569 | 143.5569 | 223.5647 | 272.1441 | 245.3988 | 158.996 | 143.5569 | 284.0921 | 143.5569 | 143.5569 | 143.5569 | 380.2333 | 523.9393 | 444.8224 | 189.2282 | 143.5569 | 539 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 15 | 2391 | 10.8 | 10.8 | 5.7542 | 7.828 | 15 | 46 | 46 | 51.14 | 288.2636 | 37.2764 | 225.3537 | 0 | 0 | 0 | 11.4484 | 33.3908 | 35.7733 | 17.2004 | 0 | 33.7364 | 130.0154 | 130.0154 | 130.0154 | 153.7031 | 199.1038 | 204.0335 | 165.6044 | 130.0154 | 288.2636 | 130.0154 | 130.0154 | 130.0154 | 165.1514 | 232.4946 | 239.8068 | 182.8048 | 130.0154 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 16 | 2392 | 10.6 | 10.6 | 5.7542 | 7.828 | 15 | 43 | 43 | 178.9834 | 265.8261 | 29.9095 | 240.8903 | 0 | 0 | 0 | 0 | 100.0834 | 142.4184 | 101.3266 | 0.87907 | 103.1739 | 126.448 | 126.448 | 126.448 | 126.448 | 205.6163 | 239.1042 | 206.5997 | 127.1433 | 265.8261 | 126.448 | 126.448 | 126.448 | 126.448 | 305.6997 | 381.5227 | 307.9263 | 128.0224 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 17 | 2393 | 10.6 | 10.6 | 5.7542 | 7.828 | 15 | 42 | 42 | 382.3559 | 181.674 | 21.3983 | 254.4347 | 0 | 0 | 0 | 0 | 161.2359 | 318.7668 | 289.5684 | 90.7448 | 176.326 | 100.0525 | 100.0525 | 100.0525 | 100.0525 | 159.9091 | 218.3903 | 207.5508 | 133.7402 | 181.674 | 100.0525 | 100.0525 | 100.0525 | 100.0525 | 321.145 | 537.157 | 497.1192 | 224.485 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 10 | 18 | 2394 | 10.1 | 10.1 | 5.7542 | 7.828 | 15 | 43 | 43 | 100.9459 | 148.5255 | 12.3235 | 266.753 | 0 | 0 | 0 | 0 | 25.2203 | 81.8551 | 90.5404 | 46.1883 | 32.4745 | 72.4211 | 72.4211 | 72.4211 | 72.4211 | 97.2485 | 153.0012 | 161.5511 | 117.8899 | 148.5255 | 72.4211 | 72.4211 | 72.4211 | 72.4211 | 122.4687 | 234.8563 | 252.0915 | 164.0782 | 181 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 19 | 2395 | 9.6 | 9.6 | 5.7542 | 7.828 | 15 | 46 | 46 | 131.8339 | 77.9074 | 3.1354 | 278.5569 | 0 | 0 | 0 | 0 | 7.295 | 96.0848 | 128.5894 | 85.7681 | 22.0926 | 40.1707 | 40.1707 | 40.1707 | 40.1707 | 44.0693 | 91.5212 | 108.8926 | 86.0076 | 77.9074 | 40.1707 | 40.1707 | 40.1707 | 40.1707 | 51.3643 | 187.606 | 237.482 | 171.7758 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 20 | 2396 | 8.3 | 8.3 | 5.7542 | 7.828 | 15 | 49 | 49 | 22.8323 | 2.9451 | -5.7701 | 290.4718 | 3.3922 | 0 | 0 | 0 | 0 | 13.5426 | 22.5444 | 18.3399 | 5.0549 | 4.0143 | 2.2204 | 2.2204 | 2.2204 | 2.2204 | 9.3821 | 14.1424 | 11.919 | 2.9451 | 7.4065 | 2.2204 | 2.2204 | 2.2204 | 2.2204 | 22.9248 | 36.6868 | 30.2589 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 21 | 2397 | 7.8 | 7.8 | 5.7542 | 7.828 | 15 | 51 | 51 | 0 | 0 | -13.9863 | 303.0564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 22 | 2398 | 7 | 7 | 5.7542 | 7.828 | 15 | 53 | 53 | 0 | 0 | -21.0476 | 316.7852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 23 | 2399 | 6.2 | 6.2 | 5.7542 | 7.828 | 15 | 54 | 54 | 0 | 0 | -26.4165 | 331.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 10 | 24 | 2400 | 5.3 | 5.3 | 6.975 | 7.2457 | 15 | 60 | 60 | 0 | 0 | -29.5443 | 348.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 1 | 2401 | 4.8 | 4.8 | 6.975 | 7.2457 | 15 | 61 | 61 | 0 | 0 | -30.0309 | 5.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 2 | 2402 | 4.1 | 4.1 | 6.975 | 7.2457 | 15 | 63 | 63 | 0 | 0 | -27.431 | 22.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 3 | 2403 | 4.1 | 4.1 | 6.975 | 7.2457 | 15 | 67 | 67 | 0 | 0 | -22.8047 | 37.9257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 4 | 2404 | 3.4 | 3.4 | 6.975 | 7.2457 | 15 | 71 | 71 | 0 | 0 | -16.291 | 52.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 5 | 2405 | 3 | 3 | 6.975 | 7.2457 | 15 | 76 | 76 | 0 | 0 | -8.4387 | 65.0172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 6 | 2406 | 3.4 | 3.4 | 6.975 | 7.2457 | 15 | 79 | 79 | 0 | 0 | 0.26295 | 77.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 7 | 2407 | 4.6 | 4.6 | 6.975 | 7.2457 | 15 | 79 | 79 | 9.7085 | 16.5239 | 9.3921 | 88.8594 | 2.1686 | 8.2248 | 9.4631 | 5.158 | 0 | 0 | 0 | 0 | 0.47607 | 14.7929 | 35.1083 | 39.262 | 24.8208 | 7.5185 | 7.5185 | 7.5185 | 7.5185 | 16.5239 | 16.9615 | 43.3331 | 48.7251 | 29.9788 | 7.5185 | 7.5185 | 7.5185 | 7.5185 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 11 | 8 | 2408 | 5.9 | 5.9 | 6.975 | 7.2457 | 15 | 76 | 76 | 18.9954 | 79.064 | 18.5566 | 100.9167 | 0.37304 | 13.5129 | 18.7371 | 12.9853 | 0 | 0 | 0 | 0 | 3.936 | 36.4913 | 94.0006 | 116.8654 | 91.6916 | 34.8586 | 34.8586 | 34.8586 | 34.8586 | 79.064 | 36.8643 | 107.5135 | 135.6025 | 104.677 | 34.8586 | 34.8586 | 34.8586 | 34.8586 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 9 | 2409 | 7.9 | 7.9 | 6.975 | 7.2457 | 15 | 69 | 69 | 351.1081 | 146.0074 | 27.3342 | 113.9475 | 0 | 186.5306 | 326.8304 | 275.6774 | 63.0363 | 0 | 0 | 0 | 125.9926 | 81.4534 | 147.4806 | 197.1433 | 179.0364 | 103.7667 | 81.4534 | 81.4534 | 81.4534 | 146.0074 | 81.4534 | 334.0113 | 523.9737 | 454.7138 | 166.803 | 81.4534 | 81.4534 | 81.4534 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 10 | 2410 | 9.8 | 9.8 | 6.975 | 7.2457 | 15 | 61 | 61 | 617.3447 | 139.2634 | 35.1977 | 128.7201 | 0 | 197.0029 | 501.2052 | 511.8083 | 222.601 | 0 | 0 | 0 | 304.7366 | 94.8767 | 131.2936 | 187.5268 | 189.4868 | 136.0255 | 94.8767 | 94.8767 | 94.8767 | 139.2634 | 94.8767 | 328.2965 | 688.732 | 701.2951 | 358.6266 | 94.8767 | 94.8767 | 94.8767 | 444 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 11 | 2411 | 10.3 | 10.3 | 6.975 | 7.2457 | 15 | 57 | 57 | 572.3832 | 183.2138 | 41.4458 | 145.9406 | 0 | 51.163 | 364.9305 | 464.9268 | 292.5752 | 0 | 0 | 0 | 344.7862 | 116.5502 | 129.4177 | 208.3305 | 233.4797 | 190.1331 | 116.5502 | 116.5502 | 116.5502 | 183.2138 | 116.5502 | 180.5806 | 573.2611 | 698.4065 | 482.7083 | 116.5502 | 116.5502 | 116.5502 | 528 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 12 | 2412 | 11.1 | 11.1 | 6.975 | 7.2457 | 15 | 52 | 52 | 125.8288 | 314.7334 | 45.2258 | 165.7442 | 0 | 0 | 52.8236 | 92.6048 | 78.1393 | 17.9009 | 0 | 0 | 85.2666 | 141.9505 | 141.9505 | 211.7831 | 264.3737 | 245.2504 | 165.6155 | 141.9505 | 141.9505 | 314.7334 | 141.9505 | 141.9505 | 264.6067 | 356.9784 | 323.3898 | 183.5164 | 141.9505 | 141.9505 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 13 | 2413 | 12 | 12 | 6.975 | 7.2457 | 15 | 46 | 46 | 99.0028 | 329.2866 | 45.8123 | 186.9838 | 0 | 0 | 17.1709 | 59.9293 | 67.5819 | 35.646 | 0 | 0 | 70.7134 | 148.7134 | 148.7134 | 170.5897 | 225.0654 | 234.8152 | 194.1277 | 148.7134 | 148.7134 | 329.2866 | 148.7134 | 148.7134 | 187.7606 | 284.9947 | 302.3971 | 229.7737 | 148.7134 | 148.7134 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 14 | 2414 | 11.4 | 11.4 | 6.975 | 7.2457 | 15 | 47 | 47 | 10.3859 | 242.6293 | 43.0738 | 207.488 | 0 | 0 | 0 | 4.4584 | 7.1854 | 5.7032 | 0.88019 | 0 | 7.3707 | 117.6389 | 117.6389 | 117.6389 | 127.5772 | 133.6558 | 130.3519 | 119.6009 | 117.6389 | 242.6293 | 117.6389 | 117.6389 | 117.6389 | 132.0356 | 140.8412 | 136.0551 | 120.4811 | 117.6389 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 15 | 2415 | 12 | 12 | 6.975 | 7.2457 | 15 | 48 | 48 | 24.9837 | 264.4048 | 37.5787 | 225.6375 | 0 | 0 | 0 | 5.4915 | 16.1897 | 17.4042 | 8.4235 | 0 | 16.5952 | 125.4291 | 125.4291 | 125.4291 | 134.5249 | 152.2447 | 154.2563 | 139.3813 | 125.4291 | 264.4048 | 125.4291 | 125.4291 | 125.4291 | 140.0165 | 168.4344 | 171.6604 | 147.8048 | 125.4291 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 16 | 2416 | 12 | 12 | 6.975 | 7.2457 | 15 | 48 | 48 | 37.9275 | 244.9614 | 30.1838 | 241.1892 | 0 | 0 | 0 | 0 | 21.0165 | 30.0563 | 21.4895 | 0.33444 | 22.0386 | 111.9582 | 111.9582 | 111.9582 | 111.9582 | 161.8489 | 183.3082 | 162.9717 | 112.7521 | 244.9614 | 111.9582 | 111.9582 | 111.9582 | 111.9582 | 182.8654 | 213.3645 | 184.4612 | 113.0866 | 267 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 17 | 2417 | 11.9 | 11.9 | 6.975 | 7.2457 | 15 | 47 | 47 | 45.4943 | 200.8049 | 21.6546 | 254.732 | 0 | 0 | 0 | 0 | 18.952 | 37.7666 | 34.4581 | 10.9645 | 21.1951 | 93.5303 | 93.5303 | 93.5303 | 93.5303 | 126.7919 | 159.8125 | 154.0059 | 112.7735 | 200.8049 | 93.5303 | 93.5303 | 93.5303 | 93.5303 | 145.7439 | 197.5791 | 188.464 | 123.738 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 11 | 18 | 2418 | 11.7 | 11.7 | 6.975 | 7.2457 | 15 | 50 | 50 | 68.1922 | 146.7316 | 12.5722 | 267.0433 | 0 | 0 | 0 | 0 | 16.69 | 55.0359 | 61.1425 | 31.4327 | 22.2684 | 70.2275 | 70.2275 | 70.2275 | 70.2275 | 86.976 | 125.4562 | 131.5842 | 101.7703 | 146.7316 | 70.2275 | 70.2275 | 70.2275 | 70.2275 | 103.666 | 180.4921 | 192.7268 | 133.203 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 19 | 2419 | 10.6 | 10.6 | 6.975 | 7.2457 | 15 | 53 | 53 | 47.65 | 74.7772 | 3.3864 | 278.8388 | 0 | 0 | 0 | 0 | 2.3989 | 34.5383 | 46.4456 | 31.1457 | 8.2228 | 36.8434 | 36.8434 | 36.8434 | 36.8434 | 38.9503 | 67.1768 | 77.6344 | 64.1972 | 74.7772 | 36.8434 | 36.8434 | 36.8434 | 36.8434 | 41.3492 | 101.715 | 124.0799 | 95.3428 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 20 | 2420 | 8.8 | 8.8 | 6.975 | 7.2457 | 15 | 60 | 60 | 23.15 | 5.6667 | -5.5079 | 290.7441 | 3.5509 | 0 | 0 | 0 | 0 | 13.6361 | 22.8352 | 18.6578 | 0.33334 | 6.0037 | 3.2441 | 3.2441 | 3.2441 | 3.2441 | 13.8416 | 20.9909 | 17.7443 | 5.6667 | 9.5546 | 3.2441 | 3.2441 | 3.2441 | 3.2441 | 27.4776 | 43.826 | 36.4021 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 21 | 2421 | 6.7 | 6.7 | 6.975 | 7.2457 | 15 | 69 | 69 | 0 | 0 | -13.7049 | 303.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 22 | 2422 | 7.6 | 7.6 | 6.975 | 7.2457 | 15 | 69 | 69 | 0 | 0 | -20.7407 | 317.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 23 | 2423 | 6.2 | 6.2 | 6.975 | 7.2457 | 15 | 76 | 76 | 0 | 0 | -26.0816 | 332.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 11 | 24 | 2424 | 4.8 | 4.8 | 7.8375 | 7.1985 | 15 | 83 | 83 | 0 | 0 | -29.1848 | 348.5415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 1 | 2425 | 1.9 | 1.9 | 7.8375 | 7.1985 | 15 | 89 | 89 | 0 | 0 | -29.6566 | 5.5966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 2 | 2426 | 2.2 | 2.2 | 7.8375 | 7.1985 | 15 | 93 | 93 | 0 | 0 | -27.057 | 22.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 3 | 2427 | 0.8 | 0.8 | 7.8375 | 7.1985 | 15 | 93 | 93 | 0 | 0 | -22.4384 | 37.8407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 4 | 2428 | 0.8 | 0.8 | 7.8375 | 7.1985 | 15 | 95 | 95 | 0 | 0 | -15.9368 | 51.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 5 | 2429 | 1 | 1 | 7.8375 | 7.1985 | 15 | 96 | 96 | 0 | 0 | -8.0962 | 64.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 6 | 2430 | 1.3 | 1.3 | 7.8375 | 7.1985 | 15 | 97 | 97 | 0 | 0 | 0.59698 | 76.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 7 | 2431 | 3.4 | 3.4 | 7.8375 | 7.1985 | 15 | 96 | 96 | 145.8127 | 25.1112 | 9.7227 | 88.6808 | 32.9891 | 123.7528 | 142.0238 | 77.0992 | 0 | 0 | 0 | 0 | 7.8888 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 25.1112 | 44.6722 | 135.4359 | 153.707 | 88.7824 | 11.6832 | 11.6832 | 11.6832 | 11.6832 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 12 | 8 | 2432 | 5.6 | 5.6 | 7.8375 | 7.1985 | 15 | 95 | 95 | 229.3067 | 95.3579 | 18.8896 | 100.7355 | 5.2033 | 163.4523 | 225.9532 | 156.0937 | 0 | 0 | 0 | 0 | 48.6421 | 52.8265 | 125.3885 | 154.0471 | 122.0144 | 50.4406 | 50.4406 | 50.4406 | 50.4406 | 95.3579 | 58.0298 | 288.8408 | 380.0002 | 278.1081 | 50.4406 | 50.4406 | 50.4406 | 50.4406 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 9 | 2433 | 8.6 | 8.6 | 7.8375 | 7.1985 | 15 | 87 | 87 | 431.8605 | 134.9664 | 27.6757 | 113.7739 | 0 | 230.0486 | 401.4506 | 337.6883 | 76.1127 | 0 | 0 | 0 | 157.0336 | 79.6269 | 142.0058 | 188.4823 | 171.1928 | 100.2653 | 79.6269 | 79.6269 | 79.6269 | 134.9664 | 79.6269 | 372.0544 | 589.9329 | 508.8811 | 176.378 | 79.6269 | 79.6269 | 79.6269 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 10 | 2434 | 9.8 | 9.8 | 7.8375 | 7.1985 | 15 | 70 | 70 | 593.6601 | 146.1915 | 35.5525 | 128.5729 | 0 | 190.3441 | 481.1276 | 490.0731 | 211.9404 | 0 | 0 | 0 | 295.8085 | 98.0722 | 138.3058 | 199.7696 | 201.6604 | 142.8706 | 98.0722 | 98.0722 | 98.0722 | 146.1915 | 98.0722 | 328.6499 | 680.8972 | 691.7335 | 354.811 | 98.0722 | 98.0722 | 98.0722 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 11 | 2435 | 10.7 | 10.7 | 7.8375 | 7.1985 | 15 | 65 | 65 | 531.1431 | 196.6359 | 41.8146 | 145.8531 | 0 | 48.3719 | 337.845 | 429.4131 | 269.4368 | 0 | 0 | 0 | 322.3641 | 119.4061 | 133.1062 | 215.0925 | 241.027 | 195.7176 | 119.4061 | 119.4061 | 119.4061 | 196.6359 | 119.4061 | 181.4781 | 552.9376 | 670.4401 | 465.1544 | 119.4061 | 119.4061 | 119.4061 | 519 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 12 | 2436 | 10.8 | 10.8 | 7.8375 | 7.1985 | 15 | 65 | 65 | 408.3109 | 260.4799 | 45.6002 | 165.7584 | 0 | 0 | 170.8181 | 298.8734 | 251.8528 | 57.3002 | 0 | 0 | 278.5201 | 136.5151 | 136.5151 | 212.3386 | 269.1804 | 248.3086 | 161.9497 | 136.5151 | 136.5151 | 260.4799 | 136.5151 | 136.5151 | 383.1567 | 568.0538 | 500.1614 | 219.2499 | 136.5151 | 136.5151 | 539 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 13 | 2437 | 11.4 | 11.4 | 7.8375 | 7.1985 | 15 | 60 | 60 | 119.2121 | 333.3208 | 46.1747 | 187.1204 | 0 | 0 | 20.5193 | 71.6751 | 80.8446 | 42.6564 | 0 | 0 | 85.6792 | 148.4448 | 148.4448 | 177.8592 | 251.1909 | 264.3353 | 209.5927 | 148.4448 | 148.4448 | 333.3208 | 148.4448 | 148.4448 | 198.3785 | 322.866 | 345.18 | 252.2492 | 148.4448 | 148.4448 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 14 | 2438 | 12.6 | 12.6 | 7.8375 | 7.1985 | 15 | 57 | 57 | 502.1276 | 241.4085 | 43.4075 | 207.7216 | 0 | 0 | 0 | 213.4918 | 345.0229 | 274.4442 | 43.0998 | 0 | 358.5915 | 136.219 | 136.219 | 136.219 | 210.9872 | 257.0514 | 232.3337 | 151.3133 | 136.219 | 241.4085 | 136.219 | 136.219 | 136.219 | 424.479 | 602.0743 | 506.7779 | 194.4131 | 136.219 | 600 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 15 | 2439 | 12.1 | 12.1 | 7.8375 | 7.1985 | 15 | 62 | 62 | 215.2499 | 303.0534 | 37.879 | 225.9207 | 0 | 0 | 0 | 46.4459 | 138.4268 | 149.3191 | 72.7424 | 0 | 143.9466 | 143.9851 | 143.9851 | 143.9851 | 177.3406 | 243.3974 | 251.2198 | 196.2256 | 143.9851 | 303.0534 | 143.9851 | 143.9851 | 143.9851 | 223.7865 | 381.8241 | 400.5389 | 268.968 | 143.9851 | 447 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 16 | 2440 | 11.8 | 11.8 | 7.8375 | 7.1985 | 15 | 64 | 64 | 227.9994 | 263.4734 | 30.4563 | 241.4869 | 0 | 0 | 0 | 0 | 125.1911 | 179.9388 | 129.2808 | 2.8918 | 133.5266 | 128.6927 | 128.6927 | 128.6927 | 128.6927 | 204.8159 | 238.1055 | 207.3026 | 130.451 | 263.4734 | 128.6927 | 128.6927 | 128.6927 | 128.6927 | 330.007 | 418.0444 | 336.5834 | 133.3429 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 17 | 2441 | 11.1 | 11.1 | 7.8375 | 7.1985 | 15 | 66 | 66 | 420.6006 | 177.0808 | 21.9094 | 255.0276 | 0 | 0 | 0 | 0 | 173.0737 | 347.6573 | 318.588 | 102.8942 | 197.9192 | 100.3365 | 100.3365 | 100.3365 | 100.3365 | 158.0161 | 216.199 | 206.5112 | 134.6277 | 177.0808 | 100.3365 | 100.3365 | 100.3365 | 100.3365 | 331.0898 | 563.8563 | 525.0992 | 237.5219 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 12 | 18 | 2442 | 10.1 | 10.1 | 7.8375 | 7.1985 | 15 | 72 | 72 | 387.5489 | 129.5817 | 12.8198 | 267.3314 | 0 | 0 | 0 | 0 | 92.8929 | 311.2997 | 347.3513 | 179.9292 | 128.4183 | 74.7871 | 74.7871 | 74.7871 | 74.7871 | 103.0206 | 169.4022 | 180.3596 | 129.474 | 129.5817 | 74.7871 | 74.7871 | 74.7871 | 74.7871 | 195.9135 | 480.7019 | 527.7109 | 309.4033 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 19 | 2443 | 9 | 9 | 7.8375 | 7.1985 | 15 | 78 | 78 | 24.8787 | 70.5836 | 3.6365 | 279.1182 | 0 | 0 | 0 | 0 | 1.1294 | 17.9334 | 24.2322 | 16.3361 | 4.4164 | 34.7336 | 34.7336 | 34.7336 | 34.7336 | 36.3681 | 60.6852 | 69.8002 | 58.3737 | 70.5836 | 34.7336 | 34.7336 | 34.7336 | 34.7336 | 37.4975 | 78.6186 | 94.0324 | 74.7098 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 20 | 2444 | 8.6 | 8.6 | 7.8375 | 7.1985 | 15 | 77 | 77 | 56.4195 | 3.63 | -5.2465 | 291.0137 | 8.9229 | 0 | 0 | 0 | 0 | 33.0017 | 55.5944 | 45.6206 | 18.37 | 6.7615 | 4.0266 | 4.0266 | 4.0266 | 4.0266 | 14.1416 | 21.0662 | 18.0093 | 3.63 | 15.6844 | 4.0266 | 4.0266 | 4.0266 | 4.0266 | 47.1433 | 76.6606 | 63.6299 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 21 | 2445 | 8.5 | 8.5 | 7.8375 | 7.1985 | 15 | 75 | 75 | 0 | 0 | -13.4243 | 303.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 22 | 2446 | 8 | 8 | 7.8375 | 7.1985 | 15 | 75 | 75 | 0 | 0 | -20.435 | 317.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 23 | 2447 | 7.7 | 7.7 | 7.8375 | 7.1985 | 15 | 77 | 77 | 0 | 0 | -25.7482 | 332.3241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 12 | 24 | 2448 | 7.6 | 7.6 | 7.3083 | 7.1474 | 15 | 80 | 80 | 0 | 0 | -28.8273 | 348.6693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 1 | 2449 | 7.5 | 7.5 | 7.3083 | 7.1474 | 15 | 82 | 82 | 0 | 0 | -29.2847 | 5.6477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 2 | 2450 | 7.5 | 7.5 | 7.3083 | 7.1474 | 15 | 81 | 81 | 0 | 0 | -26.6857 | 22.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 3 | 2451 | 7.5 | 7.5 | 7.3083 | 7.1474 | 15 | 77 | 77 | 0 | 0 | -22.0749 | 37.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 4 | 2452 | 7.4 | 7.4 | 7.3083 | 7.1474 | 15 | 75 | 75 | 0 | 0 | -15.5854 | 51.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 5 | 2453 | 7.3 | 7.3 | 7.3083 | 7.1474 | 15 | 79 | 79 | 0 | 0 | -7.7565 | 64.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 6 | 2454 | 7.3 | 7.3 | 7.3083 | 7.1474 | 15 | 79 | 79 | 0 | 0 | 0.92818 | 76.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 7 | 2455 | 7.7 | 7.7 | 7.3083 | 7.1474 | 15 | 79 | 79 | 204.0015 | 26.9366 | 10.0503 | 88.5021 | 46.7374 | 173.443 | 198.548 | 107.3463 | 0 | 0 | 0 | 0 | 12.0634 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 26.9366 | 59.9553 | 186.6609 | 211.7659 | 120.5642 | 13.2179 | 13.2179 | 13.2179 | 13.2179 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 13 | 8 | 2456 | 8.1 | 8.1 | 7.3083 | 7.1474 | 15 | 75 | 75 | 83.249 | 98.9345 | 19.2196 | 100.5539 | 2.1428 | 59.458 | 81.9435 | 56.4276 | 0 | 0 | 0 | 0 | 18.0655 | 48.7903 | 125.4455 | 155.5183 | 121.3926 | 45.9245 | 45.9245 | 45.9245 | 45.9245 | 98.9345 | 50.9331 | 184.9035 | 237.4618 | 177.8202 | 45.9245 | 45.9245 | 45.9245 | 45.9245 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 9 | 2457 | 8.5 | 8.5 | 7.3083 | 7.1474 | 15 | 70 | 70 | 110.2768 | 170.3791 | 28.0141 | 113.5992 | 0 | 58.8994 | 102.3688 | 85.872 | 19.0725 | 0 | 0 | 0 | 40.6209 | 79.8247 | 137.8481 | 180.6711 | 164.4196 | 98.6136 | 79.8247 | 79.8247 | 79.8247 | 170.3791 | 79.8247 | 196.7475 | 283.0399 | 250.2916 | 117.6861 | 79.8247 | 79.8247 | 79.8247 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 10 | 2458 | 8.3 | 8.3 | 7.3083 | 7.1474 | 15 | 72 | 72 | 19.8298 | 193.0279 | 35.9043 | 128.4241 | 0 | 6.3879 | 16.0423 | 16.2993 | 7.0084 | 0 | 0 | 0 | 9.9721 | 89.3341 | 105.7587 | 130.582 | 131.2429 | 107.3542 | 89.3341 | 89.3341 | 89.3341 | 193.0279 | 89.3341 | 112.1466 | 146.6243 | 147.5422 | 114.3626 | 89.3341 | 89.3341 | 89.3341 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 11 | 2459 | 9 | 9 | 7.3083 | 7.1474 | 15 | 66 | 66 | 18.7286 | 232.5488 | 42.1806 | 145.7637 | 0 | 1.7373 | 11.8848 | 15.0703 | 9.4279 | 0 | 0 | 0 | 11.4512 | 108.9428 | 113.1283 | 137.5766 | 145.2515 | 131.6573 | 108.9428 | 108.9428 | 108.9428 | 232.5488 | 108.9428 | 114.8656 | 149.4614 | 160.3219 | 141.0852 | 108.9428 | 108.9428 | 108.9428 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 12 | 2460 | 10 | 10 | 7.3083 | 7.1474 | 15 | 59 | 59 | 69.1251 | 308.5415 | 45.9721 | 165.7711 | 0 | 0 | 28.819 | 50.3227 | 42.3481 | 9.5665 | 0 | 0 | 47.4585 | 138.5291 | 138.5291 | 188.5037 | 225.7929 | 211.9642 | 155.1183 | 138.5291 | 138.5291 | 308.5415 | 138.5291 | 138.5291 | 217.3226 | 276.1156 | 254.3123 | 164.6848 | 138.5291 | 138.5291 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 13 | 2461 | 9.2 | 9.2 | 7.3083 | 7.1474 | 15 | 58 | 58 | 45.3223 | 311.2271 | 46.5346 | 187.2564 | 0 | 0 | 7.7424 | 27.0648 | 30.533 | 16.1153 | 0 | 0 | 32.7729 | 138.6074 | 138.6074 | 158.0299 | 206.5017 | 215.2019 | 179.0341 | 138.6074 | 138.6074 | 311.2271 | 138.6074 | 138.6074 | 165.7724 | 233.5665 | 245.7349 | 195.1494 | 138.6074 | 138.6074 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 14 | 2462 | 9.9 | 9.9 | 7.3083 | 7.1474 | 15 | 54 | 54 | 96.6887 | 330.5247 | 43.7389 | 207.9549 | 0 | 0 | 0 | 40.715 | 65.981 | 52.5962 | 8.4013 | 0 | 69.4753 | 149.1891 | 149.1891 | 149.1891 | 201.5453 | 234.0354 | 216.8236 | 159.9924 | 149.1891 | 330.5247 | 149.1891 | 149.1891 | 149.1891 | 242.2603 | 300.0164 | 269.4198 | 168.3937 | 149.1891 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 15 | 2463 | 10.1 | 10.1 | 7.3083 | 7.1474 | 15 | 57 | 57 | 93.4364 | 309.1 | 38.1771 | 226.2031 | 0 | 0 | 0 | 19.7882 | 59.6307 | 64.5423 | 31.6459 | 0 | 62.9 | 140.5512 | 140.5512 | 140.5512 | 165.268 | 215.0339 | 221.1689 | 180.0791 | 140.5512 | 309.1 | 140.5512 | 140.5512 | 140.5512 | 185.0562 | 274.6646 | 285.7112 | 211.7251 | 140.5512 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 16 | 2464 | 9.4 | 9.4 | 7.3083 | 7.1474 | 15 | 58 | 58 | 17.7588 | 222.5194 | 30.7271 | 241.7832 | 0 | 0 | 0 | 0 | 9.6619 | 13.9572 | 10.0765 | 0.29312 | 10.4806 | 106.4934 | 106.4934 | 106.4934 | 106.4934 | 123.1458 | 130.5487 | 123.8603 | 106.9986 | 222.5194 | 106.4934 | 106.4934 | 106.4934 | 106.4934 | 132.8078 | 144.5059 | 133.9368 | 107.2917 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 17 | 2465 | 9.4 | 9.4 | 7.3083 | 7.1474 | 15 | 58 | 58 | 41.4022 | 202.326 | 22.1628 | 255.3215 | 0 | 0 | 0 | 0 | 16.8272 | 34.0738 | 31.3604 | 10.2766 | 19.674 | 94.0748 | 94.0748 | 94.0748 | 94.0748 | 126.3444 | 159.4185 | 154.2151 | 113.7823 | 202.326 | 94.0748 | 94.0748 | 94.0748 | 94.0748 | 143.1716 | 193.4923 | 185.5755 | 124.0589 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 13 | 18 | 2466 | 8 | 8 | 7.3083 | 7.1474 | 15 | 68 | 68 | 22.3818 | 131.477 | 13.0662 | 267.6174 | 0 | 0 | 0 | 0 | 5.2524 | 17.8927 | 20.0516 | 10.4646 | 7.523 | 62.9061 | 62.9061 | 62.9061 | 62.9061 | 68.9053 | 83.3426 | 85.8085 | 74.8585 | 131.477 | 62.9061 | 62.9061 | 62.9061 | 62.9061 | 74.1577 | 101.2353 | 105.8602 | 85.3231 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 19 | 2467 | 6.8 | 6.8 | 7.3083 | 7.1474 | 15 | 81 | 81 | 3.8471 | 43.2982 | 3.8855 | 279.3951 | 0 | 0 | 0 | 0 | 0.15579 | 2.7578 | 3.7443 | 2.5374 | 0.70182 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 43.2982 | 21.0913 | 21.0913 | 21.0913 | 21.0913 | 21.2471 | 23.8491 | 24.8356 | 23.6288 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 20 | 2468 | 6.3 | 6.3 | 7.3083 | 7.1474 | 15 | 83 | 83 | 3.9467 | 5.9031 | -4.9861 | 291.2803 | 0.64279 | 0 | 0 | 0 | 0 | 2.2925 | 3.8848 | 3.2015 | 0.096934 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 5.9031 | 3.7989 | 3.1561 | 3.1561 | 3.1561 | 3.1561 | 5.4486 | 7.041 | 6.3576 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 21 | 2469 | 5.7 | 5.7 | 7.3083 | 7.1474 | 15 | 85 | 85 | 0 | 0 | -13.1448 | 303.8224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 22 | 2470 | 4.1 | 4.1 | 7.3083 | 7.1474 | 15 | 89 | 89 | 0 | 0 | -20.1304 | 317.4786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 23 | 2471 | 3.2 | 3.2 | 7.3083 | 7.1474 | 15 | 92 | 92 | 0 | 0 | -25.4164 | 332.5105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 13 | 24 | 2472 | 2.2 | 2.2 | 7.5167 | 7.2908 | 15 | 93 | 93 | 0 | 0 | -28.4718 | 348.7941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 1 | 2473 | 1.3 | 1.3 | 7.5167 | 7.2908 | 15 | 94 | 94 | 0 | 0 | -28.9152 | 5.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 2 | 2474 | 1.7 | 1.7 | 7.5167 | 7.2908 | 15 | 96 | 96 | 0 | 0 | -26.3172 | 22.2496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 3 | 2475 | 2.7 | 2.7 | 7.5167 | 7.2908 | 15 | 96 | 96 | 0 | 0 | -21.7142 | 37.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 4 | 2476 | 0.8 | 0.8 | 7.5167 | 7.2908 | 15 | 96 | 96 | 0 | 0 | -15.2368 | 51.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 5 | 2477 | 2.1 | 2.1 | 7.5167 | 7.2908 | 15 | 97 | 97 | 0 | 0 | -7.4197 | 64.5579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 6 | 2478 | 2.9 | 2.9 | 7.5167 | 7.2908 | 15 | 97 | 97 | 0 | 0 | 1.2564 | 76.5847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 7 | 2479 | 4.3 | 4.3 | 7.5167 | 7.2908 | 15 | 97 | 97 | 0.14481 | 2.9907 | 10.375 | 88.3232 | 0.033588 | 0.12332 | 0.14082 | 0.075825 | 0 | 0 | 0 | 0 | 0.0092862 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 2.9907 | 1.4298 | 1.5196 | 1.537 | 1.4721 | 1.3962 | 1.3962 | 1.3962 | 1.3962 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 14 | 8 | 2480 | 5.2 | 5.2 | 7.5167 | 7.2908 | 15 | 97 | 97 | 3.7767 | 52.1622 | 19.5465 | 100.3717 | 0.10871 | 2.7026 | 3.7134 | 2.5489 | 0 | 0 | 0 | 0 | 0.83784 | 25.6287 | 29.9758 | 31.6697 | 29.7182 | 25.4465 | 25.4465 | 25.4465 | 25.4465 | 52.1622 | 25.7374 | 32.6784 | 35.3831 | 32.2671 | 25.4465 | 25.4465 | 25.4465 | 25.4465 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 9 | 2481 | 5.4 | 5.4 | 7.5167 | 7.2908 | 15 | 96 | 96 | 2.4649 | 71.0805 | 28.3493 | 113.4235 | 0 | 1.32 | 2.2849 | 1.9114 | 0.4182 | 0 | 0 | 0 | 0.91952 | 34.9639 | 34.9639 | 34.9639 | 34.9639 | 34.9639 | 34.9639 | 34.9639 | 34.9639 | 71.0805 | 34.9639 | 36.2839 | 37.2489 | 36.8753 | 35.3821 | 34.9639 | 34.9639 | 34.9639 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 10 | 2482 | 6.6 | 6.6 | 7.5167 | 7.2908 | 15 | 95 | 95 | 3.639 | 117.1534 | 36.253 | 128.2737 | 0 | 1.1777 | 2.9387 | 2.9782 | 1.2731 | 0 | 0 | 0 | 1.8466 | 58.5422 | 58.5422 | 58.5422 | 58.5422 | 58.5422 | 58.5422 | 58.5422 | 58.5422 | 117.1534 | 58.5422 | 59.72 | 61.4809 | 61.5204 | 59.8153 | 58.5422 | 58.5422 | 58.5422 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 11 | 2483 | 8.6 | 8.6 | 7.5167 | 7.2908 | 15 | 94 | 94 | 66.8533 | 275.8268 | 42.5437 | 145.6723 | 0 | 6.3144 | 42.3237 | 53.5403 | 33.3938 | 0 | 0 | 0 | 41.1732 | 124.8606 | 135.6501 | 197.1794 | 216.3453 | 181.9207 | 124.8606 | 124.8606 | 124.8606 | 275.8268 | 124.8606 | 141.9646 | 239.5032 | 269.8857 | 215.3145 | 124.8606 | 124.8606 | 124.8606 | 317 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 12 | 2484 | 9.6 | 9.6 | 7.5167 | 7.2908 | 15 | 84 | 84 | 142.6843 | 320.4148 | 46.3413 | 165.7821 | 0 | 0 | 59.2823 | 103.306 | 86.8145 | 19.4682 | 0 | 0 | 98.5852 | 145.2375 | 145.2375 | 215.0422 | 266.8799 | 247.4612 | 168.1612 | 145.2375 | 145.2375 | 320.4148 | 145.2375 | 145.2375 | 274.3245 | 370.1859 | 334.2757 | 187.6294 | 145.2375 | 145.2375 | 419 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 13 | 2485 | 10.5 | 10.5 | 7.5167 | 7.2908 | 15 | 70 | 70 | 293.2146 | 311.7017 | 46.8921 | 187.3914 | 0 | 0 | 49.7174 | 173.9064 | 196.2233 | 103.5953 | 0 | 0 | 213.2983 | 148.5858 | 148.5858 | 182.1643 | 266.0397 | 281.1123 | 218.5526 | 148.5858 | 148.5858 | 311.7017 | 148.5858 | 148.5858 | 231.8817 | 439.9461 | 477.3356 | 322.1479 | 148.5858 | 148.5858 | 525 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 14 | 2486 | 10 | 10 | 7.5167 | 7.2908 | 15 | 69 | 69 | 94.2115 | 331.8956 | 44.0679 | 208.1875 | 0 | 0 | 0 | 39.2898 | 63.8467 | 51.0031 | 8.2825 | 0 | 68.1044 | 149.565 | 149.565 | 149.565 | 201.5018 | 233.9634 | 216.9855 | 160.5136 | 149.565 | 331.8956 | 149.565 | 149.565 | 149.565 | 240.7917 | 297.8101 | 267.9886 | 168.7961 | 149.565 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 15 | 2487 | 10.4 | 10.4 | 7.5167 | 7.2908 | 15 | 65 | 65 | 170.3449 | 312.5793 | 38.4731 | 226.4846 | 0 | 0 | 0 | 35.4018 | 107.8802 | 117.1639 | 57.8145 | 0 | 115.4207 | 144.3822 | 144.3822 | 144.3822 | 177.5926 | 245.5846 | 254.2937 | 198.618 | 144.3822 | 312.5793 | 144.3822 | 144.3822 | 144.3822 | 212.9944 | 353.4649 | 371.4576 | 256.4326 | 144.3822 | 428 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 16 | 2488 | 10.5 | 10.5 | 7.5167 | 7.2908 | 15 | 63 | 63 | 12.7455 | 211.4211 | 30.996 | 242.078 | 0 | 0 | 0 | 0 | 6.8707 | 9.9751 | 7.2363 | 0.25852 | 7.5789 | 102.0842 | 102.0842 | 102.0842 | 102.0842 | 114.7514 | 120.475 | 115.4255 | 102.5608 | 211.4211 | 102.0842 | 102.0842 | 102.0842 | 102.0842 | 121.6221 | 130.4501 | 122.6618 | 102.8193 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 17 | 2489 | 10.3 | 10.3 | 7.5167 | 7.2908 | 15 | 64 | 64 | 163.0778 | 221.7598 | 22.4147 | 255.6133 | 0 | 0 | 0 | 0 | 65.4596 | 133.6268 | 123.5172 | 41.0529 | 78.2402 | 107.0047 | 107.0047 | 107.0047 | 107.0047 | 157.6213 | 210.3315 | 202.5142 | 138.7488 | 221.7598 | 107.0047 | 107.0047 | 107.0047 | 107.0047 | 223.0809 | 343.9582 | 326.0314 | 179.8017 | 300 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 18 | 2490 | 9.4 | 9.4 | 7.5167 | 7.2908 | 15 | 70 | 70 | 20.9159 | 131.871 | 13.3114 | 267.901 | 0 | 0 | 0 | 0 | 4.8042 | 16.6407 | 18.7293 | 9.8465 | 7.129 | 63.148 | 63.148 | 63.148 | 63.148 | 68.8221 | 82.8018 | 85.2686 | 74.7774 | 131.871 | 63.148 | 63.148 | 63.148 | 63.148 | 73.6263 | 99.4425 | 103.9979 | 84.6239 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 19 | 2491 | 7.9 | 7.9 | 7.5167 | 7.2908 | 15 | 77 | 77 | 28.1199 | 75.7332 | 4.1335 | 279.6694 | 0 | 0 | 0 | 0 | 1.0023 | 20.0453 | 27.346 | 18.6278 | 5.2668 | 37.1354 | 37.1354 | 37.1354 | 37.1354 | 38.5311 | 65.0499 | 75.2168 | 63.0761 | 75.7332 | 37.1354 | 37.1354 | 37.1354 | 37.1354 | 39.5333 | 85.0952 | 102.5628 | 81.7039 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 20 | 2492 | 7.4 | 7.4 | 7.5167 | 7.2908 | 15 | 82 | 82 | 4.8368 | 7.8569 | -4.7266 | 291.544 | 0.8103 | 0 | 0 | 0 | 0 | 2.7898 | 4.7557 | 3.9358 | 0.14312 | 4.2435 | 4.1926 | 4.1926 | 4.1926 | 4.1926 | 4.3678 | 4.4913 | 4.4398 | 7.8569 | 5.0538 | 4.1926 | 4.1926 | 4.1926 | 4.1926 | 7.1576 | 9.247 | 8.3755 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 21 | 2493 | 7.2 | 7.2 | 7.5167 | 7.2908 | 15 | 82 | 82 | 0 | 0 | -12.8662 | 304.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 22 | 2494 | 6.7 | 6.7 | 7.5167 | 7.2908 | 15 | 85 | 85 | 0 | 0 | -19.8271 | 317.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 23 | 2495 | 6.4 | 6.4 | 7.5167 | 7.2908 | 15 | 92 | 92 | 0 | 0 | -25.0862 | 332.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 14 | 24 | 2496 | 6.5 | 6.5 | 6.4333 | 7.0864 | 15 | 94 | 94 | 0 | 0 | -28.1184 | 348.9159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 1 | 2497 | 6.7 | 6.7 | 6.4333 | 7.0864 | 15 | 95 | 95 | 0 | 0 | -28.5482 | 5.7439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 2 | 2498 | 6.8 | 6.8 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0 | 0 | -25.9515 | 22.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 3 | 2499 | 6.7 | 6.7 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0 | 0 | -21.3565 | 37.5845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 4 | 2500 | 6.6 | 6.6 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0 | 0 | -14.8912 | 51.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 5 | 2501 | 6.6 | 6.6 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0 | 0 | -7.086 | 64.4053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 6 | 2502 | 6.3 | 6.3 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0 | 0 | 1.5816 | 76.4156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 7 | 2503 | 6.4 | 6.4 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0.12484 | 2.9914 | 10.6965 | 88.1442 | 0.02931 | 0.1065 | 0.1213 | 0.065046 | 0 | 0 | 0 | 0 | 0.0086247 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 2.9914 | 1.4234 | 1.5006 | 1.5154 | 1.4591 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 15 | 8 | 2504 | 6.5 | 6.5 | 6.4333 | 7.0864 | 15 | 96 | 96 | 0.25263 | 13.9427 | 19.8701 | 100.189 | 0.008039 | 0.18113 | 0.24811 | 0.16976 | 0 | 0 | 0 | 0 | 0.057256 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 13.9427 | 6.5593 | 6.7324 | 6.7994 | 6.721 | 6.5513 | 6.5513 | 6.5513 | 6.5513 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 9 | 2505 | 6.5 | 6.5 | 6.4333 | 7.0864 | 15 | 95 | 95 | 0.50545 | 32.8091 | 28.6813 | 113.2467 | 0 | 0.27137 | 0.46786 | 0.39029 | 0.084089 | 0 | 0 | 0 | 0.1909 | 15.6184 | 15.6184 | 15.6184 | 15.6184 | 15.6184 | 15.6184 | 15.6184 | 15.6184 | 32.8091 | 15.6184 | 15.8898 | 16.0863 | 16.0087 | 15.7025 | 15.6184 | 15.6184 | 15.6184 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 10 | 2506 | 6.7 | 6.7 | 6.4333 | 7.0864 | 15 | 95 | 95 | 1.134 | 66.4195 | 36.5985 | 128.1217 | 0 | 0.36871 | 0.91409 | 0.92401 | 0.39266 | 0 | 0 | 0 | 0.58053 | 32.2017 | 32.2017 | 32.2017 | 32.2017 | 32.2017 | 32.2017 | 32.2017 | 32.2017 | 66.4195 | 32.2017 | 32.5704 | 33.1158 | 33.1257 | 32.5943 | 32.2017 | 32.2017 | 32.2017 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 11 | 2507 | 7.4 | 7.4 | 6.4333 | 7.0864 | 15 | 94 | 94 | 3.044 | 131.1119 | 42.9037 | 145.579 | 0 | 0.29268 | 1.9226 | 2.4262 | 1.5087 | 0 | 0 | 0 | 1.8881 | 65.4006 | 65.4006 | 65.4006 | 65.4006 | 65.4006 | 65.4006 | 65.4006 | 65.4006 | 131.1119 | 65.4006 | 65.6933 | 67.3232 | 67.8268 | 66.9093 | 65.4006 | 65.4006 | 65.4006 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 12 | 2508 | 7.3 | 7.3 | 6.4333 | 7.0864 | 15 | 93 | 93 | 3.8199 | 164.3442 | 46.7078 | 165.7914 | 0 | 0 | 1.5817 | 2.7505 | 2.3081 | 0.5137 | 0 | 0 | 2.6558 | 82.8196 | 82.8196 | 82.8196 | 82.8196 | 82.8196 | 82.8196 | 82.8196 | 82.8196 | 164.3442 | 82.8196 | 82.8196 | 84.4013 | 85.5701 | 85.1278 | 83.3333 | 82.8196 | 82.8196 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 13 | 2509 | 7.1 | 7.1 | 6.4333 | 7.0864 | 15 | 90 | 90 | 1.932 | 123.5863 | 47.247 | 187.5255 | 0 | 0 | 0.32519 | 1.1381 | 1.2843 | 0.6782 | 0 | 0 | 1.4137 | 61.2071 | 61.2071 | 61.2071 | 61.2071 | 61.2071 | 61.2071 | 61.2071 | 61.2071 | 123.5863 | 61.2071 | 61.2071 | 61.5322 | 62.3451 | 62.4914 | 61.8853 | 61.2071 | 61.2071 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 14 | 2510 | 7.4 | 7.4 | 6.4333 | 7.0864 | 15 | 91 | 91 | 1.6272 | 112.8168 | 44.3946 | 208.4194 | 0 | 0 | 0 | 0.67204 | 1.0951 | 0.87662 | 0.14466 | 0 | 1.1832 | 55.6417 | 55.6417 | 55.6417 | 55.6417 | 55.6417 | 55.6417 | 55.6417 | 55.6417 | 112.8168 | 55.6417 | 55.6417 | 55.6417 | 56.3138 | 56.7368 | 56.5184 | 55.7864 | 55.6417 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 15 | 2511 | 7.2 | 7.2 | 6.4333 | 7.0864 | 15 | 88 | 88 | 1.7543 | 109.8038 | 38.767 | 226.7649 | 0 | 0 | 0 | 0.35771 | 1.1024 | 1.2014 | 0.59657 | 0 | 1.1962 | 54.1041 | 54.1041 | 54.1041 | 54.1041 | 54.1041 | 54.1041 | 54.1041 | 54.1041 | 109.8038 | 54.1041 | 54.1041 | 54.1041 | 54.4618 | 55.2066 | 55.3055 | 54.7007 | 54.1041 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 16 | 2512 | 7.6 | 7.6 | 6.4333 | 7.0864 | 15 | 86 | 86 | 0.57857 | 55.6534 | 31.2631 | 242.3712 | 0 | 0 | 0 | 0 | 0.30901 | 0.45089 | 0.32866 | 0.013893 | 0.34659 | 26.791 | 26.791 | 26.791 | 26.791 | 26.791 | 26.791 | 26.791 | 26.791 | 55.6534 | 26.791 | 26.791 | 26.791 | 26.791 | 27.1 | 27.2419 | 27.1197 | 26.8049 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 17 | 2513 | 7.5 | 7.5 | 6.4333 | 7.0864 | 15 | 82 | 82 | 0.49793 | 41.7589 | 22.6651 | 255.9031 | 0 | 0 | 0 | 0 | 0.19738 | 0.40621 | 0.37709 | 0.12707 | 0.24115 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 41.7589 | 19.9496 | 19.9496 | 19.9496 | 19.9496 | 20.147 | 20.3559 | 20.3267 | 20.0767 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 18 | 2514 | 7.3 | 7.3 | 6.4333 | 7.0864 | 15 | 84 | 84 | 0.26842 | 21.9073 | 13.5553 | 268.1822 | 0 | 0 | 0 | 0 | 0.060329 | 0.21253 | 0.24023 | 0.12721 | 0.092743 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 21.9073 | 10.3313 | 10.3313 | 10.3313 | 10.3313 | 10.3916 | 10.5438 | 10.5715 | 10.4585 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 19 | 2515 | 7.2 | 7.2 | 6.4333 | 7.0864 | 15 | 86 | 86 | 0.064569 | 5.9876 | 4.3805 | 279.941 | 0 | 0 | 0 | 0 | 0.0019911 | 0.045771 | 0.062738 | 0.042955 | 0.012405 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 5.9876 | 2.7794 | 2.7794 | 2.7794 | 2.7794 | 2.7814 | 2.8252 | 2.8422 | 2.8224 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 20 | 2516 | 7.2 | 7.2 | 6.4333 | 7.0864 | 15 | 88 | 88 | 0 | 0 | -4.4681 | 291.8047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 21 | 2517 | 7 | 7 | 6.4333 | 7.0864 | 15 | 91 | 91 | 0 | 0 | -12.5888 | 304.3167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 22 | 2518 | 7 | 7 | 6.4333 | 7.0864 | 15 | 94 | 94 | 0 | 0 | -19.5251 | 317.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 23 | 2519 | 7.2 | 7.2 | 6.4333 | 7.0864 | 15 | 95 | 95 | 0 | 0 | -24.7578 | 332.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 15 | 24 | 2520 | 7.3 | 7.3 | 6.9792 | 7.018 | 15 | 96 | 96 | 0 | 0 | -27.7672 | 349.0346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 1 | 2521 | 7.5 | 7.5 | 6.9792 | 7.018 | 15 | 96 | 96 | 0 | 0 | -28.1839 | 5.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 2 | 2522 | 7.5 | 7.5 | 6.9792 | 7.018 | 15 | 97 | 97 | 0 | 0 | -25.5888 | 22.1939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 3 | 2523 | 7.4 | 7.4 | 6.9792 | 7.018 | 15 | 97 | 97 | 0 | 0 | -21.0018 | 37.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 4 | 2524 | 7.3 | 7.3 | 6.9792 | 7.018 | 15 | 97 | 97 | 0 | 0 | -14.5487 | 51.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 5 | 2525 | 6.9 | 6.9 | 6.9792 | 7.018 | 15 | 97 | 97 | 0 | 0 | -6.7553 | 64.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 6 | 2526 | 6.6 | 6.6 | 6.9792 | 7.018 | 15 | 97 | 97 | 0 | 0 | 1.9036 | 76.2467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 7 | 2527 | 7.6 | 7.6 | 6.9792 | 7.018 | 15 | 97 | 97 | 50.9575 | 32.2289 | 11.0147 | 87.9652 | 12.108 | 43.5416 | 49.4691 | 26.4183 | 0 | 0 | 0 | 0 | 3.7711 | 34.0711 | 84.5334 | 94.0492 | 57.0443 | 14.6333 | 14.6333 | 14.6333 | 14.6333 | 32.2289 | 46.1791 | 128.0751 | 143.5184 | 83.4625 | 14.6333 | 14.6333 | 14.6333 | 14.6333 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 16 | 8 | 2528 | 7.7 | 7.7 | 6.9792 | 7.018 | 15 | 97 | 97 | 11.3493 | 80.3739 | 20.1904 | 100.0059 | 0.39556 | 8.152 | 11.1332 | 7.5926 | 0 | 0 | 0 | 0 | 2.6261 | 38.4186 | 74.461 | 88.3136 | 71.8616 | 36.5805 | 36.5805 | 36.5805 | 36.5805 | 80.3739 | 38.8141 | 82.6131 | 99.4467 | 79.4543 | 36.5805 | 36.5805 | 36.5805 | 36.5805 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 9 | 2529 | 7.7 | 7.7 | 6.9792 | 7.018 | 15 | 97 | 97 | 1.8568 | 63.2902 | 29.0098 | 113.0689 | 0 | 0.99942 | 1.7162 | 1.4276 | 0.30279 | 0 | 0 | 0 | 0.70979 | 30.8946 | 30.8946 | 30.8946 | 30.8946 | 30.8946 | 30.8946 | 30.8946 | 30.8946 | 63.2902 | 30.8946 | 31.8941 | 32.6108 | 32.3223 | 31.1974 | 30.8946 | 30.8946 | 30.8946 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 10 | 2530 | 8.5 | 8.5 | 6.9792 | 7.018 | 15 | 97 | 97 | 1.8373 | 85.0512 | 36.9406 | 127.968 | 0 | 0.60013 | 1.4783 | 1.4905 | 0.62961 | 0 | 0 | 0 | 0.94877 | 41.6814 | 41.6814 | 41.6814 | 41.6814 | 41.6814 | 41.6814 | 41.6814 | 41.6814 | 85.0512 | 41.6814 | 42.2815 | 43.1597 | 43.1719 | 42.311 | 41.6814 | 41.6814 | 41.6814 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 11 | 2531 | 8.8 | 8.8 | 6.9792 | 7.018 | 15 | 96 | 96 | 3.9748 | 150.5173 | 43.2605 | 145.4835 | 0 | 0.38893 | 2.5045 | 3.153 | 1.9545 | 0 | 0 | 0 | 2.4827 | 75.7398 | 75.7398 | 75.7398 | 75.7398 | 75.7398 | 75.7398 | 75.7398 | 75.7398 | 150.5173 | 75.7398 | 76.1287 | 78.2443 | 78.8928 | 77.6943 | 75.7398 | 75.7398 | 75.7398 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 12 | 2532 | 9.3 | 9.3 | 6.9792 | 7.018 | 15 | 94 | 94 | 7.7247 | 222.5965 | 47.0713 | 165.7988 | 0 | 0 | 3.1877 | 5.5316 | 4.6352 | 1.0236 | 0 | 0 | 5.4035 | 108.3811 | 108.3811 | 116.1643 | 121.8874 | 119.6987 | 110.8804 | 108.3811 | 108.3811 | 222.5965 | 108.3811 | 108.3811 | 119.352 | 127.419 | 124.3339 | 111.9039 | 108.3811 | 108.3811 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 13 | 2533 | 9.4 | 9.4 | 6.9792 | 7.018 | 15 | 93 | 93 | 2.5361 | 142.1336 | 47.5993 | 187.6584 | 0 | 0 | 0.42376 | 1.4837 | 1.6745 | 0.88443 | 0 | 0 | 1.8664 | 70.8936 | 70.8936 | 70.8936 | 70.8936 | 70.8936 | 70.8936 | 70.8936 | 70.8936 | 142.1336 | 70.8936 | 70.8936 | 71.3173 | 72.3773 | 72.5681 | 71.778 | 70.8936 | 70.8936 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 14 | 2534 | 9.5 | 9.5 | 6.9792 | 7.018 | 15 | 89 | 89 | 1.9349 | 123.5848 | 44.7188 | 208.6504 | 0 | 0 | 0 | 0.79139 | 1.2931 | 1.0373 | 0.17387 | 0 | 1.4152 | 61.2048 | 61.2048 | 61.2048 | 61.2048 | 61.2048 | 61.2048 | 61.2048 | 61.2048 | 123.5848 | 61.2048 | 61.2048 | 61.2048 | 61.9962 | 62.4979 | 62.2421 | 61.3787 | 61.2048 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 15 | 2535 | 9.4 | 9.4 | 6.9792 | 7.018 | 15 | 89 | 89 | 1.6411 | 106.874 | 39.0586 | 227.044 | 0 | 0 | 0 | 0.32825 | 1.0233 | 1.1189 | 0.55909 | 0 | 1.126 | 52.5978 | 52.5978 | 52.5978 | 52.5978 | 52.5978 | 52.5978 | 52.5978 | 52.5978 | 106.874 | 52.5978 | 52.5978 | 52.5978 | 52.9261 | 53.6211 | 53.7167 | 53.1569 | 52.5978 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 16 | 2536 | 9.8 | 9.8 | 6.9792 | 7.018 | 15 | 83 | 83 | 4.7161 | 158.1543 | 31.5283 | 242.6626 | 0 | 0 | 0 | 0 | 2.4954 | 3.6597 | 2.6802 | 0.13061 | 2.8457 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 158.1543 | 79.7298 | 79.7298 | 79.7298 | 79.7298 | 82.2252 | 83.3894 | 82.4099 | 79.8604 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 17 | 2537 | 9.8 | 9.8 | 6.9792 | 7.018 | 15 | 83 | 83 | 1.9102 | 82.0664 | 22.9139 | 256.1907 | 0 | 0 | 0 | 0 | 0.74771 | 1.5514 | 1.4464 | 0.49401 | 0.93365 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 82.0664 | 40.0896 | 40.0896 | 40.0896 | 40.0896 | 40.8373 | 41.6411 | 41.536 | 40.5836 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 16 | 18 | 2538 | 9.1 | 9.1 | 6.9792 | 7.018 | 15 | 86 | 86 | 1.0461 | 43.6337 | 13.798 | 268.4609 | 0 | 0 | 0 | 0 | 0.22999 | 0.82427 | 0.93571 | 0.49901 | 0.36628 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 43.6337 | 20.9173 | 20.9173 | 20.9173 | 20.9173 | 21.1473 | 21.7416 | 21.853 | 21.4163 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 19 | 2539 | 8.7 | 8.7 | 6.9792 | 7.018 | 15 | 89 | 89 | 0.20672 | 10.9593 | 4.6263 | 280.2096 | 0 | 0 | 0 | 0 | 0.0053921 | 0.14571 | 0.20068 | 0.13809 | 0.040705 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 10.9593 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1247 | 5.265 | 5.32 | 5.2574 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 20 | 2540 | 8.4 | 8.4 | 6.9792 | 7.018 | 15 | 92 | 92 | 0 | 0 | -4.2107 | 292.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 21 | 2541 | 8.2 | 8.2 | 6.9792 | 7.018 | 15 | 93 | 93 | 0 | 0 | -12.3124 | 304.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 22 | 2542 | 8 | 8 | 6.9792 | 7.018 | 15 | 95 | 95 | 0 | 0 | -19.2245 | 318.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 23 | 2543 | 7.9 | 7.9 | 6.9792 | 7.018 | 15 | 95 | 95 | 0 | 0 | -24.4312 | 333.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 16 | 24 | 2544 | 7.7 | 7.7 | 8.2792 | 7.408 | 15 | 96 | 96 | 0 | 0 | -27.4184 | 349.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 1 | 2545 | 7.7 | 7.7 | 8.2792 | 7.408 | 15 | 97 | 97 | 0 | 0 | -27.8223 | 5.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 2 | 2546 | 7.8 | 7.8 | 8.2792 | 7.408 | 15 | 96 | 96 | 0 | 0 | -25.2292 | 22.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 3 | 2547 | 7.7 | 7.7 | 8.2792 | 7.408 | 15 | 97 | 97 | 0 | 0 | -20.6503 | 37.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 4 | 2548 | 7.6 | 7.6 | 8.2792 | 7.408 | 15 | 97 | 97 | 0 | 0 | -14.2094 | 51.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 5 | 2549 | 7.5 | 7.5 | 8.2792 | 7.408 | 15 | 97 | 97 | 0 | 0 | -6.4279 | 64.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 6 | 2550 | 7.4 | 7.4 | 8.2792 | 7.408 | 15 | 97 | 97 | 0 | 0 | 2.2223 | 76.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 7 | 2551 | 7.7 | 7.7 | 8.2792 | 7.408 | 15 | 97 | 97 | 0.38345 | 5.9698 | 11.3295 | 87.786 | 0.09219 | 0.32817 | 0.37191 | 0.19779 | 0 | 0 | 0 | 0 | 0.030248 | 2.821 | 2.821 | 2.821 | 2.821 | 2.821 | 2.821 | 2.821 | 2.821 | 5.9698 | 2.9132 | 3.1491 | 3.1929 | 3.0188 | 2.821 | 2.821 | 2.821 | 2.821 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 17 | 8 | 2552 | 8.1 | 8.1 | 8.2792 | 7.408 | 15 | 97 | 97 | 1.8086 | 38.573 | 20.5072 | 99.8222 | 0.068509 | 1.3015 | 1.772 | 1.2046 | 0 | 0 | 0 | 0 | 0.427 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 38.573 | 18.8384 | 20.0713 | 20.5419 | 19.9745 | 18.7699 | 18.7699 | 18.7699 | 18.7699 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 9 | 2553 | 8.5 | 8.5 | 8.2792 | 7.408 | 15 | 97 | 97 | 2.6951 | 76.9575 | 29.3348 | 112.8901 | 0 | 1.4543 | 2.4873 | 2.0633 | 0.43062 | 0 | 0 | 0 | 1.0425 | 37.9621 | 37.9621 | 37.9621 | 37.9621 | 37.9621 | 37.9621 | 37.9621 | 37.9621 | 76.9575 | 37.9621 | 39.4164 | 40.4494 | 40.0254 | 38.3927 | 37.9621 | 37.9621 | 37.9621 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 10 | 2554 | 9.2 | 9.2 | 8.2792 | 7.408 | 15 | 96 | 96 | 4.7217 | 136.541 | 37.2792 | 127.8125 | 0 | 1.5493 | 3.7921 | 3.8136 | 1.6011 | 0 | 0 | 0 | 2.459 | 67.5495 | 69.3473 | 71.95 | 71.9749 | 69.4074 | 67.5495 | 67.5495 | 67.5495 | 136.541 | 67.5495 | 70.8966 | 75.7421 | 75.7884 | 71.0085 | 67.5495 | 67.5495 | 67.5495 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 11 | 2555 | 9 | 9 | 8.2792 | 7.408 | 15 | 94 | 94 | 3.3793 | 139.8749 | 43.6141 | 145.3859 | 0 | 0.33642 | 2.1243 | 2.6677 | 1.6485 | 0 | 0 | 0 | 2.1251 | 70.0233 | 70.0233 | 70.0233 | 70.0233 | 70.0233 | 70.0233 | 70.0233 | 70.0233 | 139.8749 | 70.0233 | 70.3597 | 72.1475 | 72.691 | 71.6717 | 70.0233 | 70.0233 | 70.0233 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 12 | 2556 | 9.2 | 9.2 | 8.2792 | 7.408 | 15 | 92 | 92 | 1.2593 | 96.1138 | 47.4319 | 165.8043 | 0 | 0 | 0.51793 | 0.89683 | 0.75038 | 0.16437 | 0 | 0 | 0.8862 | 47.0955 | 47.0955 | 47.0955 | 47.0955 | 47.0955 | 47.0955 | 47.0955 | 47.0955 | 96.1138 | 47.0955 | 47.0955 | 47.6134 | 47.9923 | 47.8459 | 47.2599 | 47.0955 | 47.0955 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 13 | 2557 | 9.8 | 9.8 | 8.2792 | 7.408 | 15 | 90 | 90 | 1.1385 | 96.1574 | 47.9489 | 187.7901 | 0 | 0 | 0.18887 | 0.66151 | 0.74664 | 0.3944 | 0 | 0 | 0.84261 | 47.1228 | 47.1228 | 47.1228 | 47.1228 | 47.1228 | 47.1228 | 47.1228 | 47.1228 | 96.1574 | 47.1228 | 47.1228 | 47.3116 | 47.7843 | 47.8694 | 47.5172 | 47.1228 | 47.1228 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 14 | 2558 | 10.6 | 10.6 | 8.2792 | 7.408 | 15 | 83 | 83 | 18.4086 | 278.4594 | 45.0404 | 208.8804 | 0 | 0 | 0 | 7.4564 | 12.2162 | 9.8199 | 1.6713 | 0 | 13.5406 | 132.8798 | 132.8798 | 132.8798 | 147.8893 | 157.4706 | 152.647 | 136.244 | 132.8798 | 278.4594 | 132.8798 | 132.8798 | 132.8798 | 155.3457 | 169.6868 | 162.4669 | 137.9153 | 132.8798 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 15 | 2559 | 9.6 | 9.6 | 8.2792 | 7.408 | 15 | 86 | 86 | 1.9692 | 117.6405 | 39.3479 | 227.3216 | 0 | 0 | 0 | 0.38633 | 1.2184 | 1.3368 | 0.67206 | 0 | 1.3595 | 58.1463 | 58.1463 | 58.1463 | 58.1463 | 58.1463 | 58.1463 | 58.1463 | 58.1463 | 117.6405 | 58.1463 | 58.1463 | 58.1463 | 58.5326 | 59.3647 | 59.483 | 58.8183 | 58.1463 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 16 | 2560 | 10 | 10 | 8.2792 | 7.408 | 15 | 89 | 89 | 3.6189 | 139.8008 | 31.7916 | 242.9521 | 0 | 0 | 0 | 0 | 1.8971 | 2.7962 | 2.0574 | 0.11337 | 2.1992 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 139.8008 | 69.8971 | 69.8971 | 69.8971 | 69.8971 | 71.7942 | 72.6934 | 71.9545 | 70.0105 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 17 | 2561 | 11.3 | 11.3 | 8.2792 | 7.408 | 15 | 84 | 84 | 184.4216 | 226.0433 | 23.1611 | 256.4759 | 0 | 0 | 0 | 0 | 71.2811 | 149.1213 | 139.6084 | 48.3147 | 90.9567 | 109.97 | 109.97 | 109.97 | 109.97 | 159.0893 | 212.7286 | 206.1732 | 143.2633 | 226.0433 | 109.97 | 109.97 | 109.97 | 109.97 | 230.3704 | 361.8499 | 345.7816 | 191.578 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 17 | 18 | 2562 | 10.5 | 10.5 | 8.2792 | 7.408 | 15 | 78 | 78 | 123.5893 | 164.162 | 14.0393 | 268.7369 | 0 | 0 | 0 | 0 | 26.5725 | 96.9091 | 110.4777 | 59.3299 | 43.838 | 80.0488 | 80.0488 | 80.0488 | 80.0488 | 102.9164 | 163.4464 | 175.1232 | 131.1067 | 164.162 | 80.0488 | 80.0488 | 80.0488 | 80.0488 | 129.4889 | 260.3555 | 285.6009 | 190.4366 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 19 | 2563 | 9.8 | 9.8 | 8.2792 | 7.408 | 15 | 83 | 83 | 37.0865 | 84.5213 | 4.871 | 280.4754 | 0 | 0 | 0 | 0 | 0.7931 | 25.9954 | 35.97 | 24.8738 | 7.4787 | 41.2471 | 41.2471 | 41.2471 | 41.2471 | 42.2089 | 72.769 | 84.864 | 71.4089 | 84.5213 | 41.2471 | 41.2471 | 41.2471 | 41.2471 | 43.002 | 98.7644 | 120.834 | 96.2827 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 20 | 2564 | 7.7 | 7.7 | 8.2792 | 7.408 | 15 | 88 | 88 | 6.912 | 13.6928 | -3.9543 | 292.3164 | 1.2522 | 0 | 0 | 0 | 0 | 3.9033 | 6.7722 | 5.6741 | 0.30724 | 7.8975 | 7.1803 | 7.1803 | 7.1803 | 7.1803 | 9.4158 | 11.059 | 10.43 | 13.6928 | 9.1496 | 7.1803 | 7.1803 | 7.1803 | 7.1803 | 13.3191 | 17.8312 | 16.1041 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 21 | 2565 | 6.8 | 6.8 | 8.2792 | 7.408 | 15 | 93 | 93 | 0 | 0 | -12.0373 | 304.7971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 22 | 2566 | 6 | 6 | 8.2792 | 7.408 | 15 | 94 | 94 | 0 | 0 | -18.9253 | 318.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 23 | 2567 | 4.2 | 4.2 | 8.2792 | 7.408 | 15 | 95 | 95 | 0 | 0 | -24.1064 | 333.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 17 | 24 | 2568 | 5.2 | 5.2 | 8.2875 | 7.6531 | 15 | 95 | 95 | 0 | 0 | -27.072 | 349.2628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 1 | 2569 | 3.2 | 3.2 | 8.2875 | 7.6531 | 15 | 96 | 96 | 0 | 0 | -27.4635 | 5.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 2 | 2570 | 2.9 | 2.9 | 8.2875 | 7.6531 | 15 | 97 | 97 | 0 | 0 | -24.8728 | 22.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 3 | 2571 | 3 | 3 | 8.2875 | 7.6531 | 15 | 97 | 97 | 0 | 0 | -20.3022 | 37.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 4 | 2572 | 3.5 | 3.5 | 8.2875 | 7.6531 | 15 | 97 | 97 | 0 | 0 | -13.8734 | 51.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 5 | 2573 | 3.4 | 3.4 | 8.2875 | 7.6531 | 15 | 96 | 96 | 0 | 0 | -6.1039 | 63.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 6 | 2574 | 4.1 | 4.1 | 8.2875 | 7.6531 | 15 | 97 | 97 | 0 | 0 | 2.5376 | 75.9093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 7 | 2575 | 5.1 | 5.1 | 8.2875 | 7.6531 | 15 | 98 | 98 | 59.5342 | 37.0158 | 11.6409 | 87.6067 | 14.4799 | 51.0291 | 57.6862 | 30.5515 | 0 | 0 | 0 | 0 | 4.9842 | 39.6539 | 96.9072 | 107.3353 | 64.8297 | 16.9717 | 16.9717 | 16.9717 | 16.9717 | 37.0158 | 54.1338 | 147.9363 | 165.0215 | 95.3812 | 16.9717 | 16.9717 | 16.9717 | 16.9717 | 42 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 18 | 8 | 2576 | 7 | 7 | 8.2875 | 7.6531 | 15 | 97 | 97 | 15.3068 | 88.3149 | 20.8204 | 99.638 | 0.62605 | 11.0344 | 14.9789 | 10.149 | 0 | 0 | 0 | 0 | 3.6851 | 42.3689 | 83.9748 | 99.7426 | 80.4357 | 39.8664 | 39.8664 | 39.8664 | 39.8664 | 88.3149 | 42.995 | 95.0092 | 114.7216 | 90.5847 | 39.8664 | 39.8664 | 39.8664 | 39.8664 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 9 | 2577 | 9.3 | 9.3 | 8.2875 | 7.6531 | 15 | 95 | 95 | 49.4144 | 169.6643 | 29.6562 | 112.7102 | 0 | 26.7306 | 45.5356 | 37.6665 | 7.7329 | 0 | 0 | 0 | 19.3357 | 78.2737 | 130.005 | 166.398 | 151.1691 | 93.239 | 78.2737 | 78.2737 | 78.2737 | 169.6643 | 78.2737 | 156.7356 | 211.9337 | 188.8356 | 100.9718 | 78.2737 | 78.2737 | 78.2737 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 10 | 2578 | 11 | 11 | 8.2875 | 7.6531 | 15 | 91 | 91 | 10.7745 | 180.3421 | 37.6142 | 127.6554 | 0 | 3.5514 | 8.6372 | 8.6635 | 3.6148 | 0 | 0 | 0 | 5.6579 | 85.3503 | 95.9459 | 111.1197 | 111.1982 | 96.1352 | 85.3503 | 85.3503 | 85.3503 | 180.3421 | 85.3503 | 99.4973 | 119.757 | 119.8617 | 99.7501 | 85.3503 | 85.3503 | 85.3503 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 11 | 2579 | 11.1 | 11.1 | 8.2875 | 7.6531 | 15 | 85 | 85 | 8.87 | 208.3845 | 43.9642 | 145.2861 | 0 | 0.89821 | 5.5627 | 6.9686 | 4.2924 | 0 | 0 | 0 | 5.6155 | 100.253 | 102.705 | 115.4384 | 119.2763 | 111.9707 | 100.253 | 100.253 | 100.253 | 208.3845 | 100.253 | 103.6032 | 121.001 | 126.245 | 116.2631 | 100.253 | 100.253 | 100.253 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 12 | 2580 | 12.1 | 12.1 | 8.2875 | 7.6531 | 15 | 82 | 82 | 8.8315 | 232.7487 | 47.7894 | 165.8078 | 0 | 0 | 3.62 | 6.2545 | 5.2252 | 1.1351 | 0 | 0 | 6.2513 | 112.7577 | 112.7577 | 121.9368 | 128.6171 | 126.0072 | 115.6359 | 112.7577 | 112.7577 | 232.7487 | 112.7577 | 112.7577 | 125.5568 | 134.8716 | 131.2324 | 116.7709 | 112.7577 | 112.7577 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 13 | 2581 | 11.7 | 11.7 | 8.2875 | 7.6531 | 15 | 77 | 77 | 3.667 | 172.271 | 48.2956 | 187.9204 | 0 | 0 | 0.60404 | 2.116 | 2.3885 | 1.2618 | 0 | 0 | 2.729 | 86.8968 | 86.8968 | 86.8968 | 86.8968 | 86.8968 | 86.8968 | 86.8968 | 86.8968 | 172.271 | 86.8968 | 86.8968 | 87.5009 | 89.0129 | 89.2853 | 88.1586 | 86.8968 | 86.8968 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 14 | 2582 | 11.9 | 11.9 | 8.2875 | 7.6531 | 15 | 78 | 78 | 6.7464 | 226.01 | 45.3595 | 209.1092 | 0 | 0 | 0 | 2.7061 | 4.4455 | 3.5808 | 0.61847 | 0 | 4.99 | 111.6156 | 111.6156 | 111.6156 | 116.6324 | 119.8569 | 118.2539 | 112.7622 | 111.6156 | 226.01 | 111.6156 | 111.6156 | 111.6156 | 119.3384 | 124.3024 | 121.8346 | 113.3806 | 111.6156 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 15 | 2583 | 12.8 | 12.8 | 8.2875 | 7.6531 | 15 | 73 | 73 | 60.8524 | 307.7361 | 39.635 | 227.5977 | 0 | 0 | 0 | 11.7074 | 37.3577 | 41.1243 | 20.8009 | 0 | 42.2639 | 138.1641 | 138.1641 | 138.1641 | 159.8862 | 207.478 | 214.4666 | 176.7583 | 138.1641 | 307.7361 | 138.1641 | 138.1641 | 138.1641 | 171.5936 | 244.8357 | 255.591 | 197.5592 | 138.1641 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 16 | 2584 | 12.6 | 12.6 | 8.2875 | 7.6531 | 15 | 72 | 72 | 34.4479 | 253.9199 | 32.0529 | 243.2395 | 0 | 0 | 0 | 0 | 17.8895 | 26.5019 | 19.5899 | 1.2024 | 21.0801 | 115.4906 | 115.4906 | 115.4906 | 115.4906 | 163.0065 | 185.8819 | 167.523 | 118.6843 | 253.9199 | 115.4906 | 115.4906 | 115.4906 | 115.4906 | 180.896 | 212.3838 | 187.1129 | 119.8867 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 17 | 2585 | 12.4 | 12.4 | 8.2875 | 7.6531 | 15 | 65 | 65 | 357.7091 | 200.0153 | 23.4067 | 256.7587 | 0 | 0 | 0 | 0 | 136.51 | 287.9466 | 270.708 | 94.8923 | 177.9847 | 108.0379 | 108.0379 | 108.0379 | 108.0379 | 162.8528 | 223.6615 | 216.7394 | 146.1414 | 200.0153 | 108.0379 | 108.0379 | 108.0379 | 108.0379 | 299.3629 | 511.6081 | 487.4474 | 241.0337 | 378 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 18 | 18 | 2586 | 11.9 | 11.9 | 8.2875 | 7.6531 | 15 | 66 | 66 | 156.1325 | 165.9124 | 14.2793 | 269.0101 | 0 | 0 | 0 | 0 | 32.8196 | 121.8305 | 139.4748 | 75.4166 | 56.0876 | 82.0056 | 82.0056 | 82.0056 | 82.0056 | 104.4839 | 165.4481 | 177.5328 | 133.6589 | 165.9124 | 82.0056 | 82.0056 | 82.0056 | 82.0056 | 137.3035 | 287.2786 | 317.0076 | 209.0755 | 222 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 19 | 2587 | 10.4 | 10.4 | 8.2875 | 7.6531 | 15 | 66 | 66 | 625.5139 | 56.9248 | 5.1146 | 280.7381 | 0 | 0 | 0 | 0 | 10.4721 | 435.981 | 606.0982 | 421.1712 | 129.0752 | 42.4829 | 42.4829 | 42.4829 | 42.4829 | 43.8335 | 98.7113 | 120.6513 | 96.8013 | 56.9248 | 42.4829 | 42.4829 | 42.4829 | 42.4829 | 54.3056 | 534.6923 | 726.7494 | 517.9725 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 20 | 2588 | 8.1 | 8.1 | 8.2875 | 7.6531 | 15 | 78 | 78 | 33.1656 | 20.3641 | -3.6991 | 292.5673 | 6.1548 | 0 | 0 | 0 | 0 | 18.5971 | 32.4551 | 27.3014 | 1.6359 | 16.214 | 10.8651 | 10.8651 | 10.8651 | 10.8651 | 27.027 | 39.0704 | 34.5915 | 20.3641 | 22.3688 | 10.8651 | 10.8651 | 10.8651 | 10.8651 | 45.6242 | 71.5256 | 61.8929 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 21 | 2589 | 5.6 | 5.6 | 8.2875 | 7.6531 | 15 | 86 | 86 | 0 | 0 | -11.7634 | 305.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 22 | 2590 | 4.1 | 4.1 | 8.2875 | 7.6531 | 15 | 91 | 91 | 0 | 0 | -18.6278 | 318.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 23 | 2591 | 3.5 | 3.5 | 8.2875 | 7.6531 | 15 | 94 | 94 | 0 | 0 | -23.7837 | 333.3886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 18 | 24 | 2592 | 2.5 | 2.5 | 7.6333 | 7.6343 | 15 | 94 | 94 | 0 | 0 | -26.728 | 349.3721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 1 | 2593 | 2.8 | 2.8 | 7.6333 | 7.6343 | 15 | 95 | 95 | 0 | 0 | -27.1076 | 5.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 2 | 2594 | 1.5 | 1.5 | 7.6333 | 7.6343 | 15 | 96 | 96 | 0 | 0 | -24.5197 | 22.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 3 | 2595 | 1.9 | 1.9 | 7.6333 | 7.6343 | 15 | 96 | 96 | 0 | 0 | -19.9574 | 37.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 4 | 2596 | 0.9 | 0.9 | 7.6333 | 7.6343 | 15 | 96 | 96 | 0 | 0 | -13.5409 | 51.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 5 | 2597 | 0.6 | 0.6 | 7.6333 | 7.6343 | 15 | 96 | 96 | 0 | 0 | -5.7833 | 63.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 6 | 2598 | 0.7 | 0.7 | 7.6333 | 7.6343 | 15 | 97 | 97 | 0 | 0 | 2.8493 | 75.7408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 7 | 2599 | 3.4 | 3.4 | 7.6333 | 7.6343 | 15 | 97 | 97 | 136.1948 | 40.9451 | 11.9486 | 87.4274 | 33.5046 | 116.9132 | 131.8356 | 69.5305 | 0 | 0 | 0 | 0 | 12.0549 | 33.1555 | 64.1897 | 69.7419 | 46.5598 | 20.6893 | 20.6893 | 20.6893 | 20.6893 | 40.9451 | 66.6601 | 181.1028 | 201.5775 | 116.0903 | 20.6893 | 20.6893 | 20.6893 | 20.6893 | 53 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 19 | 8 | 2600 | 7.9 | 7.9 | 7.6333 | 7.6343 | 15 | 97 | 97 | 398.4392 | 94.2386 | 21.13 | 99.4534 | 17.4969 | 287.7292 | 389.4136 | 262.9849 | 0 | 0 | 0 | 0 | 97.7614 | 59.7498 | 124.7976 | 149.2742 | 118.8414 | 55.5381 | 55.5381 | 55.5381 | 55.5381 | 94.2386 | 77.2467 | 412.5268 | 538.6878 | 381.8263 | 55.5381 | 55.5381 | 55.5381 | 55.5381 | 192 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 9 | 2601 | 10.5 | 10.5 | 7.6333 | 7.6343 | 15 | 93 | 93 | 592.9678 | 115.3426 | 29.9738 | 112.5293 | 0 | 321.5527 | 545.5883 | 450.0257 | 90.8441 | 0 | 0 | 0 | 234.6574 | 78.0704 | 134.5953 | 173.9779 | 157.1792 | 94.0397 | 78.0704 | 78.0704 | 78.0704 | 115.3426 | 78.0704 | 456.1481 | 719.5663 | 607.2049 | 184.8838 | 78.0704 | 78.0704 | 78.0704 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 10 | 2602 | 11.2 | 11.2 | 7.6333 | 7.6343 | 15 | 75 | 75 | 606.9639 | 150.6723 | 37.9456 | 127.4966 | 0 | 200.961 | 485.6589 | 485.8644 | 201.4571 | 0 | 0 | 0 | 321.3277 | 100.7727 | 139.9681 | 195.4956 | 195.5357 | 140.0649 | 100.7727 | 100.7727 | 100.7727 | 150.6723 | 100.7727 | 340.9291 | 681.1546 | 681.4001 | 341.522 | 100.7727 | 100.7727 | 100.7727 | 472 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 11 | 2603 | 12.6 | 12.6 | 7.6333 | 7.6343 | 15 | 61 | 61 | 433.8103 | 234.5521 | 44.3109 | 145.184 | 0 | 44.6731 | 271.4191 | 339.1715 | 208.2418 | 0 | 0 | 0 | 276.4479 | 128.2324 | 145.4858 | 233.0581 | 259.225 | 208.6582 | 128.2324 | 128.2324 | 128.2324 | 234.5521 | 128.2324 | 190.1589 | 504.4772 | 598.3965 | 416.8999 | 128.2324 | 128.2324 | 128.2324 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 12 | 2604 | 11.7 | 11.7 | 7.6333 | 7.6343 | 15 | 63 | 63 | 6.0944 | 209.6613 | 48.1436 | 165.8091 | 0 | 0 | 2.4898 | 4.2922 | 3.5802 | 0.77105 | 0 | 0 | 4.3387 | 103.4177 | 103.4177 | 108.1903 | 111.6452 | 110.2805 | 104.8957 | 103.4177 | 103.4177 | 209.6613 | 103.4177 | 103.4177 | 110.6801 | 115.9374 | 113.8608 | 105.6668 | 103.4177 | 103.4177 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 13 | 2605 | 12.3 | 12.3 | 7.6333 | 7.6343 | 15 | 54 | 54 | 10.1046 | 253.4394 | 48.6395 | 188.0492 | 0 | 0 | 1.6529 | 5.7909 | 6.5367 | 3.4533 | 0 | 0 | 7.5606 | 122.7979 | 122.7979 | 126.7734 | 136.7258 | 138.5194 | 131.1036 | 122.7979 | 122.7979 | 253.4394 | 122.7979 | 122.7979 | 128.4263 | 142.5167 | 145.0561 | 134.5569 | 122.7979 | 122.7979 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 14 | 2606 | 12 | 12 | 7.6333 | 7.6343 | 15 | 64 | 64 | 491.3541 | 253.579 | 45.6759 | 209.3367 | 0 | 0 | 0 | 195.1773 | 321.4856 | 259.472 | 45.4633 | 0 | 365.421 | 140.0925 | 140.0925 | 140.0925 | 212.7582 | 259.7837 | 236.6956 | 157.0187 | 140.0925 | 253.579 | 140.0925 | 140.0925 | 140.0925 | 407.9355 | 581.2692 | 496.1676 | 202.482 | 140.0925 | 619 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 15 | 2607 | 10.8 | 10.8 | 7.6333 | 7.6343 | 15 | 71 | 71 | 13.0387 | 248.8909 | 39.9197 | 227.8721 | 0 | 0 | 0 | 2.4596 | 7.942 | 8.772 | 4.4635 | 0 | 9.1091 | 120.0865 | 120.0865 | 120.0865 | 125.1553 | 136.4532 | 138.1637 | 129.2848 | 120.0865 | 248.8909 | 120.0865 | 120.0865 | 120.0865 | 127.6149 | 144.3952 | 146.9357 | 133.7484 | 120.0865 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 16 | 2608 | 12 | 12 | 7.6333 | 7.6343 | 15 | 68 | 68 | 160.4514 | 284.142 | 32.3122 | 243.5248 | 0 | 0 | 0 | 0 | 82.5453 | 122.9027 | 91.2654 | 6.166 | 98.858 | 132.6147 | 132.6147 | 132.6147 | 132.6147 | 209.1093 | 246.5085 | 217.1902 | 138.3288 | 284.142 | 132.6147 | 132.6147 | 132.6147 | 132.6147 | 291.6547 | 369.4113 | 308.4557 | 144.4948 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 17 | 2609 | 12.9 | 12.9 | 7.6333 | 7.6343 | 15 | 57 | 57 | 915.0552 | 90.75 | 23.6506 | 257.0389 | 0 | 0 | 0 | 0 | 344.771 | 733.2868 | 692.2532 | 245.707 | 459.25 | 92.1816 | 92.1816 | 92.1816 | 92.1816 | 117.5317 | 146.0983 | 143.0812 | 110.2478 | 90.75 | 92.1816 | 92.1816 | 92.1816 | 92.1816 | 462.3027 | 879.3851 | 835.3344 | 355.9549 | 550 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 19 | 18 | 2610 | 12.2 | 12.2 | 7.6333 | 7.6343 | 15 | 56 | 56 | 508.7512 | 120.9653 | 14.5179 | 269.2805 | 0 | 0 | 0 | 0 | 104.5232 | 395.0399 | 454.1475 | 247.2217 | 185.0347 | 76.7379 | 76.7379 | 76.7379 | 76.7379 | 99.9813 | 164.585 | 177.7291 | 131.7139 | 120.9653 | 76.7379 | 76.7379 | 76.7379 | 76.7379 | 204.5045 | 559.6249 | 631.8767 | 378.9356 | 306 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 19 | 2611 | 11.7 | 11.7 | 7.6333 | 7.6343 | 15 | 60 | 60 | 540.8032 | 66.8906 | 5.3569 | 280.9977 | 0 | 0 | 0 | 0 | 6.5738 | 374.8144 | 523.4938 | 365.5176 | 114.1094 | 45.3753 | 45.3753 | 45.3753 | 45.3753 | 46.4292 | 105.464 | 129.2997 | 103.9736 | 66.8906 | 45.3753 | 45.3753 | 45.3753 | 45.3753 | 53.0031 | 480.2784 | 652.7934 | 469.4912 | 181 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 20 | 2612 | 8.5 | 8.5 | 7.6333 | 7.6343 | 15 | 74 | 74 | 10.3564 | 18.4391 | -3.4451 | 292.8147 | 1.9671 | 0 | 0 | 0 | 0 | 5.7663 | 10.1218 | 8.5481 | 0.56086 | 11.0751 | 9.559 | 9.559 | 9.559 | 9.559 | 14.0035 | 17.3606 | 16.1477 | 18.4391 | 13.0422 | 9.559 | 9.559 | 9.559 | 9.559 | 19.7698 | 27.4824 | 24.6958 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 21 | 2613 | 8.4 | 8.4 | 7.6333 | 7.6343 | 15 | 77 | 77 | 0 | 0 | -11.4909 | 305.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 22 | 2614 | 6.3 | 6.3 | 7.6333 | 7.6343 | 15 | 84 | 84 | 0 | 0 | -18.3318 | 318.7678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 23 | 2615 | 3.9 | 3.9 | 7.6333 | 7.6343 | 15 | 91 | 91 | 0 | 0 | -23.4631 | 333.5531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 19 | 24 | 2616 | 2.9 | 2.9 | 7.4833 | 7.6124 | 15 | 92 | 92 | 0 | 0 | -26.3867 | 349.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 1 | 2617 | 2.6 | 2.6 | 7.4833 | 7.6124 | 15 | 94 | 94 | 0 | 0 | -26.7548 | 5.9477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 2 | 2618 | 1 | 1 | 7.4833 | 7.6124 | 15 | 94 | 94 | 0 | 0 | -24.17 | 22.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 3 | 2619 | 1.2 | 1.2 | 7.4833 | 7.6124 | 15 | 95 | 95 | 0 | 0 | -19.6161 | 37.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 4 | 2620 | 2.3 | 2.3 | 7.4833 | 7.6124 | 15 | 96 | 96 | 0 | 0 | -13.2119 | 50.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 5 | 2621 | 3.5 | 3.5 | 7.4833 | 7.6124 | 15 | 97 | 97 | 0 | 0 | -5.4663 | 63.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 6 | 2622 | 4.4 | 4.4 | 7.4833 | 7.6124 | 15 | 97 | 97 | 0 | 0 | 3.1575 | 75.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 7 | 2623 | 6.2 | 6.2 | 7.4833 | 7.6124 | 15 | 97 | 97 | 10.7668 | 31.9959 | 12.2526 | 87.2479 | 2.6785 | 9.256 | 10.4114 | 5.468 | 0 | 0 | 0 | 0 | 1.0041 | 28.6143 | 62.1877 | 68.0854 | 42.8524 | 14.9422 | 14.9422 | 14.9422 | 14.9422 | 31.9959 | 31.2928 | 71.4437 | 78.4968 | 48.3204 | 14.9422 | 14.9422 | 14.9422 | 14.9422 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 20 | 8 | 2624 | 8.9 | 8.9 | 7.4833 | 7.6124 | 15 | 95 | 95 | 281.2423 | 107.7111 | 21.4357 | 99.2683 | 13.196 | 203.4453 | 274.519 | 184.7833 | 0 | 0 | 0 | 0 | 70.2889 | 63.8366 | 138.1888 | 165.9654 | 130.8954 | 58.6794 | 58.6794 | 58.6794 | 58.6794 | 107.7111 | 77.0326 | 341.634 | 440.4845 | 315.6787 | 58.6794 | 58.6794 | 58.6794 | 58.6794 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 9 | 2625 | 10.7 | 10.7 | 7.4833 | 7.6124 | 15 | 86 | 86 | 613.778 | 112.4165 | 30.2876 | 112.3473 | 0 | 333.6463 | 563.8633 | 463.7768 | 92.0161 | 0 | 0 | 0 | 245.5835 | 78.1101 | 134.3653 | 173.1816 | 156.3063 | 93.6247 | 78.1101 | 78.1101 | 78.1101 | 112.4165 | 78.1101 | 468.0117 | 737.0449 | 620.0831 | 185.6408 | 78.1101 | 78.1101 | 78.1101 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 10 | 2626 | 11.8 | 11.8 | 7.4833 | 7.6124 | 15 | 71 | 71 | 634.0489 | 144.6534 | 38.2731 | 127.3361 | 0 | 210.8679 | 506.3845 | 505.2679 | 208.1723 | 0 | 0 | 0 | 338.3466 | 100.2684 | 138.9042 | 193.0495 | 192.8449 | 138.4103 | 100.2684 | 100.2684 | 100.2684 | 144.6534 | 100.2684 | 349.7721 | 699.434 | 698.1129 | 346.5826 | 100.2684 | 100.2684 | 100.2684 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 11 | 2627 | 10.7 | 10.7 | 7.4833 | 7.6124 | 15 | 75 | 75 | 31.5517 | 262.7641 | 44.6539 | 145.0797 | 0 | 3.3034 | 19.6946 | 24.549 | 15.0229 | 0 | 0 | 0 | 20.2359 | 118.4487 | 128.9188 | 180.8702 | 196.256 | 166.0633 | 118.4487 | 118.4487 | 118.4487 | 262.7641 | 118.4487 | 132.2222 | 200.5648 | 220.805 | 181.0862 | 118.4487 | 118.4487 | 118.4487 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 12 | 2628 | 11.1 | 11.1 | 7.4833 | 7.6124 | 15 | 75 | 75 | 16.617 | 266.1034 | 48.4947 | 165.8081 | 0 | 0 | 6.7666 | 11.6383 | 9.6924 | 2.0688 | 0 | 0 | 11.8966 | 126.3374 | 126.3374 | 142.0346 | 153.3358 | 148.8218 | 131.1367 | 126.3374 | 126.3374 | 266.1034 | 126.3374 | 126.3374 | 148.8012 | 164.9741 | 158.5142 | 133.2055 | 126.3374 | 126.3374 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 13 | 2629 | 11 | 11 | 7.4833 | 7.6124 | 15 | 75 | 75 | 4.6932 | 196.4697 | 48.9804 | 188.1763 | 0 | 0 | 0.76252 | 2.6713 | 3.0152 | 1.5929 | 0 | 0 | 3.5303 | 99.0569 | 99.0569 | 99.4547 | 100.4505 | 100.63 | 99.888 | 99.0569 | 99.0569 | 196.4697 | 99.0569 | 99.0569 | 100.2173 | 103.1218 | 103.6452 | 101.4809 | 99.0569 | 99.0569 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 14 | 2630 | 11.2 | 11.2 | 7.4833 | 7.6124 | 15 | 72 | 72 | 5.1379 | 204.1585 | 45.9896 | 209.5627 | 0 | 0 | 0 | 2.0211 | 3.3378 | 2.6993 | 0.47958 | 0 | 3.8415 | 102.5289 | 102.5289 | 102.5289 | 104.2297 | 105.3378 | 104.8005 | 102.9324 | 102.5289 | 204.1585 | 102.5289 | 102.5289 | 102.5289 | 106.2508 | 108.6756 | 107.4998 | 103.412 | 102.5289 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 15 | 2631 | 11.8 | 11.8 | 7.4833 | 7.6124 | 15 | 70 | 70 | 9.5971 | 235.2566 | 40.202 | 228.1447 | 0 | 0 | 0 | 1.7749 | 5.7999 | 6.4274 | 3.2898 | 0 | 6.7434 | 114.6358 | 114.6358 | 114.6358 | 118.3138 | 126.6545 | 127.9549 | 121.453 | 114.6358 | 235.2566 | 114.6358 | 114.6358 | 114.6358 | 120.0887 | 132.4544 | 134.3822 | 124.7428 | 114.6358 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 16 | 2632 | 12.2 | 12.2 | 7.4833 | 7.6124 | 15 | 62 | 62 | 62.4845 | 275.2441 | 32.5695 | 243.8077 | 0 | 0 | 0 | 0 | 31.8439 | 47.6521 | 35.5463 | 2.618 | 38.7559 | 125.2387 | 125.2387 | 125.2387 | 125.2387 | 177.9715 | 204.1495 | 184.1026 | 129.574 | 275.2441 | 125.2387 | 125.2387 | 125.2387 | 125.2387 | 209.8155 | 251.8017 | 219.649 | 132.192 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 17 | 2633 | 12.8 | 12.8 | 7.4833 | 7.6124 | 15 | 58 | 58 | 292.0147 | 216.1995 | 23.8929 | 257.3165 | 0 | 0 | 0 | 0 | 108.6215 | 232.9524 | 220.8229 | 79.3384 | 147.8005 | 111.1995 | 111.1995 | 111.1995 | 111.1995 | 167.584 | 232.1232 | 225.8268 | 152.3834 | 216.1995 | 111.1995 | 111.1995 | 111.1995 | 111.1995 | 276.2056 | 465.0756 | 446.6498 | 231.7218 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 20 | 18 | 2634 | 11.9 | 11.9 | 7.4833 | 7.6124 | 15 | 60 | 60 | 244.2879 | 163.0717 | 14.7551 | 269.548 | 0 | 0 | 0 | 0 | 49.0408 | 188.7578 | 217.9031 | 119.4037 | 89.9283 | 85.1323 | 85.1323 | 85.1323 | 85.1323 | 111.0425 | 184.8606 | 200.2593 | 148.2181 | 163.0717 | 85.1323 | 85.1323 | 85.1323 | 85.1323 | 160.0833 | 373.6185 | 418.1624 | 267.6217 | 253 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 19 | 2635 | 11.1 | 11.1 | 7.4833 | 7.6124 | 15 | 66 | 66 | 77.0145 | 97.3956 | 5.5979 | 281.254 | 0 | 0 | 0 | 0 | 0.58758 | 53.0755 | 74.4725 | 52.2445 | 16.6044 | 48.394 | 48.394 | 48.394 | 48.394 | 49.0031 | 103.4143 | 125.5953 | 102.5529 | 97.3956 | 48.394 | 48.394 | 48.394 | 48.394 | 49.5907 | 156.4898 | 200.0678 | 154.7974 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 20 | 2636 | 9.4 | 9.4 | 7.4833 | 7.6124 | 15 | 73 | 73 | 13.732 | 21.1906 | -3.1923 | 293.0587 | 2.6671 | 0 | 0 | 0 | 0 | 7.5919 | 13.4037 | 11.3638 | 0.80942 | 12.9775 | 10.9239 | 10.9239 | 10.9239 | 10.9239 | 16.7693 | 21.2442 | 19.6736 | 21.1906 | 15.6446 | 10.9239 | 10.9239 | 10.9239 | 10.9239 | 24.3612 | 34.6479 | 31.0374 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 21 | 2637 | 6.4 | 6.4 | 7.4833 | 7.6124 | 15 | 84 | 84 | 0 | 0 | -11.2197 | 305.4904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 22 | 2638 | 4.7 | 4.7 | 7.4833 | 7.6124 | 15 | 91 | 91 | 0 | 0 | -18.0376 | 318.9693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 23 | 2639 | 3.8 | 3.8 | 7.4833 | 7.6124 | 15 | 93 | 93 | 0 | 0 | -23.1446 | 333.7138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 20 | 24 | 2640 | 2.9 | 2.9 | 7.65 | 7.6454 | 15 | 94 | 94 | 0 | 0 | -26.0481 | 349.5813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 1 | 2641 | 2.3 | 2.3 | 7.65 | 7.6454 | 15 | 95 | 95 | 0 | 0 | -26.4052 | 5.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 2 | 2642 | 1.8 | 1.8 | 7.65 | 7.6454 | 15 | 96 | 96 | 0 | 0 | -23.8237 | 22.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 3 | 2643 | 1.3 | 1.3 | 7.65 | 7.6454 | 15 | 96 | 96 | 0 | 0 | -19.2784 | 37.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 4 | 2644 | 0.7 | 0.7 | 7.65 | 7.6454 | 15 | 96 | 96 | 0 | 0 | -12.8866 | 50.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 5 | 2645 | 0.9 | 0.9 | 7.65 | 7.6454 | 15 | 96 | 96 | 0 | 0 | -5.1529 | 63.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 6 | 2646 | 1 | 1 | 7.65 | 7.6454 | 15 | 97 | 97 | 0 | 3 | 3.4619 | 75.4042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 7 | 2647 | 3.2 | 3.2 | 7.65 | 7.6454 | 15 | 98 | 98 | 369.5188 | 38.8011 | 12.5528 | 87.0685 | 92.948 | 318.1196 | 356.9411 | 186.6714 | 0 | 0 | 0 | 0 | 36.1989 | 26.3698 | 39.4358 | 41.6885 | 31.8082 | 20.9763 | 20.9763 | 20.9763 | 20.9763 | 38.8011 | 119.3177 | 357.5554 | 398.6296 | 218.4796 | 20.9763 | 20.9763 | 20.9763 | 20.9763 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 21 | 8 | 2648 | 6.2 | 6.2 | 7.65 | 7.6454 | 15 | 97 | 97 | 213.0111 | 114.8026 | 21.7375 | 99.0828 | 10.6335 | 154.3478 | 207.6472 | 139.3097 | 0 | 0 | 0 | 0 | 54.1974 | 65.6155 | 141.3872 | 169.4888 | 133.4586 | 60.0091 | 60.0091 | 60.0091 | 60.0091 | 114.8026 | 76.249 | 295.735 | 377.136 | 272.7683 | 60.0091 | 60.0091 | 60.0091 | 60.0091 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 9 | 2649 | 8.9 | 8.9 | 7.65 | 7.6454 | 15 | 94 | 94 | 179.8849 | 185.2459 | 30.5974 | 112.1644 | 0 | 98.0195 | 164.9982 | 135.3232 | 26.3777 | 0 | 0 | 0 | 72.7541 | 90.0954 | 163.1891 | 213.1354 | 191.0066 | 109.7654 | 90.0954 | 90.0954 | 90.0954 | 185.2459 | 90.0954 | 261.2086 | 378.1337 | 326.3299 | 136.1431 | 90.0954 | 90.0954 | 90.0954 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 10 | 2650 | 12.2 | 12.2 | 7.65 | 7.6454 | 15 | 81 | 81 | 692.5409 | 130.5526 | 38.5966 | 127.1738 | 0 | 231.3452 | 552.0653 | 549.393 | 224.8937 | 0 | 0 | 0 | 372.4474 | 98.3199 | 135.0627 | 186.0003 | 185.5759 | 134.0381 | 98.3199 | 98.3199 | 98.3199 | 130.5526 | 98.3199 | 366.4079 | 738.0656 | 734.9689 | 358.9318 | 98.3199 | 98.3199 | 98.3199 | 503 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 11 | 2651 | 13.4 | 13.4 | 7.65 | 7.6454 | 15 | 66 | 66 | 847.7172 | 116.8853 | 44.9932 | 144.973 | 0 | 90.2171 | 527.9157 | 656.3685 | 400.3295 | 0 | 0 | 0 | 547.1147 | 111.0363 | 119.2146 | 158.8927 | 170.5371 | 147.3268 | 111.0363 | 111.0363 | 111.0363 | 116.8853 | 111.0363 | 209.4317 | 686.8084 | 826.9056 | 547.6563 | 111.0363 | 111.0363 | 111.0363 | 664 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 12 | 2652 | 14.3 | 14.3 | 7.65 | 7.6454 | 15 | 60 | 60 | 457.6892 | 256.5171 | 48.8423 | 165.8048 | 0 | 0 | 185.7766 | 318.7828 | 265.0503 | 56.055 | 0 | 0 | 329.4829 | 139.0007 | 139.0007 | 212.7955 | 265.6287 | 244.2849 | 161.2671 | 139.0007 | 139.0007 | 256.5171 | 139.0007 | 139.0007 | 398.5722 | 584.4114 | 509.3352 | 217.322 | 139.0007 | 139.0007 | 586 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 13 | 2653 | 14.9 | 14.9 | 7.65 | 7.6454 | 15 | 56 | 56 | 853.0823 | 135.9653 | 49.3182 | 188.3016 | 0 | 0 | 137.68 | 482.2323 | 544.2994 | 287.5234 | 0 | 0 | 645.0347 | 125.967 | 125.967 | 139.2817 | 172.6026 | 178.605 | 153.7727 | 125.967 | 125.967 | 135.9653 | 125.967 | 125.967 | 276.9617 | 654.8349 | 722.9044 | 441.2961 | 125.967 | 125.967 | 781 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 14 | 2654 | 16 | 16 | 7.65 | 7.6454 | 15 | 56 | 56 | 824.7709 | 141.1054 | 46.3005 | 209.7871 | 0 | 0 | 0 | 321.2913 | 531.9998 | 431.07 | 77.6253 | 0 | 619.8946 | 125.226 | 125.226 | 125.226 | 158.2139 | 179.8479 | 169.4852 | 133.196 | 125.226 | 141.1054 | 125.226 | 125.226 | 125.226 | 479.5052 | 711.8477 | 600.5552 | 210.8213 | 125.226 | 761 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 15 | 2655 | 16.5 | 16.5 | 7.65 | 7.6454 | 15 | 51 | 51 | 827.9647 | 131.9435 | 40.4819 | 228.4152 | 0 | 0 | 0 | 150.1021 | 496.4439 | 551.9756 | 284.1675 | 0 | 585.0565 | 119.1138 | 119.1138 | 119.1138 | 133.84 | 167.819 | 173.2671 | 146.9929 | 119.1138 | 131.9435 | 119.1138 | 119.1138 | 119.1138 | 283.9421 | 664.2628 | 725.2426 | 431.1604 | 119.1138 | 717 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 16 | 2656 | 16.7 | 16.7 | 7.65 | 7.6454 | 15 | 52 | 52 | 762.5099 | 131.9538 | 32.8247 | 244.0881 | 0 | 0 | 0 | 0 | 384.9447 | 578.9436 | 433.8052 | 34.5496 | 476.0462 | 108.0728 | 108.0728 | 108.0728 | 108.0728 | 162.2231 | 189.513 | 169.0964 | 112.9329 | 131.9538 | 108.0728 | 108.0728 | 108.0728 | 108.0728 | 547.1678 | 768.4566 | 602.9015 | 147.4824 | 608 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 17 | 2657 | 16.5 | 16.5 | 7.65 | 7.6454 | 15 | 49 | 49 | 612.0114 | 143.6647 | 24.1335 | 257.5912 | 0 | 0 | 0 | 0 | 224.74 | 486.0158 | 462.5901 | 168.1854 | 312.3353 | 97.2142 | 97.2142 | 97.2142 | 97.2142 | 139.6641 | 189.0151 | 184.5903 | 128.9818 | 143.6647 | 97.2142 | 97.2142 | 97.2142 | 97.2142 | 364.4042 | 675.0309 | 647.1804 | 297.1672 | 456 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 18 | 2658 | 16.4 | 16.4 | 7.65 | 7.6454 | 15 | 52 | 52 | 77.2525 | 168.224 | 14.9909 | 269.8123 | 0 | 0 | 0 | 0 | 15.1495 | 59.399 | 68.8534 | 37.9744 | 28.776 | 79.9742 | 79.9742 | 79.9742 | 79.9742 | 94.9932 | 138.8614 | 148.2343 | 117.6214 | 168.224 | 79.9742 | 79.9742 | 79.9742 | 79.9742 | 110.1427 | 198.2604 | 217.0876 | 155.5957 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 19 | 2659 | 15.2 | 15.2 | 7.65 | 7.6454 | 15 | 56 | 56 | 311.7953 | 92.3572 | 5.8376 | 281.507 | 0 | 0 | 0 | 0 | 0.98673 | 213.6659 | 301.1824 | 212.2704 | 68.6428 | 52.5491 | 52.5491 | 52.5491 | 52.5491 | 52.8686 | 121.7259 | 150.0603 | 121.2741 | 92.3572 | 52.5491 | 52.5491 | 52.5491 | 52.5491 | 53.8553 | 335.3917 | 451.2428 | 333.5445 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 20 | 2660 | 10.9 | 10.9 | 7.65 | 7.6454 | 15 | 67 | 67 | 5.995 | 18.6182 | -2.9409 | 293.2991 | 1.1897 | 0 | 0 | 0 | 0 | 3.2911 | 5.8441 | 4.9736 | 0.3818 | 11.0266 | 9.6629 | 9.6629 | 9.6629 | 9.6629 | 13.4351 | 16.3612 | 15.3635 | 18.6182 | 12.2163 | 9.6629 | 9.6629 | 9.6629 | 9.6629 | 16.7262 | 22.2052 | 20.3372 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 21 | 2661 | 9.9 | 9.9 | 7.65 | 7.6454 | 15 | 83 | 83 | 0 | 0 | -10.95 | 305.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 22 | 2662 | 7.8 | 7.8 | 7.65 | 7.6454 | 15 | 87 | 87 | 0 | 0 | -17.7452 | 319.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 23 | 2663 | 7.4 | 7.4 | 7.65 | 7.6454 | 15 | 90 | 90 | 0 | 0 | -22.8284 | 333.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 21 | 24 | 2664 | 5.4 | 5.4 | 9.1583 | 8.0999 | 15 | 92 | 92 | 0 | 0 | -25.7122 | 349.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 1 | 2665 | 4.6 | 4.6 | 9.1583 | 8.0999 | 15 | 94 | 94 | 0 | 0 | -26.0587 | 6.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 2 | 2666 | 4.8 | 4.8 | 9.1583 | 8.0999 | 15 | 95 | 95 | 0 | 0 | -23.4811 | 22.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 3 | 2667 | 5.5 | 5.5 | 9.1583 | 8.0999 | 15 | 96 | 96 | 0 | 0 | -18.9444 | 36.9766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 4 | 2668 | 6.8 | 6.8 | 9.1583 | 8.0999 | 15 | 97 | 97 | 0 | 0 | -12.565 | 50.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 5 | 2669 | 7.2 | 7.2 | 9.1583 | 8.0999 | 15 | 96 | 96 | 0 | 0 | -4.8434 | 63.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 6 | 2670 | 7.6 | 7.6 | 9.1583 | 8.0999 | 15 | 95 | 95 | 0 | 0 | 3.7624 | 75.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 7 | 2671 | 9.7 | 9.7 | 9.1583 | 8.0999 | 15 | 92 | 92 | 7.435 | 32.237 | 12.8491 | 86.889 | 1.8906 | 6.4097 | 7.174 | 3.736 | 0 | 0 | 0 | 0 | 0.76296 | 27.5315 | 58.8687 | 64.1692 | 40.3279 | 14.4212 | 14.4212 | 14.4212 | 14.4212 | 32.237 | 29.4221 | 65.2784 | 71.3432 | 44.0639 | 14.4212 | 14.4212 | 14.4212 | 14.4212 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 22 | 8 | 2672 | 12.3 | 12.3 | 9.1583 | 8.0999 | 15 | 79 | 79 | 402.9364 | 98.6817 | 22.0353 | 98.8969 | 21.3201 | 292.4506 | 392.2675 | 262.2994 | 0 | 0 | 0 | 0 | 104.3183 | 63.5111 | 129.9307 | 154.3831 | 122.5445 | 58.2883 | 58.2883 | 58.2883 | 58.2883 | 98.6817 | 84.8312 | 422.3813 | 546.6506 | 384.8439 | 58.2883 | 58.2883 | 58.2883 | 58.2883 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 9 | 2673 | 14.1 | 14.1 | 9.1583 | 8.0999 | 15 | 72 | 72 | 304.7743 | 172.4315 | 30.9031 | 111.9805 | 0 | 166.4669 | 279.1123 | 228.2574 | 43.6925 | 0 | 0 | 0 | 124.5685 | 92.2012 | 165.6037 | 215.2739 | 192.8498 | 111.4671 | 92.2012 | 92.2012 | 92.2012 | 172.4315 | 92.2012 | 332.0706 | 494.3861 | 421.1072 | 155.1596 | 92.2012 | 92.2012 | 92.2012 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 10 | 2674 | 15.4 | 15.4 | 9.1583 | 8.0999 | 15 | 63 | 63 | 80.5327 | 245.3585 | 38.9161 | 127.0098 | 0 | 27.0211 | 64.0772 | 63.5977 | 25.8635 | 0 | 0 | 0 | 43.6415 | 112.3956 | 149.7595 | 200.9993 | 200.3362 | 148.1587 | 112.3956 | 112.3956 | 112.3956 | 245.3585 | 112.3956 | 176.7806 | 265.0765 | 263.9339 | 174.0223 | 112.3956 | 112.3956 | 112.3956 | 289 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 11 | 2675 | 16.8 | 16.8 | 9.1583 | 8.0999 | 15 | 55 | 55 | 112.2701 | 299.0942 | 45.3286 | 144.8639 | 0 | 12.1425 | 69.7547 | 86.5056 | 52.5827 | 0 | 0 | 0 | 72.9058 | 136.8694 | 150.1456 | 213.1369 | 231.4518 | 194.3616 | 136.8694 | 136.8694 | 136.8694 | 299.0942 | 136.8694 | 162.288 | 282.8916 | 317.9574 | 246.9442 | 136.8694 | 136.8694 | 136.8694 | 372 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 12 | 2676 | 18.1 | 18.1 | 9.1583 | 8.0999 | 15 | 51 | 51 | 583.6314 | 213.5826 | 49.1864 | 165.7991 | 0 | 0 | 236.1454 | 404.2504 | 335.551 | 70.2904 | 0 | 0 | 422.4174 | 130.9196 | 130.9196 | 190.0471 | 232.1383 | 214.9369 | 148.5193 | 130.9196 | 130.9196 | 213.5826 | 130.9196 | 130.9196 | 426.1925 | 636.3887 | 550.4879 | 218.8097 | 130.9196 | 130.9196 | 636 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 13 | 2677 | 18.6 | 18.6 | 9.1583 | 8.0999 | 15 | 48 | 48 | 558.3189 | 233.6944 | 49.6529 | 188.4249 | 0 | 0 | 89.5224 | 313.4522 | 353.7659 | 186.8484 | 0 | 0 | 424.3056 | 138.7342 | 138.7342 | 166.4844 | 235.8983 | 248.3948 | 196.6536 | 138.7342 | 138.7342 | 233.6944 | 138.7342 | 138.7342 | 256.0068 | 549.3504 | 602.1606 | 383.5019 | 138.7342 | 138.7342 | 658 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 14 | 2678 | 20.4 | 20.4 | 9.1583 | 8.0999 | 15 | 43 | 43 | 752.1503 | 162.7889 | 46.6086 | 210.0097 | 0 | 0 | 0 | 290.1642 | 481.6997 | 391.062 | 71.3456 | 0 | 568.2111 | 126.9502 | 126.9502 | 126.9502 | 174.4193 | 205.7533 | 190.9256 | 138.6219 | 126.9502 | 162.7889 | 126.9502 | 126.9502 | 126.9502 | 464.5835 | 687.453 | 581.9876 | 209.9675 | 126.9502 | 731 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 15 | 2679 | 19.8 | 19.8 | 9.1583 | 8.0999 | 15 | 43 | 43 | 654.0454 | 185.2836 | 40.7593 | 228.6836 | 0 | 0 | 0 | 116.2179 | 389.08 | 434.0243 | 224.7231 | 0 | 464.7164 | 125.3916 | 125.3916 | 125.3916 | 149.2855 | 205.385 | 214.6254 | 171.5938 | 125.3916 | 185.2836 | 125.3916 | 125.3916 | 125.3916 | 265.5034 | 594.465 | 648.6497 | 396.3169 | 125.3916 | 650 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 16 | 2680 | 19.7 | 19.7 | 9.1583 | 8.0999 | 15 | 46 | 46 | 148.142 | 289.9194 | 33.0779 | 244.366 | 0 | 0 | 0 | 0 | 74.084 | 111.9797 | 84.2792 | 7.2091 | 93.0806 | 134.0741 | 134.0741 | 134.0741 | 134.0741 | 209.5825 | 248.2068 | 219.9738 | 141.4218 | 289.9194 | 134.0741 | 134.0741 | 134.0741 | 134.0741 | 283.6665 | 360.1865 | 304.253 | 148.631 | 383 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 17 | 2681 | 18.4 | 18.4 | 9.1583 | 8.0999 | 15 | 44 | 44 | 127.2088 | 237.5528 | 24.3723 | 257.863 | 0 | 0 | 0 | 0 | 46.114 | 100.561 | 96.1008 | 35.346 | 65.4472 | 111.7835 | 111.7835 | 111.7835 | 111.7835 | 159.6983 | 216.2717 | 211.6373 | 148.5099 | 237.5528 | 111.7835 | 111.7835 | 111.7835 | 111.7835 | 205.8123 | 316.8328 | 307.7381 | 183.8559 | 303 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 18 | 2682 | 17.6 | 17.6 | 9.1583 | 8.0999 | 15 | 49 | 49 | 8.3046 | 121.8708 | 15.2251 | 270.0734 | 0 | 0 | 0 | 0 | 1.5904 | 6.3539 | 7.3954 | 4.1047 | 3.1292 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 61.5148 | 67.0622 | 68.2751 | 64.4428 | 121.8708 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 63.1052 | 73.4162 | 75.6705 | 68.5476 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 19 | 2683 | 17 | 17 | 9.1583 | 8.0999 | 15 | 52 | 52 | 2.9089 | 46.3465 | 6.076 | 281.7566 | 0.0035979 | 0 | 0 | 0 | 0 | 1.9821 | 2.8068 | 1.9872 | 0.65349 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 46.3465 | 22.5213 | 22.5177 | 22.5177 | 22.5177 | 22.5177 | 24.4998 | 25.3245 | 24.5049 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 20 | 2684 | 15.9 | 15.9 | 9.1583 | 8.0999 | 15 | 58 | 58 | 0.12791 | 2.9913 | -2.6908 | 293.5358 | 0.025916 | 0 | 0 | 0 | 0 | 0.069727 | 0.12453 | 0.10638 | 0.008747 | 1.382 | 1.382 | 1.382 | 1.382 | 1.382 | 1.382 | 1.382 | 1.382 | 2.9913 | 1.4079 | 1.382 | 1.382 | 1.382 | 1.382 | 1.4517 | 1.5065 | 1.4884 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 21 | 2685 | 14.8 | 14.8 | 9.1583 | 8.0999 | 15 | 59 | 59 | 0 | 0 | -10.6819 | 305.9335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 22 | 2686 | 14.1 | 14.1 | 9.1583 | 8.0999 | 15 | 61 | 61 | 0 | 0 | -17.4546 | 319.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 23 | 2687 | 14 | 14 | 9.1583 | 8.0999 | 15 | 60 | 60 | 0 | 0 | -22.5146 | 334.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 22 | 24 | 2688 | 13.7 | 13.7 | 13.6208 | 9.5986 | 15 | 66 | 66 | 0 | 0 | -25.3793 | 349.7776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 1 | 2689 | 12.6 | 12.6 | 13.6208 | 9.5986 | 15 | 76 | 76 | 0 | 0 | -25.7156 | 6.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 2 | 2690 | 12.1 | 12.1 | 13.6208 | 9.5986 | 15 | 82 | 82 | 0 | 0 | -23.1421 | 21.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 3 | 2691 | 12.1 | 12.1 | 13.6208 | 9.5986 | 15 | 86 | 86 | 0 | 0 | -18.6142 | 36.8882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 4 | 2692 | 11.3 | 11.3 | 13.6208 | 9.5986 | 15 | 87 | 87 | 0 | 0 | -12.2472 | 50.5883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 5 | 2693 | 10.9 | 10.9 | 13.6208 | 9.5986 | 15 | 90 | 90 | 0 | 0 | -4.5377 | 63.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 6 | 2694 | 10.5 | 10.5 | 13.6208 | 9.5986 | 15 | 90 | 90 | 0 | 0 | 4.0591 | 75.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 7 | 2695 | 10.9 | 10.9 | 13.6208 | 9.5986 | 15 | 90 | 90 | 17.455 | 40.1284 | 13.1414 | 86.7095 | 4.4863 | 15.0681 | 16.8233 | 8.7236 | 0 | 0 | 0 | 0 | 1.8716 | 37.5271 | 82.0828 | 89.4731 | 55.3688 | 18.6375 | 18.6375 | 18.6375 | 18.6375 | 40.1284 | 42.0134 | 97.1509 | 106.2964 | 64.0924 | 18.6375 | 18.6375 | 18.6375 | 18.6375 | 42 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 23 | 8 | 2696 | 12.6 | 12.6 | 13.6208 | 9.5986 | 15 | 86 | 86 | 85.0702 | 119.6007 | 22.329 | 98.7107 | 4.755 | 61.8442 | 82.7058 | 55.1195 | 0 | 0 | 0 | 0 | 22.3993 | 61.6172 | 130.0121 | 155.0052 | 121.9558 | 55.9205 | 55.9205 | 55.9205 | 55.9205 | 119.6007 | 66.3723 | 191.8563 | 237.711 | 177.0753 | 55.9205 | 55.9205 | 55.9205 | 55.9205 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 9 | 2697 | 14.2 | 14.2 | 13.6208 | 9.5986 | 15 | 78 | 78 | 395.6718 | 158.6099 | 31.2047 | 111.7957 | 0 | 216.6239 | 361.7817 | 295.0127 | 55.4293 | 0 | 0 | 0 | 163.3901 | 90.6158 | 160.567 | 207.4407 | 185.88 | 108.5148 | 90.6158 | 90.6158 | 90.6158 | 158.6099 | 90.6158 | 377.1909 | 569.2224 | 480.8927 | 163.9441 | 90.6158 | 90.6158 | 90.6158 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 10 | 2698 | 15.4 | 15.4 | 13.6208 | 9.5986 | 15 | 75 | 75 | 339.1539 | 222.8344 | 39.2315 | 126.8441 | 0 | 114.2971 | 269.3487 | 266.6195 | 107.7082 | 0 | 0 | 0 | 185.1656 | 117.6152 | 169.8441 | 240.6961 | 239.4489 | 166.8333 | 117.6152 | 117.6152 | 117.6152 | 222.8344 | 117.6152 | 284.1412 | 510.0447 | 506.0684 | 274.5415 | 117.6152 | 117.6152 | 117.6152 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 11 | 2699 | 16.2 | 16.2 | 13.6208 | 9.5986 | 15 | 68 | 68 | 652.7316 | 170.5718 | 45.6601 | 144.7524 | 0 | 71.7285 | 404.6196 | 500.4901 | 303.1802 | 0 | 0 | 0 | 426.4282 | 117.8287 | 131.8051 | 196.6691 | 215.3495 | 176.9036 | 117.8287 | 117.8287 | 117.8287 | 170.5718 | 117.8287 | 203.5336 | 601.2887 | 715.8396 | 480.0838 | 117.8287 | 117.8287 | 117.8287 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 12 | 2700 | 16.5 | 16.5 | 13.6208 | 9.5986 | 15 | 62 | 62 | 537.4805 | 230.9279 | 49.527 | 165.7908 | 0 | 0 | 216.7931 | 370.2236 | 306.7821 | 63.6318 | 0 | 0 | 391.0721 | 135.833 | 135.833 | 204.4419 | 252.9982 | 232.9208 | 155.9707 | 135.833 | 135.833 | 230.9279 | 135.833 | 135.833 | 421.235 | 623.2218 | 539.7029 | 219.6025 | 135.833 | 135.833 | 622 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 13 | 2701 | 17.4 | 17.4 | 13.6208 | 9.5986 | 15 | 64 | 64 | 348.5633 | 308.7834 | 49.9844 | 188.5463 | 0 | 0 | 55.5356 | 194.3573 | 219.3271 | 115.8181 | 0 | 0 | 266.2166 | 151.4103 | 151.4103 | 182.8987 | 261.61 | 275.7678 | 217.0787 | 151.4103 | 151.4103 | 308.7834 | 151.4103 | 151.4103 | 238.4343 | 455.9673 | 495.0949 | 332.8968 | 151.4103 | 151.4103 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 14 | 2702 | 17.5 | 17.5 | 13.6208 | 9.5986 | 15 | 59 | 59 | 632.7862 | 205.5646 | 46.9139 | 210.2303 | 0 | 0 | 0 | 241.7569 | 402.3614 | 327.2681 | 60.4655 | 0 | 480.4354 | 132.9015 | 132.9015 | 132.9015 | 188.081 | 224.7381 | 207.5984 | 146.7024 | 132.9015 | 205.5646 | 132.9015 | 132.9015 | 132.9015 | 429.8379 | 627.0995 | 534.8665 | 207.1679 | 132.9015 | 686 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 15 | 2703 | 17.5 | 17.5 | 13.6208 | 9.5986 | 15 | 62 | 62 | 568.4871 | 215.8899 | 41.0342 | 228.9496 | 0 | 0 | 0 | 98.9989 | 335.522 | 375.5008 | 195.5164 | 0 | 406.1101 | 129.6505 | 129.6505 | 129.6505 | 155.367 | 216.8077 | 227.1929 | 180.439 | 129.6505 | 215.8899 | 129.6505 | 129.6505 | 129.6505 | 254.3659 | 552.3297 | 602.6937 | 375.9554 | 129.6505 | 622 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 16 | 2704 | 17.2 | 17.2 | 13.6208 | 9.5986 | 15 | 63 | 63 | 329.9139 | 260.4069 | 33.3289 | 244.6411 | 0 | 0 | 0 | 0 | 163.432 | 248.269 | 187.6735 | 17.1413 | 208.5931 | 131.8288 | 131.8288 | 131.8288 | 131.8288 | 217.0977 | 261.3606 | 229.7455 | 140.7721 | 260.4069 | 131.8288 | 131.8288 | 131.8288 | 131.8288 | 380.5297 | 509.6296 | 417.4189 | 157.9134 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 17 | 2705 | 16.1 | 16.1 | 13.6208 | 9.5986 | 15 | 65 | 65 | 138.1594 | 239.3543 | 24.6094 | 258.1317 | 0 | 0 | 0 | 0 | 49.4399 | 108.7199 | 104.3132 | 38.8013 | 71.6457 | 113.0875 | 113.0875 | 113.0875 | 113.0875 | 160.6244 | 217.6227 | 213.3857 | 150.3953 | 239.3543 | 113.0875 | 113.0875 | 113.0875 | 113.0875 | 210.0643 | 326.3426 | 317.6989 | 189.1966 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 23 | 18 | 2706 | 15.9 | 15.9 | 13.6208 | 9.5986 | 15 | 63 | 63 | 231.1037 | 169.9346 | 15.4578 | 270.3313 | 0 | 0 | 0 | 0 | 43.2122 | 175.9513 | 205.6205 | 114.84 | 88.0654 | 87.691 | 87.691 | 87.691 | 87.691 | 112.3762 | 188.2042 | 205.153 | 153.2941 | 169.9346 | 87.691 | 87.691 | 87.691 | 87.691 | 155.5884 | 364.1555 | 410.7735 | 268.1341 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 19 | 2707 | 14.8 | 14.8 | 13.6208 | 9.5986 | 15 | 66 | 66 | 80.1272 | 103.6424 | 6.313 | 282.0027 | 0.44659 | 0 | 0 | 0 | 0 | 54.2923 | 77.2274 | 54.9238 | 18.3576 | 51.7805 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 107.6087 | 131.3883 | 108.2636 | 103.6424 | 52.2271 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 161.901 | 208.6158 | 163.1874 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 20 | 2708 | 12.9 | 12.9 | 13.6208 | 9.5986 | 15 | 74 | 74 | 9.4075 | 24.313 | -2.4421 | 293.7688 | 1.9445 | 0 | 0 | 0 | 0 | 5.0922 | 9.146 | 7.8422 | 0.68704 | 14.9094 | 12.4646 | 12.4646 | 12.4646 | 12.4646 | 18.8669 | 23.9635 | 22.3242 | 24.313 | 16.8539 | 12.4646 | 12.4646 | 12.4646 | 12.4646 | 23.9591 | 33.1095 | 30.1664 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 21 | 2709 | 11.2 | 11.2 | 13.6208 | 9.5986 | 15 | 83 | 83 | 0 | 0 | -10.4154 | 306.1492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 22 | 2710 | 10.7 | 10.7 | 13.6208 | 9.5986 | 15 | 86 | 86 | 0 | 0 | -17.166 | 319.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 23 | 2711 | 10.2 | 10.2 | 13.6208 | 9.5986 | 15 | 90 | 90 | 0 | 0 | -22.2032 | 334.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 23 | 24 | 2712 | 9.1 | 9.1 | 13.575 | 10.7191 | 15 | 92 | 92 | 0 | 0 | -25.0493 | 349.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 1 | 2713 | 11.3 | 11.3 | 13.575 | 10.7191 | 15 | 92 | 92 | 0 | 0 | -25.3759 | 6.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 2 | 2714 | 10.7 | 10.7 | 13.575 | 10.7191 | 15 | 92 | 92 | 0 | 0 | -22.807 | 21.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 3 | 2715 | 9.8 | 9.8 | 13.575 | 10.7191 | 15 | 93 | 93 | 0 | 0 | -18.288 | 36.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 4 | 2716 | 11.7 | 11.7 | 13.575 | 10.7191 | 15 | 92 | 92 | 0 | 0 | -11.9334 | 50.4628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 5 | 2717 | 11.5 | 11.5 | 13.575 | 10.7191 | 15 | 90 | 90 | 0 | 0 | -4.236 | 63.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 6 | 2718 | 11.5 | 11.5 | 13.575 | 10.7191 | 15 | 92 | 92 | 0 | 0 | 4.3516 | 74.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 7 | 2719 | 12.1 | 12.1 | 13.575 | 10.7191 | 15 | 92 | 92 | 17.9207 | 41.9968 | 13.4295 | 86.53 | 4.6547 | 15.4905 | 17.2521 | 8.9077 | 0 | 0 | 0 | 0 | 2.0032 | 39.3845 | 85.5892 | 93.1011 | 57.5198 | 19.5365 | 19.5365 | 19.5365 | 19.5365 | 41.9968 | 44.0392 | 101.0796 | 110.3532 | 66.4276 | 19.5365 | 19.5365 | 19.5365 | 19.5365 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 24 | 8 | 2720 | 12.8 | 12.8 | 13.575 | 10.7191 | 15 | 91 | 91 | 42.3365 | 113.6683 | 22.6185 | 98.5241 | 2.4924 | 30.8268 | 41.1033 | 27.3021 | 0 | 0 | 0 | 0 | 11.3317 | 58.0527 | 117.3324 | 138.8323 | 109.9582 | 52.8384 | 52.8384 | 52.8384 | 52.8384 | 113.6683 | 60.5451 | 148.1592 | 179.9356 | 137.2602 | 52.8384 | 52.8384 | 52.8384 | 52.8384 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 9 | 2721 | 14.7 | 14.7 | 13.575 | 10.7191 | 15 | 84 | 84 | 174.9069 | 191.0451 | 31.5019 | 111.6099 | 0 | 95.9821 | 159.6707 | 129.8264 | 23.9315 | 0 | 0 | 0 | 72.9549 | 92.5576 | 166.5744 | 215.6879 | 192.6734 | 111.0125 | 92.5576 | 92.5576 | 92.5576 | 191.0451 | 92.5576 | 262.5565 | 375.3586 | 322.4998 | 134.944 | 92.5576 | 92.5576 | 92.5576 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 10 | 2722 | 16.6 | 16.6 | 13.575 | 10.7191 | 15 | 78 | 78 | 253.8392 | 241.3993 | 39.5426 | 126.6767 | 0 | 85.9199 | 201.2168 | 198.6436 | 79.7077 | 0 | 0 | 0 | 139.6007 | 120.1959 | 167.5899 | 231.1886 | 229.7692 | 164.1632 | 120.1959 | 120.1959 | 120.1959 | 241.3993 | 120.1959 | 253.5099 | 432.4054 | 428.4128 | 243.871 | 120.1959 | 120.1959 | 120.1959 | 381 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 11 | 2723 | 18.4 | 18.4 | 13.575 | 10.7191 | 15 | 71 | 71 | 634.0824 | 177.3091 | 45.9876 | 144.6384 | 0 | 70.783 | 392.1657 | 483.823 | 292.0634 | 0 | 0 | 0 | 416.6909 | 119.1844 | 133.702 | 199.6175 | 218.4164 | 179.0865 | 119.1844 | 119.1844 | 119.1844 | 177.3091 | 119.1844 | 204.485 | 591.7832 | 702.2394 | 471.15 | 119.1844 | 119.1844 | 119.1844 | 594 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 12 | 2724 | 19.3 | 19.3 | 13.575 | 10.7191 | 15 | 64 | 64 | 588.4145 | 213.653 | 49.8639 | 165.78 | 0 | 0 | 236.6091 | 403.0675 | 333.4145 | 68.4517 | 0 | 0 | 430.347 | 131.5656 | 131.5656 | 190.4255 | 231.8344 | 214.5072 | 148.5939 | 131.5656 | 131.5656 | 213.653 | 131.5656 | 131.5656 | 427.0346 | 634.9019 | 547.9217 | 217.0456 | 131.5656 | 131.5656 | 644 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 13 | 2725 | 19.6 | 19.6 | 13.575 | 10.7191 | 15 | 64 | 64 | 325.4404 | 317.233 | 50.3126 | 188.6654 | 0 | 0 | 51.5319 | 180.2309 | 203.3531 | 107.3538 | 0 | 0 | 249.767 | 152.4607 | 152.4607 | 184.4251 | 264.255 | 278.5973 | 219.0505 | 152.4607 | 152.4607 | 317.233 | 152.4607 | 152.4607 | 235.957 | 444.4858 | 481.9504 | 326.4043 | 152.4607 | 152.4607 | 567 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 14 | 2726 | 19.7 | 19.7 | 13.575 | 10.7191 | 15 | 67 | 67 | 132.3906 | 351.9908 | 47.2161 | 210.4489 | 0 | 0 | 0 | 50.0926 | 83.5794 | 68.1066 | 12.7378 | 0 | 101.0092 | 155.8528 | 155.8528 | 155.8528 | 222.6341 | 267.2773 | 246.6496 | 172.8343 | 155.8528 | 351.9908 | 155.8528 | 155.8528 | 155.8528 | 272.7267 | 350.8568 | 314.7561 | 185.5721 | 155.8528 | 453 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 15 | 2727 | 20.1 | 20.1 | 13.575 | 10.7191 | 15 | 65 | 65 | 364.2376 | 285.4225 | 41.3065 | 229.2132 | 0 | 0 | 0 | 62.1582 | 213.2813 | 239.4671 | 125.3763 | 0 | 261.5775 | 143.8542 | 143.8542 | 143.8542 | 175.4781 | 252.3642 | 265.6866 | 207.6413 | 143.8542 | 285.4225 | 143.8542 | 143.8542 | 143.8542 | 237.6363 | 465.6455 | 505.1538 | 333.0176 | 143.8542 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 16 | 2728 | 19.9 | 19.9 | 13.575 | 10.7191 | 15 | 62 | 62 | 538.6378 | 201.3462 | 33.5778 | 244.9134 | 0 | 0 | 0 | 0 | 264.3156 | 403.5255 | 306.3557 | 29.7269 | 342.6538 | 121.5772 | 121.5772 | 121.5772 | 121.5772 | 196.9813 | 236.6951 | 208.9745 | 130.0577 | 201.3462 | 121.5772 | 121.5772 | 121.5772 | 121.5772 | 461.2968 | 640.2207 | 515.3302 | 159.7845 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 17 | 2729 | 19.5 | 19.5 | 13.575 | 10.7191 | 15 | 59 | 59 | 539.0127 | 165.3117 | 24.8446 | 258.3973 | 0 | 0 | 0 | 0 | 190.4007 | 422.2203 | 406.709 | 152.953 | 281.6883 | 103.4348 | 103.4348 | 103.4348 | 103.4348 | 150.9077 | 208.7077 | 204.8403 | 141.5708 | 165.3117 | 103.4348 | 103.4348 | 103.4348 | 103.4348 | 341.3085 | 630.9281 | 611.5492 | 294.5238 | 447 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 24 | 18 | 2730 | 18 | 18 | 13.575 | 10.7191 | 15 | 64 | 64 | 115.7357 | 177.4108 | 15.689 | 270.5858 | 0 | 0 | 0 | 0 | 21.1229 | 87.6821 | 102.8784 | 57.8098 | 44.5892 | 85.5793 | 85.5793 | 85.5793 | 85.5793 | 105.9166 | 170.0006 | 184.6317 | 141.2392 | 177.4108 | 85.5793 | 85.5793 | 85.5793 | 85.5793 | 127.0396 | 257.6827 | 287.51 | 199.049 | 222 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 19 | 2731 | 16.7 | 16.7 | 13.575 | 10.7191 | 15 | 68 | 68 | 82.3162 | 105.7789 | 6.5485 | 282.2452 | 0.81027 | 0 | 0 | 0 | 0 | 55.4619 | 79.2452 | 56.6078 | 19.2211 | 53.1654 | 52.3364 | 52.3364 | 52.3364 | 52.3364 | 109.0781 | 133.4102 | 110.2504 | 105.7789 | 53.9757 | 52.3364 | 52.3364 | 52.3364 | 52.3364 | 164.54 | 212.6555 | 166.8582 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 20 | 2732 | 14.6 | 14.6 | 13.575 | 10.7191 | 15 | 74 | 74 | 5.3434 | 21.5852 | -2.195 | 293.998 | 1.1259 | 0 | 0 | 0 | 0 | 2.8722 | 5.1878 | 4.4644 | 0.41481 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 21.5852 | 11.5778 | 10.4519 | 10.4519 | 10.4519 | 10.4519 | 13.324 | 15.6396 | 14.9163 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 21 | 2733 | 13.7 | 13.7 | 13.575 | 10.7191 | 15 | 78 | 78 | 0 | 0 | -10.1505 | 306.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 22 | 2734 | 12.9 | 12.9 | 13.575 | 10.7191 | 15 | 81 | 81 | 0 | 0 | -16.8794 | 319.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 23 | 2735 | 10.7 | 10.7 | 13.575 | 10.7191 | 15 | 87 | 87 | 0 | 0 | -21.8943 | 334.3183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 24 | 24 | 2736 | 9.6 | 9.6 | 14.8083 | 11.9083 | 15 | 92 | 92 | 0 | 0 | -24.7224 | 349.9608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 1 | 2737 | 9.4 | 9.4 | 14.8083 | 11.9083 | 15 | 93 | 93 | 0 | 0 | -25.0397 | 6.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 2 | 2738 | 8.3 | 8.3 | 14.8083 | 11.9083 | 15 | 95 | 95 | 0 | 0 | -22.4757 | 21.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 3 | 2739 | 8.2 | 8.2 | 14.8083 | 11.9083 | 15 | 96 | 96 | 0 | 0 | -17.9658 | 36.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 4 | 2740 | 8.6 | 8.6 | 14.8083 | 11.9083 | 15 | 96 | 96 | 0 | 0 | -11.6237 | 50.3373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 5 | 2741 | 6.9 | 6.9 | 14.8083 | 11.9083 | 15 | 96 | 96 | 0 | 0 | -3.9384 | 62.8922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 6 | 2742 | 7.1 | 7.1 | 14.8083 | 11.9083 | 15 | 97 | 97 | 0 | 3 | 4.6401 | 74.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 7 | 2743 | 8.8 | 8.8 | 14.8083 | 11.9083 | 15 | 97 | 97 | 5.361 | 32.3766 | 13.7135 | 86.3507 | 1.407 | 4.6399 | 5.1549 | 2.6502 | 0 | 0 | 0 | 0 | 0.6234 | 23.579 | 43.2067 | 46.3331 | 31.1266 | 15.0371 | 15.0371 | 15.0371 | 15.0371 | 32.3766 | 24.986 | 47.8467 | 51.488 | 33.7768 | 15.0371 | 15.0371 | 15.0371 | 15.0371 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 25 | 8 | 2744 | 9.8 | 9.8 | 14.8083 | 11.9083 | 15 | 97 | 97 | 7.0632 | 84.0791 | 22.9037 | 98.3372 | 0.43676 | 5.1511 | 6.848 | 4.5334 | 0 | 0 | 0 | 0 | 1.9209 | 41.3015 | 59.555 | 66.1252 | 57.1634 | 39.6104 | 39.6104 | 39.6104 | 39.6104 | 84.0791 | 41.7383 | 64.7061 | 72.9732 | 61.6968 | 39.6104 | 39.6104 | 39.6104 | 39.6104 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 9 | 2745 | 9.9 | 9.9 | 14.8083 | 11.9083 | 15 | 97 | 97 | 6.2944 | 125.3487 | 31.7948 | 111.4233 | 0 | 3.4621 | 5.7369 | 4.6511 | 0.84073 | 0 | 0 | 0 | 2.6513 | 60.3516 | 69.9577 | 76.2693 | 73.2566 | 62.6843 | 60.3516 | 60.3516 | 60.3516 | 125.3487 | 60.3516 | 73.4198 | 82.0062 | 77.9077 | 63.525 | 60.3516 | 60.3516 | 60.3516 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 10 | 2746 | 10.2 | 10.2 | 14.8083 | 11.9083 | 15 | 97 | 97 | 3.0726 | 117.2981 | 39.8494 | 126.5076 | 0 | 1.0445 | 2.4311 | 2.3935 | 0.95387 | 0 | 0 | 0 | 1.7019 | 58.3837 | 58.3837 | 58.3837 | 58.3837 | 58.3837 | 58.3837 | 58.3837 | 58.3837 | 117.2981 | 58.3837 | 59.4283 | 60.8148 | 60.7772 | 59.3376 | 58.3837 | 58.3837 | 58.3837 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 11 | 2747 | 11.4 | 11.4 | 14.8083 | 11.9083 | 15 | 97 | 97 | 2.6954 | 131.2185 | 46.3109 | 144.522 | 0 | 0.30559 | 1.6633 | 2.0466 | 1.2311 | 0 | 0 | 0 | 1.7815 | 65.3424 | 65.3424 | 65.3424 | 65.3424 | 65.3424 | 65.3424 | 65.3424 | 65.3424 | 131.2185 | 65.3424 | 65.648 | 67.0056 | 67.389 | 66.5735 | 65.3424 | 65.3424 | 65.3424 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 12 | 2748 | 13.4 | 13.4 | 14.8083 | 11.9083 | 15 | 94 | 94 | 21.5075 | 284.1905 | 50.1969 | 165.7664 | 0 | 0 | 8.6224 | 14.6515 | 12.0979 | 2.4576 | 0 | 0 | 15.8095 | 134.1916 | 134.1916 | 152.2112 | 164.8112 | 159.4747 | 139.3276 | 134.1916 | 134.1916 | 284.1905 | 134.1916 | 134.1916 | 160.8336 | 179.4627 | 171.5726 | 141.7852 | 134.1916 | 134.1916 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 13 | 2749 | 15.5 | 15.5 | 14.8083 | 11.9083 | 15 | 80 | 80 | 480.4263 | 265.5292 | 50.6374 | 188.7822 | 0 | 0 | 75.6179 | 264.2613 | 298.104 | 157.3214 | 0 | 0 | 370.4708 | 143.9497 | 143.9497 | 173.7816 | 248.203 | 261.5542 | 206.0143 | 143.9497 | 143.9497 | 265.5292 | 143.9497 | 143.9497 | 249.3995 | 512.4643 | 559.6582 | 363.3357 | 143.9497 | 143.9497 | 636 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 14 | 2750 | 16.9 | 16.9 | 14.8083 | 11.9083 | 15 | 71 | 71 | 435.424 | 280.1934 | 47.5154 | 210.6653 | 0 | 0 | 0 | 163.1693 | 272.9197 | 222.7974 | 42.1634 | 0 | 333.8066 | 145.0027 | 145.0027 | 145.0027 | 218.7215 | 268.3061 | 245.6611 | 164.0519 | 145.0027 | 280.1934 | 145.0027 | 145.0027 | 145.0027 | 381.8908 | 541.2257 | 468.4585 | 206.2153 | 145.0027 | 614 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 15 | 2751 | 15.5 | 15.5 | 14.8083 | 11.9083 | 15 | 73 | 73 | 289.6013 | 307.9461 | 41.5762 | 229.4743 | 0 | 0 | 0 | 48.4265 | 168.2428 | 189.5048 | 99.7574 | 0 | 209.0539 | 146.2693 | 146.2693 | 146.2693 | 179.1101 | 260.3646 | 274.7836 | 213.9206 | 146.2693 | 307.9461 | 146.2693 | 146.2693 | 146.2693 | 227.5366 | 428.6074 | 464.2883 | 313.678 | 146.2693 | 517 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 16 | 2752 | 14.3 | 14.3 | 14.8083 | 11.9083 | 15 | 73 | 73 | 590.485 | 186.107 | 33.8244 | 245.1826 | 0 | 0 | 0 | 0 | 287.0291 | 440.3802 | 335.7625 | 34.4597 | 377.893 | 118.0299 | 118.0299 | 118.0299 | 118.0299 | 183.1687 | 217.9704 | 194.2283 | 125.8502 | 186.107 | 118.0299 | 118.0299 | 118.0299 | 118.0299 | 470.1978 | 658.3506 | 529.9908 | 160.3099 | 564 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 17 | 2753 | 13.6 | 13.6 | 14.8083 | 11.9083 | 15 | 77 | 77 | 341.7133 | 214.0645 | 25.078 | 258.6596 | 0 | 0 | 0 | 0 | 119.1511 | 266.4466 | 257.6614 | 97.9416 | 179.9355 | 113.346 | 113.346 | 113.346 | 113.346 | 165.6575 | 230.3254 | 226.4683 | 156.3458 | 214.0645 | 113.346 | 113.346 | 113.346 | 113.346 | 284.8085 | 496.772 | 484.1297 | 254.2874 | 394 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 25 | 18 | 2754 | 12.5 | 12.5 | 14.8083 | 11.9083 | 15 | 77 | 77 | 9.3506 | 129.3587 | 15.9185 | 270.8368 | 0 | 0 | 0 | 0 | 1.6654 | 7.0493 | 8.3038 | 4.6941 | 3.6413 | 63.0263 | 63.0263 | 63.0263 | 63.0263 | 65.2627 | 72.4927 | 74.1774 | 69.33 | 129.3587 | 63.0263 | 63.0263 | 63.0263 | 63.0263 | 66.928 | 79.5419 | 82.4812 | 74.0241 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 19 | 2755 | 11.7 | 11.7 | 14.8083 | 11.9083 | 15 | 80 | 80 | 84.5587 | 107.8879 | 6.7825 | 282.484 | 1.1876 | 0 | 0 | 0 | 0 | 56.6532 | 81.3074 | 58.3328 | 20.1121 | 54.5426 | 53.3443 | 53.3443 | 53.3443 | 53.3443 | 110.5084 | 135.3848 | 112.2031 | 107.8879 | 55.7302 | 53.3443 | 53.3443 | 53.3443 | 53.3443 | 167.1616 | 216.6923 | 170.5359 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 20 | 2756 | 10.2 | 10.2 | 14.8083 | 11.9083 | 15 | 83 | 83 | 238.0005 | 36.4416 | -1.9494 | 294.2233 | 51.0879 | 0 | 0 | 0 | 0 | 127.0382 | 230.7471 | 199.2874 | 19.5584 | 37.8775 | 21.1628 | 21.1628 | 21.1628 | 21.1628 | 62.7266 | 96.6576 | 86.3648 | 36.4416 | 88.9653 | 21.1628 | 21.1628 | 21.1628 | 21.1628 | 189.7648 | 327.4047 | 285.6522 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 21 | 2757 | 8.3 | 8.3 | 14.8083 | 11.9083 | 15 | 89 | 89 | 0 | 0 | -9.8874 | 306.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 22 | 2758 | 7.9 | 7.9 | 14.8083 | 11.9083 | 15 | 91 | 91 | 0 | 0 | -16.595 | 319.9163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 23 | 2759 | 7.2 | 7.2 | 14.8083 | 11.9083 | 15 | 93 | 93 | 0 | 0 | -21.5881 | 334.4597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 25 | 24 | 2760 | 6.5 | 6.5 | 10.5042 | 11.7793 | 15 | 94 | 94 | 0 | 0 | -24.3986 | 350.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 1 | 2761 | 5.2 | 5.2 | 10.5042 | 11.7793 | 15 | 95 | 95 | 0 | 0 | -24.7071 | 6.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 2 | 2762 | 4.6 | 4.6 | 10.5042 | 11.7793 | 15 | 97 | 97 | 0 | 0 | -22.1484 | 21.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 3 | 2763 | 6.1 | 6.1 | 10.5042 | 11.7793 | 15 | 97 | 97 | 0 | 0 | -17.6476 | 36.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 4 | 2764 | 6.1 | 6.1 | 10.5042 | 11.7793 | 15 | 97 | 97 | 0 | 0 | -11.3181 | 50.2119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 5 | 2765 | 5.6 | 5.6 | 10.5042 | 11.7793 | 15 | 97 | 97 | 0 | 0 | -3.645 | 62.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 6 | 2766 | 6.3 | 6.3 | 10.5042 | 11.7793 | 15 | 97 | 97 | 0 | 0 | 4.9243 | 74.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 7 | 2767 | 6.5 | 6.5 | 10.5042 | 11.7793 | 15 | 98 | 98 | 2.2114 | 21.733 | 13.9931 | 86.1714 | 0.58631 | 1.9163 | 2.1237 | 1.0871 | 0 | 0 | 0 | 0 | 0.26699 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 21.733 | 11.2362 | 12.5662 | 12.7737 | 11.7371 | 10.6499 | 10.6499 | 10.6499 | 10.6499 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 26 | 8 | 2768 | 8.2 | 8.2 | 10.5042 | 11.7793 | 15 | 98 | 98 | 3.5759 | 63.0123 | 23.1845 | 98.15 | 0.23168 | 2.6118 | 3.462 | 2.2842 | 0 | 0 | 0 | 0 | 0.98767 | 31.257 | 31.7403 | 31.913 | 31.6738 | 31.21 | 31.21 | 31.21 | 31.21 | 63.0123 | 31.4887 | 34.3522 | 35.375 | 33.958 | 31.21 | 31.21 | 31.21 | 31.21 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 9 | 2769 | 10 | 10 | 10.5042 | 11.7793 | 15 | 95 | 95 | 6.8332 | 130.0941 | 32.0833 | 111.2359 | 0 | 3.7671 | 6.218 | 5.0264 | 0.89049 | 0 | 0 | 0 | 2.9059 | 62.3645 | 73.4955 | 80.7374 | 77.2167 | 64.9957 | 62.3645 | 62.3645 | 62.3645 | 130.0941 | 62.3645 | 77.2626 | 86.9554 | 82.2431 | 65.8862 | 62.3645 | 62.3645 | 62.3645 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 10 | 2770 | 11.7 | 11.7 | 10.5042 | 11.7793 | 15 | 92 | 92 | 67.2948 | 248.4654 | 40.1517 | 126.3369 | 0 | 22.9764 | 53.1457 | 52.1829 | 20.6521 | 0 | 0 | 0 | 37.5346 | 113.2754 | 150.5552 | 199.5057 | 197.9436 | 146.784 | 113.2754 | 113.2754 | 113.2754 | 248.4654 | 113.2754 | 173.5316 | 252.6514 | 250.1265 | 167.4362 | 113.2754 | 113.2754 | 113.2754 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 11 | 2771 | 12.4 | 12.4 | 10.5042 | 11.7793 | 15 | 81 | 81 | 10.448 | 226.0554 | 46.6299 | 144.4031 | 0 | 1.2029 | 6.4329 | 7.8947 | 4.7318 | 0 | 0 | 0 | 6.9446 | 108.3525 | 111.5718 | 125.5693 | 129.4814 | 121.0166 | 108.3525 | 108.3525 | 108.3525 | 226.0554 | 108.3525 | 112.7746 | 132.0022 | 137.3761 | 125.7484 | 108.3525 | 108.3525 | 108.3525 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 12 | 2772 | 11.2 | 11.2 | 10.5042 | 11.7793 | 15 | 80 | 80 | 1.0784 | 93.2033 | 50.5262 | 165.7501 | 0 | 0 | 0.43108 | 0.73063 | 0.60219 | 0.12099 | 0 | 0 | 0.79665 | 45.627 | 45.627 | 45.627 | 45.627 | 45.627 | 45.627 | 45.627 | 45.627 | 93.2033 | 45.627 | 45.627 | 46.0581 | 46.3576 | 46.2292 | 45.748 | 45.627 | 45.627 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 13 | 2773 | 8.3 | 8.3 | 10.5042 | 11.7793 | 15 | 90 | 90 | 0.62419 | 74.5164 | 50.9587 | 188.8966 | 0 | 0 | 0.097677 | 0.34103 | 0.38461 | 0.20289 | 0 | 0 | 0.48357 | 36.2458 | 36.2458 | 36.2458 | 36.2458 | 36.2458 | 36.2458 | 36.2458 | 36.2458 | 74.5164 | 36.2458 | 36.2458 | 36.3434 | 36.5868 | 36.6304 | 36.4487 | 36.2458 | 36.2458 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 14 | 2774 | 8.6 | 8.6 | 10.5042 | 11.7793 | 15 | 91 | 91 | 1.7542 | 123.6489 | 47.8116 | 210.8793 | 0 | 0 | 0 | 0.65107 | 1.0916 | 0.89273 | 0.17088 | 0 | 1.3511 | 61.2488 | 61.2488 | 61.2488 | 61.2488 | 61.2488 | 61.2488 | 61.2488 | 61.2488 | 123.6489 | 61.2488 | 61.2488 | 61.2488 | 61.8999 | 62.3405 | 62.1416 | 61.4197 | 61.2488 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 15 | 2775 | 9.6 | 9.6 | 10.5042 | 11.7793 | 15 | 88 | 88 | 7.2286 | 225.7555 | 41.8432 | 229.7326 | 0 | 0 | 0 | 1.1843 | 4.1664 | 4.7078 | 2.4915 | 0 | 5.2445 | 111.2877 | 111.2877 | 111.2877 | 113.4785 | 118.9948 | 119.9963 | 115.8965 | 111.2877 | 225.7555 | 111.2877 | 111.2877 | 111.2877 | 114.6629 | 123.1612 | 124.7042 | 118.388 | 111.2877 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 16 | 2776 | 9.3 | 9.3 | 10.5042 | 11.7793 | 15 | 88 | 88 | 2.6333 | 126.3049 | 34.0689 | 245.4488 | 0 | 0 | 0 | 0 | 1.268 | 1.955 | 1.4969 | 0.16185 | 1.6951 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 126.3049 | 62.7197 | 62.7197 | 62.7197 | 62.7197 | 63.9877 | 64.6747 | 64.2166 | 62.8816 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 17 | 2777 | 8.1 | 8.1 | 10.5042 | 11.7793 | 15 | 92 | 92 | 0.79618 | 57.5776 | 25.3095 | 258.9186 | 0 | 0 | 0 | 0 | 0.27404 | 0.61796 | 0.5999 | 0.23042 | 0.42235 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 57.5776 | 27.7442 | 27.7442 | 27.7442 | 27.7442 | 28.0183 | 28.3622 | 28.3441 | 27.9747 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 26 | 18 | 2778 | 7.8 | 7.8 | 10.5042 | 11.7793 | 15 | 93 | 93 | 0.55744 | 35.7806 | 16.1464 | 271.0843 | 0 | 0 | 0 | 0 | 0.096857 | 0.41818 | 0.49453 | 0.2812 | 0.21935 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 35.7806 | 17.0415 | 17.0415 | 17.0415 | 17.0415 | 17.1383 | 17.4596 | 17.536 | 17.3227 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 19 | 2779 | 8.1 | 8.1 | 10.5042 | 11.7793 | 15 | 95 | 95 | 0.072701 | 7.9824 | 7.0149 | 282.7191 | 0.0013215 | 0 | 0 | 0 | 0 | 0.048437 | 0.069821 | 0.050305 | 0.017604 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 7.9824 | 3.7173 | 3.716 | 3.716 | 3.716 | 3.716 | 3.7644 | 3.7858 | 3.7663 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 20 | 2780 | 9.4 | 9.4 | 10.5042 | 11.7793 | 15 | 95 | 95 | 0 | 0 | -1.7054 | 294.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 21 | 2781 | 7.9 | 7.9 | 10.5042 | 11.7793 | 15 | 95 | 95 | 0 | 0 | -9.6261 | 306.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 22 | 2782 | 7.1 | 7.1 | 10.5042 | 11.7793 | 15 | 94 | 94 | 0 | 0 | -16.3128 | 320.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 23 | 2783 | 7.4 | 7.4 | 10.5042 | 11.7793 | 15 | 93 | 93 | 0 | 0 | -21.2846 | 334.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 26 | 24 | 2784 | 7.8 | 7.8 | 8.0542 | 11.0147 | 15 | 87 | 87 | 0 | 0 | -24.0781 | 350.1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 1 | 2785 | 8.3 | 8.3 | 8.0542 | 11.0147 | 15 | 79 | 79 | 0 | 0 | -24.3783 | 6.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 2 | 2786 | 8.4 | 8.4 | 8.0542 | 11.0147 | 15 | 78 | 78 | 0 | 0 | -21.8252 | 21.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 3 | 2787 | 8.3 | 8.3 | 8.0542 | 11.0147 | 15 | 80 | 80 | 0 | 0 | -17.3337 | 36.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 4 | 2788 | 7.7 | 7.7 | 8.0542 | 11.0147 | 15 | 80 | 80 | 0 | 0 | -11.0168 | 50.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 5 | 2789 | 7.6 | 7.6 | 8.0542 | 11.0147 | 15 | 81 | 81 | 0 | 0 | -3.3559 | 62.5925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 6 | 2790 | 7.2 | 7.2 | 8.0542 | 11.0147 | 15 | 82 | 82 | 0 | 0 | 5.2042 | 74.3998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 7 | 2791 | 8.3 | 8.3 | 8.0542 | 11.0147 | 15 | 77 | 77 | 389.5471 | 48.2544 | 14.2683 | 85.9922 | 104.3266 | 337.9805 | 373.6501 | 190.4405 | 0 | 0 | 0 | 0 | 48.7456 | 41.3319 | 73.2291 | 78.0985 | 53.0877 | 27.0898 | 27.0898 | 27.0898 | 27.0898 | 48.2544 | 145.6584 | 411.2096 | 451.7486 | 243.5282 | 27.0898 | 27.0898 | 27.0898 | 27.0898 | 97 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 27 | 8 | 2792 | 8.9 | 8.9 | 8.0542 | 11.0147 | 15 | 72 | 72 | 269.5751 | 121.4127 | 23.4608 | 97.9627 | 18.2598 | 197.1981 | 260.6204 | 171.3748 | 0 | 0 | 0 | 0 | 75.5873 | 73.166 | 149.3016 | 176.2868 | 138.3142 | 65.3967 | 65.3967 | 65.3967 | 65.3967 | 121.4127 | 91.4258 | 346.4997 | 436.9073 | 309.689 | 65.3967 | 65.3967 | 65.3967 | 65.3967 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 9 | 2793 | 9 | 9 | 8.0542 | 11.0147 | 15 | 69 | 69 | 499.3536 | 143.6527 | 32.3671 | 111.0476 | 0 | 275.9136 | 453.657 | 365.6543 | 63.4562 | 0 | 0 | 0 | 214.3473 | 89.0813 | 157.2676 | 201.1931 | 179.4451 | 104.7632 | 89.0813 | 89.0813 | 89.0813 | 143.6527 | 89.0813 | 433.1812 | 654.8501 | 545.0994 | 168.2194 | 89.0813 | 89.0813 | 89.0813 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 10 | 2794 | 9.8 | 9.8 | 8.0542 | 11.0147 | 15 | 62 | 62 | 212.7544 | 252.5223 | 40.4495 | 126.1646 | 0 | 72.954 | 167.7106 | 164.2247 | 64.5381 | 0 | 0 | 0 | 119.4777 | 122.2607 | 172.31 | 237.3168 | 234.9253 | 166.5364 | 122.2607 | 122.2607 | 122.2607 | 252.5223 | 122.2607 | 245.264 | 405.0274 | 399.1499 | 231.0745 | 122.2607 | 122.2607 | 122.2607 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 11 | 2795 | 10.4 | 10.4 | 8.0542 | 11.0147 | 15 | 66 | 66 | 227.409 | 298.0101 | 46.9446 | 144.2817 | 0 | 26.5804 | 139.7103 | 170.9999 | 102.12 | 0 | 0 | 0 | 151.9899 | 142.6403 | 161.0317 | 239.3081 | 260.9579 | 213.2988 | 142.6403 | 142.6403 | 142.6403 | 298.0101 | 142.6403 | 187.6121 | 379.0184 | 431.9577 | 315.4188 | 142.6403 | 142.6403 | 142.6403 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 12 | 2796 | 11.1 | 11.1 | 8.0542 | 11.0147 | 15 | 60 | 60 | 202.736 | 335.5135 | 50.8514 | 165.7309 | 0 | 0 | 80.8033 | 136.5968 | 112.3737 | 22.3237 | 0 | 0 | 150.4865 | 155.4286 | 155.4286 | 223.4085 | 270.3476 | 249.9688 | 174.2096 | 155.4286 | 155.4286 | 335.5135 | 155.4286 | 155.4286 | 304.2118 | 406.9444 | 362.3425 | 196.5333 | 155.4286 | 155.4286 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 13 | 2797 | 11 | 11 | 8.0542 | 11.0147 | 15 | 63 | 63 | 51.7678 | 337.7119 | 51.2765 | 189.0084 | 0 | 0 | 8.0556 | 28.0934 | 31.6745 | 16.7011 | 0 | 0 | 40.2881 | 149.0205 | 149.0205 | 168.014 | 215.2596 | 223.7032 | 188.3987 | 149.0205 | 149.0205 | 337.7119 | 149.0205 | 149.0205 | 176.0696 | 243.353 | 255.3777 | 205.0998 | 149.0205 | 149.0205 | 378 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 14 | 2798 | 9.6 | 9.6 | 8.0542 | 11.0147 | 15 | 67 | 67 | 12.2553 | 271.5175 | 48.1046 | 211.0907 | 0 | 0 | 0 | 4.5053 | 7.5719 | 6.2029 | 1.2004 | 0 | 9.4825 | 131.2596 | 131.2596 | 131.2596 | 141.3895 | 148.2845 | 145.2065 | 133.9587 | 131.2596 | 271.5175 | 131.2596 | 131.2596 | 131.2596 | 145.8948 | 155.8564 | 151.4095 | 135.1591 | 131.2596 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 15 | 2799 | 10.8 | 10.8 | 8.0542 | 11.0147 | 15 | 61 | 61 | 63.2965 | 322.8498 | 42.1076 | 229.988 | 0 | 0 | 0 | 10.1605 | 36.1959 | 41.0283 | 21.8268 | 0 | 46.1502 | 144.1331 | 144.1331 | 144.1331 | 162.9992 | 211.3419 | 220.3146 | 184.6612 | 144.1331 | 322.8498 | 144.1331 | 144.1331 | 144.1331 | 173.1597 | 247.5379 | 261.3429 | 206.488 | 144.1331 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 16 | 2800 | 10.9 | 10.9 | 8.0542 | 11.0147 | 15 | 59 | 59 | 93.8809 | 295.2189 | 34.311 | 245.7117 | 0 | 0 | 0 | 0 | 44.7807 | 69.3853 | 53.3449 | 6.0557 | 60.7811 | 134.9262 | 134.9262 | 134.9262 | 134.9262 | 188.3961 | 217.7748 | 198.622 | 142.157 | 295.2189 | 134.9262 | 134.9262 | 134.9262 | 134.9262 | 233.1768 | 287.1601 | 251.9668 | 148.2127 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 17 | 2801 | 10.1 | 10.1 | 8.0542 | 11.0147 | 15 | 63 | 63 | 28.887 | 215.565 | 25.5391 | 259.174 | 0 | 0 | 0 | 0 | 9.8144 | 22.3183 | 21.7484 | 8.4386 | 15.435 | 99.3716 | 99.3716 | 99.3716 | 99.3716 | 126.3705 | 160.768 | 159.2002 | 122.5856 | 215.565 | 99.3716 | 99.3716 | 99.3716 | 99.3716 | 136.185 | 183.0863 | 180.9486 | 131.0242 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 27 | 18 | 2802 | 10.6 | 10.6 | 8.0542 | 11.0147 | 15 | 66 | 66 | 31.6541 | 162.4165 | 16.3726 | 271.3281 | 0 | 0 | 0 | 0 | 5.3645 | 23.6297 | 28.0529 | 16.0431 | 12.5835 | 76.4402 | 76.4402 | 76.4402 | 76.4402 | 87.7938 | 126.4502 | 135.8115 | 110.3939 | 162.4165 | 76.4402 | 76.4402 | 76.4402 | 76.4402 | 93.1583 | 150.0799 | 163.8643 | 126.4369 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 19 | 2803 | 9.1 | 9.1 | 8.0542 | 11.0147 | 15 | 73 | 73 | 3.4428 | 55.1518 | 7.2457 | 282.9504 | 0.076559 | 0 | 0 | 0 | 0 | 2.2809 | 3.3023 | 2.3892 | 0.8482 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 55.1518 | 27.0453 | 26.9688 | 26.9688 | 26.9688 | 26.9688 | 29.2497 | 30.2711 | 29.358 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 20 | 2804 | 8.3 | 8.3 | 8.0542 | 11.0147 | 15 | 81 | 81 | 0.51368 | 7.9532 | -1.463 | 294.6621 | 0.1142 | 0 | 0 | 0 | 0 | 0.27041 | 0.49662 | 0.43191 | 0.046805 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 7.9532 | 3.83 | 3.7158 | 3.7158 | 3.7158 | 3.7158 | 3.9862 | 4.2125 | 4.1478 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 21 | 2805 | 8.3 | 8.3 | 8.0542 | 11.0147 | 15 | 85 | 85 | 0 | 0 | -9.3668 | 306.9715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 22 | 2806 | 8.7 | 8.7 | 8.0542 | 11.0147 | 15 | 88 | 88 | 0 | 0 | -16.0328 | 320.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 23 | 2807 | 9.1 | 9.1 | 8.0542 | 11.0147 | 15 | 87 | 87 | 0 | 0 | -20.9839 | 334.7307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 27 | 24 | 2808 | 9.1 | 9.1 | 9.1917 | 10.7078 | 15 | 82 | 82 | 0 | 0 | -23.761 | 350.2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 1 | 2809 | 8.9 | 8.9 | 9.1917 | 10.7078 | 15 | 83 | 83 | 0 | 0 | -24.0532 | 6.1576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 2 | 2810 | 9 | 9 | 9.1917 | 10.7078 | 15 | 84 | 84 | 0 | 0 | -21.5062 | 21.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 3 | 2811 | 8.3 | 8.3 | 9.1917 | 10.7078 | 15 | 87 | 87 | 0 | 0 | -17.024 | 36.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 4 | 2812 | 7.7 | 7.7 | 9.1917 | 10.7078 | 15 | 90 | 90 | 0 | 0 | -10.7197 | 49.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 5 | 2813 | 7.7 | 7.7 | 9.1917 | 10.7078 | 15 | 91 | 91 | 0 | 0 | -3.0711 | 62.4431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 6 | 2814 | 7.8 | 7.8 | 9.1917 | 10.7078 | 15 | 92 | 92 | 0 | 0 | 5.4797 | 74.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 7 | 2815 | 7.9 | 7.9 | 9.1917 | 10.7078 | 15 | 93 | 93 | 0.48121 | 10.9377 | 14.5391 | 85.8133 | 0.13016 | 0.418 | 0.46099 | 0.23393 | 0 | 0 | 0 | 0 | 0.062306 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 10.9377 | 5.3015 | 5.5893 | 5.6323 | 5.4052 | 5.1713 | 5.1713 | 5.1713 | 5.1713 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 28 | 8 | 2816 | 7.8 | 7.8 | 9.1917 | 10.7078 | 15 | 92 | 92 | 0.79144 | 30.7748 | 23.7325 | 97.7752 | 0.05593 | 0.57982 | 0.76405 | 0.50072 | 0 | 0 | 0 | 0 | 0.22519 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 30.7748 | 14.7629 | 15.2867 | 15.471 | 15.2076 | 14.7069 | 14.7069 | 14.7069 | 14.7069 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 9 | 2817 | 8 | 8 | 9.1917 | 10.7078 | 15 | 93 | 93 | 0.38693 | 32.8324 | 32.6464 | 110.8587 | 0 | 0.21428 | 0.35095 | 0.28205 | 0.04792 | 0 | 0 | 0 | 0.16761 | 15.6077 | 15.6077 | 15.6077 | 15.6077 | 15.6077 | 15.6077 | 15.6077 | 15.6077 | 32.8324 | 15.6077 | 15.822 | 15.9587 | 15.8897 | 15.6556 | 15.6077 | 15.6077 | 15.6077 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 10 | 2818 | 8.2 | 8.2 | 9.1917 | 10.7078 | 15 | 94 | 94 | 1.0814 | 71.3886 | 40.7426 | 125.9907 | 0 | 0.37242 | 0.85092 | 0.83095 | 0.32423 | 0 | 0 | 0 | 0.61137 | 34.656 | 34.656 | 34.656 | 34.656 | 34.656 | 34.656 | 34.656 | 34.656 | 71.3886 | 34.656 | 35.0284 | 35.5069 | 35.4869 | 34.9802 | 34.656 | 34.656 | 34.656 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 11 | 2819 | 9.2 | 9.2 | 9.1917 | 10.7078 | 15 | 94 | 94 | 1.3047 | 93.1233 | 47.2548 | 144.1578 | 0 | 0.15479 | 0.7998 | 0.9763 | 0.58089 | 0 | 0 | 0 | 0.8767 | 45.5948 | 45.5948 | 45.5948 | 45.5948 | 45.5948 | 45.5948 | 45.5948 | 45.5948 | 93.1233 | 45.5948 | 45.7496 | 46.3946 | 46.5711 | 46.1757 | 45.5948 | 45.5948 | 45.5948 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 12 | 2820 | 12.1 | 12.1 | 9.1917 | 10.7078 | 15 | 92 | 92 | 7.9588 | 238.0644 | 51.1726 | 165.7088 | 0 | 0 | 3.1631 | 5.3331 | 4.379 | 0.85974 | 0 | 0 | 5.9356 | 116.0958 | 116.0958 | 123.7896 | 129.0676 | 126.7469 | 118.187 | 116.0958 | 116.0958 | 238.0644 | 116.0958 | 116.0958 | 126.9527 | 134.4007 | 131.126 | 119.0467 | 116.0958 | 116.0958 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 13 | 2821 | 12.3 | 12.3 | 9.1917 | 10.7078 | 15 | 85 | 85 | 14.0063 | 281.0512 | 51.5907 | 189.1175 | 0 | 0 | 2.1678 | 7.5502 | 8.5099 | 4.4846 | 0 | 0 | 10.9488 | 134.9998 | 134.9998 | 139.9994 | 152.4135 | 154.6268 | 145.3429 | 134.9998 | 134.9998 | 281.0512 | 134.9998 | 134.9998 | 142.1672 | 159.9637 | 163.1367 | 149.8274 | 134.9998 | 134.9998 | 292 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 14 | 2822 | 12.3 | 12.3 | 9.1917 | 10.7078 | 15 | 86 | 86 | 5.7375 | 223.5407 | 48.3945 | 211.2995 | 0 | 0 | 0 | 2.0893 | 3.5195 | 2.8881 | 0.56484 | 0 | 4.4593 | 111.5001 | 111.5001 | 111.5001 | 114.5115 | 116.5731 | 115.6629 | 112.3143 | 111.5001 | 223.5407 | 111.5001 | 111.5001 | 111.5001 | 116.6008 | 120.0926 | 118.551 | 112.8791 | 111.5001 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 15 | 2823 | 12.1 | 12.1 | 9.1917 | 10.7078 | 15 | 84 | 84 | 8.2435 | 235.9605 | 42.3692 | 230.2403 | 0 | 0 | 0 | 1.2964 | 4.677 | 5.3179 | 2.8436 | 0 | 6.0395 | 115.7038 | 115.7038 | 115.7038 | 118.3312 | 125.1826 | 126.4815 | 121.4669 | 115.7038 | 235.9605 | 115.7038 | 115.7038 | 115.7038 | 119.6276 | 129.8596 | 131.7994 | 124.3105 | 115.7038 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 16 | 2824 | 13.4 | 13.4 | 9.1917 | 10.7078 | 15 | 84 | 84 | 3.9265 | 155.4436 | 34.5509 | 245.9712 | 0 | 0 | 0 | 0 | 1.8554 | 2.8889 | 2.2301 | 0.26496 | 2.5564 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 155.4436 | 78.1236 | 78.1236 | 78.1236 | 78.1236 | 79.9789 | 81.0124 | 80.3536 | 78.3885 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 17 | 2825 | 13.3 | 13.3 | 9.1917 | 10.7078 | 15 | 73 | 73 | 14.6824 | 195.0993 | 25.7667 | 259.4259 | 0 | 0 | 0 | 0 | 4.9241 | 11.2917 | 11.0448 | 4.328 | 7.9007 | 93.7332 | 93.7332 | 93.7332 | 93.7332 | 102.2781 | 113.328 | 112.8995 | 101.2437 | 195.0993 | 93.7332 | 93.7332 | 93.7332 | 93.7332 | 107.2022 | 124.6197 | 123.9443 | 105.5716 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 18 | 2826 | 13.7 | 13.7 | 9.1917 | 10.7078 | 15 | 71 | 71 | 41.0049 | 169.5364 | 16.597 | 271.5681 | 0 | 0 | 0 | 0 | 6.7765 | 30.4602 | 36.3007 | 20.8768 | 16.4636 | 79.6842 | 79.6842 | 79.6842 | 79.6842 | 91.5252 | 132.9092 | 143.1147 | 116.1635 | 169.5364 | 79.6842 | 79.6842 | 79.6842 | 79.6842 | 98.3017 | 163.3694 | 179.4154 | 137.0402 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 19 | 2827 | 13.1 | 13.1 | 9.1917 | 10.7078 | 15 | 70 | 70 | 46.4365 | 107.3655 | 7.4749 | 283.1777 | 1.2178 | 0 | 0 | 0 | 0 | 30.5946 | 44.4852 | 32.3169 | 11.6345 | 53.2469 | 51.7801 | 51.7801 | 51.7801 | 51.7801 | 88.6304 | 105.3611 | 90.7048 | 107.3655 | 54.4648 | 51.7801 | 51.7801 | 51.7801 | 51.7801 | 119.2251 | 149.8463 | 123.0217 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 20 | 2828 | 11.8 | 11.8 | 9.1917 | 10.7078 | 15 | 70 | 70 | 9.8596 | 32.0584 | -1.2225 | 294.8754 | 2.2286 | 0 | 0 | 0 | 0 | 5.1546 | 9.5184 | 8.3064 | 0.94164 | 20.0284 | 16.2461 | 16.2461 | 16.2461 | 16.2461 | 24.9945 | 32.4005 | 30.3435 | 32.0584 | 22.257 | 16.2461 | 16.2461 | 16.2461 | 16.2461 | 30.1491 | 41.9189 | 38.6499 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 21 | 2829 | 11.3 | 11.3 | 9.1917 | 10.7078 | 15 | 71 | 71 | 0 | 0 | -9.1094 | 307.1666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 22 | 2830 | 11.4 | 11.4 | 9.1917 | 10.7078 | 15 | 68 | 68 | 0 | 0 | -15.7553 | 320.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 23 | 2831 | 10.7 | 10.7 | 9.1917 | 10.7078 | 15 | 72 | 72 | 0 | 0 | -20.6861 | 334.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 28 | 24 | 2832 | 7.4 | 7.4 | 10.225 | 10.6271 | 15 | 85 | 85 | 0 | 0 | -23.4473 | 350.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 1 | 2833 | 7.3 | 7.3 | 10.225 | 10.6271 | 15 | 89 | 89 | 0 | 0 | -23.7321 | 6.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 2 | 2834 | 7.7 | 7.7 | 10.225 | 10.6271 | 15 | 82 | 82 | 0 | 0 | -21.1914 | 21.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 3 | 2835 | 7.5 | 7.5 | 10.225 | 10.6271 | 15 | 81 | 81 | 0 | 0 | -16.7188 | 36.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 4 | 2836 | 5.8 | 5.8 | 10.225 | 10.6271 | 15 | 85 | 85 | 0 | 0 | -10.4272 | 49.8361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 5 | 2837 | 6.7 | 6.7 | 10.225 | 10.6271 | 15 | 82 | 82 | 0 | 0 | -2.7907 | 62.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 6 | 2838 | 6.5 | 6.5 | 10.225 | 10.6271 | 15 | 84 | 84 | 0 | 8 | 5.7507 | 74.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 8 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 3.8965 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 7 | 2839 | 7.8 | 7.8 | 10.225 | 10.6271 | 15 | 80 | 80 | 381.3931 | 51.9832 | 14.8053 | 85.6346 | 104.1683 | 331.6787 | 364.8962 | 184.3624 | 0 | 0 | 0 | 0 | 51.0168 | 51.0602 | 95.2917 | 101.7496 | 66.6512 | 30.8083 | 30.8083 | 30.8083 | 30.8083 | 51.9832 | 155.2286 | 426.9704 | 466.6458 | 251.0136 | 30.8083 | 30.8083 | 30.8083 | 30.8083 | 103 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 29 | 8 | 2840 | 8.7 | 8.7 | 10.225 | 10.6271 | 15 | 75 | 75 | 469.312 | 100.5573 | 23.9995 | 97.5876 | 34.5367 | 344.3264 | 452.4144 | 295.4842 | 0 | 0 | 0 | 0 | 135.4427 | 70.2203 | 138.1652 | 161.8718 | 127.4529 | 62.6455 | 62.6455 | 62.6455 | 62.6455 | 100.5573 | 104.7569 | 482.4916 | 614.2861 | 422.937 | 62.6455 | 62.6455 | 62.6455 | 62.6455 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 9 | 2841 | 10.2 | 10.2 | 10.225 | 10.6271 | 15 | 69 | 69 | 775.5361 | 89.0542 | 32.9208 | 110.6691 | 0 | 430.441 | 702.2865 | 562.742 | 93.551 | 0 | 0 | 0 | 338.9458 | 78.127 | 128.603 | 160.4812 | 144.1174 | 89.0973 | 78.127 | 78.127 | 78.127 | 89.0542 | 78.127 | 559.044 | 862.7677 | 706.8594 | 182.6482 | 78.127 | 78.127 | 78.127 | 428 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 10 | 2842 | 8.1 | 8.1 | 10.225 | 10.6271 | 15 | 79 | 79 | 9.9584 | 191.3335 | 41.0309 | 125.8153 | 0 | 3.4441 | 7.8213 | 7.6168 | 2.9506 | 0 | 0 | 0 | 5.6665 | 91.2106 | 101.0044 | 113.4516 | 112.8703 | 99.6011 | 91.2106 | 91.2106 | 91.2106 | 191.3335 | 91.2106 | 104.4485 | 121.2729 | 120.4872 | 102.5517 | 91.2106 | 91.2106 | 91.2106 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 11 | 2843 | 7.6 | 7.6 | 10.225 | 10.6271 | 15 | 87 | 87 | 0.69599 | 68.5299 | 47.5605 | 144.0314 | 0 | 0.083803 | 0.42575 | 0.51829 | 0.30723 | 0 | 0 | 0 | 0.47014 | 33.1933 | 33.1933 | 33.1933 | 33.1933 | 33.1933 | 33.1933 | 33.1933 | 33.1933 | 68.5299 | 33.1933 | 33.2772 | 33.6191 | 33.7116 | 33.5006 | 33.1933 | 33.1933 | 33.1933 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 12 | 2844 | 8 | 8 | 10.225 | 10.6271 | 15 | 88 | 88 | 3.7651 | 175.1791 | 51.4896 | 165.6837 | 0 | 0 | 1.4923 | 2.5092 | 2.0563 | 0.39883 | 0 | 0 | 2.8209 | 88.4989 | 88.4989 | 88.4989 | 88.4989 | 88.4989 | 88.4989 | 88.4989 | 88.4989 | 175.1791 | 88.4989 | 88.4989 | 89.9911 | 91.0081 | 90.5552 | 88.8977 | 88.4989 | 88.4989 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 13 | 2845 | 11.4 | 11.4 | 10.225 | 10.6271 | 15 | 67 | 67 | 241.2965 | 346.5577 | 51.9012 | 189.2238 | 0 | 0 | 37.1518 | 129.2102 | 145.579 | 76.6696 | 0 | 0 | 189.4423 | 155.2653 | 155.2653 | 188.6051 | 271.2178 | 285.9071 | 224.0682 | 155.2653 | 155.2653 | 346.5577 | 155.2653 | 155.2653 | 225.7569 | 400.428 | 431.4861 | 300.7378 | 155.2653 | 155.2653 | 536 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 14 | 2846 | 12.3 | 12.3 | 10.225 | 10.6271 | 15 | 60 | 60 | 213.2714 | 350.5162 | 48.6811 | 211.5055 | 0 | 0 | 0 | 76.9316 | 129.8909 | 106.7618 | 21.0931 | 0 | 166.4838 | 161.7203 | 161.7203 | 161.7203 | 224.4421 | 267.6195 | 248.7625 | 178.9174 | 161.7203 | 350.5162 | 161.7203 | 161.7203 | 161.7203 | 301.3738 | 397.5104 | 355.5244 | 200.0105 | 161.7203 | 517 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 15 | 2847 | 11.8 | 11.8 | 10.225 | 10.6271 | 15 | 62 | 62 | 25.8248 | 291.9905 | 42.628 | 230.4895 | 0 | 0 | 0 | 3.9788 | 14.5373 | 16.58 | 8.9104 | 0 | 19.0095 | 138.6089 | 138.6089 | 138.6089 | 145.3118 | 163.099 | 166.5402 | 153.6196 | 138.6089 | 291.9905 | 138.6089 | 138.6089 | 138.6089 | 149.2906 | 177.6363 | 183.1202 | 162.53 | 138.6089 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 16 | 2848 | 12 | 12 | 10.225 | 10.6271 | 15 | 69 | 69 | 1.5566 | 98.981 | 34.7884 | 246.2273 | 0 | 0 | 0 | 0 | 0.72864 | 1.14 | 0.88359 | 0.10956 | 1.019 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 98.981 | 48.5804 | 48.5804 | 48.5804 | 48.5804 | 49.3091 | 49.7204 | 49.464 | 48.69 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 17 | 2849 | 12.1 | 12.1 | 10.225 | 10.6271 | 15 | 71 | 71 | 28.2359 | 217.7009 | 25.9923 | 259.6741 | 0 | 0 | 0 | 0 | 9.3478 | 21.6158 | 21.2216 | 8.3961 | 15.2991 | 100.2498 | 100.2498 | 100.2498 | 100.2498 | 126.6674 | 161.3378 | 160.2237 | 123.9777 | 217.7009 | 100.2498 | 100.2498 | 100.2498 | 100.2498 | 136.0151 | 182.9536 | 181.4453 | 132.3738 | 233 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 18 | 2850 | 12 | 12 | 10.225 | 10.6271 | 15 | 68 | 68 | 28.7834 | 163.3308 | 16.8197 | 271.8043 | 0 | 0 | 0 | 0 | 4.6375 | 21.2772 | 25.453 | 14.7188 | 11.6692 | 76.8089 | 76.8089 | 76.8089 | 76.8089 | 87.4895 | 125.8125 | 135.4298 | 110.7078 | 163.3308 | 76.8089 | 76.8089 | 76.8089 | 76.8089 | 92.127 | 147.0897 | 160.8828 | 125.4266 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 19 | 2851 | 11.3 | 11.3 | 10.225 | 10.6271 | 15 | 71 | 71 | 1.333 | 35.6605 | 7.7023 | 283.4011 | 0.040175 | 0 | 0 | 0 | 0 | 0.87339 | 1.2753 | 0.9302 | 0.33947 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 35.6605 | 17.1217 | 17.0815 | 17.0815 | 17.0815 | 17.0815 | 17.9549 | 18.3568 | 18.0117 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 20 | 2852 | 10.5 | 10.5 | 10.225 | 10.6271 | 15 | 73 | 73 | 103.3041 | 45.6863 | -0.9837 | 295.0845 | 23.7264 | 0 | 0 | 0 | 0 | 53.6399 | 99.5846 | 87.1941 | 10.3137 | 43.0212 | 24.6588 | 24.6588 | 24.6588 | 24.6588 | 66.172 | 101.7297 | 92.1403 | 45.6863 | 66.7476 | 24.6588 | 24.6588 | 24.6588 | 24.6588 | 119.8118 | 201.3143 | 179.3344 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 21 | 2853 | 10.9 | 10.9 | 10.225 | 10.6271 | 15 | 74 | 74 | 0 | 0 | -8.8541 | 307.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 22 | 2854 | 9.5 | 9.5 | 10.225 | 10.6271 | 15 | 73 | 73 | 0 | 0 | -15.4802 | 320.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 23 | 2855 | 9.7 | 9.7 | 10.225 | 10.6271 | 15 | 68 | 68 | 0 | 0 | -20.3913 | 334.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 29 | 24 | 2856 | 9.9 | 9.9 | 9.3875 | 10.1234 | 15 | 64 | 64 | 0 | 0 | -23.1372 | 350.3613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 1 | 2857 | 8.3 | 8.3 | 9.3875 | 10.1234 | 15 | 78 | 78 | 0 | 0 | -23.4149 | 6.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 2 | 2858 | 8.6 | 8.6 | 9.3875 | 10.1234 | 15 | 85 | 85 | 0 | 0 | -20.881 | 21.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 3 | 2859 | 8.8 | 8.8 | 9.3875 | 10.1234 | 15 | 83 | 83 | 0 | 0 | -16.418 | 36.2579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 4 | 2860 | 8 | 8 | 9.3875 | 10.1234 | 15 | 87 | 87 | 0 | 0 | -10.1391 | 49.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 5 | 2861 | 8.1 | 8.1 | 9.3875 | 10.1234 | 15 | 90 | 90 | 0 | 0 | -2.5149 | 62.1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 6 | 2862 | 7.9 | 7.9 | 9.3875 | 10.1234 | 15 | 91 | 91 | 0 | 0 | 6.0172 | 73.9017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 7 | 2863 | 8.2 | 8.2 | 9.3875 | 10.1234 | 15 | 92 | 92 | 3.3681 | 30.5352 | 15.0668 | 85.4562 | 0.92879 | 2.9324 | 3.2182 | 1.6189 | 0 | 0 | 0 | 0 | 0.46478 | 16.2079 | 19.0081 | 19.4076 | 17.1724 | 14.9098 | 14.9098 | 14.9098 | 14.9098 | 30.5352 | 17.1367 | 21.9405 | 22.6258 | 18.7912 | 14.9098 | 14.9098 | 14.9098 | 14.9098 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2002 | 4 | 30 | 8 | 2864 | 9.1 | 9.1 | 9.3875 | 10.1234 | 15 | 91 | 91 | 34.6779 | 120.8528 | 24.2619 | 97.4 | 2.6528 | 25.4795 | 33.3806 | 21.7278 | 0 | 0 | 0 | 0 | 10.1472 | 62.5952 | 117.0186 | 135.8565 | 108.0739 | 56.2703 | 56.2703 | 56.2703 | 56.2703 | 120.8528 | 65.248 | 142.498 | 169.2371 | 129.8017 | 56.2703 | 56.2703 | 56.2703 | 56.2703 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 9 | 2865 | 9.4 | 9.4 | 9.3875 | 10.1234 | 15 | 86 | 86 | 7.0373 | 135.8976 | 33.1905 | 110.4789 | 0 | 3.9145 | 6.3623 | 5.0831 | 0.82633 | 0 | 0 | 0 | 3.1024 | 65.1545 | 76.5767 | 83.719 | 79.9865 | 67.5656 | 65.1545 | 65.1545 | 65.1545 | 135.8976 | 65.1545 | 80.4912 | 90.0813 | 85.0696 | 68.392 | 65.1545 | 65.1545 | 65.1545 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 10 | 2866 | 10.3 | 10.3 | 9.3875 | 10.1234 | 15 | 80 | 80 | 11.0505 | 196.6721 | 41.3145 | 125.6384 | 0 | 3.838 | 8.6632 | 8.4136 | 3.2354 | 0 | 0 | 0 | 6.3279 | 93.4302 | 104.2127 | 117.7686 | 117.0673 | 102.5197 | 93.4302 | 93.4302 | 93.4302 | 196.6721 | 93.4302 | 108.0508 | 126.4318 | 125.4809 | 105.7551 | 93.4302 | 93.4302 | 93.4302 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 11 | 2867 | 9.9 | 9.9 | 9.3875 | 10.1234 | 15 | 84 | 84 | 4.8481 | 179.7083 | 47.8615 | 143.9025 | 0 | 0.59232 | 2.9594 | 3.5929 | 2.1217 | 0 | 0 | 0 | 3.2917 | 89.7141 | 90.2976 | 92.6293 | 93.2533 | 91.8041 | 89.7141 | 89.7141 | 89.7141 | 179.7083 | 89.7141 | 90.8899 | 95.5886 | 96.8461 | 93.9258 | 89.7141 | 89.7141 | 89.7141 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 12 | 2868 | 10.8 | 10.8 | 9.3875 | 10.1234 | 15 | 79 | 79 | 1.9305 | 126.5471 | 51.8024 | 165.6555 | 0 | 0 | 0.76309 | 1.2796 | 1.0465 | 0.20044 | 0 | 0 | 1.4529 | 62.7603 | 62.7603 | 62.7603 | 62.7603 | 62.7603 | 62.7603 | 62.7603 | 62.7603 | 126.5471 | 62.7603 | 62.7603 | 63.5233 | 64.0399 | 63.8068 | 62.9607 | 62.7603 | 62.7603 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 13 | 2869 | 11.4 | 11.4 | 9.3875 | 10.1234 | 15 | 76 | 76 | 0.79406 | 85.3739 | 52.208 | 189.3272 | 0 | 0 | 0.12165 | 0.4224 | 0.47572 | 0.25036 | 0 | 0 | 0.62606 | 41.7105 | 41.7105 | 41.7105 | 41.7105 | 41.7105 | 41.7105 | 41.7105 | 41.7105 | 85.3739 | 41.7105 | 41.7105 | 41.8322 | 42.1329 | 42.1862 | 41.9609 | 41.7105 | 41.7105 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 14 | 2870 | 11.9 | 11.9 | 9.3875 | 10.1234 | 15 | 75 | 75 | 0.95952 | 93.2478 | 48.9644 | 211.7085 | 0 | 0 | 0 | 0.34289 | 0.58022 | 0.47766 | 0.095297 | 0 | 0.75222 | 45.6933 | 45.6933 | 45.6933 | 45.6933 | 45.6933 | 45.6933 | 45.6933 | 45.6933 | 93.2478 | 45.6933 | 45.6933 | 45.6933 | 46.0362 | 46.2735 | 46.171 | 45.7886 | 45.6933 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 15 | 2871 | 12.5 | 12.5 | 9.3875 | 10.1234 | 15 | 73 | 73 | 2.2573 | 134.3307 | 42.884 | 230.7354 | 0 | 0 | 0 | 0.34072 | 1.2608 | 1.4423 | 0.77893 | 0 | 1.6693 | 66.8156 | 66.8156 | 66.8156 | 66.8156 | 66.8156 | 66.8156 | 66.8156 | 66.8156 | 134.3307 | 66.8156 | 66.8156 | 66.8156 | 67.1563 | 68.0764 | 68.2579 | 67.5945 | 66.8156 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 16 | 2872 | 13.1 | 13.1 | 9.3875 | 10.1234 | 15 | 71 | 71 | 7.4322 | 206.1086 | 35.0234 | 246.4797 | 0 | 0 | 0 | 0 | 3.4467 | 5.4186 | 4.2163 | 0.54423 | 4.8914 | 101.3988 | 101.3988 | 101.3988 | 101.3988 | 107.3488 | 110.7528 | 108.6774 | 102.3383 | 206.1086 | 101.3988 | 101.3988 | 101.3988 | 101.3988 | 110.7954 | 116.1714 | 112.8938 | 102.8825 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 17 | 2873 | 12.5 | 12.5 | 9.3875 | 10.1234 | 15 | 72 | 72 | 6.4493 | 163.482 | 26.2158 | 259.9184 | 0 | 0 | 0 | 0 | 2.1077 | 4.9146 | 4.8426 | 1.9339 | 3.518 | 80.8306 | 80.8306 | 80.8306 | 80.8306 | 83.3372 | 86.6755 | 86.5899 | 83.1306 | 163.482 | 80.8306 | 80.8306 | 80.8306 | 80.8306 | 85.4449 | 91.5901 | 91.4325 | 85.0645 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2002 | 4 | 30 | 18 | 2874 | 12.7 | 12.7 | 9.3875 | 10.1234 | 15 | 73 | 73 | 1.2495 | 55.4886 | 17.0405 | 272.0366 | 0 | 0 | 0 | 0 | 0.19623 | 0.91919 | 1.1037 | 0.64168 | 0.51139 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 55.4886 | 26.7727 | 26.7727 | 26.7727 | 26.7727 | 26.9689 | 27.6919 | 27.8764 | 27.4144 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 19 | 2875 | 12.7 | 12.7 | 9.3875 | 10.1234 | 15 | 76 | 76 | 3.7099 | 60.0401 | 7.9279 | 283.6204 | 0.12606 | 0 | 0 | 0 | 0 | 2.4174 | 3.5448 | 2.5957 | 0.95985 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 60.0401 | 29.579 | 29.4529 | 29.4529 | 29.4529 | 29.4529 | 31.8703 | 32.9977 | 32.0486 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 20 | 2876 | 13.4 | 13.4 | 9.3875 | 10.1234 | 15 | 73 | 73 | 1.7794 | 16.8147 | -0.74683 | 295.2895 | 0.41502 | 0 | 0 | 0 | 0 | 0.91767 | 1.7128 | 1.5046 | 0.18526 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 16.8147 | 8.4122 | 7.9972 | 7.9972 | 7.9972 | 7.9972 | 8.9149 | 9.71 | 9.5018 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 21 | 2877 | 13 | 13 | 9.3875 | 10.1234 | 15 | 73 | 73 | 0 | 0 | -8.6009 | 307.5441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 22 | 2878 | 13.1 | 13.1 | 9.3875 | 10.1234 | 15 | 74 | 74 | 0 | 0 | -15.2077 | 320.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 23 | 2879 | 13.2 | 13.2 | 9.3875 | 10.1234 | 15 | 78 | 78 | 0 | 0 | -20.0995 | 335.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2002 | 4 | 30 | 24 | 2880 | 11.5 | 11.5 | 10.7667 | 10.09 | 15 | 92 | 92 | 0 | 0 | -22.8307 | 350.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 1 | 2881 | 10.2 | 10.2 | 10.7667 | 10.09 | 15 | 92 | 92 | 0 | 0 | -23.1019 | 6.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 2 | 2882 | 11.4 | 11.4 | 10.7667 | 10.09 | 15 | 92 | 92 | 0 | 0 | -20.5751 | 21.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 3 | 2883 | 11.5 | 11.5 | 10.7667 | 10.09 | 15 | 92 | 92 | 0 | 0 | -16.1218 | 36.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 4 | 2884 | 11.5 | 11.5 | 10.7667 | 10.09 | 15 | 93 | 93 | 0 | 0 | -9.8556 | 49.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 5 | 2885 | 11.5 | 11.5 | 10.7667 | 10.09 | 15 | 94 | 94 | 0 | 0 | -2.2438 | 61.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 6 | 2886 | 11.6 | 11.6 | 10.7667 | 10.09 | 15 | 94 | 94 | 0 | 0 | 6.2789 | 73.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 7 | 2887 | 11.5 | 11.5 | 10.7667 | 10.09 | 15 | 91 | 91 | 1.1927 | 18.8304 | 15.3237 | 85.2781 | 0.33201 | 1.0395 | 1.1381 | 0.56998 | 0 | 0 | 0 | 0 | 0.16956 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 18.8304 | 9.3882 | 10.0957 | 10.1942 | 9.6261 | 9.0561 | 9.0561 | 9.0561 | 9.0561 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 1 | 8 | 2888 | 11.7 | 11.7 | 10.7667 | 10.09 | 15 | 91 | 91 | 2.3809 | 55.2939 | 24.5194 | 97.2125 | 0.18903 | 1.7518 | 2.2884 | 1.4845 | 0 | 0 | 0 | 0 | 0.70609 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 55.2939 | 27.2942 | 28.857 | 29.3936 | 28.5897 | 27.1052 | 27.1052 | 27.1052 | 27.1052 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 9 | 2889 | 11.9 | 11.9 | 10.7667 | 10.09 | 15 | 92 | 92 | 2.6757 | 87.8104 | 33.4552 | 110.2881 | 0 | 1.4917 | 2.4152 | 1.9239 | 0.30564 | 0 | 0 | 0 | 1.1896 | 43.3614 | 43.3614 | 43.3614 | 43.3614 | 43.3614 | 43.3614 | 43.3614 | 43.3614 | 87.8104 | 43.3614 | 44.853 | 45.7765 | 45.2853 | 43.667 | 43.3614 | 43.3614 | 43.3614 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 10 | 2890 | 12.6 | 12.6 | 10.7667 | 10.09 | 15 | 87 | 87 | 11.4961 | 199.376 | 41.5931 | 125.4601 | 0 | 4.0097 | 8.9963 | 8.713 | 3.3257 | 0 | 0 | 0 | 6.624 | 94.6122 | 105.7777 | 119.6634 | 118.8744 | 103.873 | 94.6122 | 94.6122 | 94.6122 | 199.376 | 94.6122 | 109.7874 | 128.6597 | 127.5874 | 107.1987 | 94.6122 | 94.6122 | 94.6122 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 11 | 2891 | 13.2 | 13.2 | 10.7667 | 10.09 | 15 | 85 | 85 | 15.7845 | 250.2287 | 48.1578 | 143.7712 | 0 | 1.9565 | 9.6153 | 11.6416 | 6.8484 | 0 | 0 | 0 | 10.7713 | 118.5143 | 123.2734 | 141.9035 | 146.8325 | 135.1731 | 118.5143 | 118.5143 | 118.5143 | 250.2287 | 118.5143 | 125.2299 | 151.5188 | 158.4741 | 142.0215 | 118.5143 | 118.5143 | 118.5143 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 12 | 2892 | 14.7 | 14.7 | 10.7667 | 10.09 | 15 | 81 | 81 | 114.1153 | 346.738 | 52.1108 | 165.6243 | 0 | 0 | 44.9903 | 75.234 | 61.4066 | 11.6081 | 0 | 0 | 86.262 | 152.6236 | 152.6236 | 222.0915 | 268.7895 | 247.4392 | 170.5472 | 152.6236 | 152.6236 | 346.738 | 152.6236 | 152.6236 | 267.0818 | 344.0235 | 308.8458 | 182.1552 | 152.6236 | 152.6236 | 433 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 13 | 2893 | 15.4 | 15.4 | 10.7667 | 10.09 | 15 | 76 | 76 | 155.1943 | 363.1334 | 52.5109 | 189.4275 | 0 | 0 | 23.6636 | 82.0172 | 92.3262 | 48.5518 | 0 | 0 | 122.8666 | 161.4157 | 161.4157 | 189.1232 | 257.4489 | 269.5196 | 218.2646 | 161.4157 | 161.4157 | 363.1334 | 161.4157 | 161.4157 | 212.7868 | 339.466 | 361.8458 | 266.8164 | 161.4157 | 161.4157 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 14 | 2894 | 16.3 | 16.3 | 10.7667 | 10.09 | 15 | 75 | 75 | 184.2326 | 357.9676 | 49.2443 | 211.9084 | 0 | 0 | 0 | 65.2274 | 110.6116 | 91.201 | 18.3662 | 0 | 145.0324 | 161.9235 | 161.9235 | 161.9235 | 224.9461 | 268.7964 | 250.0419 | 179.6689 | 161.9235 | 357.9676 | 161.9235 | 161.9235 | 161.9235 | 290.1735 | 379.408 | 341.243 | 198.035 | 161.9235 | 503 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 15 | 2895 | 16.6 | 16.6 | 10.7667 | 10.09 | 15 | 75 | 75 | 48.8503 | 319.713 | 43.1371 | 230.9779 | 0 | 0 | 0 | 7.2236 | 27.0722 | 31.0623 | 16.8565 | 0 | 36.287 | 142.0708 | 142.0708 | 142.0708 | 158.9482 | 205.3228 | 214.6452 | 181.4545 | 142.0708 | 319.713 | 142.0708 | 142.0708 | 142.0708 | 166.1719 | 232.395 | 245.7074 | 198.3109 | 142.0708 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 16 | 2896 | 16.2 | 16.2 | 10.7667 | 10.09 | 15 | 77 | 77 | 87.7728 | 299.9314 | 35.2561 | 246.7284 | 0 | 0 | 0 | 0 | 40.3269 | 63.7013 | 49.7603 | 6.6704 | 58.0686 | 136.468 | 136.468 | 136.468 | 136.468 | 188.3797 | 218.4689 | 200.5231 | 145.0546 | 299.9314 | 136.468 | 136.468 | 136.468 | 136.468 | 228.7066 | 282.1702 | 250.2834 | 151.7251 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 17 | 2897 | 14.7 | 14.7 | 10.7667 | 10.09 | 15 | 79 | 79 | 329.7166 | 224.9553 | 26.4372 | 260.1589 | 0 | 0 | 0 | 0 | 106.3742 | 250.1103 | 247.3352 | 99.6745 | 181.0447 | 117.3023 | 117.3023 | 117.3023 | 117.3023 | 167.3027 | 234.8649 | 233.5605 | 164.1536 | 224.9553 | 117.3023 | 117.3023 | 117.3023 | 117.3023 | 273.6769 | 484.9752 | 480.8957 | 263.8282 | 406 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 1 | 18 | 2898 | 13.8 | 13.8 | 10.7667 | 10.09 | 15 | 84 | 84 | 13.5367 | 147.4086 | 17.2594 | 272.2649 | 0 | 0 | 0 | 0 | 2.0717 | 9.9097 | 11.9427 | 6.9799 | 5.5914 | 70.9563 | 70.9563 | 70.9563 | 70.9563 | 74.144 | 86.2042 | 89.3324 | 81.6962 | 147.4086 | 70.9563 | 70.9563 | 70.9563 | 70.9563 | 76.2157 | 96.1139 | 101.2752 | 88.676 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 19 | 2899 | 12.8 | 12.8 | 10.7667 | 10.09 | 15 | 87 | 87 | 3.2543 | 57.145 | 8.1517 | 283.8356 | 0.12282 | 0 | 0 | 0 | 0 | 2.109 | 3.1053 | 2.2827 | 0.85498 | 27.939 | 27.939 | 27.939 | 27.939 | 27.939 | 27.939 | 27.939 | 27.939 | 57.145 | 28.0618 | 27.939 | 27.939 | 27.939 | 27.939 | 30.048 | 31.0444 | 30.2217 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 20 | 2900 | 12.3 | 12.3 | 10.7667 | 10.09 | 15 | 89 | 89 | 0.68847 | 10.9254 | -0.51192 | 295.4903 | 0.16297 | 0 | 0 | 0 | 0 | 0.35268 | 0.66174 | 0.58316 | 0.074582 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 10.9254 | 5.2925 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.4822 | 5.7912 | 5.7127 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 21 | 2901 | 12 | 12 | 10.7667 | 10.09 | 15 | 91 | 91 | 0 | 0 | -8.3499 | 307.7264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 22 | 2902 | 11.3 | 11.3 | 10.7667 | 10.09 | 15 | 93 | 93 | 0 | 0 | -14.9378 | 320.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 23 | 2903 | 10.6 | 10.6 | 10.7667 | 10.09 | 15 | 94 | 94 | 0 | 0 | -19.811 | 335.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 1 | 24 | 2904 | 10.1 | 10.1 | 12.725 | 10.5992 | 15 | 95 | 95 | 0 | 0 | -22.5279 | 350.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 1 | 2905 | 9.6 | 9.6 | 12.725 | 10.5992 | 15 | 97 | 97 | 0 | 0 | -22.793 | 6.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 2 | 2906 | 9.5 | 9.5 | 12.725 | 10.5992 | 15 | 97 | 97 | 0 | 0 | -20.2737 | 21.5802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 3 | 2907 | 9.4 | 9.4 | 12.725 | 10.5992 | 15 | 98 | 98 | 0 | 0 | -15.8302 | 36.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 4 | 2908 | 9.4 | 9.4 | 12.725 | 10.5992 | 15 | 97 | 97 | 0 | 0 | -9.5768 | 49.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 5 | 2909 | 9.5 | 9.5 | 12.725 | 10.5992 | 15 | 96 | 96 | 0 | 0 | -1.9773 | 61.8493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 6 | 2910 | 9.7 | 9.7 | 12.725 | 10.5992 | 15 | 95 | 95 | 0 | 0 | 6.5359 | 73.5719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 7 | 2911 | 9.4 | 9.4 | 12.725 | 10.5992 | 15 | 95 | 95 | 0.1124 | 5.9836 | 15.5757 | 85.1004 | 0.031582 | 0.098073 | 0.10711 | 0.053409 | 0 | 0 | 0 | 0 | 0.016442 | 2.784 | 2.784 | 2.784 | 2.784 | 2.784 | 2.784 | 2.784 | 2.784 | 5.9836 | 2.8156 | 2.8821 | 2.8911 | 2.8374 | 2.784 | 2.784 | 2.784 | 2.784 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 2 | 8 | 2912 | 9.1 | 9.1 | 12.725 | 10.5992 | 15 | 96 | 96 | 0.35818 | 21.8924 | 24.7719 | 97.025 | 0.029469 | 0.26392 | 0.34377 | 0.22224 | 0 | 0 | 0 | 0 | 0.10762 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 21.8924 | 10.376 | 10.6105 | 10.6903 | 10.5688 | 10.3466 | 10.3466 | 10.3466 | 10.3466 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 9 | 2913 | 9.4 | 9.4 | 12.725 | 10.5992 | 15 | 96 | 96 | 0.43085 | 35.8069 | 33.7149 | 110.0969 | 0 | 0.24071 | 0.38826 | 0.30838 | 0.047845 | 0 | 0 | 0 | 0.19314 | 17.0545 | 17.0545 | 17.0545 | 17.0545 | 17.0545 | 17.0545 | 17.0545 | 17.0545 | 35.8069 | 17.0545 | 17.2952 | 17.4428 | 17.3629 | 17.1023 | 17.0545 | 17.0545 | 17.0545 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 10 | 2914 | 9.9 | 9.9 | 12.725 | 10.5992 | 15 | 96 | 96 | 0.66877 | 57.6123 | 41.8667 | 125.2804 | 0 | 0.23424 | 0.52242 | 0.50456 | 0.19114 | 0 | 0 | 0 | 0.38768 | 27.7609 | 27.7609 | 27.7609 | 27.7609 | 27.7609 | 27.7609 | 27.7609 | 27.7609 | 57.6123 | 27.7609 | 27.9951 | 28.2833 | 28.2654 | 27.952 | 27.7609 | 27.7609 | 27.7609 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 11 | 2915 | 10.1 | 10.1 | 12.725 | 10.5992 | 15 | 94 | 94 | 0.93211 | 80.3608 | 48.4492 | 143.6374 | 0 | 0.11719 | 0.56665 | 0.68417 | 0.40092 | 0 | 0 | 0 | 0.63919 | 39.1285 | 39.1285 | 39.1285 | 39.1285 | 39.1285 | 39.1285 | 39.1285 | 39.1285 | 80.3608 | 39.1285 | 39.2457 | 39.6952 | 39.8127 | 39.5294 | 39.1285 | 39.1285 | 39.1285 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 12 | 2916 | 10.1 | 10.1 | 12.725 | 10.5992 | 15 | 95 | 95 | 1.1592 | 99.12 | 52.4147 | 165.59 | 0 | 0 | 0.45585 | 0.76014 | 0.61914 | 0.11547 | 0 | 0 | 0.88 | 48.648 | 48.648 | 48.648 | 48.648 | 48.648 | 48.648 | 48.648 | 48.648 | 99.12 | 48.648 | 48.648 | 49.1038 | 49.4081 | 49.2671 | 48.7634 | 48.648 | 48.648 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 13 | 2917 | 10.8 | 10.8 | 12.725 | 10.5992 | 15 | 92 | 92 | 3.1279 | 169.5136 | 52.8098 | 189.5247 | 0 | 0 | 0.47479 | 1.6423 | 1.8478 | 0.97089 | 0 | 0 | 2.4864 | 85.3631 | 85.3631 | 85.3631 | 85.3631 | 85.3631 | 85.3631 | 85.3631 | 85.3631 | 169.5136 | 85.3631 | 85.3631 | 85.8379 | 87.0055 | 87.211 | 86.334 | 85.3631 | 85.3631 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 14 | 2918 | 11.6 | 11.6 | 12.725 | 10.5992 | 15 | 89 | 89 | 2.3106 | 145.1736 | 49.5208 | 212.105 | 0 | 0 | 0 | 0.81057 | 1.3774 | 1.1374 | 0.23111 | 0 | 1.8264 | 72.4806 | 72.4806 | 72.4806 | 72.4806 | 72.4806 | 72.4806 | 72.4806 | 72.4806 | 145.1736 | 72.4806 | 72.4806 | 72.4806 | 73.2911 | 73.858 | 73.618 | 72.7117 | 72.4806 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 15 | 2919 | 11.8 | 11.8 | 12.725 | 10.5992 | 15 | 88 | 88 | 2.4887 | 142.1432 | 43.3872 | 231.2168 | 0 | 0 | 0 | 0.36054 | 1.3685 | 1.5748 | 0.85863 | 0 | 1.8568 | 70.9071 | 70.9071 | 70.9071 | 70.9071 | 70.9071 | 70.9071 | 70.9071 | 70.9071 | 142.1432 | 70.9071 | 70.9071 | 70.9071 | 71.2676 | 72.2756 | 72.4819 | 71.7657 | 70.9071 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 16 | 2920 | 11.8 | 11.8 | 12.725 | 10.5992 | 15 | 88 | 88 | 2.2488 | 120.5046 | 35.4863 | 246.9732 | 0 | 0 | 0 | 0 | 1.0237 | 1.6247 | 1.274 | 0.17698 | 1.4954 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 120.5046 | 59.6749 | 59.6749 | 59.6749 | 59.6749 | 60.6985 | 61.2995 | 60.9488 | 59.8518 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 17 | 2921 | 11.9 | 11.9 | 12.725 | 10.5992 | 15 | 87 | 87 | 2.3208 | 101.7175 | 26.6565 | 260.3954 | 0 | 0 | 0 | 0 | 0.73918 | 1.7524 | 1.7391 | 0.70707 | 1.2825 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 101.7175 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.8418 | 51.8551 | 51.8418 | 50.8097 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 2 | 18 | 2922 | 11.8 | 11.8 | 12.725 | 10.5992 | 15 | 86 | 86 | 2.1634 | 74.0984 | 17.4763 | 272.489 | 0 | 0 | 0 | 0 | 0.32259 | 1.5761 | 1.9063 | 1.1199 | 0.90165 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 74.0984 | 36.1764 | 36.1764 | 36.1764 | 36.1764 | 36.499 | 37.7525 | 38.0827 | 37.2963 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 19 | 2923 | 11.4 | 11.4 | 12.725 | 10.5992 | 15 | 87 | 87 | 1.429 | 38.6189 | 8.3736 | 284.0466 | 0.059194 | 0 | 0 | 0 | 0 | 0.92103 | 1.3617 | 1.0047 | 0.38105 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 38.6189 | 18.5963 | 18.5371 | 18.5371 | 18.5371 | 18.5371 | 19.4582 | 19.8989 | 19.5419 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 20 | 2924 | 11 | 11 | 12.725 | 10.5992 | 15 | 89 | 89 | 0.19007 | 5.9786 | -0.27903 | 295.6868 | 0.04564 | 0 | 0 | 0 | 0 | 0.096717 | 0.18242 | 0.16126 | 0.02138 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 5.9786 | 2.8234 | 2.7777 | 2.7777 | 2.7777 | 2.7777 | 2.8744 | 2.9601 | 2.939 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 21 | 2925 | 10.7 | 10.7 | 12.725 | 10.5992 | 15 | 90 | 90 | 0 | 0 | -8.1013 | 307.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 22 | 2926 | 10.3 | 10.3 | 12.725 | 10.5992 | 15 | 92 | 92 | 0 | 0 | -14.6706 | 321.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 23 | 2927 | 10.2 | 10.2 | 12.725 | 10.5992 | 15 | 92 | 92 | 0 | 0 | -19.5257 | 335.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 2 | 24 | 2928 | 10.1 | 10.1 | 10.3542 | 10.5648 | 15 | 92 | 92 | 0 | 0 | -22.229 | 350.5622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 1 | 2929 | 10 | 10 | 10.3542 | 10.5648 | 15 | 92 | 92 | 0 | 0 | -22.4884 | 6.2147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 2 | 2930 | 10 | 10 | 10.3542 | 10.5648 | 15 | 92 | 92 | 0 | 0 | -19.9769 | 21.5315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 3 | 2931 | 10.2 | 10.2 | 10.3542 | 10.5648 | 15 | 92 | 92 | 0 | 0 | -15.5434 | 35.9817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 4 | 2932 | 10.1 | 10.1 | 10.3542 | 10.5648 | 15 | 93 | 93 | 0 | 0 | -9.3028 | 49.3368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 5 | 2933 | 10 | 10 | 10.3542 | 10.5648 | 15 | 93 | 93 | 0 | 0 | -1.7156 | 61.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 6 | 2934 | 10.1 | 10.1 | 10.3542 | 10.5648 | 15 | 93 | 93 | 0 | 0 | 6.7882 | 73.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 7 | 2935 | 10.4 | 10.4 | 10.3542 | 10.5648 | 15 | 94 | 94 | 0.10648 | 5.984 | 15.8228 | 84.9232 | 0.030193 | 0.093003 | 0.10133 | 0.050303 | 0 | 0 | 0 | 0 | 0.016007 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 5.984 | 2.8136 | 2.8764 | 2.8847 | 2.8337 | 2.7834 | 2.7834 | 2.7834 | 2.7834 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 3 | 8 | 2936 | 10.7 | 10.7 | 10.3542 | 10.5648 | 15 | 94 | 94 | 0.2606 | 18.9207 | 25.0196 | 96.8377 | 0.022187 | 0.19228 | 0.24974 | 0.16091 | 0 | 0 | 0 | 0 | 0.079298 | 8.912 | 8.912 | 8.912 | 8.912 | 8.912 | 8.912 | 8.912 | 8.912 | 18.9207 | 8.9342 | 9.1043 | 9.1617 | 9.0729 | 8.912 | 8.912 | 8.912 | 8.912 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 9 | 2937 | 10.9 | 10.9 | 10.3542 | 10.5648 | 15 | 91 | 91 | 1.0264 | 55.5362 | 33.9696 | 109.9053 | 0 | 0.5747 | 0.92349 | 0.73131 | 0.11074 | 0 | 0 | 0 | 0.46384 | 26.8121 | 26.8121 | 26.8121 | 26.8121 | 26.8121 | 26.8121 | 26.8121 | 26.8121 | 55.5362 | 26.8121 | 27.3868 | 27.7356 | 27.5434 | 26.9229 | 26.8121 | 26.8121 | 26.8121 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 10 | 2938 | 11.3 | 11.3 | 10.3542 | 10.5648 | 15 | 90 | 90 | 1.2897 | 80.248 | 42.1352 | 125.0995 | 0 | 0.45362 | 1.0057 | 0.9686 | 0.36415 | 0 | 0 | 0 | 0.75204 | 39.1232 | 39.1232 | 39.1232 | 39.1232 | 39.1232 | 39.1232 | 39.1232 | 39.1232 | 80.248 | 39.1232 | 39.5768 | 40.1289 | 40.0918 | 39.4874 | 39.1232 | 39.1232 | 39.1232 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 11 | 2939 | 11.9 | 11.9 | 10.3542 | 10.5648 | 15 | 89 | 89 | 1.9937 | 117.6263 | 48.7356 | 143.5012 | 0 | 0.2542 | 1.2096 | 1.4564 | 0.8501 | 0 | 0 | 0 | 1.3737 | 58.1917 | 58.1917 | 58.1917 | 58.1917 | 58.1917 | 58.1917 | 58.1917 | 58.1917 | 117.6263 | 58.1917 | 58.4459 | 59.4013 | 59.6481 | 59.0418 | 58.1917 | 58.1917 | 58.1917 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 12 | 2940 | 12.6 | 12.6 | 10.3542 | 10.5648 | 15 | 88 | 88 | 12.628 | 268.373 | 52.7142 | 165.5524 | 0 | 0 | 4.9539 | 8.2371 | 6.6951 | 1.2312 | 0 | 0 | 9.627 | 128.8497 | 128.8497 | 141.0349 | 149.1105 | 145.3177 | 131.8782 | 128.8497 | 128.8497 | 268.373 | 128.8497 | 128.8497 | 145.9888 | 157.3476 | 152.0128 | 133.1094 | 128.8497 | 128.8497 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 13 | 2941 | 13.2 | 13.2 | 10.3542 | 10.5648 | 15 | 85 | 85 | 12.8287 | 281.7623 | 53.1047 | 189.6185 | 0 | 0 | 1.939 | 6.6926 | 7.5258 | 3.9505 | 0 | 0 | 10.2377 | 135.8197 | 135.8197 | 140.376 | 151.5464 | 153.5043 | 145.1028 | 135.8197 | 135.8197 | 281.7623 | 135.8197 | 135.8197 | 142.315 | 158.239 | 161.0301 | 149.0533 | 135.8197 | 135.8197 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 14 | 2942 | 13.4 | 13.4 | 10.3542 | 10.5648 | 15 | 85 | 85 | 5.7621 | 228.4274 | 49.7938 | 212.2983 | 0 | 0 | 0 | 2.003 | 3.4107 | 2.8204 | 0.57801 | 0 | 4.5726 | 113.9686 | 113.9686 | 113.9686 | 116.95 | 119.0452 | 118.1666 | 114.829 | 113.9686 | 228.4274 | 113.9686 | 113.9686 | 113.9686 | 118.953 | 122.4559 | 120.9871 | 115.407 | 113.9686 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 15 | 2943 | 13.1 | 13.1 | 10.3542 | 10.5648 | 15 | 88 | 88 | 3.7721 | 175.1736 | 43.6344 | 231.4519 | 0 | 0 | 0 | 0.5354 | 2.0583 | 2.3754 | 1.3011 | 0 | 2.8264 | 88.4507 | 88.4507 | 88.4507 | 88.4507 | 88.4507 | 88.4507 | 88.4507 | 88.4507 | 175.1736 | 88.4507 | 88.4507 | 88.4507 | 88.9861 | 90.509 | 90.8262 | 89.7518 | 88.4507 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 16 | 2944 | 13.5 | 13.5 | 10.3542 | 10.5648 | 15 | 85 | 85 | 12.7022 | 235.5116 | 35.7139 | 247.2141 | 0 | 0 | 0 | 0 | 5.729 | 9.1351 | 7.1899 | 1.033 | 8.4884 | 113.7422 | 113.7422 | 113.7422 | 113.7422 | 125.0922 | 131.8401 | 127.9865 | 115.7888 | 235.5116 | 113.7422 | 113.7422 | 113.7422 | 113.7422 | 130.8212 | 140.9751 | 135.1764 | 116.8218 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 17 | 2945 | 13.6 | 13.6 | 10.3542 | 10.5648 | 15 | 85 | 85 | 3.5412 | 126.0307 | 26.8736 | 260.6278 | 0 | 0 | 0 | 0 | 1.1136 | 2.6619 | 2.6509 | 1.0871 | 1.9693 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 126.0307 | 62.8122 | 62.8122 | 62.8122 | 62.8122 | 63.9257 | 65.474 | 65.4631 | 63.8992 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 3 | 18 | 2946 | 13.4 | 13.4 | 10.3542 | 10.5648 | 15 | 87 | 87 | 2.4808 | 79.957 | 17.6912 | 272.709 | 0 | 0 | 0 | 0 | 0.36037 | 1.7987 | 2.1834 | 1.2891 | 1.043 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 79.957 | 39.1754 | 39.1754 | 39.1754 | 39.1754 | 39.5358 | 40.9741 | 41.3588 | 40.4645 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 19 | 2947 | 13.5 | 13.5 | 10.3542 | 10.5648 | 15 | 88 | 88 | 3.0721 | 57.1689 | 8.5935 | 284.2534 | 0.13833 | 0 | 0 | 0 | 0 | 1.9694 | 2.9235 | 2.1651 | 0.83112 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 57.1689 | 28.0628 | 27.9245 | 27.9245 | 27.9245 | 27.9245 | 29.8939 | 30.848 | 30.0895 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 20 | 2948 | 13.4 | 13.4 | 10.3542 | 10.5648 | 15 | 89 | 89 | 1.4212 | 16.8343 | -0.04824 | 295.8789 | 0.34598 | 0 | 0 | 0 | 0 | 0.71841 | 1.362 | 1.2077 | 0.16569 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 16.8343 | 8.3358 | 7.9898 | 7.9898 | 7.9898 | 7.9898 | 8.7082 | 9.3517 | 9.1975 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 21 | 2949 | 13 | 13 | 10.3542 | 10.5648 | 15 | 91 | 91 | 0 | 0 | -7.855 | 308.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 22 | 2950 | 12.8 | 12.8 | 10.3542 | 10.5648 | 15 | 92 | 92 | 0 | 0 | -14.4063 | 321.2142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 23 | 2951 | 12.3 | 12.3 | 10.3542 | 10.5648 | 15 | 90 | 90 | 0 | 0 | -19.2438 | 335.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 3 | 24 | 2952 | 11.9 | 11.9 | 11.8875 | 11.0132 | 15 | 90 | 90 | 0 | 0 | -21.934 | 350.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 1 | 2953 | 11.6 | 11.6 | 11.8875 | 11.0132 | 15 | 90 | 90 | 0 | 0 | -22.1881 | 6.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 2 | 2954 | 11.2 | 11.2 | 11.8875 | 11.0132 | 15 | 91 | 91 | 0 | 0 | -19.6848 | 21.4816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 3 | 2955 | 11.1 | 11.1 | 11.8875 | 11.0132 | 15 | 92 | 92 | 0 | 0 | -15.2614 | 35.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 4 | 2956 | 10.9 | 10.9 | 11.8875 | 11.0132 | 15 | 92 | 92 | 0 | 0 | -9.0337 | 49.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 5 | 2957 | 10.7 | 10.7 | 11.8875 | 11.0132 | 15 | 92 | 92 | 0 | 0 | -1.4587 | 61.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 6 | 2958 | 10.6 | 10.6 | 11.8875 | 11.0132 | 15 | 92 | 92 | 0 | 0 | 7.0355 | 73.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 7 | 2959 | 10.5 | 10.5 | 11.8875 | 11.0132 | 15 | 92 | 92 | 1.3592 | 21.7903 | 16.065 | 84.7465 | 0.3889 | 1.1884 | 1.2917 | 0.63838 | 0 | 0 | 0 | 0 | 0.20974 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 21.7903 | 10.897 | 11.6965 | 11.7998 | 11.1465 | 10.5081 | 10.5081 | 10.5081 | 10.5081 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 4 | 8 | 2960 | 10.6 | 10.6 | 11.8875 | 11.0132 | 15 | 92 | 92 | 3.1633 | 66.0255 | 25.2622 | 96.6507 | 0.27833 | 2.3373 | 3.027 | 1.9436 | 0 | 0 | 0 | 0 | 0.97448 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 66.0255 | 32.935 | 34.994 | 35.6837 | 34.6003 | 32.6567 | 32.6567 | 32.6567 | 32.6567 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 9 | 2961 | 11.1 | 11.1 | 11.8875 | 11.0132 | 15 | 90 | 90 | 6.825 | 138.8915 | 34.2191 | 109.7135 | 0 | 3.8296 | 6.1307 | 4.8406 | 0.71485 | 0 | 0 | 0 | 3.1085 | 66.7903 | 77.4871 | 83.9145 | 80.3108 | 68.787 | 66.7903 | 66.7903 | 66.7903 | 138.8915 | 66.7903 | 81.3167 | 90.0453 | 85.1514 | 69.5019 | 66.7903 | 66.7903 | 66.7903 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 10 | 2962 | 12.1 | 12.1 | 11.8875 | 11.0132 | 15 | 87 | 87 | 39.4788 | 245.8458 | 42.3985 | 124.9173 | 0 | 13.9441 | 30.7315 | 29.5168 | 11.0116 | 0 | 0 | 0 | 23.1542 | 111.4548 | 146.8325 | 189.4242 | 186.3425 | 139.3925 | 111.4548 | 111.4548 | 111.4548 | 245.8458 | 111.4548 | 160.7766 | 220.1557 | 215.8593 | 150.4041 | 111.4548 | 111.4548 | 111.4548 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 11 | 2963 | 12.8 | 12.8 | 11.8875 | 11.0132 | 15 | 83 | 83 | 134.7234 | 317.7382 | 49.0171 | 143.3626 | 0 | 17.4175 | 81.5793 | 97.953 | 56.9472 | 0 | 0 | 0 | 93.2618 | 143.4952 | 165.0895 | 244.6375 | 264.9377 | 214.0985 | 143.4952 | 143.4952 | 143.4952 | 317.7382 | 143.4952 | 182.507 | 326.2168 | 362.8907 | 271.0457 | 143.4952 | 143.4952 | 143.4952 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 12 | 2964 | 15 | 15 | 11.8875 | 11.0132 | 15 | 77 | 77 | 72.1873 | 341.7432 | 53.009 | 165.5116 | 0 | 0 | 28.2518 | 46.8395 | 37.9893 | 6.8854 | 0 | 0 | 55.2568 | 151.6772 | 151.6772 | 201.5966 | 234.4402 | 218.8023 | 163.8434 | 151.6772 | 151.6772 | 341.7432 | 151.6772 | 151.6772 | 229.8485 | 281.2797 | 256.7916 | 170.7289 | 151.6772 | 151.6772 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 13 | 2965 | 17.4 | 17.4 | 11.8875 | 11.0132 | 15 | 72 | 72 | 615.2548 | 221.1254 | 53.3955 | 189.709 | 0 | 0 | 92.6161 | 318.9306 | 358.4199 | 187.9517 | 0 | 0 | 492.8746 | 138.1137 | 138.1137 | 161.0038 | 216.9373 | 226.6971 | 184.5659 | 138.1137 | 138.1137 | 221.1254 | 138.1137 | 138.1137 | 253.6199 | 535.8679 | 585.1169 | 372.5176 | 138.1137 | 138.1137 | 714 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 14 | 2966 | 18.2 | 18.2 | 11.8875 | 11.0132 | 15 | 66 | 66 | 779.4598 | 160.053 | 50.0633 | 212.488 | 0 | 0 | 0 | 268.5181 | 458.1249 | 379.3683 | 78.383 | 0 | 620.947 | 130.7176 | 130.7176 | 130.7176 | 162.4496 | 184.8563 | 175.5493 | 139.9805 | 130.7176 | 160.053 | 130.7176 | 130.7176 | 130.7176 | 430.9677 | 642.9812 | 554.9176 | 218.3634 | 130.7176 | 781 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 15 | 2967 | 18.8 | 18.8 | 11.8875 | 11.0132 | 15 | 68 | 68 | 934.4144 | 138.93 | 43.8786 | 231.6832 | 0 | 0 | 0 | 129.9519 | 505.9669 | 585.5934 | 322.1871 | 0 | 703.07 | 132.4576 | 132.4576 | 132.4576 | 144.0648 | 177.6504 | 184.7626 | 161.2352 | 132.4576 | 138.93 | 132.4576 | 132.4576 | 132.4576 | 274.0168 | 683.6173 | 770.3559 | 483.4224 | 132.4576 | 842 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 16 | 2968 | 18.1 | 18.1 | 11.8875 | 11.0132 | 15 | 71 | 71 | 778.6396 | 135.1326 | 35.939 | 247.4509 | 0 | 0 | 0 | 0 | 347.9812 | 557.4378 | 440.355 | 65.3181 | 522.8674 | 114.5978 | 114.5978 | 114.5978 | 114.5978 | 151.7016 | 174.0351 | 161.551 | 121.5624 | 135.1326 | 114.5978 | 114.5978 | 114.5978 | 114.5978 | 499.6827 | 731.4729 | 601.906 | 186.8805 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 17 | 2969 | 18.3 | 18.3 | 11.8875 | 11.0132 | 15 | 71 | 71 | 331.9631 | 228.2661 | 27.0885 | 260.8559 | 0 | 0 | 0 | 0 | 103.0673 | 248.4005 | 248.2241 | 102.6414 | 185.7339 | 118.8609 | 118.8609 | 118.8609 | 118.8609 | 167.427 | 235.9091 | 235.826 | 167.2263 | 228.2661 | 118.8609 | 118.8609 | 118.8609 | 118.8609 | 270.4943 | 484.3096 | 484.05 | 269.8676 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 4 | 18 | 2970 | 17.7 | 17.7 | 11.8875 | 11.0132 | 15 | 73 | 73 | 221.7921 | 188.9514 | 17.9041 | 272.9248 | 0 | 0 | 0 | 0 | 31.3802 | 160.0418 | 194.9531 | 115.6635 | 94.0486 | 95.3757 | 95.3757 | 95.3757 | 95.3757 | 111.387 | 177.0348 | 194.8478 | 154.3914 | 188.9514 | 95.3757 | 95.3757 | 95.3757 | 95.3757 | 142.7672 | 337.0767 | 389.801 | 270.0549 | 283 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 19 | 2971 | 15.6 | 15.6 | 11.8875 | 11.0132 | 15 | 80 | 80 | 127.9098 | 125.9076 | 8.8113 | 284.4559 | 6.2106 | 0 | 0 | 0 | 0 | 81.5622 | 121.5569 | 90.3452 | 35.0924 | 67.1875 | 62.6102 | 62.6102 | 62.6102 | 62.6102 | 122.7227 | 152.1995 | 129.196 | 125.9076 | 73.398 | 62.6102 | 62.6102 | 62.6102 | 62.6102 | 204.2849 | 273.7563 | 219.5412 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 20 | 2972 | 14.1 | 14.1 | 11.8875 | 11.0132 | 15 | 87 | 87 | 63.9331 | 53.2884 | 0.18037 | 296.0667 | 15.7715 | 0 | 0 | 0 | 0 | 32.1075 | 61.1784 | 54.4118 | 7.7116 | 42.0523 | 27.1762 | 27.1762 | 27.1762 | 27.1762 | 57.4608 | 84.8813 | 78.4989 | 53.2884 | 57.8239 | 27.1762 | 27.1762 | 27.1762 | 27.1762 | 89.5683 | 146.0597 | 132.9107 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 21 | 2973 | 12.8 | 12.8 | 11.8875 | 11.0132 | 15 | 90 | 90 | 0 | 0 | -7.6112 | 308.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 22 | 2974 | 11.9 | 11.9 | 11.8875 | 11.0132 | 15 | 92 | 92 | 0 | 0 | -14.1449 | 321.3571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 23 | 2975 | 11.2 | 11.2 | 11.8875 | 11.0132 | 15 | 93 | 93 | 0 | 0 | -18.9654 | 335.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 4 | 24 | 2976 | 10.6 | 10.6 | 13.4542 | 11.765 | 15 | 94 | 94 | 0 | 0 | -21.6429 | 350.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 1 | 2977 | 10.4 | 10.4 | 13.4542 | 11.765 | 15 | 93 | 93 | 0 | 0 | -21.8923 | 6.2217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 2 | 2978 | 10.3 | 10.3 | 13.4542 | 11.765 | 15 | 94 | 94 | 0 | 0 | -19.3975 | 21.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 3 | 2979 | 10.1 | 10.1 | 13.4542 | 11.765 | 15 | 93 | 93 | 0 | 0 | -14.9843 | 35.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 4 | 2980 | 9.7 | 9.7 | 13.4542 | 11.765 | 15 | 93 | 93 | 0 | 0 | -8.7694 | 49.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 5 | 2981 | 9.2 | 9.2 | 13.4542 | 11.765 | 15 | 94 | 94 | 0 | 0 | -1.2068 | 61.4088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 6 | 2982 | 9.3 | 9.3 | 13.4542 | 11.765 | 15 | 94 | 94 | 4.4789 | 2.31 | 7.2779 | 73.0815 | 2.143 | 4.2956 | 3.9319 | 1.265 | 0 | 0 | 0 | 0 | 11.69 | 3.1496 | 4.2335 | 4.0503 | 2.7075 | 2.0705 | 2.0705 | 2.0705 | 2.0705 | 2.31 | 5.2925 | 8.529 | 7.9822 | 3.9724 | 2.0705 | 2.0705 | 2.0705 | 2.0705 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 7 | 2983 | 11.1 | 11.1 | 13.4542 | 11.765 | 15 | 87 | 87 | 243.1997 | 69.5167 | 16.3021 | 84.5704 | 70.2037 | 212.8413 | 230.7993 | 113.5583 | 0 | 0 | 0 | 0 | 38.4833 | 65.4569 | 121.8865 | 128.9909 | 82.6087 | 37.6833 | 37.6833 | 37.6833 | 37.6833 | 69.5167 | 135.6606 | 334.7277 | 359.7903 | 196.1669 | 37.6833 | 37.6833 | 37.6833 | 37.6833 | 108 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 5 | 8 | 2984 | 13.7 | 13.7 | 13.4542 | 11.765 | 15 | 78 | 78 | 424.7448 | 114.5833 | 25.4996 | 96.464 | 38.5745 | 314.2476 | 405.8387 | 259.695 | 0 | 0 | 0 | 0 | 132.4167 | 78.1786 | 148.1238 | 171.3628 | 134.2825 | 68.3913 | 68.3913 | 68.3913 | 68.3913 | 114.5833 | 116.7531 | 462.3714 | 577.2015 | 393.9775 | 68.3913 | 68.3913 | 68.3913 | 68.3913 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 9 | 2985 | 17.5 | 17.5 | 13.4542 | 11.765 | 15 | 62 | 62 | 636.7935 | 121.7454 | 34.4635 | 109.5214 | 0 | 358.0807 | 571.1084 | 449.5886 | 64.7059 | 0 | 0 | 0 | 292.2546 | 86.7537 | 146.754 | 182.449 | 162.0871 | 97.5959 | 86.7537 | 86.7537 | 86.7537 | 121.7454 | 86.7537 | 504.8346 | 753.5575 | 611.6757 | 162.3018 | 86.7537 | 86.7537 | 86.7537 | 414 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 10 | 2986 | 20 | 20 | 13.4542 | 11.765 | 15 | 54 | 54 | 694.9722 | 140.105 | 42.6566 | 124.7341 | 0 | 246.488 | 540.0581 | 517.2695 | 191.4714 | 0 | 0 | 0 | 409.895 | 105.4092 | 145.5843 | 193.4334 | 189.719 | 136.6171 | 105.4092 | 105.4092 | 105.4092 | 140.105 | 105.4092 | 392.0723 | 733.4915 | 706.9885 | 328.0885 | 105.4092 | 105.4092 | 105.4092 | 550 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 11 | 2987 | 22.3 | 22.3 | 13.4542 | 11.765 | 15 | 36 | 36 | 756.1351 | 146.1845 | 49.2934 | 143.2218 | 0 | 99.1034 | 456.9917 | 547.1805 | 316.8383 | 0 | 0 | 0 | 525.8155 | 118.0922 | 133.1001 | 187.2975 | 200.9554 | 166.0731 | 118.0922 | 118.0922 | 118.0922 | 146.1845 | 118.0922 | 232.2035 | 644.2892 | 748.1359 | 482.9115 | 118.0922 | 118.0922 | 118.0922 | 672 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 12 | 2988 | 23.4 | 23.4 | 13.4542 | 11.765 | 15 | 35 | 35 | 785.3642 | 152.4378 | 53.2991 | 165.4676 | 0 | 0 | 306.6661 | 506.9388 | 410.2537 | 73.2475 | 0 | 0 | 603.5622 | 127.5923 | 127.5923 | 162.4473 | 185.2099 | 174.2209 | 135.9175 | 127.5923 | 127.5923 | 152.4378 | 127.5923 | 127.5923 | 469.1134 | 692.1488 | 584.4746 | 209.165 | 127.5923 | 127.5923 | 756 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 13 | 2989 | 24 | 24 | 13.4542 | 11.765 | 15 | 33 | 33 | 797.353 | 155.8567 | 53.6822 | 189.796 | 0 | 0 | 119.5742 | 410.7278 | 461.2826 | 241.6244 | 0 | 0 | 641.1433 | 131.3192 | 131.3192 | 144.8725 | 177.8737 | 183.6039 | 158.7064 | 131.3192 | 131.3192 | 155.8567 | 131.3192 | 131.3192 | 264.4466 | 588.6015 | 644.8865 | 400.3308 | 131.3192 | 131.3192 | 797 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 14 | 2990 | 24.6 | 24.6 | 13.4542 | 11.765 | 15 | 33 | 33 | 777.9096 | 160.9502 | 50.3291 | 212.674 | 0 | 0 | 0 | 265.6043 | 454.0099 | 376.4626 | 78.3886 | 0 | 622.0498 | 131.0316 | 131.0316 | 131.0316 | 162.5998 | 184.9927 | 175.7758 | 140.3484 | 131.0316 | 160.9502 | 131.0316 | 131.0316 | 131.0316 | 428.2041 | 639.0025 | 552.2384 | 218.7371 | 131.0316 | 783 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 15 | 2991 | 25.1 | 25.1 | 13.4542 | 11.765 | 15 | 30 | 30 | 744.4129 | 162.6075 | 44.1196 | 231.9105 | 0 | 0 | 0 | 101.4461 | 400.0159 | 464.2619 | 256.5495 | 0 | 562.3925 | 126.0464 | 126.0464 | 126.0464 | 142.7691 | 191.986 | 202.5764 | 168.3367 | 126.0464 | 162.6075 | 126.0464 | 126.0464 | 126.0464 | 244.2151 | 592.0019 | 666.8383 | 424.8862 | 126.0464 | 725 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 16 | 2992 | 24.8 | 24.8 | 13.4542 | 11.765 | 15 | 31 | 31 | 683.359 | 163.9412 | 36.1615 | 247.6834 | 0 | 0 | 0 | 0 | 302.6318 | 487.0113 | 386.1061 | 59.0253 | 461.0588 | 117.9254 | 117.9254 | 117.9254 | 117.9254 | 172.701 | 206.0732 | 187.8096 | 128.6089 | 163.9412 | 117.9254 | 117.9254 | 117.9254 | 117.9254 | 475.3328 | 693.0844 | 573.9158 | 187.6341 | 625 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 17 | 2993 | 24.7 | 24.7 | 13.4542 | 11.765 | 15 | 30 | 30 | 571.7468 | 167.1968 | 27.301 | 261.0798 | 0 | 0 | 0 | 0 | 175.282 | 425.8988 | 427.0299 | 178.0127 | 321.8032 | 106.4323 | 106.4323 | 106.4323 | 106.4323 | 144.7991 | 199.6556 | 199.9032 | 145.3968 | 167.1968 | 106.4323 | 106.4323 | 106.4323 | 106.4323 | 320.0811 | 625.5544 | 626.9331 | 323.4095 | 489 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 18 | 2994 | 24.1 | 24.1 | 13.4542 | 11.765 | 15 | 33 | 33 | 412.8797 | 159.4634 | 18.1148 | 273.1362 | 0 | 0 | 0 | 0 | 56.889 | 296.5183 | 362.4512 | 216.0651 | 176.5366 | 91.4505 | 91.4505 | 91.4505 | 91.4505 | 109.4873 | 185.4619 | 206.366 | 159.9542 | 159.4634 | 91.4505 | 91.4505 | 91.4505 | 91.4505 | 166.3763 | 481.9802 | 568.8172 | 376.0192 | 336 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 19 | 2995 | 23.1 | 23.1 | 13.4542 | 11.765 | 15 | 36 | 36 | 186.7546 | 126.0631 | 9.0271 | 284.654 | 9.711 | 0 | 0 | 0 | 0 | 118.4555 | 177.2323 | 132.1889 | 51.9369 | 69.2756 | 64.4223 | 64.4223 | 64.4223 | 64.4223 | 123.6245 | 153.0002 | 130.4882 | 126.0631 | 78.9866 | 64.4223 | 64.4223 | 64.4223 | 64.4223 | 242.08 | 330.2326 | 262.6771 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 20 | 2996 | 21.3 | 21.3 | 13.4542 | 11.765 | 15 | 41 | 41 | 20.173 | 47.4866 | 0.40673 | 296.25 | 5.0402 | 0 | 0 | 0 | 0 | 10.0656 | 19.2751 | 17.1935 | 2.5134 | 30.823 | 23.6158 | 23.6158 | 23.6158 | 23.6158 | 38.0091 | 51.1783 | 48.2017 | 47.4866 | 35.8632 | 23.6158 | 23.6158 | 23.6158 | 23.6158 | 48.0747 | 70.4533 | 65.3952 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 21 | 2997 | 19.4 | 19.4 | 13.4542 | 11.765 | 15 | 46 | 46 | 0 | 0 | -7.37 | 308.4117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 22 | 2998 | 18.5 | 18.5 | 13.4542 | 11.765 | 15 | 47 | 47 | 0 | 0 | -13.8865 | 321.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 23 | 2999 | 17.2 | 17.2 | 13.4542 | 11.765 | 15 | 51 | 51 | 0 | 0 | -18.6905 | 335.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 5 | 24 | 3000 | 15.7 | 15.7 | 17.8958 | 13.4648 | 15 | 59 | 59 | 0 | 0 | -21.356 | 350.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 1 | 3001 | 14.4 | 14.4 | 17.8958 | 13.4648 | 15 | 65 | 65 | 0 | 0 | -21.601 | 6.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 2 | 3002 | 13.7 | 13.7 | 17.8958 | 13.4648 | 15 | 70 | 70 | 0 | 0 | -19.1151 | 21.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 3 | 3003 | 13.5 | 13.5 | 17.8958 | 13.4648 | 15 | 72 | 72 | 0 | 0 | -14.7122 | 35.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 4 | 3004 | 12.6 | 12.6 | 17.8958 | 13.4648 | 15 | 79 | 79 | 0 | 0 | -8.5102 | 48.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 5 | 3005 | 12.4 | 12.4 | 17.8958 | 13.4648 | 15 | 80 | 80 | 0 | 0 | -0.95995 | 61.2631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 6 | 3006 | 13.6 | 13.6 | 17.8958 | 13.4648 | 15 | 76 | 76 | 3.6043 | 2.31 | 7.5152 | 72.9194 | 1.7326 | 3.4596 | 3.1599 | 1.0092 | 0 | 0 | 0 | 0 | 11.69 | 3.1376 | 4.2718 | 4.075 | 2.6625 | 1.9996 | 1.9996 | 1.9996 | 1.9996 | 2.31 | 4.8703 | 7.7314 | 7.2349 | 3.6717 | 1.9996 | 1.9996 | 1.9996 | 1.9996 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 7 | 3007 | 15.3 | 15.3 | 17.8958 | 13.4648 | 15 | 71 | 71 | 220.9265 | 72.1883 | 16.5342 | 84.395 | 64.3325 | 193.5355 | 209.368 | 102.5555 | 0 | 0 | 0 | 0 | 35.8117 | 66.8423 | 123.5177 | 130.4627 | 83.609 | 38.6226 | 38.6226 | 38.6226 | 38.6226 | 72.1883 | 131.1748 | 317.0531 | 339.8306 | 186.1645 | 38.6226 | 38.6226 | 38.6226 | 38.6226 | 108 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 6 | 8 | 3008 | 17.7 | 17.7 | 17.8958 | 13.4648 | 15 | 65 | 65 | 443.6357 | 113.0801 | 25.7319 | 96.2777 | 41.5382 | 328.6605 | 423.258 | 269.9166 | 0 | 0 | 0 | 0 | 139.9199 | 78.6583 | 148.4203 | 171.4046 | 134.1473 | 68.5657 | 68.5657 | 68.5657 | 68.5657 | 113.0801 | 120.1964 | 477.0808 | 594.6626 | 404.064 | 68.5657 | 68.5657 | 68.5657 | 68.5657 | 253 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 9 | 3009 | 20.8 | 20.8 | 17.8958 | 13.4648 | 15 | 59 | 59 | 590.4897 | 132.9737 | 34.7025 | 109.3292 | 0 | 332.7495 | 528.7443 | 415.0079 | 58.1655 | 0 | 0 | 0 | 273.0263 | 90.3994 | 157.1338 | 196.4414 | 173.631 | 102.0647 | 90.3994 | 90.3994 | 90.3994 | 132.9737 | 90.3994 | 489.8832 | 725.1857 | 588.6389 | 160.2302 | 90.3994 | 90.3994 | 90.3994 | 406 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 10 | 3010 | 22 | 22 | 17.8958 | 13.4648 | 15 | 51 | 51 | 660.2448 | 150.4498 | 42.9094 | 124.5498 | 0 | 235.1409 | 512.2036 | 489.2244 | 179.6642 | 0 | 0 | 0 | 391.5502 | 107.444 | 149.4819 | 199.0146 | 194.9064 | 139.5639 | 107.444 | 107.444 | 107.444 | 150.4498 | 107.444 | 384.6228 | 711.2182 | 684.1308 | 319.2281 | 107.444 | 107.444 | 107.444 | 542 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 11 | 3011 | 24 | 24 | 17.8958 | 13.4648 | 15 | 46 | 46 | 691.8544 | 166.7497 | 49.5645 | 143.0786 | 0 | 91.9121 | 417.3646 | 498.3306 | 287.3813 | 0 | 0 | 0 | 483.2503 | 121.4088 | 138.0303 | 196.8854 | 211.5274 | 173.3791 | 121.4088 | 121.4088 | 121.4088 | 166.7497 | 121.4088 | 229.9424 | 614.2501 | 709.858 | 460.7604 | 121.4088 | 121.4088 | 121.4088 | 650 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 12 | 3012 | 24.8 | 24.8 | 17.8958 | 13.4648 | 15 | 40 | 40 | 741.7425 | 166.749 | 53.5843 | 165.4203 | 0 | 0 | 288.9983 | 476.3134 | 384.6105 | 67.608 | 0 | 0 | 572.251 | 128.7318 | 128.7318 | 177.419 | 208.9757 | 193.5266 | 140.1216 | 128.7318 | 128.7318 | 166.749 | 128.7318 | 128.7318 | 466.4173 | 685.2891 | 578.1372 | 207.7297 | 128.7318 | 128.7318 | 739 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 13 | 3013 | 25.9 | 25.9 | 17.8958 | 13.4648 | 15 | 37 | 37 | 763.2473 | 167.042 | 53.9646 | 189.8794 | 0 | 0 | 114.0557 | 390.7179 | 438.5029 | 229.4189 | 0 | 0 | 615.958 | 132.5009 | 132.5009 | 146.6791 | 181.0708 | 187.0109 | 161.0198 | 132.5009 | 132.5009 | 167.042 | 132.5009 | 132.5009 | 260.7347 | 571.7887 | 625.5139 | 390.4387 | 132.5009 | 132.5009 | 783 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 14 | 3014 | 26.3 | 26.3 | 17.8958 | 13.4648 | 15 | 41 | 41 | 748.8179 | 171.0123 | 50.5912 | 212.8562 | 0 | 0 | 0 | 253.4297 | 433.9857 | 360.3188 | 75.582 | 0 | 600.9877 | 131.8569 | 131.8569 | 131.8569 | 175.0021 | 205.741 | 193.1995 | 144.7244 | 131.8569 | 171.0123 | 131.8569 | 131.8569 | 131.8569 | 428.4318 | 639.7267 | 553.5183 | 220.3064 | 131.8569 | 772 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 15 | 3015 | 26.3 | 26.3 | 17.8958 | 13.4648 | 15 | 38 | 38 | 225.6825 | 336.8231 | 44.3576 | 232.1337 | 0 | 0 | 0 | 30.1399 | 120.3553 | 140.0682 | 77.731 | 0 | 171.1769 | 150.629 | 150.629 | 150.629 | 178.841 | 263.2855 | 281.7374 | 223.3878 | 150.629 | 336.8231 | 150.629 | 150.629 | 150.629 | 208.9809 | 383.6408 | 421.8056 | 301.1188 | 150.629 | 508 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 16 | 3016 | 25.7 | 25.7 | 17.8958 | 13.4648 | 15 | 37 | 37 | 283.9653 | 288.5255 | 36.3813 | 247.9117 | 0 | 0 | 0 | 0 | 124.6257 | 201.4609 | 160.283 | 25.2135 | 192.4745 | 139.0269 | 139.0269 | 139.0269 | 139.0269 | 220.6022 | 270.8956 | 243.9421 | 155.5306 | 288.5255 | 139.0269 | 139.0269 | 139.0269 | 139.0269 | 345.2279 | 472.3564 | 404.225 | 180.7441 | 481 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 17 | 3017 | 25.5 | 25.5 | 17.8958 | 13.4648 | 15 | 28 | 28 | 88.1073 | 256.121 | 27.5113 | 261.2994 | 0 | 0 | 0 | 0 | 26.6737 | 65.3378 | 65.7279 | 27.6155 | 49.879 | 118.4072 | 118.4072 | 118.4072 | 118.4072 | 149.0012 | 193.348 | 193.7954 | 150.0814 | 256.121 | 118.4072 | 118.4072 | 118.4072 | 118.4072 | 175.6749 | 258.6858 | 259.5233 | 177.6969 | 306 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 18 | 3018 | 24.3 | 24.3 | 17.8958 | 13.4648 | 15 | 36 | 36 | 10.2943 | 145.5627 | 18.3234 | 273.3433 | 0 | 0 | 0 | 0 | 1.3811 | 7.3584 | 9.0252 | 5.4051 | 4.4373 | 70.5921 | 70.5921 | 70.5921 | 70.5921 | 72.7442 | 82.0579 | 84.6551 | 79.0144 | 145.5627 | 70.5921 | 70.5921 | 70.5921 | 70.5921 | 74.1254 | 89.4163 | 93.6802 | 84.4195 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 19 | 3019 | 24.2 | 24.2 | 17.8958 | 13.4648 | 15 | 39 | 39 | 37.7561 | 117.3608 | 9.2407 | 284.8476 | 2.0902 | 0 | 0 | 0 | 0 | 23.8228 | 35.7807 | 26.7788 | 10.6392 | 59.4028 | 56.2195 | 56.2195 | 56.2195 | 56.2195 | 92.5005 | 110.7119 | 97.0024 | 117.3608 | 61.493 | 56.2195 | 56.2195 | 56.2195 | 56.2195 | 116.3233 | 146.4926 | 123.7812 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 20 | 3020 | 22.2 | 22.2 | 17.8958 | 13.4648 | 15 | 45 | 45 | 5.2538 | 35.3249 | 0.63077 | 296.4288 | 1.3288 | 0 | 0 | 0 | 0 | 2.6047 | 5.0125 | 4.484 | 0.67511 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 35.3249 | 18.6323 | 17.3035 | 17.3035 | 17.3035 | 17.3035 | 19.9083 | 22.316 | 21.7875 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 21 | 3021 | 20.4 | 20.4 | 17.8958 | 13.4648 | 15 | 53 | 53 | 0 | 0 | -7.1314 | 308.5719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 22 | 3022 | 19.7 | 19.7 | 17.8958 | 13.4648 | 15 | 56 | 56 | 0 | 0 | -13.6312 | 321.6298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 23 | 3023 | 18.7 | 18.7 | 17.8958 | 13.4648 | 15 | 57 | 57 | 0 | 0 | -18.4192 | 335.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 6 | 24 | 3024 | 17.4 | 17.4 | 20.0583 | 15.3957 | 15 | 63 | 63 | 0 | 0 | -21.0733 | 350.7847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 1 | 3025 | 16.5 | 16.5 | 20.0583 | 15.3957 | 15 | 65 | 65 | 0 | 0 | -21.3143 | 6.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 2 | 3026 | 16.9 | 16.9 | 20.0583 | 15.3957 | 15 | 63 | 63 | 0 | 0 | -18.8376 | 21.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 3 | 3027 | 16.4 | 16.4 | 20.0583 | 15.3957 | 15 | 64 | 64 | 0 | 0 | -14.4452 | 35.6091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 4 | 3028 | 15.1 | 15.1 | 20.0583 | 15.3957 | 15 | 68 | 68 | 0 | 0 | -8.2561 | 48.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 5 | 3029 | 14.5 | 14.5 | 20.0583 | 15.3957 | 15 | 70 | 70 | 0 | 0 | -0.71813 | 61.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 6 | 3030 | 14.2 | 14.2 | 20.0583 | 15.3957 | 15 | 71 | 71 | 4.4994 | 3.1446 | 7.7475 | 72.758 | 2.1731 | 4.3222 | 3.9394 | 1.249 | 0 | 0 | 0 | 0 | 13.8554 | 4.0715 | 5.61 | 5.336 | 3.4099 | 2.5158 | 2.5158 | 2.5158 | 2.5158 | 3.1446 | 6.2445 | 9.9322 | 9.2754 | 4.6589 | 2.5158 | 2.5158 | 2.5158 | 2.5158 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 7 | 3031 | 15.4 | 15.4 | 20.0583 | 15.3957 | 15 | 68 | 68 | 277.6288 | 70.9435 | 16.7611 | 84.2203 | 81.5401 | 243.4373 | 262.7322 | 128.1222 | 0 | 0 | 0 | 0 | 46.0565 | 61.5616 | 106.3191 | 111.6534 | 74.4395 | 39.0193 | 39.0193 | 39.0193 | 39.0193 | 70.9435 | 143.1018 | 349.7565 | 374.3856 | 202.5617 | 39.0193 | 39.0193 | 39.0193 | 39.0193 | 117 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 7 | 8 | 3032 | 17.6 | 17.6 | 20.0583 | 15.3957 | 15 | 62 | 62 | 523.0115 | 102.1771 | 25.959 | 96.0919 | 50.4316 | 387.9734 | 498.2457 | 316.6524 | 0 | 0 | 0 | 0 | 166.8229 | 76.8206 | 144.3715 | 166.4399 | 130.0983 | 66.728 | 66.728 | 66.728 | 66.728 | 102.1771 | 127.2523 | 532.345 | 664.6855 | 446.7507 | 66.728 | 66.728 | 66.728 | 66.728 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 9 | 3033 | 19.4 | 19.4 | 20.0583 | 15.3957 | 15 | 59 | 59 | 658.0838 | 118.5092 | 34.9362 | 109.137 | 0 | 371.6234 | 588.3469 | 460.4248 | 62.7921 | 0 | 0 | 0 | 306.4908 | 86.9408 | 146.3698 | 181.0276 | 160.5706 | 96.9823 | 86.9408 | 86.9408 | 86.9408 | 118.5092 | 86.9408 | 517.9932 | 769.3745 | 620.9954 | 159.7744 | 86.9408 | 86.9408 | 86.9408 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 10 | 3034 | 20.8 | 20.8 | 20.0583 | 15.3957 | 15 | 55 | 55 | 729.93 | 131.809 | 43.1567 | 124.3646 | 0 | 261.0299 | 565.3209 | 538.4545 | 196.1688 | 0 | 0 | 0 | 435.191 | 104.6697 | 143.6006 | 188.9836 | 184.9767 | 133.927 | 104.6697 | 104.6697 | 104.6697 | 131.809 | 104.6697 | 404.6306 | 754.3045 | 723.4312 | 330.0959 | 104.6697 | 104.6697 | 104.6697 | 567 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 11 | 3035 | 22.6 | 22.6 | 20.0583 | 15.3957 | 15 | 47 | 47 | 757.2526 | 146.7829 | 49.8304 | 142.9333 | 0 | 101.9509 | 455.9891 | 542.9151 | 311.8088 | 0 | 0 | 0 | 531.2171 | 118.7497 | 134.1924 | 187.8191 | 200.9859 | 165.9799 | 118.7497 | 118.7497 | 118.7497 | 146.7829 | 118.7497 | 236.1433 | 643.8082 | 743.901 | 477.7887 | 118.7497 | 118.7497 | 118.7497 | 678 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 12 | 3036 | 24.3 | 24.3 | 20.0583 | 15.3957 | 15 | 44 | 44 | 773.7904 | 156.7671 | 53.8647 | 165.3697 | 0 | 0 | 300.8514 | 494.3586 | 398.2773 | 68.8905 | 0 | 0 | 599.2329 | 128.5074 | 128.5074 | 163.8602 | 186.5991 | 175.3086 | 136.6027 | 128.5074 | 128.5074 | 156.7671 | 128.5074 | 128.5074 | 464.7116 | 680.9577 | 573.5859 | 205.4932 | 128.5074 | 128.5074 | 756 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 13 | 3037 | 25.7 | 25.7 | 20.0583 | 15.3957 | 15 | 38 | 38 | 786.7388 | 159.8284 | 54.2427 | 189.9591 | 0 | 0 | 117.1813 | 400.2744 | 448.8922 | 234.555 | 0 | 0 | 637.1716 | 132.0871 | 132.0871 | 145.7859 | 178.8801 | 184.5637 | 159.5072 | 132.0871 | 132.0871 | 159.8284 | 132.0871 | 132.0871 | 262.9672 | 579.1545 | 633.4559 | 394.0622 | 132.0871 | 132.0871 | 797 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 14 | 3038 | 25.8 | 25.8 | 20.0583 | 15.3957 | 15 | 34 | 34 | 619.5672 | 219.9666 | 50.8496 | 213.0345 | 0 | 0 | 0 | 207.8726 | 356.5905 | 296.4226 | 62.6143 | 0 | 499.0334 | 137.9199 | 137.9199 | 137.9199 | 188.9158 | 225.3996 | 210.6391 | 153.2806 | 137.9199 | 219.9666 | 137.9199 | 137.9199 | 137.9199 | 396.7884 | 581.9902 | 507.0616 | 215.8949 | 137.9199 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 15 | 3039 | 26 | 26 | 20.0583 | 15.3957 | 15 | 38 | 38 | 607.527 | 212.4168 | 44.5923 | 232.3526 | 0 | 0 | 0 | 79.5219 | 321.5603 | 375.233 | 209.0993 | 0 | 462.5832 | 132.9652 | 132.9652 | 132.9652 | 152.2522 | 210.9554 | 223.973 | 183.6795 | 132.9652 | 212.4168 | 132.9652 | 132.9652 | 132.9652 | 231.7741 | 532.5157 | 599.206 | 392.7788 | 132.9652 | 675 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 16 | 3040 | 26.9 | 26.9 | 20.0583 | 15.3957 | 15 | 34 | 34 | 728.6001 | 150.9261 | 36.5983 | 248.1355 | 0 | 0 | 0 | 0 | 316.9145 | 514.5846 | 410.8179 | 66.3997 | 496.0739 | 116.4981 | 116.4981 | 116.4981 | 116.4981 | 167.2707 | 198.9392 | 182.3149 | 127.1359 | 150.9261 | 116.4981 | 116.4981 | 116.4981 | 116.4981 | 484.1852 | 713.5238 | 593.1328 | 193.5357 | 647 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 17 | 3041 | 21.5 | 21.5 | 20.0583 | 15.3957 | 15 | 64 | 64 | 180.0618 | 258.4862 | 27.7191 | 261.5144 | 0 | 0 | 0 | 0 | 53.8359 | 132.9341 | 134.1613 | 56.7987 | 102.5138 | 123.3799 | 123.3799 | 123.3799 | 123.3799 | 164.8313 | 225.7336 | 226.6785 | 167.1125 | 258.4862 | 123.3799 | 123.3799 | 123.3799 | 123.3799 | 218.6671 | 358.6677 | 360.8398 | 223.9112 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 7 | 18 | 3042 | 24 | 24 | 20.0583 | 15.3957 | 15 | 49 | 49 | 60.5333 | 190.7015 | 18.5298 | 273.5458 | 0 | 0 | 0 | 0 | 7.9072 | 43.0678 | 52.9998 | 31.8853 | 26.2985 | 89.3288 | 89.3288 | 89.3288 | 89.3288 | 99.9488 | 147.1716 | 160.5109 | 132.1527 | 190.7015 | 89.3288 | 89.3288 | 89.3288 | 89.3288 | 107.856 | 190.2394 | 213.5107 | 164.038 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 19 | 3043 | 21 | 21 | 20.0583 | 15.3957 | 15 | 67 | 67 | 3.3675 | 63.0389 | 9.452 | 285.0368 | 0.19747 | 0 | 0 | 0 | 0 | 2.1138 | 3.1868 | 2.393 | 0.9611 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 63.0389 | 31.1012 | 30.9037 | 30.9037 | 30.9037 | 30.9037 | 33.0175 | 34.0905 | 33.2968 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 20 | 3044 | 18.9 | 18.9 | 20.0583 | 15.3957 | 15 | 77 | 77 | 2.3898 | 24.6837 | 0.8524 | 296.6032 | 0.6116 | 0 | 0 | 0 | 0 | 1.1774 | 2.2767 | 2.0423 | 0.31627 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 24.6837 | 12.4652 | 11.8536 | 11.8536 | 11.8536 | 11.8536 | 13.031 | 14.1302 | 13.8959 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 21 | 3045 | 17 | 17 | 20.0583 | 15.3957 | 15 | 78 | 78 | 0 | 0 | -6.8956 | 308.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 22 | 3046 | 15.7 | 15.7 | 20.0583 | 15.3957 | 15 | 87 | 87 | 0 | 0 | -13.3791 | 321.7597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 23 | 3047 | 14.7 | 14.7 | 20.0583 | 15.3957 | 15 | 91 | 91 | 0 | 0 | -18.1517 | 335.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 7 | 24 | 3048 | 13.6 | 13.6 | 19.3542 | 16.6504 | 15 | 94 | 94 | 0 | 0 | -20.7948 | 350.8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 1 | 3049 | 13.5 | 13.5 | 19.3542 | 16.6504 | 15 | 94 | 94 | 0 | 0 | -21.0324 | 6.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 2 | 3050 | 12.6 | 12.6 | 19.3542 | 16.6504 | 15 | 95 | 95 | 0 | 0 | -18.5652 | 21.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 3 | 3051 | 13 | 13 | 19.3542 | 16.6504 | 15 | 97 | 97 | 0 | 0 | -14.1833 | 35.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 4 | 3052 | 11.2 | 11.2 | 19.3542 | 16.6504 | 15 | 97 | 97 | 0 | 0 | -8.0071 | 48.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 5 | 3053 | 11.1 | 11.1 | 19.3542 | 16.6504 | 15 | 99 | 99 | 0 | 0 | -0.48145 | 60.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 6 | 3054 | 12.1 | 12.1 | 19.3542 | 16.6504 | 15 | 98 | 98 | 10.1064 | 5.3315 | 7.9746 | 72.5975 | 4.9036 | 9.7158 | 8.8367 | 2.7811 | 0 | 0 | 0 | 0 | 13.6685 | 5.9623 | 8.4352 | 7.9834 | 4.8717 | 3.4425 | 3.4425 | 3.4425 | 3.4425 | 5.3315 | 10.8659 | 18.151 | 16.8201 | 7.6528 | 3.4425 | 3.4425 | 3.4425 | 3.4425 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 7 | 3055 | 15.7 | 15.7 | 19.3542 | 16.6504 | 15 | 98 | 98 | 477.4184 | 58.02 | 16.9829 | 84.0464 | 141.4063 | 419.008 | 451.1604 | 219.0292 | 0 | 0 | 0 | 0 | 80.98 | 58.2798 | 102.1011 | 107.1766 | 70.5331 | 35.9578 | 35.9578 | 35.9578 | 35.9578 | 58.02 | 199.6861 | 521.109 | 558.337 | 289.5623 | 35.9578 | 35.9578 | 35.9578 | 35.9578 | 139 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 8 | 8 | 3056 | 18.9 | 18.9 | 19.3542 | 16.6504 | 15 | 81 | 81 | 560.1892 | 97.3547 | 26.1807 | 95.9067 | 55.5705 | 416.0908 | 532.8708 | 337.5023 | 0 | 0 | 0 | 0 | 180.6453 | 74.3027 | 136.3132 | 156.3997 | 122.7957 | 64.7444 | 64.7444 | 64.7444 | 64.7444 | 97.3547 | 129.8732 | 552.404 | 689.2705 | 460.298 | 64.7444 | 64.7444 | 64.7444 | 64.7444 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 9 | 3057 | 21.6 | 21.6 | 19.3542 | 16.6504 | 15 | 68 | 68 | 670.8123 | 116.3719 | 35.1645 | 108.9449 | 0 | 379.6067 | 598.7954 | 467.2178 | 61.9504 | 0 | 0 | 0 | 314.6281 | 86.9205 | 145.8883 | 179.9369 | 159.4977 | 96.5438 | 86.9205 | 86.9205 | 86.9205 | 116.3719 | 86.9205 | 525.495 | 778.7322 | 626.7155 | 158.4942 | 86.9205 | 86.9205 | 86.9205 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 10 | 3058 | 22.6 | 22.6 | 19.3542 | 16.6504 | 15 | 60 | 60 | 727.5262 | 132.9831 | 43.3986 | 124.1786 | 0 | 261.2369 | 562.5369 | 534.3104 | 193.0921 | 0 | 0 | 0 | 436.0169 | 105.1816 | 144.4609 | 189.7641 | 185.52 | 134.2147 | 105.1816 | 105.1816 | 105.1816 | 132.9831 | 105.1816 | 405.6979 | 752.301 | 719.8303 | 327.3068 | 105.1816 | 105.1816 | 105.1816 | 569 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 11 | 3059 | 24.4 | 24.4 | 19.3542 | 16.6504 | 15 | 55 | 55 | 831.652 | 128.1344 | 50.0909 | 142.7858 | 0 | 113.4507 | 499.9075 | 593.5253 | 339.4639 | 0 | 0 | 0 | 585.8656 | 118.3212 | 129.2447 | 166.4544 | 175.4683 | 151.0062 | 118.3212 | 118.3212 | 118.3212 | 128.1344 | 118.3212 | 242.6954 | 666.3619 | 768.9935 | 490.4701 | 118.3212 | 118.3212 | 118.3212 | 714 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 12 | 3060 | 25 | 25 | 19.3542 | 16.6504 | 15 | 49 | 49 | 785.2548 | 153.6505 | 54.1401 | 165.3158 | 0 | 0 | 304.6951 | 499.1533 | 401.2143 | 68.2494 | 0 | 0 | 610.3495 | 128.4472 | 128.4472 | 163.2297 | 185.4281 | 174.2478 | 136.2382 | 128.4472 | 128.4472 | 153.6505 | 128.4472 | 128.4472 | 467.9248 | 684.5814 | 575.4621 | 204.4876 | 128.4472 | 128.4472 | 764 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 13 | 3061 | 23.7 | 23.7 | 19.3542 | 16.6504 | 15 | 58 | 58 | 37.8181 | 338.2656 | 54.5164 | 190.035 | 0 | 0 | 5.6159 | 19.1246 | 21.4304 | 11.1826 | 0 | 0 | 30.7344 | 148.2375 | 148.2375 | 165.8753 | 208.3024 | 215.5443 | 183.3588 | 148.2375 | 148.2375 | 338.2656 | 148.2375 | 148.2375 | 171.4912 | 227.4271 | 236.9748 | 194.5414 | 148.2375 | 148.2375 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 14 | 3062 | 24 | 24 | 19.3542 | 16.6504 | 15 | 53 | 53 | 33.379 | 331.021 | 51.1042 | 213.2087 | 0 | 0 | 0 | 11.1036 | 19.0791 | 15.8783 | 3.3762 | 0 | 26.979 | 145.2805 | 145.2805 | 145.2805 | 183.3564 | 210.7054 | 199.7294 | 156.858 | 145.2805 | 331.021 | 145.2805 | 145.2805 | 145.2805 | 194.4601 | 229.7846 | 215.6077 | 160.2342 | 145.2805 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 15 | 3063 | 25.5 | 25.5 | 19.3542 | 16.6504 | 15 | 51 | 51 | 454.2585 | 269.8155 | 44.8238 | 232.5671 | 0 | 0 | 0 | 58.2861 | 238.6477 | 279.2127 | 156.2187 | 0 | 347.1845 | 142.533 | 142.533 | 142.533 | 167.1478 | 243.3159 | 260.4468 | 208.5054 | 142.533 | 269.8155 | 142.533 | 142.533 | 142.533 | 225.4339 | 481.9636 | 539.6595 | 364.7241 | 142.533 | 617 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 16 | 3064 | 24.4 | 24.4 | 19.3542 | 16.6504 | 15 | 53 | 53 | 71.0898 | 304.3859 | 36.8127 | 248.3548 | 0 | 0 | 0 | 0 | 30.6483 | 49.9833 | 40.0387 | 6.64 | 48.6141 | 137.2857 | 137.2857 | 137.2857 | 137.2857 | 185.8389 | 216.4695 | 200.7152 | 147.8048 | 304.3859 | 137.2857 | 137.2857 | 137.2857 | 137.2857 | 216.4873 | 266.4527 | 240.7539 | 154.4447 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 17 | 3065 | 24.7 | 24.7 | 19.3542 | 16.6504 | 15 | 50 | 50 | 524.2486 | 182.8843 | 27.9245 | 261.7249 | 0 | 0 | 0 | 0 | 154.8141 | 385.3247 | 390.1173 | 166.3845 | 300.1157 | 111.4229 | 111.4229 | 111.4229 | 111.4229 | 153.7099 | 216.6731 | 217.9822 | 156.8703 | 182.8843 | 111.4229 | 111.4229 | 111.4229 | 111.4229 | 308.524 | 601.9978 | 608.0995 | 323.2548 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 8 | 18 | 3066 | 23.4 | 23.4 | 19.3542 | 16.6504 | 15 | 61 | 61 | 58.4242 | 191.4228 | 18.7338 | 273.7439 | 0 | 0 | 0 | 0 | 7.4297 | 41.3755 | 51.0842 | 30.8684 | 25.5772 | 89.5838 | 89.5838 | 89.5838 | 89.5838 | 99.9044 | 147.0589 | 160.5453 | 132.4633 | 191.4228 | 89.5838 | 89.5838 | 89.5838 | 89.5838 | 107.3341 | 188.4345 | 211.6294 | 163.3317 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 19 | 3067 | 22.9 | 22.9 | 19.3542 | 16.6504 | 15 | 62 | 62 | 50.4266 | 124.4287 | 9.6611 | 285.2215 | 3.1182 | 0 | 0 | 0 | 0 | 31.491 | 47.6532 | 35.9008 | 14.5713 | 63.4216 | 59.5665 | 59.5665 | 59.5665 | 59.5665 | 98.4994 | 118.481 | 103.9513 | 124.4287 | 66.5399 | 59.5665 | 59.5665 | 59.5665 | 59.5665 | 129.9903 | 166.1341 | 139.8521 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 20 | 3068 | 20.6 | 20.6 | 19.3542 | 16.6504 | 15 | 66 | 66 | 13.1802 | 48.206 | 1.0716 | 296.773 | 3.4114 | 0 | 0 | 0 | 0 | 6.4531 | 12.5374 | 11.2775 | 1.794 | 30.8299 | 23.9873 | 23.9873 | 23.9873 | 23.9873 | 36.931 | 49.135 | 46.6079 | 48.206 | 34.2413 | 23.9873 | 23.9873 | 23.9873 | 23.9873 | 43.3841 | 61.6725 | 57.8854 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 21 | 3069 | 18.6 | 18.6 | 19.3542 | 16.6504 | 15 | 73 | 73 | 0 | 6 | -6.6625 | 308.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 6 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 2.8677 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 22 | 3070 | 17.6 | 17.6 | 19.3542 | 16.6504 | 15 | 77 | 77 | 0 | 0 | -13.1302 | 321.8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 23 | 3071 | 17.5 | 17.5 | 19.3542 | 16.6504 | 15 | 80 | 80 | 0 | 0 | -17.888 | 335.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 8 | 24 | 3072 | 16.3 | 16.3 | 19.2042 | 17.5498 | 15 | 88 | 88 | 0 | 0 | -20.5208 | 350.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 1 | 3073 | 15.7 | 15.7 | 19.2042 | 17.5498 | 15 | 91 | 91 | 0 | 0 | -20.7552 | 6.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 2 | 3074 | 16.3 | 16.3 | 19.2042 | 17.5498 | 15 | 87 | 87 | 0 | 0 | -18.298 | 21.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 3 | 3075 | 15.9 | 15.9 | 19.2042 | 17.5498 | 15 | 89 | 89 | 0 | 0 | -13.9266 | 35.4214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 4 | 3076 | 15.3 | 15.3 | 19.2042 | 17.5498 | 15 | 93 | 93 | 0 | 0 | -7.7633 | 48.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 5 | 3077 | 14.3 | 14.3 | 19.2042 | 17.5498 | 15 | 96 | 96 | 0 | 0 | -0.24998 | 60.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 6 | 3078 | 15.1 | 15.1 | 19.2042 | 17.5498 | 15 | 96 | 96 | 8.3124 | 6.8093 | 8.1964 | 72.438 | 4.0514 | 7.997 | 7.2581 | 2.2675 | 0 | 0 | 0 | 0 | 15.1907 | 7.355 | 10.6596 | 10.0407 | 5.8609 | 3.9619 | 3.9619 | 3.9619 | 3.9619 | 6.8093 | 11.4065 | 18.6566 | 17.2988 | 8.1284 | 3.9619 | 3.9619 | 3.9619 | 3.9619 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 7 | 3079 | 16.7 | 16.7 | 19.2042 | 17.5498 | 15 | 89 | 89 | 16.8981 | 64.0719 | 17.1993 | 83.8734 | 5.0467 | 14.844 | 15.9459 | 7.7069 | 0 | 0 | 0 | 0 | 2.9281 | 50.0144 | 88.3759 | 92.6903 | 60.4303 | 30.2539 | 30.2539 | 30.2539 | 30.2539 | 64.0719 | 55.0611 | 103.2199 | 108.6362 | 68.1372 | 30.2539 | 30.2539 | 30.2539 | 30.2539 | 67 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 9 | 8 | 3080 | 18.8 | 18.8 | 19.2042 | 17.5498 | 15 | 78 | 78 | 209.0041 | 145.8834 | 26.3971 | 95.7222 | 21.3085 | 155.4404 | 198.5175 | 125.3057 | 0 | 0 | 0 | 0 | 68.1166 | 85.5072 | 163.7472 | 188.8743 | 146.1694 | 73.0778 | 73.0778 | 73.0778 | 73.0778 | 145.8834 | 106.8157 | 319.1877 | 387.3918 | 271.4751 | 73.0778 | 73.0778 | 73.0778 | 73.0778 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 9 | 3081 | 18.8 | 18.8 | 19.2042 | 17.5498 | 15 | 78 | 78 | 37.5133 | 196.2843 | 35.3873 | 108.753 | 0 | 21.2727 | 33.4345 | 26.0108 | 3.3503 | 0 | 0 | 0 | 17.7157 | 90.1349 | 141.8068 | 171.348 | 153.3156 | 98.2729 | 90.1349 | 90.1349 | 90.1349 | 196.2843 | 90.1349 | 163.0796 | 204.7825 | 179.3264 | 101.6232 | 90.1349 | 90.1349 | 90.1349 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 10 | 3082 | 20.7 | 20.7 | 19.2042 | 17.5498 | 15 | 69 | 69 | 102.493 | 274.263 | 43.635 | 123.9919 | 0 | 36.9528 | 79.1222 | 74.9429 | 26.863 | 0 | 0 | 0 | 61.737 | 125.8035 | 168.0269 | 216.2108 | 211.4354 | 156.498 | 125.8035 | 125.8035 | 125.8035 | 274.263 | 125.8035 | 204.9797 | 295.3331 | 286.3783 | 183.361 | 125.8035 | 125.8035 | 125.8035 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 11 | 3083 | 22.6 | 22.6 | 19.2042 | 17.5498 | 15 | 60 | 60 | 586.2401 | 204.3244 | 50.3459 | 142.6363 | 0 | 81.0177 | 351.7873 | 416.4848 | 237.2111 | 0 | 0 | 0 | 414.6756 | 127.3212 | 146.8588 | 212.1554 | 227.7573 | 184.5251 | 127.3212 | 127.3212 | 127.3212 | 204.3244 | 127.3212 | 227.8764 | 563.9427 | 644.242 | 421.7361 | 127.3212 | 127.3212 | 127.3212 | 619 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 12 | 3084 | 23.7 | 23.7 | 19.2042 | 17.5498 | 15 | 55 | 55 | 691.1747 | 185.8511 | 54.4105 | 165.2586 | 0 | 0 | 267.676 | 437.1626 | 350.5652 | 58.6115 | 0 | 0 | 539.1489 | 131.9088 | 131.9088 | 184.1252 | 217.1874 | 200.2946 | 143.3423 | 131.9088 | 131.9088 | 185.8511 | 131.9088 | 131.9088 | 451.8012 | 654.35 | 550.8599 | 201.9539 | 131.9088 | 131.9088 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 13 | 3085 | 24.5 | 24.5 | 19.2042 | 17.5498 | 15 | 55 | 55 | 679.8942 | 198.5976 | 54.7855 | 190.1071 | 0 | 0 | 100.684 | 341.7737 | 382.6569 | 199.385 | 0 | 0 | 554.4024 | 136.4779 | 136.4779 | 157.5002 | 207.8384 | 216.3746 | 178.1084 | 136.4779 | 136.4779 | 198.5976 | 136.4779 | 136.4779 | 258.1842 | 549.6121 | 599.0315 | 377.4934 | 136.4779 | 136.4779 | 753 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 14 | 3086 | 25.3 | 25.3 | 19.2042 | 17.5498 | 15 | 51 | 51 | 725.8017 | 180.3735 | 51.355 | 213.3787 | 0 | 0 | 0 | 239.4151 | 412.0304 | 343.2838 | 73.4463 | 0 | 588.6265 | 133.6142 | 133.6142 | 133.6142 | 177.3667 | 208.9116 | 196.3484 | 147.0363 | 133.6142 | 180.3735 | 133.6142 | 133.6142 | 133.6142 | 416.7818 | 620.942 | 539.6322 | 220.4826 | 133.6142 | 769 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 15 | 3087 | 23.8 | 23.8 | 19.2042 | 17.5498 | 15 | 58 | 58 | 26.7154 | 304.5069 | 45.0521 | 232.7771 | 0 | 0 | 0 | 3.3608 | 13.9317 | 16.3416 | 9.1788 | 0 | 20.4931 | 134.9804 | 134.9804 | 134.9804 | 147.9905 | 188.9121 | 198.2413 | 170.5131 | 134.9804 | 304.5069 | 134.9804 | 134.9804 | 134.9804 | 151.3512 | 202.8438 | 214.5828 | 179.6919 | 134.9804 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 16 | 3088 | 24.1 | 24.1 | 19.2042 | 17.5498 | 15 | 54 | 54 | 99.9526 | 312.3568 | 37.0242 | 248.5695 | 0 | 0 | 0 | 0 | 42.7149 | 69.9634 | 56.2282 | 9.5553 | 68.6432 | 142.1487 | 142.1487 | 142.1487 | 142.1487 | 192.1867 | 224.1066 | 208.0167 | 153.3422 | 312.3568 | 142.1487 | 142.1487 | 142.1487 | 142.1487 | 234.9016 | 294.07 | 264.2449 | 162.8975 | 381 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 17 | 3089 | 24.2 | 24.2 | 19.2042 | 17.5498 | 15 | 55 | 55 | 433.1693 | 208.6919 | 28.1274 | 261.9308 | 0 | 0 | 0 | 0 | 126.3582 | 316.9833 | 321.9239 | 138.2859 | 249.3081 | 116.1245 | 116.1245 | 116.1245 | 116.1245 | 161.4958 | 229.9433 | 231.7173 | 165.7786 | 208.6919 | 116.1245 | 116.1245 | 116.1245 | 116.1245 | 287.854 | 546.9266 | 553.6412 | 304.0645 | 458 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 9 | 18 | 3090 | 24.2 | 24.2 | 19.2042 | 17.5498 | 15 | 55 | 55 | 231.684 | 194.8149 | 18.9355 | 273.9373 | 0 | 0 | 0 | 0 | 28.6805 | 163.3276 | 202.2995 | 122.7672 | 102.1851 | 98.7246 | 98.7246 | 98.7246 | 98.7246 | 116.3245 | 198.9512 | 222.8664 | 174.0611 | 194.8149 | 98.7246 | 98.7246 | 98.7246 | 98.7246 | 145.0051 | 362.2787 | 425.166 | 296.8283 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 19 | 3091 | 23.5 | 23.5 | 19.2042 | 17.5498 | 15 | 57 | 57 | 105.0269 | 133.2853 | 9.8677 | 285.4015 | 6.8214 | 0 | 0 | 0 | 0 | 65.2571 | 99.1088 | 74.904 | 30.7147 | 71.6556 | 65.377 | 65.377 | 65.377 | 65.377 | 125.4413 | 156.5993 | 134.3205 | 133.2853 | 78.4769 | 65.377 | 65.377 | 65.377 | 65.377 | 190.6984 | 255.7081 | 209.2245 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 20 | 3092 | 21.8 | 21.8 | 19.2042 | 17.5498 | 15 | 61 | 61 | 11.6641 | 48.3691 | 1.2881 | 296.9382 | 3.052 | 0 | 0 | 0 | 0 | 5.6759 | 11.0789 | 9.992 | 1.6309 | 25.091 | 23.7288 | 23.7288 | 23.7288 | 23.7288 | 26.2621 | 28.6735 | 28.1884 | 48.3691 | 28.1429 | 23.7288 | 23.7288 | 23.7288 | 23.7288 | 31.938 | 39.7524 | 38.1804 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 21 | 3093 | 19.7 | 19.7 | 19.2042 | 17.5498 | 15 | 74 | 74 | 0 | 0 | -6.4323 | 309.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 22 | 3094 | 16.6 | 16.6 | 19.2042 | 17.5498 | 15 | 90 | 90 | 0 | 0 | -12.8847 | 322.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 23 | 3095 | 15.7 | 15.7 | 19.2042 | 17.5498 | 15 | 90 | 90 | 0 | 0 | -17.6283 | 336.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 9 | 24 | 3096 | 14.6 | 14.6 | 19.6625 | 18.4841 | 15 | 94 | 94 | 0 | 0 | -20.2512 | 350.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 1 | 3097 | 14.5 | 14.5 | 19.6625 | 18.4841 | 15 | 96 | 96 | 0 | 0 | -20.4829 | 6.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 2 | 3098 | 13.6 | 13.6 | 19.6625 | 18.4841 | 15 | 97 | 97 | 0 | 0 | -18.0359 | 21.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 3 | 3099 | 13.8 | 13.8 | 19.6625 | 18.4841 | 15 | 97 | 97 | 0 | 0 | -13.6752 | 35.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 4 | 3100 | 14.2 | 14.2 | 19.6625 | 18.4841 | 15 | 98 | 98 | 0 | 0 | -7.5248 | 48.4731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 5 | 3101 | 13.9 | 13.9 | 19.6625 | 18.4841 | 15 | 97 | 97 | 0 | 0 | -0.023784 | 60.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 6 | 3102 | 13.6 | 13.6 | 19.6625 | 18.4841 | 15 | 97 | 97 | 55.6576 | 12.4112 | 8.413 | 72.2793 | 27.2486 | 53.5844 | 48.5312 | 15.0491 | 0 | 0 | 0 | 0 | 1.5888 | 9.5371 | 13.8802 | 13.0469 | 7.5252 | 5.0434 | 5.0434 | 5.0434 | 5.0434 | 12.4112 | 36.7856 | 67.4646 | 61.5781 | 22.5743 | 5.0434 | 5.0434 | 5.0434 | 5.0434 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 7 | 3103 | 15.9 | 15.9 | 19.6625 | 18.4841 | 15 | 96 | 96 | 94.9132 | 80.2124 | 17.4105 | 83.7014 | 28.5785 | 83.4495 | 89.4369 | 43.0334 | 0 | 0 | 0 | 0 | 16.7876 | 74.4655 | 143.5832 | 151.1252 | 92.6735 | 38.4668 | 38.4668 | 38.4668 | 38.4668 | 80.2124 | 103.0439 | 227.0327 | 240.5621 | 135.7069 | 38.4668 | 38.4668 | 38.4668 | 38.4668 | 97 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 10 | 8 | 3104 | 18.3 | 18.3 | 19.6625 | 18.4841 | 15 | 83 | 83 | 246.0547 | 143.9788 | 26.6081 | 95.5385 | 25.7578 | 183.2272 | 233.3646 | 146.8002 | 0 | 0 | 0 | 0 | 81.0212 | 88.6003 | 167.1996 | 192.2252 | 149.0175 | 75.7436 | 75.7436 | 75.7436 | 75.7436 | 143.9788 | 114.3581 | 350.4268 | 425.5899 | 295.8177 | 75.7436 | 75.7436 | 75.7436 | 75.7436 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 9 | 3105 | 21.3 | 21.3 | 19.6625 | 18.4841 | 15 | 73 | 73 | 476.0588 | 162.6765 | 35.6046 | 108.5614 | 0 | 270.5193 | 423.6526 | 328.6159 | 41.0805 | 0 | 0 | 0 | 226.3235 | 97.7292 | 172.5983 | 214.9795 | 188.6771 | 109.0986 | 97.7292 | 97.7292 | 97.7292 | 162.6765 | 97.7292 | 443.1176 | 638.6321 | 517.293 | 150.1791 | 97.7292 | 97.7292 | 97.7292 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 10 | 3106 | 23.3 | 23.3 | 19.6625 | 18.4841 | 15 | 64 | 64 | 571.4602 | 179.0813 | 43.8657 | 123.8046 | 0 | 206.87 | 440.4592 | 416.0334 | 147.9009 | 0 | 0 | 0 | 345.9187 | 114.7976 | 165.8851 | 223.571 | 217.5389 | 151.3224 | 114.7976 | 114.7976 | 114.7976 | 179.0813 | 114.7976 | 372.755 | 664.0302 | 633.5723 | 299.2233 | 114.7976 | 114.7976 | 114.7976 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 11 | 3107 | 24.6 | 24.6 | 19.6625 | 18.4841 | 15 | 57 | 57 | 618.5421 | 193.7307 | 50.5954 | 142.4848 | 0 | 86.5834 | 370.5557 | 437.4615 | 248.1083 | 0 | 0 | 0 | 439.2693 | 126.2093 | 145.42 | 208.4263 | 223.271 | 181.2583 | 126.2093 | 126.2093 | 126.2093 | 193.7307 | 126.2093 | 232.0034 | 578.982 | 660.7325 | 429.3666 | 126.2093 | 126.2093 | 126.2093 | 633 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 12 | 3108 | 25.8 | 25.8 | 19.6625 | 18.4841 | 15 | 52 | 52 | 534.1799 | 245.8626 | 54.6756 | 165.198 | 0 | 0 | 206.4986 | 336.2043 | 268.9661 | 44.1712 | 0 | 0 | 418.1374 | 141.6606 | 141.6606 | 211.0959 | 254.7095 | 232.1006 | 156.5132 | 141.6606 | 141.6606 | 245.8626 | 141.6606 | 141.6606 | 417.5945 | 590.9138 | 501.0666 | 200.6843 | 141.6606 | 141.6606 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 13 | 3109 | 25.4 | 25.4 | 19.6625 | 18.4841 | 15 | 52 | 52 | 244.2851 | 358.1521 | 55.0502 | 190.1751 | 0 | 0 | 36.0856 | 122.0785 | 136.5595 | 71.0458 | 0 | 0 | 199.8479 | 158.1931 | 158.1931 | 191.2767 | 270.1157 | 283.392 | 223.3285 | 158.1931 | 158.1931 | 358.1521 | 158.1931 | 158.1931 | 227.3623 | 392.1942 | 419.9515 | 294.3743 | 158.1931 | 158.1931 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 14 | 3110 | 26.8 | 26.8 | 19.6625 | 18.4841 | 15 | 47 | 47 | 658.3962 | 206.2789 | 51.6018 | 213.5444 | 0 | 0 | 0 | 215.3895 | 371.2363 | 309.618 | 66.6296 | 0 | 535.7211 | 136.9056 | 136.9056 | 136.9056 | 184.627 | 219.1563 | 205.5042 | 151.668 | 136.9056 | 206.2789 | 136.9056 | 136.9056 | 136.9056 | 400.0165 | 590.3926 | 515.1222 | 218.2976 | 136.9056 | 742 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 15 | 3111 | 26.5 | 26.5 | 19.6625 | 18.4841 | 15 | 49 | 49 | 218.8452 | 342.5273 | 45.277 | 232.9825 | 0 | 0 | 0 | 26.9969 | 113.2919 | 133.2221 | 75.1125 | 0 | 168.4727 | 159.1521 | 159.1521 | 159.1521 | 180.0508 | 246.8531 | 262.2813 | 217.2978 | 159.1521 | 342.5273 | 159.1521 | 159.1521 | 159.1521 | 207.0477 | 360.145 | 395.5034 | 292.4104 | 159.1521 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 16 | 3112 | 25.9 | 25.9 | 19.6625 | 18.4841 | 15 | 48 | 48 | 36.688 | 285.6997 | 37.2328 | 248.7795 | 0 | 0 | 0 | 0 | 15.5431 | 25.5665 | 20.6133 | 3.5852 | 25.3003 | 128.1996 | 128.1996 | 128.1996 | 128.1996 | 170.9453 | 198.5108 | 184.889 | 138.0593 | 285.6997 | 128.1996 | 128.1996 | 128.1996 | 128.1996 | 186.4884 | 224.0772 | 205.5023 | 141.6445 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 17 | 3113 | 23.5 | 23.5 | 19.6625 | 18.4841 | 15 | 47 | 47 | 2.1255 | 101.7703 | 28.3278 | 262.132 | 0 | 0 | 0 | 0 | 0.61255 | 1.5486 | 1.5776 | 0.68237 | 1.2297 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 101.7703 | 50.0961 | 50.0961 | 50.0961 | 50.0961 | 50.7086 | 51.6447 | 51.6736 | 50.7784 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 10 | 18 | 3114 | 21.2 | 21.2 | 19.6625 | 18.4841 | 15 | 58 | 58 | 0.12266 | 18.9455 | 19.1348 | 274.126 | 0 | 0 | 0 | 0 | 0.014781 | 0.086083 | 0.10696 | 0.06518 | 0.054495 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 18.9455 | 8.9267 | 8.9267 | 8.9267 | 8.9267 | 8.9415 | 9.0128 | 9.0337 | 8.9919 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 19 | 3115 | 20 | 20 | 19.6625 | 18.4841 | 15 | 72 | 72 | 0.22141 | 16.9345 | 10.0719 | 285.5769 | 0.01505 | 0 | 0 | 0 | 0 | 0.13688 | 0.20863 | 0.15817 | 0.065507 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 16.9345 | 7.9705 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 8.0923 | 8.1641 | 8.1136 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 20 | 3116 | 19.5 | 19.5 | 19.6625 | 18.4841 | 15 | 77 | 77 | 0.63863 | 13.9084 | 1.5021 | 297.0988 | 0.16885 | 0 | 0 | 0 | 0 | 0.3089 | 0.6057 | 0.54769 | 0.091621 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 13.9084 | 6.7141 | 6.5452 | 6.5452 | 6.5452 | 6.5452 | 6.8541 | 7.1509 | 7.0929 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 21 | 3117 | 18.7 | 18.7 | 19.6625 | 18.4841 | 15 | 81 | 81 | 0 | 0 | -6.2052 | 309.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 22 | 3118 | 18.3 | 18.3 | 19.6625 | 18.4841 | 15 | 81 | 81 | 0 | 0 | -12.6427 | 322.1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 23 | 3119 | 17.2 | 17.2 | 19.6625 | 18.4841 | 15 | 88 | 88 | 0 | 0 | -17.3725 | 336.1059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 10 | 24 | 3120 | 17.5 | 17.5 | 19.7208 | 19.1404 | 15 | 73 | 73 | 0 | 0 | -19.9861 | 350.9564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 1 | 3121 | 16.4 | 16.4 | 19.7208 | 19.1404 | 15 | 75 | 75 | 0 | 0 | -20.2156 | 6.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 2 | 3122 | 15.6 | 15.6 | 19.7208 | 19.1404 | 15 | 75 | 75 | 0 | 0 | -17.7791 | 21.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 3 | 3123 | 15 | 15 | 19.7208 | 19.1404 | 15 | 75 | 75 | 0 | 0 | -13.4291 | 35.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 4 | 3124 | 14.5 | 14.5 | 19.7208 | 19.1404 | 15 | 75 | 75 | 0 | 0 | -7.2917 | 48.3514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 5 | 3125 | 13.3 | 13.3 | 19.7208 | 19.1404 | 15 | 80 | 80 | 0 | 0 | 0.19708 | 60.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 6 | 3126 | 13.1 | 13.1 | 19.7208 | 19.1404 | 15 | 79 | 79 | 17.9868 | 5.7518 | 8.6243 | 72.1218 | 8.8447 | 17.3287 | 15.6619 | 4.8205 | 0 | 0 | 0 | 0 | 27.2482 | 13.0877 | 19.9665 | 18.615 | 9.825 | 5.9166 | 5.9166 | 5.9166 | 5.9166 | 5.7518 | 21.9324 | 37.2952 | 34.2768 | 14.6454 | 5.9166 | 5.9166 | 5.9166 | 5.9166 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 7 | 3127 | 14.2 | 14.2 | 19.7208 | 19.1404 | 15 | 77 | 77 | 285.7253 | 76.4563 | 17.6163 | 83.5305 | 86.7244 | 251.4313 | 268.8532 | 128.7845 | 0 | 0 | 0 | 0 | 51.5437 | 72.3127 | 128.9618 | 134.9539 | 86.7788 | 42.4848 | 42.4848 | 42.4848 | 42.4848 | 76.4563 | 159.0371 | 380.3931 | 403.8071 | 215.5634 | 42.4848 | 42.4848 | 42.4848 | 42.4848 | 128 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 11 | 8 | 3128 | 16.1 | 16.1 | 19.7208 | 19.1404 | 15 | 72 | 72 | 528.102 | 105.3622 | 26.8137 | 95.3557 | 56.7131 | 393.7484 | 500.1312 | 313.544 | 0 | 0 | 0 | 0 | 175.6378 | 80.4167 | 148.0786 | 169.4357 | 131.9771 | 69.0312 | 69.0312 | 69.0312 | 69.0312 | 105.3622 | 137.1298 | 541.8271 | 669.5669 | 445.5211 | 69.0312 | 69.0312 | 69.0312 | 69.0312 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 9 | 3129 | 17.8 | 17.8 | 19.7208 | 19.1404 | 15 | 66 | 66 | 411.8443 | 177.9317 | 35.8164 | 108.3703 | 0 | 234.5118 | 365.9574 | 283.0301 | 34.3076 | 0 | 0 | 0 | 197.0683 | 100.7242 | 178.812 | 222.5808 | 194.9677 | 112.1479 | 100.7242 | 100.7242 | 100.7242 | 177.9317 | 100.7242 | 413.3238 | 588.5382 | 477.9978 | 146.4556 | 100.7242 | 100.7242 | 100.7242 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 10 | 3130 | 19.8 | 19.8 | 19.7208 | 19.1404 | 15 | 61 | 61 | 583.2028 | 176.2794 | 44.0908 | 123.6168 | 0 | 211.9722 | 448.8171 | 422.751 | 149.0431 | 0 | 0 | 0 | 354.7206 | 114.5251 | 165.29 | 222.0115 | 215.769 | 150.2192 | 114.5251 | 114.5251 | 114.5251 | 176.2794 | 114.5251 | 377.2622 | 670.8286 | 638.52 | 299.2623 | 114.5251 | 114.5251 | 114.5251 | 531 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 11 | 3131 | 21.8 | 21.8 | 19.7208 | 19.1404 | 15 | 49 | 49 | 784.643 | 140.6097 | 50.8393 | 142.3314 | 0 | 111.2298 | 469.3098 | 552.4745 | 312.0071 | 0 | 0 | 0 | 559.3903 | 120.2011 | 132.274 | 171.1401 | 180.1668 | 154.0664 | 120.2011 | 120.2011 | 120.2011 | 140.6097 | 120.2011 | 243.5038 | 640.4499 | 732.6413 | 466.0735 | 120.2011 | 120.2011 | 120.2011 | 700 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 12 | 3132 | 23 | 23 | 19.7208 | 19.1404 | 15 | 49 | 49 | 804.4274 | 149.1892 | 54.9356 | 165.1342 | 0 | 0 | 310.4318 | 503.8409 | 402.1069 | 64.8241 | 0 | 0 | 631.8108 | 128.7779 | 128.7779 | 162.6198 | 183.7045 | 172.6139 | 135.8447 | 128.7779 | 128.7779 | 149.1892 | 128.7779 | 128.7779 | 473.0516 | 687.5454 | 574.7208 | 200.6688 | 128.7779 | 128.7779 | 781 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 13 | 3133 | 23.9 | 23.9 | 19.7208 | 19.1404 | 15 | 45 | 45 | 788.9401 | 160.5209 | 55.3101 | 190.2391 | 0 | 0 | 116.2823 | 391.9888 | 438.0736 | 227.5408 | 0 | 0 | 647.4791 | 132.9644 | 132.9644 | 146.5532 | 178.7723 | 184.1577 | 159.5548 | 132.9644 | 132.9644 | 160.5209 | 132.9644 | 132.9644 | 262.8354 | 570.7611 | 622.2313 | 387.0957 | 132.9644 | 132.9644 | 808 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 14 | 3134 | 24.6 | 24.6 | 19.7208 | 19.1404 | 15 | 42 | 42 | 781.6723 | 161.9335 | 51.8446 | 213.7056 | 0 | 0 | 0 | 253.6475 | 437.7915 | 365.4832 | 79.0798 | 0 | 638.0665 | 132.3709 | 132.3709 | 132.3709 | 162.4764 | 184.3325 | 175.7502 | 141.7569 | 132.3709 | 161.9335 | 132.3709 | 132.3709 | 132.3709 | 416.1238 | 622.124 | 541.2334 | 220.8367 | 132.3709 | 800 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 15 | 3135 | 24.8 | 24.8 | 19.7208 | 19.1404 | 15 | 45 | 45 | 466.4643 | 267.6586 | 45.4985 | 233.1831 | 0 | 0 | 0 | 56.4404 | 239.7373 | 282.5993 | 159.9185 | 0 | 360.3414 | 142.7465 | 142.7465 | 142.7465 | 165.8902 | 241.0519 | 258.6277 | 208.3218 | 142.7465 | 267.6586 | 142.7465 | 142.7465 | 142.7465 | 222.3306 | 480.7892 | 541.2269 | 368.2403 | 142.7465 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 16 | 3136 | 23.1 | 23.1 | 19.7208 | 19.1404 | 15 | 52 | 52 | 305.6485 | 288.372 | 37.4386 | 248.9846 | 0 | 0 | 0 | 0 | 128.3839 | 212.0562 | 171.5089 | 30.494 | 211.628 | 140.4203 | 140.4203 | 140.4203 | 140.4203 | 218.5342 | 269.4438 | 244.7732 | 158.9741 | 288.372 | 140.4203 | 140.4203 | 140.4203 | 140.4203 | 346.918 | 481.5 | 416.2821 | 189.4681 | 500 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 17 | 3137 | 23 | 23 | 19.7208 | 19.1404 | 15 | 50 | 50 | 577.6001 | 170.1288 | 28.5255 | 262.3283 | 0 | 0 | 0 | 0 | 164.4693 | 419.0184 | 428.1122 | 186.4237 | 335.8712 | 108.711 | 108.711 | 108.711 | 108.711 | 144.684 | 200.3595 | 202.3485 | 149.4859 | 170.1288 | 108.711 | 108.711 | 108.711 | 108.711 | 309.1533 | 619.3779 | 630.4607 | 335.9096 | 506 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 11 | 18 | 3138 | 22 | 22 | 19.7208 | 19.1404 | 15 | 49 | 49 | 502.0373 | 147.3931 | 19.3316 | 274.3101 | 0 | 0 | 0 | 0 | 58.8843 | 350.7451 | 437.1442 | 267.4702 | 224.6069 | 91.2185 | 91.2185 | 91.2185 | 91.2185 | 105.9052 | 178.6997 | 200.2489 | 157.9296 | 147.3931 | 91.2185 | 91.2185 | 91.2185 | 91.2185 | 164.7894 | 529.4447 | 637.3931 | 425.3998 | 372 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 19 | 3139 | 20.1 | 20.1 | 19.7208 | 19.1404 | 15 | 54 | 54 | 198.8985 | 134.4871 | 10.2736 | 285.7477 | 14.1052 | 0 | 0 | 0 | 0 | 122.3636 | 187.1535 | 142.3114 | 59.5129 | 78.3957 | 70.0774 | 70.0774 | 70.0774 | 70.0774 | 142.2384 | 180.4467 | 154.0022 | 134.4871 | 92.5009 | 70.0774 | 70.0774 | 70.0774 | 70.0774 | 264.6021 | 367.6002 | 296.3136 | 194 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 20 | 3140 | 19.3 | 19.3 | 19.7208 | 19.1404 | 15 | 51 | 51 | 44.85 | 62.4056 | 1.7133 | 297.2547 | 11.9772 | 0 | 0 | 0 | 0 | 21.5649 | 42.4746 | 38.5032 | 6.5944 | 41.7891 | 30.7488 | 30.7488 | 30.7488 | 30.7488 | 50.6267 | 69.9007 | 66.24 | 62.4056 | 53.7663 | 30.7488 | 30.7488 | 30.7488 | 30.7488 | 72.1916 | 112.3752 | 104.7432 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 21 | 3141 | 17.8 | 17.8 | 19.7208 | 19.1404 | 15 | 53 | 53 | 0.69691 | 0.99 | -5.9811 | 309.305 | 0.319 | 0 | 0 | 0 | 0 | 0.21231 | 0.61926 | 0.66345 | 5.01 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 0.99 | 1.3455 | 1.0265 | 1.0265 | 1.0265 | 1.0265 | 1.2388 | 1.6457 | 1.6899 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 22 | 3142 | 16.4 | 16.4 | 19.7208 | 19.1404 | 15 | 62 | 62 | 0 | 0 | -12.4043 | 322.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 23 | 3143 | 15.2 | 15.2 | 19.7208 | 19.1404 | 15 | 69 | 69 | 0 | 0 | -17.1208 | 336.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 11 | 24 | 3144 | 13.9 | 13.9 | 18.5292 | 19.222 | 15 | 75 | 75 | 0 | 0 | -19.7257 | 350.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 1 | 3145 | 13.3 | 13.3 | 18.5292 | 19.222 | 15 | 78 | 78 | 0 | 0 | -19.9534 | 6.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 2 | 3146 | 13.1 | 13.1 | 18.5292 | 19.222 | 15 | 77 | 77 | 0 | 0 | -17.5276 | 21.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 3 | 3147 | 12.3 | 12.3 | 18.5292 | 19.222 | 15 | 82 | 82 | 0 | 0 | -13.1885 | 35.1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 4 | 3148 | 11.8 | 11.8 | 18.5292 | 19.222 | 15 | 84 | 84 | 0 | 0 | -7.064 | 48.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 5 | 3149 | 11.6 | 11.6 | 18.5292 | 19.222 | 15 | 86 | 86 | 0 | 0 | 0.41256 | 60.4044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 6 | 3150 | 11.5 | 11.5 | 18.5292 | 19.222 | 15 | 88 | 88 | 28.4148 | 16.3993 | 8.8302 | 71.9653 | 14.033 | 27.3933 | 24.707 | 7.5476 | 0 | 0 | 0 | 0 | 5.6007 | 25.4111 | 41.7571 | 38.4705 | 17.4764 | 8.242 | 8.242 | 8.242 | 8.242 | 16.3993 | 39.4441 | 69.1504 | 63.1774 | 25.024 | 8.242 | 8.242 | 8.242 | 8.242 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 7 | 3151 | 12.9 | 12.9 | 18.5292 | 19.222 | 15 | 82 | 82 | 184.2121 | 83.133 | 17.8166 | 83.3607 | 56.3547 | 162.2388 | 173.0856 | 82.5412 | 0 | 0 | 0 | 0 | 33.867 | 74.1814 | 131.7945 | 137.6964 | 88.4299 | 43.518 | 43.518 | 43.518 | 43.518 | 83.133 | 130.5362 | 294.0333 | 310.782 | 170.9711 | 43.518 | 43.518 | 43.518 | 43.518 | 117 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 12 | 8 | 3152 | 15.2 | 15.2 | 18.5292 | 19.222 | 15 | 72 | 72 | 327.952 | 136.8685 | 27.0137 | 95.1739 | 36.0988 | 244.8205 | 310.1297 | 193.7691 | 0 | 0 | 0 | 0 | 110.1315 | 89.0573 | 165.1516 | 188.9615 | 146.5396 | 75.8967 | 75.8967 | 75.8967 | 75.8967 | 136.8685 | 125.1561 | 409.9721 | 499.0912 | 340.3087 | 75.8967 | 75.8967 | 75.8967 | 75.8967 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 9 | 3153 | 18 | 18 | 18.5292 | 19.222 | 15 | 59 | 59 | 670.8557 | 118.9664 | 36.0225 | 108.1797 | 0 | 382.7798 | 595.2286 | 459.0006 | 53.8963 | 0 | 0 | 0 | 323.0336 | 88.7848 | 148.7304 | 182.0012 | 160.6671 | 97.2253 | 88.7848 | 88.7848 | 88.7848 | 118.9664 | 88.7848 | 531.5102 | 777.2298 | 619.6677 | 151.1215 | 88.7848 | 88.7848 | 88.7848 | 442 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 10 | 3154 | 19.7 | 19.7 | 18.5292 | 19.222 | 15 | 51 | 51 | 530.8697 | 192.6039 | 44.3102 | 123.4287 | 0 | 193.7246 | 407.9275 | 383.172 | 133.9596 | 0 | 0 | 0 | 324.3961 | 117.7741 | 171.6981 | 231.3223 | 224.4315 | 155.0623 | 117.7741 | 117.7741 | 117.7741 | 192.6039 | 117.7741 | 365.4227 | 639.2498 | 607.6036 | 289.0219 | 117.7741 | 117.7741 | 117.7741 | 517 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 11 | 3155 | 22.2 | 22.2 | 18.5292 | 19.222 | 15 | 43 | 43 | 803.4894 | 136.0141 | 51.0775 | 142.1763 | 0 | 115.328 | 479.8387 | 563.2663 | 316.7402 | 0 | 0 | 0 | 574.9859 | 119.9994 | 131.9412 | 169.6851 | 178.3238 | 152.7968 | 119.9994 | 119.9994 | 119.9994 | 136.0141 | 119.9994 | 247.2692 | 649.5238 | 741.5901 | 469.537 | 119.9994 | 119.9994 | 119.9994 | 711 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 12 | 3156 | 23.8 | 23.8 | 18.5292 | 19.222 | 15 | 38 | 38 | 799.7047 | 150.8309 | 55.1902 | 165.0671 | 0 | 0 | 308.1067 | 498.4932 | 396.8691 | 62.7645 | 0 | 0 | 630.1691 | 129.1181 | 129.1181 | 163.1562 | 184.1892 | 172.9623 | 136.052 | 129.1181 | 129.1181 | 150.8309 | 129.1181 | 129.1181 | 471.263 | 682.6824 | 569.8314 | 198.8165 | 129.1181 | 129.1181 | 781 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 13 | 3157 | 24.5 | 24.5 | 18.5292 | 19.222 | 15 | 41 | 41 | 762.1371 | 169.5852 | 55.5654 | 190.299 | 0 | 0 | 112.1118 | 376.5258 | 420.3762 | 217.9759 | 0 | 0 | 627.4148 | 133.8891 | 133.8891 | 147.9868 | 181.2363 | 186.7503 | 161.299 | 133.8891 | 133.8891 | 169.5852 | 133.8891 | 133.8891 | 260.0986 | 557.7621 | 607.1265 | 379.2748 | 133.8891 | 133.8891 | 797 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 14 | 3158 | 25.1 | 25.1 | 18.5292 | 19.222 | 15 | 39 | 39 | 764.764 | 167.7914 | 52.0833 | 213.8621 | 0 | 0 | 0 | 246.1898 | 425.4801 | 355.5299 | 77.3151 | 0 | 626.2086 | 133.0434 | 133.0434 | 133.0434 | 163.6705 | 185.9749 | 177.2728 | 142.6617 | 133.0434 | 167.7914 | 133.0434 | 133.0434 | 133.0434 | 409.8603 | 611.455 | 532.8027 | 219.9769 | 133.0434 | 794 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 15 | 3159 | 25.2 | 25.2 | 18.5292 | 19.222 | 15 | 41 | 41 | 743.3419 | 165.8371 | 45.7166 | 233.3789 | 0 | 0 | 0 | 88.2393 | 379.3137 | 448.1913 | 254.5245 | 0 | 576.1629 | 128.061 | 128.061 | 128.061 | 142.8292 | 191.5452 | 203.0729 | 170.6597 | 128.061 | 165.8371 | 128.061 | 128.061 | 128.061 | 231.0685 | 570.8588 | 651.2642 | 425.1842 | 128.061 | 742 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 16 | 3160 | 25.4 | 25.4 | 18.5292 | 19.222 | 15 | 41 | 41 | 673.4555 | 170.8771 | 37.6413 | 249.1847 | 0 | 0 | 0 | 0 | 280.4913 | 465.1932 | 377.3912 | 68.5185 | 468.1229 | 120.7369 | 120.7369 | 120.7369 | 120.7369 | 173.6294 | 208.4588 | 191.9019 | 133.6575 | 170.8771 | 120.7369 | 120.7369 | 120.7369 | 120.7369 | 454.1208 | 673.652 | 569.2931 | 202.176 | 639 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 17 | 3161 | 25.2 | 25.2 | 18.5292 | 19.222 | 15 | 44 | 44 | 466.744 | 202.2497 | 28.7206 | 262.5198 | 0 | 0 | 0 | 0 | 131.3365 | 337.1517 | 345.468 | 151.4139 | 272.7503 | 115.8765 | 115.8765 | 115.8765 | 115.8765 | 158.861 | 226.2214 | 228.9432 | 165.4321 | 202.2497 | 115.8765 | 115.8765 | 115.8765 | 115.8765 | 290.1975 | 563.373 | 574.4112 | 316.8459 | 475 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 18 | 3162 | 24.7 | 24.7 | 18.5292 | 19.222 | 15 | 43 | 43 | 356.8744 | 178.2435 | 19.5258 | 274.4893 | 0 | 0 | 0 | 0 | 40.7435 | 248.2295 | 310.306 | 190.6095 | 160.7565 | 97.9731 | 97.9731 | 97.9731 | 97.9731 | 113.2078 | 190.7902 | 214.0017 | 169.2452 | 178.2435 | 97.9731 | 97.9731 | 97.9731 | 97.9731 | 153.9513 | 439.0197 | 524.3077 | 359.8546 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 19 | 3163 | 23.5 | 23.5 | 18.5292 | 19.222 | 15 | 44 | 44 | 243.421 | 132.3673 | 10.4727 | 285.9137 | 17.9575 | 0 | 0 | 0 | 0 | 149.0303 | 228.7182 | 174.4261 | 73.6327 | 79.18 | 70.6251 | 70.6251 | 70.6251 | 70.6251 | 141.6225 | 179.5855 | 153.7209 | 132.3673 | 97.1375 | 70.6251 | 70.6251 | 70.6251 | 70.6251 | 290.6528 | 408.3037 | 328.147 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 20 | 3164 | 21.7 | 21.7 | 18.5292 | 19.222 | 15 | 47 | 47 | 39.9519 | 62.986 | 1.9218 | 297.406 | 10.7719 | 0 | 0 | 0 | 0 | 19.0982 | 37.7808 | 34.3319 | 6.014 | 41.9841 | 30.9919 | 30.9919 | 30.9919 | 30.9919 | 50.4807 | 69.5455 | 66.026 | 62.986 | 52.756 | 30.9919 | 30.9919 | 30.9919 | 30.9919 | 69.5789 | 107.3262 | 100.358 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 21 | 3165 | 19.8 | 19.8 | 18.5292 | 19.222 | 15 | 52 | 52 | 1.6786 | 2.2391 | -5.7601 | 309.4379 | 0.77221 | 0 | 0 | 0 | 0 | 0.5071 | 1.4894 | 1.5992 | 0.76087 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 2.2391 | 2.0379 | 1.2657 | 1.2657 | 1.2657 | 1.2657 | 1.7728 | 2.7551 | 2.8649 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 22 | 3166 | 18.7 | 18.7 | 18.5292 | 19.222 | 15 | 53 | 53 | 0 | 0 | -12.1694 | 322.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 23 | 3167 | 17.2 | 17.2 | 18.5292 | 19.222 | 15 | 56 | 56 | 0 | 0 | -16.8734 | 336.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 12 | 24 | 3168 | 15.8 | 15.8 | 18.8417 | 19.1654 | 15 | 57 | 57 | 0 | 0 | -19.4699 | 351.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 1 | 3169 | 15.5 | 15.5 | 18.8417 | 19.1654 | 15 | 54 | 54 | 0 | 0 | -19.6962 | 6.1643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 2 | 3170 | 14.5 | 14.5 | 18.8417 | 19.1654 | 15 | 55 | 55 | 0 | 0 | -17.2816 | 20.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 3 | 3171 | 13.8 | 13.8 | 18.8417 | 19.1654 | 15 | 56 | 56 | 0 | 0 | -12.9534 | 35.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 4 | 3172 | 13.1 | 13.1 | 18.8417 | 19.1654 | 15 | 57 | 57 | 0 | 0 | -6.8418 | 48.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 5 | 3173 | 12.6 | 12.6 | 18.8417 | 19.1654 | 15 | 59 | 59 | 0 | 0 | 0.62259 | 60.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 6 | 3174 | 12.7 | 12.7 | 18.8417 | 19.1654 | 15 | 59 | 59 | 33.9859 | 17.97 | 9.0307 | 71.8101 | 16.8559 | 32.785 | 29.509 | 8.9471 | 0 | 0 | 0 | 0 | 4.03 | 28.0803 | 46.3287 | 42.5757 | 19.0198 | 8.77 | 8.77 | 8.77 | 8.77 | 17.97 | 44.9362 | 79.1137 | 72.0847 | 27.9669 | 8.77 | 8.77 | 8.77 | 8.77 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 7 | 3175 | 13.5 | 13.5 | 18.8417 | 19.1654 | 15 | 59 | 59 | 120.1547 | 85.5036 | 18.0115 | 83.1921 | 37.0435 | 105.9096 | 112.7352 | 53.5221 | 0 | 0 | 0 | 0 | 22.4964 | 78.4605 | 147.3601 | 154.1891 | 94.9472 | 41.3989 | 41.3989 | 41.3989 | 41.3989 | 85.5036 | 115.504 | 253.2697 | 266.9244 | 148.4693 | 41.3989 | 41.3989 | 41.3989 | 41.3989 | 108 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 13 | 8 | 3176 | 14.9 | 14.9 | 18.8417 | 19.1654 | 15 | 55 | 55 | 95.6131 | 153.5892 | 27.2083 | 94.9931 | 10.7786 | 71.4637 | 90.2864 | 56.2206 | 0 | 0 | 0 | 0 | 32.4108 | 83.3234 | 146.6805 | 166.332 | 130.7662 | 72.0702 | 72.0702 | 72.0702 | 72.0702 | 153.5892 | 94.1019 | 218.1443 | 256.6184 | 186.9867 | 72.0702 | 72.0702 | 72.0702 | 72.0702 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 9 | 3177 | 18.6 | 18.6 | 18.8417 | 19.1654 | 15 | 47 | 47 | 616.6836 | 132.23 | 36.2229 | 107.9898 | 0 | 352.5858 | 546.3666 | 420.0932 | 47.735 | 0 | 0 | 0 | 298.77 | 91.4495 | 154.6436 | 189.375 | 166.743 | 100.0051 | 91.4495 | 91.4495 | 91.4495 | 132.23 | 91.4495 | 507.2294 | 735.7416 | 586.8362 | 147.74 | 91.4495 | 91.4495 | 91.4495 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 10 | 3178 | 19.8 | 19.8 | 18.8417 | 19.1654 | 15 | 42 | 42 | 770.0288 | 124.3297 | 44.5238 | 123.2404 | 0 | 282.1178 | 590.831 | 553.4435 | 191.8562 | 0 | 0 | 0 | 472.6703 | 105.2733 | 143.4205 | 185.1638 | 180.1083 | 131.2156 | 105.2733 | 105.2733 | 105.2733 | 124.3297 | 105.2733 | 425.5382 | 775.9948 | 733.5518 | 323.0718 | 105.2733 | 105.2733 | 105.2733 | 597 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 11 | 3179 | 21.9 | 21.9 | 18.8417 | 19.1654 | 15 | 34 | 34 | 739.918 | 154.5672 | 51.31 | 142.0195 | 0 | 107.5142 | 441.216 | 516.4594 | 289.168 | 0 | 0 | 0 | 531.4328 | 121.3815 | 138.6174 | 192.1137 | 204.1762 | 167.7386 | 121.3815 | 121.3815 | 121.3815 | 154.5672 | 121.3815 | 246.1315 | 633.3297 | 720.6356 | 456.9066 | 121.3815 | 121.3815 | 121.3815 | 686 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 12 | 3180 | 23.3 | 23.3 | 18.8417 | 19.1654 | 15 | 33 | 33 | 714.7542 | 178.9715 | 55.4394 | 164.9968 | 0 | 0 | 274.9561 | 443.4482 | 352.1743 | 54.6015 | 0 | 0 | 565.0285 | 131.8116 | 131.8116 | 182.3542 | 213.3266 | 196.5485 | 141.8485 | 131.8116 | 131.8116 | 178.9715 | 131.8116 | 131.8116 | 457.3104 | 656.7747 | 548.7228 | 196.45 | 131.8116 | 131.8116 | 744 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 13 | 3181 | 23.8 | 23.8 | 18.8417 | 19.1654 | 15 | 31 | 31 | 740.6762 | 177.423 | 55.8158 | 190.3546 | 0 | 0 | 108.7705 | 363.8888 | 405.8459 | 210.064 | 0 | 0 | 611.577 | 134.6561 | 134.6561 | 153.905 | 199.0528 | 206.4778 | 171.8307 | 134.6561 | 134.6561 | 177.423 | 134.6561 | 134.6561 | 262.6755 | 562.9415 | 612.3238 | 381.8947 | 134.6561 | 134.6561 | 789 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 14 | 3182 | 24.1 | 24.1 | 18.8417 | 19.1654 | 15 | 32 | 32 | 788.4737 | 160.4251 | 52.3179 | 214.014 | 0 | 0 | 0 | 251.8477 | 435.7929 | 364.4565 | 79.6264 | 0 | 647.5749 | 132.6235 | 132.6235 | 132.6235 | 162.0529 | 183.5476 | 175.2117 | 141.9281 | 132.6235 | 160.4251 | 132.6235 | 132.6235 | 132.6235 | 413.9006 | 619.3405 | 539.6682 | 221.5546 | 132.6235 | 808 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 15 | 3183 | 24.3 | 24.3 | 18.8417 | 19.1654 | 15 | 30 | 30 | 602.1107 | 217.7778 | 45.9311 | 233.5696 | 0 | 0 | 0 | 70.1405 | 305.0836 | 361.3129 | 205.8899 | 0 | 468.2222 | 134.7355 | 134.7355 | 134.7355 | 152.219 | 210.7817 | 224.7976 | 186.0564 | 134.7355 | 217.7778 | 134.7355 | 134.7355 | 134.7355 | 222.3595 | 515.8653 | 586.1105 | 391.9463 | 134.7355 | 686 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 16 | 3184 | 25 | 25 | 18.8417 | 19.1654 | 15 | 30 | 30 | 675.4649 | 170.6911 | 37.8411 | 249.3798 | 0 | 0 | 0 | 0 | 278.9891 | 464.5558 | 377.992 | 70.0056 | 471.3089 | 120.9332 | 120.9332 | 120.9332 | 120.9332 | 173.3405 | 208.1987 | 191.9379 | 134.0835 | 170.6911 | 120.9332 | 120.9332 | 120.9332 | 120.9332 | 452.3297 | 672.7545 | 569.9299 | 204.0891 | 642 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 17 | 3185 | 24.7 | 24.7 | 18.8417 | 19.1654 | 15 | 29 | 29 | 651.8384 | 150.2574 | 28.9129 | 262.7063 | 0 | 0 | 0 | 0 | 181.286 | 468.8644 | 481.7885 | 212.4874 | 382.7426 | 106.1028 | 106.1028 | 106.1028 | 106.1028 | 138.7561 | 190.5548 | 192.8827 | 144.3761 | 150.2574 | 106.1028 | 106.1028 | 106.1028 | 106.1028 | 320.042 | 659.4192 | 674.6711 | 356.8635 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 18 | 3186 | 24.2 | 24.2 | 18.8417 | 19.1654 | 15 | 32 | 32 | 494.3212 | 150.8482 | 19.7175 | 274.6637 | 0 | 0 | 0 | 0 | 54.9343 | 342.3385 | 429.2054 | 264.6496 | 224.1518 | 92.5284 | 92.5284 | 92.5284 | 92.5284 | 106.628 | 180.3937 | 202.6891 | 160.4539 | 150.8482 | 92.5284 | 92.5284 | 92.5284 | 92.5284 | 161.5623 | 522.7322 | 631.8945 | 425.1035 | 375 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 19 | 3187 | 23.1 | 23.1 | 18.8417 | 19.1654 | 15 | 38 | 38 | 362.6217 | 120.1465 | 10.6692 | 286.0749 | 27.7549 | 0 | 0 | 0 | 0 | 220.9533 | 340.2301 | 260.2047 | 110.8535 | 77.5114 | 68.9116 | 68.9116 | 68.9116 | 68.9116 | 137.3735 | 174.3312 | 149.5355 | 120.1465 | 105.2663 | 68.9116 | 68.9116 | 68.9116 | 68.9116 | 358.3269 | 514.5613 | 409.7402 | 231 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 20 | 3188 | 19.5 | 19.5 | 18.8417 | 19.1654 | 15 | 42 | 42 | 121.3224 | 70.3213 | 2.1273 | 297.5526 | 33.0127 | 0 | 0 | 0 | 0 | 57.6651 | 114.5635 | 104.3521 | 18.6787 | 55.6983 | 36.0418 | 36.0418 | 36.0418 | 36.0418 | 70.3769 | 104.2553 | 98.1753 | 70.3213 | 88.711 | 36.0418 | 36.0418 | 36.0418 | 36.0418 | 128.0419 | 218.8188 | 202.5274 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 21 | 3189 | 16.1 | 16.1 | 18.8417 | 19.1654 | 15 | 68 | 68 | 10.8155 | 2.9076 | -5.5424 | 309.5663 | 4.9994 | 0 | 0 | 0 | 0 | 3.2406 | 9.5823 | 10.3108 | 0.092415 | 5.9192 | 1.6763 | 1.6763 | 1.6763 | 1.6763 | 4.4265 | 9.8086 | 10.4269 | 2.9076 | 10.9186 | 1.6763 | 1.6763 | 1.6763 | 1.6763 | 7.6671 | 19.3909 | 20.7377 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 22 | 3190 | 13.3 | 13.3 | 18.8417 | 19.1654 | 15 | 79 | 79 | 0 | 0 | -11.9383 | 322.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 23 | 3191 | 12 | 12 | 18.8417 | 19.1654 | 15 | 83 | 83 | 0 | 0 | -16.6302 | 336.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 13 | 24 | 3192 | 11.7 | 11.7 | 18.1667 | 18.8724 | 15 | 80 | 80 | 0 | 0 | -19.219 | 351.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 1 | 3193 | 12.8 | 12.8 | 18.1667 | 18.8724 | 15 | 68 | 68 | 0 | 0 | -19.4443 | 6.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 2 | 3194 | 12.5 | 12.5 | 18.1667 | 18.8724 | 15 | 71 | 71 | 0 | 0 | -17.0411 | 20.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 3 | 3195 | 11 | 11 | 18.1667 | 18.8724 | 15 | 80 | 80 | 0 | 0 | -12.7238 | 34.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 4 | 3196 | 9.8 | 9.8 | 18.1667 | 18.8724 | 15 | 84 | 84 | 0 | 0 | -6.6251 | 47.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 5 | 3197 | 9.5 | 9.5 | 18.1667 | 18.8724 | 15 | 89 | 89 | 0 | 0 | 0.82712 | 60.1255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 6 | 3198 | 11.2 | 11.2 | 18.1667 | 18.8724 | 15 | 84 | 84 | 53.3287 | 13.9431 | 9.2257 | 71.6561 | 26.5604 | 51.4759 | 46.2375 | 13.9138 | 0 | 0 | 0 | 0 | 22.0569 | 22.9076 | 35.5014 | 32.8536 | 16.5152 | 9.4823 | 9.4823 | 9.4823 | 9.4823 | 13.9431 | 49.468 | 86.9773 | 79.0911 | 30.429 | 9.4823 | 9.4823 | 9.4823 | 9.4823 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 7 | 3199 | 15.4 | 15.4 | 18.1667 | 18.8724 | 15 | 65 | 65 | 499.1414 | 62.8951 | 18.2009 | 83.0249 | 155.0578 | 440.32 | 467.6488 | 221.0352 | 0 | 0 | 0 | 0 | 95.1049 | 64.6677 | 110.2062 | 114.5689 | 75.2002 | 39.9147 | 39.9147 | 39.9147 | 39.9147 | 62.8951 | 219.7255 | 550.5262 | 582.2177 | 296.2354 | 39.9147 | 39.9147 | 39.9147 | 39.9147 | 158 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 14 | 8 | 3200 | 18.2 | 18.2 | 18.1667 | 18.8724 | 15 | 62 | 62 | 688.4172 | 81.5131 | 27.3972 | 94.8136 | 79.417 | 515.163 | 649.1335 | 402.8504 | 0 | 0 | 0 | 0 | 235.4869 | 74.6779 | 132.249 | 149.9492 | 117.4102 | 64.1853 | 64.1853 | 64.1853 | 64.1853 | 81.5131 | 154.0949 | 647.412 | 799.0828 | 520.2606 | 64.1853 | 64.1853 | 64.1853 | 64.1853 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 9 | 3201 | 20.7 | 20.7 | 18.1667 | 18.8724 | 15 | 51 | 51 | 773.8354 | 97.8611 | 36.4177 | 107.8007 | 0 | 443.3308 | 684.6173 | 524.8643 | 57.6529 | 0 | 0 | 0 | 377.1389 | 85.5832 | 139.1227 | 168.262 | 148.9692 | 92.5457 | 85.5832 | 85.5832 | 85.5832 | 97.8611 | 85.5832 | 582.4535 | 852.8793 | 673.8335 | 150.1986 | 85.5832 | 85.5832 | 85.5832 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 10 | 3202 | 22.3 | 22.3 | 18.1667 | 18.8724 | 15 | 44 | 44 | 807.6764 | 116.0386 | 44.7315 | 123.052 | 0 | 297.0819 | 618.8301 | 578.076 | 198.6929 | 0 | 0 | 0 | 497.9614 | 106.0015 | 134.3447 | 165.0411 | 161.1529 | 124.9579 | 106.0015 | 106.0015 | 106.0015 | 116.0386 | 106.0015 | 431.4266 | 783.8712 | 739.229 | 323.6507 | 106.0015 | 106.0015 | 106.0015 | 614 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 11 | 3203 | 24 | 24 | 18.1667 | 18.8724 | 15 | 36 | 36 | 837.786 | 129.1356 | 51.5367 | 141.8611 | 0 | 123.215 | 498.86 | 582.2795 | 324.6076 | 0 | 0 | 0 | 603.8644 | 120.1791 | 131.9598 | 167.8758 | 175.8517 | 151.2153 | 120.1791 | 120.1791 | 120.1791 | 129.1356 | 120.1791 | 255.1749 | 666.7358 | 758.1313 | 475.8229 | 120.1791 | 120.1791 | 120.1791 | 733 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 12 | 3204 | 25.3 | 25.3 | 18.1667 | 18.8724 | 15 | 32 | 32 | 845.3646 | 140.6474 | 55.6831 | 164.9232 | 0 | 0 | 324.7351 | 522.0619 | 413.5719 | 62.8171 | 0 | 0 | 670.3526 | 129.3366 | 129.3366 | 161.5723 | 181.1605 | 170.3909 | 135.5723 | 129.3366 | 129.3366 | 140.6474 | 129.3366 | 129.3366 | 486.3074 | 703.2224 | 583.9629 | 198.3894 | 129.3366 | 129.3366 | 811 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 13 | 3205 | 24.9 | 24.9 | 18.1667 | 18.8724 | 15 | 33 | 33 | 845.4738 | 146.8586 | 56.0614 | 190.406 | 0 | 0 | 123.9834 | 413.1117 | 460.2448 | 237.7727 | 0 | 0 | 700.1414 | 133.2376 | 133.2376 | 145.8964 | 175.4167 | 180.229 | 157.5144 | 133.2376 | 133.2376 | 146.8586 | 133.2376 | 133.2376 | 269.8799 | 588.5284 | 640.4738 | 395.2871 | 133.2376 | 133.2376 | 847 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 14 | 3206 | 26.4 | 26.4 | 18.1667 | 18.8724 | 15 | 31 | 31 | 826.6573 | 150.0724 | 52.5484 | 214.161 | 0 | 0 | 0 | 262.0348 | 453.9351 | 379.9264 | 83.362 | 0 | 680.9276 | 132.3153 | 132.3153 | 132.3153 | 160.1212 | 180.4847 | 172.6313 | 141.1613 | 132.3153 | 150.0724 | 132.3153 | 132.3153 | 132.3153 | 422.156 | 634.4198 | 552.5577 | 224.5233 | 132.3153 | 831 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 15 | 3207 | 26.7 | 26.7 | 18.1667 | 18.8724 | 15 | 31 | 31 | 787.8483 | 152.3955 | 46.1422 | 233.7553 | 0 | 0 | 0 | 90.0915 | 396.4241 | 470.5369 | 269.0155 | 0 | 614.6045 | 127.6469 | 127.6469 | 127.6469 | 137.8091 | 172.3629 | 180.7227 | 157.9914 | 127.6469 | 152.3955 | 127.6469 | 127.6469 | 127.6469 | 227.9006 | 568.787 | 651.2596 | 427.0069 | 127.6469 | 767 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 16 | 3208 | 26.6 | 26.6 | 18.1667 | 18.8724 | 15 | 31 | 31 | 762.8589 | 143.7419 | 38.0378 | 249.5698 | 0 | 0 | 0 | 0 | 312.5053 | 522.4041 | 426.2856 | 80.4548 | 534.2581 | 118.332 | 118.332 | 118.332 | 118.332 | 153.5737 | 177.2443 | 166.4049 | 127.405 | 143.7419 | 118.332 | 118.332 | 118.332 | 118.332 | 466.079 | 699.6484 | 592.6905 | 207.8599 | 678 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 17 | 3209 | 26.3 | 26.3 | 18.1667 | 18.8724 | 15 | 30 | 30 | 689.4434 | 140.2893 | 29.1025 | 262.8878 | 0 | 0 | 0 | 0 | 189.5457 | 493.8421 | 508.8526 | 225.784 | 406.7107 | 104.684 | 104.684 | 104.684 | 104.684 | 135.5532 | 185.1106 | 187.5552 | 141.4549 | 140.2893 | 104.684 | 104.684 | 104.684 | 104.684 | 325.0989 | 678.9528 | 696.4078 | 367.239 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 14 | 18 | 3210 | 25.5 | 25.5 | 18.1667 | 18.8724 | 15 | 35 | 35 | 544.1577 | 140.6568 | 19.9065 | 274.8332 | 0 | 0 | 0 | 0 | 58.8675 | 375.2385 | 471.7999 | 291.9873 | 248.3432 | 90.7253 | 90.7253 | 90.7253 | 90.7253 | 103.8667 | 174.4928 | 196.049 | 155.9079 | 140.6568 | 90.7253 | 90.7253 | 90.7253 | 90.7253 | 162.7343 | 549.7313 | 667.8489 | 447.8952 | 389 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 19 | 3211 | 24.6 | 24.6 | 18.1667 | 18.8724 | 15 | 32 | 32 | 317.1911 | 127.0394 | 10.8629 | 286.2313 | 25.128 | 0 | 0 | 0 | 0 | 192.3686 | 297.1784 | 227.905 | 97.9606 | 79.7621 | 70.8454 | 70.8454 | 70.8454 | 70.8454 | 139.1079 | 176.2999 | 151.7181 | 127.0394 | 104.8902 | 70.8454 | 70.8454 | 70.8454 | 70.8454 | 331.4765 | 473.4782 | 379.6231 | 225 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 20 | 3212 | 22.5 | 22.5 | 18.1667 | 18.8724 | 15 | 39 | 39 | 94.1328 | 71.1916 | 2.3299 | 297.6945 | 25.8402 | 0 | 0 | 0 | 0 | 44.4919 | 88.7613 | 81.0355 | 14.8084 | 55.851 | 36.0804 | 36.0804 | 36.0804 | 36.0804 | 70.1217 | 103.9927 | 98.0816 | 71.1916 | 81.6912 | 36.0804 | 36.0804 | 36.0804 | 36.0804 | 114.6136 | 192.754 | 179.1171 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 21 | 3213 | 18.3 | 18.3 | 18.1667 | 18.8724 | 15 | 63 | 63 | 4.1249 | 2.9501 | -5.328 | 309.6901 | 1.9155 | 0 | 0 | 0 | 0 | 1.226 | 3.6494 | 3.9349 | 0.049941 | 2.8664 | 1.6544 | 1.6544 | 1.6544 | 1.6544 | 2.4301 | 3.9634 | 4.1441 | 2.9501 | 4.7819 | 1.6544 | 1.6544 | 1.6544 | 1.6544 | 3.6562 | 7.6128 | 8.0791 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 22 | 3214 | 17.9 | 17.9 | 18.1667 | 18.8724 | 15 | 63 | 63 | 0 | 0 | -11.7111 | 322.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 23 | 3215 | 15.3 | 15.3 | 18.1667 | 18.8724 | 15 | 77 | 77 | 0 | 0 | -16.3914 | 336.3962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 14 | 24 | 3216 | 13.2 | 13.2 | 19.2042 | 18.9303 | 15 | 86 | 86 | 0 | 0 | -18.973 | 351.0792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 1 | 3217 | 13 | 13 | 19.2042 | 18.9303 | 15 | 92 | 92 | 0 | 0 | -19.1976 | 6.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 2 | 3218 | 13.2 | 13.2 | 19.2042 | 18.9303 | 15 | 93 | 93 | 0 | 0 | -16.8061 | 20.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 3 | 3219 | 12.3 | 12.3 | 19.2042 | 18.9303 | 15 | 95 | 95 | 0 | 0 | -12.4999 | 34.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 4 | 3220 | 11.2 | 11.2 | 19.2042 | 18.9303 | 15 | 96 | 96 | 0 | 0 | -6.414 | 47.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 5 | 3221 | 11.5 | 11.5 | 19.2042 | 18.9303 | 15 | 97 | 97 | 0 | 0 | 1.0261 | 59.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 6 | 3222 | 12.3 | 12.3 | 19.2042 | 18.9303 | 15 | 98 | 98 | 51.08 | 20.5775 | 9.4151 | 71.5034 | 25.5454 | 49.3344 | 44.224 | 13.2077 | 0 | 0 | 0 | 0 | 10.4225 | 26.0865 | 39.8896 | 36.9244 | 18.9277 | 11.2641 | 11.2641 | 11.2641 | 11.2641 | 20.5775 | 51.6319 | 89.2241 | 81.1484 | 32.1354 | 11.2641 | 11.2641 | 11.2641 | 11.2641 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 7 | 3223 | 17.5 | 17.5 | 19.2042 | 18.9303 | 15 | 78 | 78 | 324.6261 | 79.0965 | 18.3848 | 82.8591 | 101.5995 | 286.5969 | 303.7097 | 142.9135 | 0 | 0 | 0 | 0 | 62.9035 | 71.4886 | 120.0755 | 124.5699 | 82.3391 | 44.805 | 44.805 | 44.805 | 44.805 | 79.0965 | 173.0881 | 406.6724 | 428.2796 | 225.2526 | 44.805 | 44.805 | 44.805 | 44.805 | 142 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 15 | 8 | 3224 | 20.2 | 20.2 | 19.2042 | 18.9303 | 15 | 68 | 68 | 577.9363 | 100.5597 | 27.5805 | 94.6354 | 68.1761 | 433.0042 | 544.1843 | 336.5886 | 0 | 0 | 0 | 0 | 199.4403 | 79.7538 | 141.5816 | 160.4235 | 125.242 | 68.1999 | 68.1999 | 68.1999 | 68.1999 | 100.5597 | 147.9298 | 574.5858 | 704.6078 | 461.8306 | 68.1999 | 68.1999 | 68.1999 | 68.1999 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 9 | 3225 | 22.8 | 22.8 | 19.2042 | 18.9303 | 15 | 55 | 55 | 725.5048 | 108.3734 | 36.6067 | 107.6125 | 0 | 416.4767 | 640.956 | 489.972 | 51.969 | 0 | 0 | 0 | 355.6266 | 87.7891 | 144.8629 | 175.6255 | 154.9347 | 94.9109 | 87.7891 | 87.7891 | 87.7891 | 108.3734 | 87.7891 | 561.3396 | 816.5815 | 644.9067 | 146.88 | 87.7891 | 87.7891 | 87.7891 | 464 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 10 | 3226 | 24.9 | 24.9 | 19.2042 | 18.9303 | 15 | 44 | 44 | 756.5528 | 128.566 | 44.9334 | 122.8637 | 0 | 279.3711 | 578.8528 | 539.2503 | 183.7623 | 0 | 0 | 0 | 468.434 | 106.4779 | 145.7481 | 187.8451 | 182.2783 | 132.3087 | 106.4779 | 106.4779 | 106.4779 | 128.566 | 106.4779 | 425.1192 | 766.6979 | 721.5286 | 316.071 | 106.4779 | 106.4779 | 106.4779 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 11 | 3227 | 26.6 | 26.6 | 19.2042 | 18.9303 | 15 | 44 | 44 | 728.8742 | 158.8248 | 51.7575 | 141.7014 | 0 | 108.4806 | 433.4133 | 504.4583 | 279.9985 | 0 | 0 | 0 | 527.1752 | 122.4319 | 140.4114 | 194.2657 | 206.0407 | 168.8388 | 122.4319 | 122.4319 | 122.4319 | 158.8248 | 122.4319 | 248.8921 | 627.679 | 710.499 | 448.8373 | 122.4319 | 122.4319 | 122.4319 | 686 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 12 | 3228 | 27.3 | 27.3 | 19.2042 | 18.9303 | 15 | 34 | 34 | 633.3895 | 210.2263 | 55.9213 | 164.8465 | 0 | 0 | 242.9844 | 389.3834 | 307.6869 | 45.7516 | 0 | 0 | 503.7737 | 136.0345 | 136.0345 | 192.2382 | 226.1011 | 207.2042 | 146.6171 | 136.0345 | 136.0345 | 210.2263 | 136.0345 | 136.0345 | 435.2226 | 615.4845 | 514.8911 | 192.3686 | 136.0345 | 136.0345 | 714 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 13 | 3229 | 27.3 | 27.3 | 19.2042 | 18.9303 | 15 | 30 | 30 | 792.9991 | 160.4586 | 56.302 | 190.453 | 0 | 0 | 116.1536 | 385.4052 | 428.8917 | 221.1392 | 0 | 0 | 658.5414 | 133.6825 | 133.6825 | 147.177 | 178.4582 | 183.5103 | 159.3741 | 133.6825 | 133.6825 | 160.4586 | 133.6825 | 133.6825 | 263.3306 | 563.8634 | 612.402 | 380.5133 | 133.6825 | 133.6825 | 819 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 14 | 3230 | 27.9 | 27.9 | 19.2042 | 18.9303 | 15 | 30 | 30 | 775.9981 | 164.9816 | 52.7745 | 214.3031 | 0 | 0 | 0 | 244.1486 | 423.3901 | 354.6154 | 78.1118 | 0 | 641.0184 | 133.3098 | 133.3098 | 133.3098 | 162.8835 | 184.5951 | 176.2644 | 142.7715 | 133.3098 | 164.9816 | 133.3098 | 133.3098 | 133.3098 | 407.0321 | 607.9851 | 530.8798 | 220.8834 | 133.3098 | 806 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 15 | 3231 | 28.5 | 28.5 | 19.2042 | 18.9303 | 15 | 27 | 27 | 770.664 | 157.9483 | 46.3496 | 233.9357 | 0 | 0 | 0 | 86.5359 | 385.1256 | 458.1139 | 262.7453 | 0 | 603.0517 | 128.3394 | 128.3394 | 128.3394 | 138.573 | 173.8838 | 182.5153 | 159.4113 | 128.3394 | 157.9483 | 128.3394 | 128.3394 | 128.3394 | 225.1089 | 559.0093 | 640.6292 | 422.1566 | 128.3394 | 761 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 16 | 3232 | 28.3 | 28.3 | 19.2042 | 18.9303 | 15 | 32 | 32 | 706.5046 | 161.4322 | 38.2313 | 249.7546 | 0 | 0 | 0 | 0 | 287.0876 | 481.7508 | 394.2109 | 75.7476 | 496.5678 | 120.0022 | 120.0022 | 120.0022 | 120.0022 | 169.6061 | 203.2406 | 188.1152 | 133.0901 | 161.4322 | 120.0022 | 120.0022 | 120.0022 | 120.0022 | 456.6938 | 684.9914 | 582.3261 | 208.8377 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 17 | 3233 | 28.3 | 28.3 | 19.2042 | 18.9303 | 15 | 26 | 26 | 537.7335 | 184.3494 | 29.2893 | 263.0642 | 0 | 0 | 0 | 0 | 146.168 | 383.5851 | 396.3033 | 176.8724 | 318.6506 | 113.449 | 113.449 | 113.449 | 113.449 | 152.5655 | 216.1014 | 219.505 | 160.7824 | 184.3494 | 113.449 | 113.449 | 113.449 | 113.449 | 298.7334 | 599.6865 | 615.8083 | 337.6548 | 503 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 15 | 18 | 3234 | 27.5 | 27.5 | 19.2042 | 18.9303 | 15 | 33 | 33 | 386.4239 | 175.5394 | 20.0927 | 274.9977 | 0 | 0 | 0 | 0 | 40.6978 | 265.3456 | 334.5576 | 207.7902 | 177.4606 | 97.6414 | 97.6414 | 97.6414 | 97.6414 | 112.1708 | 192.3719 | 217.0812 | 171.8242 | 175.5394 | 97.6414 | 97.6414 | 97.6414 | 97.6414 | 152.8686 | 457.7176 | 551.6388 | 379.6144 | 353 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 19 | 3235 | 26.2 | 26.2 | 19.2042 | 18.9303 | 15 | 32 | 32 | 348.5602 | 124.2829 | 11.0537 | 286.3829 | 28.517 | 0 | 0 | 0 | 0 | 210.4241 | 326.1016 | 250.7532 | 108.7171 | 79.754 | 70.4275 | 70.4275 | 70.4275 | 70.4275 | 139.2468 | 177.0791 | 152.4364 | 124.2829 | 108.2709 | 70.4275 | 70.4275 | 70.4275 | 70.4275 | 349.6709 | 503.1807 | 403.1896 | 233 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 20 | 3236 | 23.2 | 23.2 | 19.2042 | 18.9303 | 15 | 41 | 41 | 6.8671 | 48.8972 | 2.5295 | 297.8316 | 1.901 | 0 | 0 | 0 | 0 | 3.228 | 6.4661 | 5.9164 | 1.1028 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 48.8972 | 26.1419 | 24.2409 | 24.2409 | 24.2409 | 24.2409 | 27.4689 | 30.707 | 30.1573 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 21 | 3237 | 20 | 20 | 19.2042 | 18.9303 | 15 | 66 | 66 | 2.4875 | 2.9612 | -5.1171 | 309.8092 | 1.1602 | 0 | 0 | 0 | 0 | 0.73355 | 2.1976 | 2.3743 | 0.03879 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 2.9612 | 2.7388 | 1.5786 | 1.5786 | 1.5786 | 1.5786 | 2.3121 | 3.7762 | 3.9529 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 22 | 3238 | 17.4 | 17.4 | 19.2042 | 18.9303 | 15 | 78 | 78 | 0 | 0 | -11.4877 | 322.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 23 | 3239 | 16 | 16 | 19.2042 | 18.9303 | 15 | 84 | 84 | 0 | 0 | -16.1571 | 336.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 15 | 24 | 3240 | 14.7 | 14.7 | 20.7542 | 19.3944 | 15 | 90 | 90 | 0 | 0 | -18.732 | 351.1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 1 | 3241 | 14.4 | 14.4 | 20.7542 | 19.3944 | 15 | 92 | 92 | 0 | 0 | -18.9563 | 6.1097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 2 | 3242 | 13.7 | 13.7 | 20.7542 | 19.3944 | 15 | 93 | 93 | 0 | 0 | -16.5768 | 20.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 3 | 3243 | 13 | 13 | 20.7542 | 19.3944 | 15 | 96 | 96 | 0 | 0 | -12.2816 | 34.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 4 | 3244 | 12.7 | 12.7 | 20.7542 | 19.3944 | 15 | 97 | 97 | 0 | 0 | -6.2085 | 47.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 5 | 3245 | 13 | 13 | 20.7542 | 19.3944 | 15 | 97 | 97 | 0 | 0 | 1.2195 | 59.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 6 | 3246 | 14.4 | 14.4 | 20.7542 | 19.3944 | 15 | 94 | 94 | 4.918 | 24.5454 | 9.5991 | 71.3522 | 2.4695 | 4.7526 | 4.2517 | 1.2602 | 0 | 0 | 0 | 0 | 0.45461 | 52.301 | 91.7618 | 83.1044 | 31.4003 | 9.6191 | 9.6191 | 9.6191 | 9.6191 | 24.5454 | 54.7705 | 96.5143 | 87.3561 | 32.6606 | 9.6191 | 9.6191 | 9.6191 | 9.6191 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 7 | 3247 | 18.3 | 18.3 | 20.7542 | 19.3944 | 15 | 77 | 77 | 90.604 | 109.0952 | 18.5631 | 82.6948 | 28.565 | 80.0519 | 84.6455 | 39.655 | 0 | 0 | 0 | 0 | 21.9048 | 96.7446 | 182.6907 | 190.3587 | 115.2569 | 49.0617 | 49.0617 | 49.0617 | 49.0617 | 109.0952 | 125.3095 | 262.7426 | 275.0042 | 154.9118 | 49.0617 | 49.0617 | 49.0617 | 49.0617 | 131 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 16 | 8 | 3248 | 21.1 | 21.1 | 20.7542 | 19.3944 | 15 | 69 | 69 | 244.6143 | 171.0889 | 27.7581 | 94.4587 | 29.4855 | 183.488 | 230.0057 | 141.7892 | 0 | 0 | 0 | 0 | 95.9111 | 102.5731 | 191.9579 | 218.9573 | 167.7555 | 85.4594 | 85.4594 | 85.4594 | 85.4594 | 171.0889 | 132.0586 | 375.4459 | 448.963 | 309.5447 | 85.4594 | 85.4594 | 85.4594 | 85.4594 | 267 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 9 | 3249 | 23.5 | 23.5 | 20.7542 | 19.3944 | 15 | 64 | 64 | 400.836 | 200.2733 | 36.7899 | 107.4255 | 0 | 230.5592 | 353.635 | 269.5562 | 27.5751 | 0 | 0 | 0 | 213.7267 | 111.9657 | 195.1988 | 239.6298 | 209.2769 | 121.9204 | 111.9657 | 111.9657 | 111.9657 | 200.2733 | 111.9657 | 425.758 | 593.2648 | 478.8331 | 149.4955 | 111.9657 | 111.9657 | 111.9657 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 10 | 3250 | 25.3 | 25.3 | 20.7542 | 19.3944 | 15 | 58 | 58 | 569.8825 | 193.4434 | 45.1294 | 122.6757 | 0 | 211.2608 | 435.4385 | 404.5423 | 136.6706 | 0 | 0 | 0 | 373.5566 | 122.8071 | 177.7662 | 236.0856 | 228.048 | 158.3617 | 122.8071 | 122.8071 | 122.8071 | 193.4434 | 122.8071 | 389.027 | 671.5241 | 632.5903 | 295.0323 | 122.8071 | 122.8071 | 122.8071 | 567 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 11 | 3251 | 26.4 | 26.4 | 20.7542 | 19.3944 | 15 | 53 | 53 | 608.2891 | 207.3967 | 51.9724 | 141.5404 | 0 | 91.6007 | 361.2353 | 419.2632 | 231.6924 | 0 | 0 | 0 | 456.6033 | 132.1522 | 153.6767 | 217.036 | 230.6715 | 186.5957 | 132.1522 | 132.1522 | 132.1522 | 207.3967 | 132.1522 | 245.2774 | 578.2713 | 649.9347 | 418.2881 | 132.1522 | 132.1522 | 132.1522 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 12 | 3252 | 27.4 | 27.4 | 20.7542 | 19.3944 | 15 | 50 | 50 | 624.2547 | 218.0532 | 56.1538 | 164.7667 | 0 | 0 | 239.186 | 382.0634 | 301.1332 | 43.8033 | 0 | 0 | 506.9468 | 138.7806 | 138.7806 | 196.2495 | 230.5785 | 211.1335 | 149.3052 | 138.7806 | 138.7806 | 218.0532 | 138.7806 | 138.7806 | 435.4355 | 612.6419 | 512.2667 | 193.1084 | 138.7806 | 138.7806 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 13 | 3253 | 28.4 | 28.4 | 20.7542 | 19.3944 | 15 | 44 | 44 | 582.1879 | 241.5418 | 56.5376 | 190.4957 | 0 | 0 | 85.1991 | 281.4738 | 312.8649 | 160.9841 | 0 | 0 | 486.4582 | 142.4894 | 142.4894 | 166.1971 | 220.8127 | 229.5477 | 187.2851 | 142.4894 | 142.4894 | 241.5418 | 142.4894 | 142.4894 | 251.3962 | 502.2865 | 542.4126 | 348.2691 | 142.4894 | 142.4894 | 728 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 14 | 3254 | 28.8 | 28.8 | 20.7542 | 19.3944 | 15 | 39 | 39 | 737.5432 | 176.6304 | 52.9964 | 214.4401 | 0 | 0 | 0 | 230.3676 | 399.8691 | 335.1326 | 74.08 | 0 | 604.3696 | 133.287 | 133.287 | 133.287 | 174.1322 | 204.1855 | 192.7074 | 146.4217 | 133.287 | 176.6304 | 133.287 | 133.287 | 133.287 | 404.4998 | 604.0546 | 527.8401 | 220.5017 | 133.287 | 781 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 15 | 3255 | 29.4 | 29.4 | 20.7542 | 19.3944 | 15 | 41 | 41 | 771.4572 | 153.9707 | 46.5533 | 234.1108 | 0 | 0 | 0 | 85.0916 | 382.9273 | 456.4493 | 262.5896 | 0 | 590.0293 | 125.5853 | 125.5853 | 125.5853 | 135.4548 | 169.9998 | 178.5273 | 156.0422 | 125.5853 | 153.9707 | 125.5853 | 125.5853 | 125.5853 | 220.5464 | 552.927 | 634.9767 | 418.6318 | 125.5853 | 744 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 16 | 3256 | 27.8 | 27.8 | 20.7542 | 19.3944 | 15 | 46 | 46 | 277.5715 | 287.4888 | 38.4217 | 249.934 | 0 | 0 | 0 | 0 | 111.8978 | 188.472 | 154.6419 | 30.2246 | 187.5112 | 137.2494 | 137.2494 | 137.2494 | 137.2494 | 212.1133 | 263.3444 | 240.7107 | 157.4708 | 287.4888 | 137.2494 | 137.2494 | 137.2494 | 137.2494 | 324.0111 | 451.8164 | 395.3526 | 187.6954 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 17 | 3257 | 28.4 | 28.4 | 20.7542 | 19.3944 | 15 | 41 | 41 | 224.9919 | 246.5152 | 29.4731 | 263.2355 | 0 | 0 | 0 | 0 | 60.4791 | 159.8421 | 165.5717 | 74.3117 | 125.4848 | 118.9839 | 118.9839 | 118.9839 | 118.9839 | 163.3005 | 236.1095 | 240.308 | 173.4364 | 246.5152 | 118.9839 | 118.9839 | 118.9839 | 118.9839 | 223.7796 | 395.9516 | 405.8797 | 247.7481 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 16 | 18 | 3258 | 18.9 | 18.9 | 20.7542 | 19.3944 | 15 | 72 | 72 | 0.49534 | 35.7922 | 20.2761 | 275.1572 | 0 | 0 | 0 | 0 | 0.050795 | 0.33872 | 0.42823 | 0.26689 | 0.20776 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 35.7922 | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0976 | 17.3856 | 17.4751 | 17.3137 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 19 | 3259 | 17.5 | 17.5 | 20.7542 | 19.3944 | 15 | 90 | 90 | 0.0082974 | 2.9978 | 11.2417 | 286.5296 | 0.00069963 | 0 | 0 | 0 | 0 | 0.0049866 | 0.0077517 | 0.005976 | 0.0022408 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 2.9978 | 1.392 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3963 | 1.399 | 1.3973 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 20 | 3260 | 16.8 | 16.8 | 20.7542 | 19.3944 | 15 | 94 | 94 | 0 | 0 | 2.7259 | 297.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 21 | 3261 | 16.6 | 16.6 | 20.7542 | 19.3944 | 15 | 94 | 94 | 0 | 6 | -4.9096 | 309.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 6 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 2.8239 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 22 | 3262 | 16 | 16 | 20.7542 | 19.3944 | 15 | 96 | 96 | 0 | 0 | -11.2683 | 322.7332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 23 | 3263 | 16.4 | 16.4 | 20.7542 | 19.3944 | 15 | 96 | 96 | 0 | 0 | -15.9273 | 336.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 16 | 24 | 3264 | 15.7 | 15.7 | 20.1625 | 19.5819 | 15 | 96 | 96 | 0 | 0 | -18.496 | 351.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 1 | 3265 | 15.5 | 15.5 | 20.1625 | 19.5819 | 15 | 96 | 96 | 0 | 0 | -18.7204 | 6.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 2 | 3266 | 15 | 15 | 20.1625 | 19.5819 | 15 | 97 | 97 | 0 | 0 | -16.3532 | 20.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 3 | 3267 | 14.7 | 14.7 | 20.1625 | 19.5819 | 15 | 96 | 96 | 0 | 0 | -12.0691 | 34.6685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 4 | 3268 | 14.6 | 14.6 | 20.1625 | 19.5819 | 15 | 93 | 93 | 0 | 0 | -6.0088 | 47.6345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 5 | 3269 | 14 | 14 | 20.1625 | 19.5819 | 15 | 87 | 87 | 0 | 0 | 1.4072 | 59.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 6 | 3270 | 13 | 13 | 20.1625 | 19.5819 | 15 | 92 | 92 | 0 | 0 | 9.7774 | 71.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 7 | 3271 | 13 | 13 | 20.1625 | 19.5819 | 15 | 96 | 96 | 0.40526 | 18.9008 | 18.7357 | 82.5322 | 0.12869 | 0.35833 | 0.37807 | 0.17634 | 0 | 0 | 0 | 0 | 0.099201 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 18.9008 | 9.0982 | 9.3279 | 9.3476 | 9.1459 | 8.9695 | 8.9695 | 8.9695 | 8.9695 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 17 | 8 | 3272 | 13.8 | 13.8 | 20.1625 | 19.5819 | 15 | 90 | 90 | 2.6242 | 76.9637 | 27.9301 | 94.2835 | 0.323 | 1.9708 | 2.4641 | 1.514 | 0 | 0 | 0 | 0 | 1.0363 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 76.9637 | 38.4786 | 40.1264 | 40.6197 | 39.6696 | 38.1556 | 38.1556 | 38.1556 | 38.1556 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 9 | 3273 | 13.3 | 13.3 | 20.1625 | 19.5819 | 15 | 77 | 77 | 25.9017 | 211.1213 | 36.9673 | 107.2396 | 0 | 14.9281 | 22.8208 | 17.3454 | 1.7093 | 0 | 0 | 0 | 13.8787 | 95.3356 | 137.3792 | 159.6083 | 144.1873 | 100.1496 | 95.3356 | 95.3356 | 95.3356 | 211.1213 | 95.3356 | 152.3073 | 182.4291 | 161.5327 | 101.8589 | 95.3356 | 95.3356 | 95.3356 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 10 | 3274 | 13.7 | 13.7 | 20.1625 | 19.5819 | 15 | 73 | 73 | 63.7549 | 289.0527 | 45.3194 | 122.488 | 0 | 23.7261 | 48.6503 | 45.0759 | 15.0966 | 0 | 0 | 0 | 41.9473 | 129.4061 | 175.1367 | 223.1769 | 216.2874 | 158.504 | 129.4061 | 129.4061 | 129.4061 | 289.0527 | 129.4061 | 198.8628 | 271.8273 | 261.3633 | 173.6007 | 129.4061 | 129.4061 | 129.4061 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 11 | 3275 | 13.9 | 13.9 | 20.1625 | 19.5819 | 15 | 73 | 73 | 5.1332 | 204.1349 | 52.1813 | 141.3782 | 0 | 0.78196 | 3.0446 | 3.5237 | 1.9387 | 0 | 0 | 0 | 3.8651 | 101.2053 | 102.5965 | 106.6221 | 107.4746 | 104.6546 | 101.2053 | 101.2053 | 101.2053 | 204.1349 | 101.2053 | 103.3785 | 109.6667 | 110.9983 | 106.5933 | 101.2053 | 101.2053 | 101.2053 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 12 | 3276 | 14.6 | 14.6 | 20.1625 | 19.5819 | 15 | 71 | 71 | 6.1708 | 238.975 | 56.3807 | 164.6837 | 0 | 0 | 2.3617 | 3.7603 | 2.9561 | 0.42033 | 0 | 0 | 5.025 | 117.9842 | 117.9842 | 123.2041 | 126.2953 | 124.518 | 118.9133 | 117.9842 | 117.9842 | 238.975 | 117.9842 | 117.9842 | 125.5658 | 130.0556 | 127.4741 | 119.3336 | 117.9842 | 117.9842 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 13 | 3277 | 14.4 | 14.4 | 20.1625 | 19.5819 | 15 | 69 | 69 | 54.4214 | 362.4072 | 56.7681 | 190.5338 | 0 | 0 | 7.9592 | 26.1775 | 29.0614 | 14.9216 | 0 | 0 | 45.5928 | 158.081 | 158.081 | 177.1235 | 220.7113 | 227.6111 | 193.7812 | 158.081 | 158.081 | 362.4072 | 158.081 | 158.081 | 185.0827 | 246.8888 | 256.6726 | 208.7027 | 158.081 | 158.081 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 14 | 3278 | 16.1 | 16.1 | 20.1625 | 19.5819 | 15 | 61 | 61 | 287.8237 | 346.5063 | 53.2139 | 214.5719 | 0 | 0 | 0 | 89.2657 | 155.0773 | 130.0467 | 28.8366 | 0 | 236.4937 | 156.896 | 156.896 | 156.896 | 225.0586 | 275.3118 | 256.1987 | 178.9154 | 156.896 | 346.5063 | 156.896 | 156.896 | 156.896 | 314.3242 | 430.3891 | 386.2454 | 207.752 | 156.896 | 583 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 15 | 3279 | 16.2 | 16.2 | 20.1625 | 19.5819 | 15 | 51 | 51 | 829.379 | 138.7634 | 46.7533 | 234.2804 | 0 | 0 | 0 | 89.8953 | 408.954 | 488.453 | 281.8228 | 0 | 636.2366 | 124.7207 | 124.7207 | 124.7207 | 133.7025 | 165.581 | 173.5241 | 152.8788 | 124.7207 | 138.7634 | 124.7207 | 124.7207 | 124.7207 | 223.5979 | 574.535 | 661.9771 | 434.7016 | 124.7207 | 775 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 16 | 3280 | 16 | 16 | 20.1625 | 19.5819 | 15 | 51 | 51 | 554.6289 | 204.9818 | 38.6089 | 250.1081 | 0 | 0 | 0 | 0 | 221.8505 | 375.0249 | 308.5148 | 61.2809 | 376.0182 | 122.926 | 122.926 | 122.926 | 122.926 | 179.9419 | 219.3079 | 202.2147 | 138.6753 | 204.9818 | 122.926 | 122.926 | 122.926 | 122.926 | 401.7924 | 594.3328 | 510.7295 | 199.9562 | 581 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 17 | 3281 | 15 | 15 | 20.1625 | 19.5819 | 15 | 55 | 55 | 498.352 | 184.7663 | 29.654 | 263.4015 | 0 | 0 | 0 | 0 | 132.5003 | 352.627 | 366.1896 | 165.2433 | 279.2337 | 109.559 | 109.559 | 109.559 | 109.559 | 147.8744 | 211.5289 | 215.4508 | 157.3428 | 184.7663 | 109.559 | 109.559 | 109.559 | 109.559 | 280.3747 | 564.1559 | 581.6404 | 322.5861 | 464 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 17 | 18 | 3282 | 13.6 | 13.6 | 20.1625 | 19.5819 | 15 | 64 | 64 | 38.7249 | 175.65 | 20.4567 | 275.3117 | 0 | 0 | 0 | 0 | 3.8671 | 26.3732 | 33.4302 | 20.9042 | 16.35 | 82.8455 | 82.8455 | 82.8455 | 82.8455 | 89.3639 | 127.3001 | 139.1954 | 118.0817 | 175.65 | 82.8455 | 82.8455 | 82.8455 | 82.8455 | 93.231 | 153.6733 | 172.6256 | 138.9859 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 19 | 3283 | 13.8 | 13.8 | 20.1625 | 19.5819 | 15 | 65 | 65 | 414.6027 | 100.7958 | 11.4268 | 286.6714 | 35.9607 | 0 | 0 | 0 | 0 | 248.0726 | 386.7884 | 298.9287 | 113.2042 | 69.7886 | 60.873 | 60.873 | 60.873 | 60.873 | 122.3766 | 156.7679 | 134.9852 | 100.7958 | 105.7493 | 60.873 | 60.873 | 60.873 | 60.873 | 370.4492 | 543.5562 | 433.9139 | 214 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 20 | 3284 | 13.2 | 13.2 | 20.1625 | 19.5819 | 15 | 65 | 65 | 2.7808 | 24.6581 | 2.9191 | 298.0915 | 0.78194 | 0 | 0 | 0 | 0 | 1.2934 | 2.6111 | 2.3992 | 0.34192 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 24.6581 | 12.5636 | 11.7816 | 11.7816 | 11.7816 | 11.7816 | 13.075 | 14.3927 | 14.1808 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 21 | 3285 | 12.8 | 12.8 | 20.1625 | 19.5819 | 15 | 63 | 63 | 0 | 3 | -4.7058 | 310.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 3 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 1.3908 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 22 | 3286 | 11.5 | 11.5 | 20.1625 | 19.5819 | 15 | 68 | 68 | 0 | 0 | -11.0531 | 322.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 23 | 3287 | 11.7 | 11.7 | 20.1625 | 19.5819 | 15 | 70 | 70 | 0 | 0 | -15.7021 | 336.5743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 17 | 24 | 3288 | 11 | 11 | 13.9333 | 18.0902 | 15 | 73 | 73 | 0 | 0 | -18.2652 | 351.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 1 | 3289 | 10.8 | 10.8 | 13.9333 | 18.0902 | 15 | 74 | 74 | 0 | 0 | -18.4901 | 6.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 2 | 3290 | 10 | 10 | 13.9333 | 18.0902 | 15 | 77 | 77 | 0 | 0 | -16.1353 | 20.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 3 | 3291 | 9.9 | 9.9 | 13.9333 | 18.0902 | 15 | 79 | 79 | 0 | 0 | -11.8624 | 34.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 4 | 3292 | 10 | 10 | 13.9333 | 18.0902 | 15 | 79 | 79 | 0 | 0 | -5.8148 | 47.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 5 | 3293 | 10.2 | 10.2 | 13.9333 | 18.0902 | 15 | 77 | 77 | 0 | 0 | 1.5893 | 59.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 6 | 3294 | 10 | 10 | 13.9333 | 18.0902 | 15 | 83 | 83 | 0.24806 | 5.9755 | 9.95 | 71.0544 | 0.12555 | 0.23998 | 0.21383 | 0.062428 | 0 | 0 | 0 | 0 | 0.024514 | 2.841 | 2.841 | 2.841 | 2.841 | 2.841 | 2.841 | 2.841 | 2.841 | 5.9755 | 2.9666 | 3.081 | 3.0549 | 2.9035 | 2.841 | 2.841 | 2.841 | 2.841 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 7 | 3295 | 9.4 | 9.4 | 13.9333 | 18.0902 | 15 | 91 | 91 | 0.5307 | 21.8685 | 18.9028 | 82.3712 | 0.16971 | 0.4696 | 0.4944 | 0.22959 | 0 | 0 | 0 | 0 | 0.13147 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 21.8685 | 10.5949 | 10.8948 | 10.9196 | 10.6547 | 10.4252 | 10.4252 | 10.4252 | 10.4252 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 18 | 8 | 3296 | 10.5 | 10.5 | 13.9333 | 18.0902 | 15 | 87 | 87 | 2.3939 | 74.0481 | 28.0963 | 94.1099 | 0.30066 | 1.7999 | 2.2447 | 1.3747 | 0 | 0 | 0 | 0 | 0.95192 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 74.0481 | 36.9023 | 38.4015 | 38.8464 | 37.9763 | 36.6016 | 36.6016 | 36.6016 | 36.6016 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 9 | 3297 | 11.6 | 11.6 | 13.9333 | 18.0902 | 15 | 84 | 84 | 3.0174 | 112.3756 | 37.1388 | 107.0551 | 0 | 1.7424 | 2.6549 | 2.0122 | 0.19077 | 0 | 0 | 0 | 1.6244 | 56.0709 | 56.0709 | 56.0709 | 56.0709 | 56.0709 | 56.0709 | 56.0709 | 56.0709 | 112.3756 | 56.0709 | 57.8133 | 58.7258 | 58.0831 | 56.2616 | 56.0709 | 56.0709 | 56.0709 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 10 | 3298 | 9.1 | 9.1 | 13.9333 | 18.0902 | 15 | 92 | 92 | 2.8545 | 134.1151 | 45.5034 | 122.3009 | 0 | 1.0664 | 2.1755 | 2.0102 | 0.6674 | 0 | 0 | 0 | 1.8849 | 67.0231 | 67.0231 | 67.0231 | 67.0231 | 67.0231 | 67.0231 | 67.0231 | 67.0231 | 134.1151 | 67.0231 | 68.0894 | 69.1985 | 69.0333 | 67.6905 | 67.0231 | 67.0231 | 67.0231 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 11 | 3299 | 12.6 | 12.6 | 13.9333 | 18.0902 | 15 | 86 | 86 | 40.8495 | 316.1502 | 52.3842 | 141.2151 | 0 | 6.2938 | 24.1997 | 27.9297 | 15.2989 | 0 | 0 | 0 | 30.8498 | 139.6773 | 157.9877 | 210.0809 | 220.9326 | 184.1861 | 139.6773 | 139.6773 | 139.6773 | 316.1502 | 139.6773 | 164.2814 | 234.2805 | 248.8623 | 199.485 | 139.6773 | 139.6773 | 139.6773 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 12 | 3300 | 13.2 | 13.2 | 13.9333 | 18.0902 | 15 | 66 | 66 | 419.6771 | 299.3383 | 56.6017 | 164.5978 | 0 | 0 | 160.4557 | 254.6503 | 199.6741 | 27.7316 | 0 | 0 | 342.6617 | 151.0545 | 151.0545 | 229.8639 | 276.1284 | 249.1264 | 164.6751 | 151.0545 | 151.0545 | 299.3383 | 151.0545 | 151.0545 | 390.3196 | 530.7787 | 448.8005 | 192.4067 | 151.0545 | 151.0545 | 642 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 13 | 3301 | 14.3 | 14.3 | 13.9333 | 18.0902 | 15 | 61 | 61 | 245.3027 | 365.9673 | 56.9935 | 190.5675 | 0 | 0 | 35.8625 | 117.4089 | 130.1788 | 66.6917 | 0 | 0 | 206.0327 | 160.0696 | 160.0696 | 193.5573 | 269.7039 | 281.6282 | 222.3451 | 160.0696 | 160.0696 | 365.9673 | 160.0696 | 160.0696 | 229.4198 | 387.1128 | 411.807 | 289.0368 | 160.0696 | 160.0696 | 572 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 14 | 3302 | 13.2 | 13.2 | 13.9333 | 18.0902 | 15 | 60 | 60 | 102.3511 | 373.6809 | 53.427 | 214.6985 | 0 | 0 | 0 | 31.5254 | 54.8086 | 45.9857 | 10.225 | 0 | 84.3191 | 165.8136 | 165.8136 | 165.8136 | 207.7038 | 238.6419 | 226.9182 | 179.4003 | 165.8136 | 373.6809 | 165.8136 | 165.8136 | 165.8136 | 239.2292 | 293.4505 | 272.9039 | 189.6253 | 165.8136 | 458 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 15 | 3303 | 13.4 | 13.4 | 13.9333 | 18.0902 | 15 | 57 | 57 | 91.0028 | 346.9864 | 46.9496 | 234.4445 | 0 | 0 | 0 | 9.6967 | 44.5805 | 53.3496 | 30.8673 | 0 | 70.0136 | 155.1069 | 155.1069 | 155.1069 | 168.3999 | 216.221 | 228.2423 | 197.4219 | 155.1069 | 346.9864 | 155.1069 | 155.1069 | 155.1069 | 178.0966 | 260.8015 | 281.5919 | 228.2891 | 155.1069 | 417 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 16 | 3304 | 15 | 15 | 13.9333 | 18.0902 | 15 | 57 | 57 | 626.9869 | 181.4498 | 38.7927 | 250.2767 | 0 | 0 | 0 | 0 | 248.8826 | 422.2056 | 348.2063 | 70.2324 | 426.5502 | 119.9779 | 119.9779 | 119.9779 | 119.9779 | 172.4175 | 208.9367 | 193.345 | 134.7759 | 181.4498 | 119.9779 | 119.9779 | 119.9779 | 119.9779 | 421.3001 | 631.1423 | 541.5513 | 205.0084 | 608 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 17 | 3305 | 15 | 15 | 13.9333 | 18.0902 | 15 | 57 | 57 | 637.3336 | 147.2904 | 29.8318 | 263.5622 | 0 | 0 | 0 | 0 | 167.6422 | 449.1886 | 467.6064 | 212.1067 | 358.7096 | 102.4222 | 102.4222 | 102.4222 | 102.4222 | 132.8485 | 183.9478 | 187.2905 | 140.9186 | 147.2904 | 102.4222 | 102.4222 | 102.4222 | 102.4222 | 300.4907 | 633.1363 | 654.8969 | 353.0253 | 506 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 18 | 18 | 3306 | 13.1 | 13.1 | 13.9333 | 18.0902 | 15 | 64 | 64 | 125.3009 | 193.7582 | 20.6343 | 275.461 | 0 | 0 | 0 | 0 | 12.1876 | 84.9938 | 108.0118 | 67.7579 | 53.2418 | 93.5707 | 93.5707 | 93.5707 | 93.5707 | 104.1605 | 167.4215 | 187.4217 | 152.4453 | 193.7582 | 93.5707 | 93.5707 | 93.5707 | 93.5707 | 116.3481 | 252.4153 | 295.4335 | 220.2032 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 19 | 3307 | 12.9 | 12.9 | 13.9333 | 18.0902 | 15 | 65 | 65 | 419.82 | 101.1502 | 11.6088 | 286.8083 | 37.3906 | 0 | 0 | 0 | 0 | 250.1137 | 391.1047 | 302.992 | 115.8498 | 70.4485 | 61.2868 | 61.2868 | 61.2868 | 61.2868 | 122.5716 | 157.1183 | 135.5282 | 101.1502 | 107.8391 | 61.2868 | 61.2868 | 61.2868 | 61.2868 | 372.6853 | 548.2231 | 438.5202 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 20 | 3308 | 11.4 | 11.4 | 13.9333 | 18.0902 | 15 | 77 | 77 | 66.6992 | 55.591 | 3.109 | 298.2143 | 18.8929 | 0 | 0 | 0 | 0 | 30.8657 | 62.5436 | 57.5843 | 8.409 | 42.1878 | 28.8567 | 28.8567 | 28.8567 | 28.8567 | 50.6359 | 72.9882 | 69.4888 | 55.591 | 61.0806 | 28.8567 | 28.8567 | 28.8567 | 28.8567 | 81.5016 | 135.5318 | 127.0731 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 21 | 3309 | 10.6 | 10.6 | 13.9333 | 18.0902 | 15 | 85 | 85 | 0 | 6 | -4.5056 | 310.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 6 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 2.8176 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 22 | 3310 | 9.4 | 9.4 | 13.9333 | 18.0902 | 15 | 89 | 89 | 0 | 0 | -10.8419 | 322.9022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 23 | 3311 | 10.2 | 10.2 | 13.9333 | 18.0902 | 15 | 83 | 83 | 0 | 0 | -15.4817 | 336.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 18 | 24 | 3312 | 9.8 | 9.8 | 11.4833 | 16.317 | 15 | 86 | 86 | 0 | 0 | -18.0395 | 351.1554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 1 | 3313 | 8.2 | 8.2 | 11.4833 | 16.317 | 15 | 93 | 93 | 0 | 0 | -18.2653 | 6.0388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 2 | 3314 | 9.8 | 9.8 | 11.4833 | 16.317 | 15 | 92 | 92 | 0 | 0 | -15.9233 | 20.6135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 3 | 3315 | 10.2 | 10.2 | 11.4833 | 16.317 | 15 | 87 | 87 | 0 | 0 | -11.6616 | 34.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 4 | 3316 | 10.2 | 10.2 | 11.4833 | 16.317 | 15 | 87 | 87 | 0 | 0 | -5.6266 | 47.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 5 | 3317 | 10.1 | 10.1 | 11.4833 | 16.317 | 15 | 90 | 90 | 0 | 0 | 1.7656 | 59.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 6 | 3318 | 9.9 | 9.9 | 11.4833 | 16.317 | 15 | 94 | 94 | 0.78453 | 10.9201 | 10.117 | 70.908 | 0.39859 | 0.75935 | 0.67529 | 0.19566 | 0 | 0 | 0 | 0 | 0.079941 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 10.9201 | 5.7426 | 6.1033 | 6.0193 | 5.5397 | 5.344 | 5.344 | 5.344 | 5.344 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 7 | 3319 | 11.6 | 11.6 | 11.4833 | 16.317 | 15 | 89 | 89 | 9.8819 | 83.5235 | 19.0641 | 82.2121 | 3.182 | 8.7505 | 9.1931 | 4.2505 | 0 | 0 | 0 | 0 | 2.4765 | 63.1344 | 109.5105 | 113.1966 | 72.0336 | 36.6342 | 36.6342 | 36.6342 | 36.6342 | 83.5235 | 66.3164 | 118.261 | 122.3897 | 76.2841 | 36.6342 | 36.6342 | 36.6342 | 36.6342 | 86 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 19 | 8 | 3320 | 11.3 | 11.3 | 11.4833 | 16.317 | 15 | 86 | 86 | 3.5557 | 90.5766 | 28.2568 | 93.9382 | 0.45539 | 2.6764 | 3.3297 | 2.0324 | 0 | 0 | 0 | 0 | 1.4234 | 45.1978 | 48.6906 | 49.7178 | 47.6778 | 44.4817 | 44.4817 | 44.4817 | 44.4817 | 90.5766 | 45.6532 | 51.367 | 53.0475 | 49.7102 | 44.4817 | 44.4817 | 44.4817 | 44.4817 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 9 | 3321 | 12.6 | 12.6 | 11.4833 | 16.317 | 15 | 74 | 74 | 26.5056 | 213.6646 | 37.3044 | 106.8721 | 0 | 15.336 | 23.2919 | 17.6037 | 1.6035 | 0 | 0 | 0 | 14.3354 | 96.4759 | 138.9549 | 160.9918 | 145.2361 | 100.9174 | 96.4759 | 96.4759 | 96.4759 | 213.6646 | 96.4759 | 154.291 | 184.2837 | 162.8398 | 102.5208 | 96.4759 | 96.4759 | 96.4759 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 10 | 3322 | 12.1 | 12.1 | 11.4833 | 16.317 | 15 | 75 | 75 | 5.6519 | 188.2548 | 45.6813 | 122.1145 | 0 | 2.1194 | 4.3022 | 3.9647 | 1.3048 | 0 | 0 | 0 | 3.7452 | 91.7264 | 97.5624 | 103.5726 | 102.6434 | 95.3193 | 91.7264 | 91.7264 | 91.7264 | 188.2548 | 91.7264 | 99.6819 | 107.8747 | 106.6082 | 96.6241 | 91.7264 | 91.7264 | 91.7264 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 11 | 3323 | 10.4 | 10.4 | 11.4833 | 16.317 | 15 | 87 | 87 | 1.5252 | 112.8449 | 52.5809 | 141.0511 | 0 | 0.23762 | 0.90251 | 1.0387 | 0.56646 | 0 | 0 | 0 | 1.1551 | 55.695 | 55.695 | 55.695 | 55.695 | 55.695 | 55.695 | 55.695 | 55.695 | 112.8449 | 55.695 | 55.9326 | 56.5975 | 56.7337 | 56.2614 | 55.695 | 55.695 | 55.695 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 12 | 3324 | 10.1 | 10.1 | 11.4833 | 16.317 | 15 | 92 | 92 | 1.5698 | 123.715 | 56.8169 | 164.509 | 0 | 0 | 0.59961 | 0.94853 | 0.74181 | 0.10055 | 0 | 0 | 1.285 | 61.3131 | 61.3131 | 61.3131 | 61.3131 | 61.3131 | 61.3131 | 61.3131 | 61.3131 | 123.715 | 61.3131 | 61.3131 | 61.9127 | 62.2616 | 62.0549 | 61.4136 | 61.3131 | 61.3131 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 13 | 3325 | 12.1 | 12.1 | 11.4833 | 16.317 | 15 | 84 | 84 | 8.8163 | 273.5768 | 57.2135 | 190.5966 | 0 | 0 | 1.2888 | 4.1994 | 4.65 | 2.3768 | 0 | 0 | 7.4232 | 133.7628 | 133.7628 | 136.8953 | 143.9697 | 145.0651 | 139.5397 | 133.7628 | 133.7628 | 273.5768 | 133.7628 | 133.7628 | 138.1841 | 148.1691 | 149.7151 | 141.9165 | 133.7628 | 133.7628 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 14 | 3326 | 12.9 | 12.9 | 11.4833 | 16.317 | 15 | 77 | 77 | 76.2345 | 368.0366 | 53.6355 | 214.8196 | 0 | 0 | 0 | 23.3249 | 40.5777 | 34.0607 | 7.5914 | 0 | 62.9634 | 161.7309 | 161.7309 | 161.7309 | 202.3075 | 232.321 | 220.9839 | 174.9371 | 161.7309 | 368.0366 | 161.7309 | 161.7309 | 161.7309 | 225.6323 | 272.8988 | 255.0446 | 182.5285 | 161.7309 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 15 | 3327 | 11.2 | 11.2 | 11.4833 | 16.317 | 15 | 86 | 86 | 0.89584 | 88.3088 | 47.142 | 234.6029 | 0 | 0 | 0 | 0.093881 | 0.43606 | 0.5228 | 0.30329 | 0 | 0.69116 | 43.226 | 43.226 | 43.226 | 43.226 | 43.226 | 43.226 | 43.226 | 43.226 | 88.3088 | 43.226 | 43.226 | 43.226 | 43.3199 | 43.6621 | 43.7488 | 43.5293 | 43.226 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 16 | 3328 | 10.2 | 10.2 | 11.4833 | 16.317 | 15 | 85 | 85 | 0.68788 | 68.5305 | 38.9732 | 250.4397 | 0 | 0 | 0 | 0 | 0.27102 | 0.46133 | 0.3814 | 0.078051 | 0.46955 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 68.5305 | 33.2411 | 33.2411 | 33.2411 | 33.2411 | 33.5121 | 33.7024 | 33.6225 | 33.3191 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 17 | 3329 | 10.9 | 10.9 | 11.4833 | 16.317 | 15 | 86 | 86 | 26.9031 | 223.7924 | 30.0066 | 263.7176 | 0 | 0 | 0 | 0 | 7.0025 | 18.8875 | 19.7085 | 8.9845 | 15.2076 | 103.0377 | 103.0377 | 103.0377 | 103.0377 | 122.8303 | 156.4232 | 158.7436 | 128.4323 | 223.7924 | 103.0377 | 103.0377 | 103.0377 | 103.0377 | 129.8328 | 175.3107 | 178.4521 | 137.4168 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 18 | 3330 | 10.9 | 10.9 | 11.4833 | 16.317 | 15 | 84 | 84 | 12.9987 | 150.4425 | 20.8089 | 275.6052 | 0 | 0 | 0 | 0 | 1.2318 | 8.7827 | 11.1888 | 7.0407 | 5.5575 | 73.6622 | 73.6622 | 73.6622 | 73.6622 | 74.8361 | 82.0322 | 84.3253 | 80.3721 | 150.4425 | 73.6622 | 73.6622 | 73.6622 | 73.6622 | 76.0679 | 90.8149 | 95.5141 | 87.4128 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 19 | 3331 | 10.3 | 10.3 | 11.4833 | 16.317 | 15 | 86 | 86 | 2.4331 | 52.3217 | 11.7877 | 286.9402 | 0.22215 | 0 | 0 | 0 | 0 | 1.4435 | 2.2635 | 1.7576 | 0.67832 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 52.3217 | 25.5506 | 25.3284 | 25.3284 | 25.3284 | 25.3284 | 26.7719 | 27.592 | 27.0861 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 20 | 3332 | 10.2 | 10.2 | 11.4833 | 16.317 | 15 | 86 | 86 | 1.1671 | 16.8493 | 3.2956 | 298.3323 | 0.3329 | 0 | 0 | 0 | 0 | 0.53744 | 1.093 | 1.0082 | 0.15069 | 7.951 | 7.951 | 7.951 | 7.951 | 7.951 | 7.951 | 7.951 | 7.951 | 16.8493 | 8.2839 | 7.951 | 7.951 | 7.951 | 7.951 | 8.4885 | 9.044 | 8.9593 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 21 | 3333 | 9.7 | 9.7 | 11.4833 | 16.317 | 15 | 76 | 76 | 0 | 19 | -4.3092 | 310.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4753 | 9.1949 | 9.1949 | 9.1949 | 9.1949 | 10.5731 | 13.4243 | 13.798 | 19 | 11.4753 | 9.1949 | 9.1949 | 9.1949 | 9.1949 | 10.5731 | 13.4243 | 13.798 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 22 | 3334 | 7.8 | 7.8 | 11.4833 | 16.317 | 15 | 86 | 86 | 0 | 0 | -10.6351 | 322.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 23 | 3335 | 6.5 | 6.5 | 11.4833 | 16.317 | 15 | 95 | 95 | 0 | 0 | -15.266 | 336.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 19 | 24 | 3336 | 7.9 | 7.9 | 10.2958 | 14.6368 | 15 | 95 | 95 | 0 | 0 | -17.8192 | 351.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 1 | 3337 | 9.2 | 9.2 | 10.2958 | 14.6368 | 15 | 88 | 88 | 0 | 0 | -18.0462 | 6.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 2 | 3338 | 9.5 | 9.5 | 10.2958 | 14.6368 | 15 | 89 | 89 | 0 | 0 | -15.7172 | 20.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 3 | 3339 | 8.8 | 8.8 | 10.2958 | 14.6368 | 15 | 93 | 93 | 0 | 0 | -11.4666 | 34.3887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 4 | 3340 | 8.7 | 8.7 | 10.2958 | 14.6368 | 15 | 93 | 93 | 0 | 0 | -5.4443 | 47.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 5 | 3341 | 8.4 | 8.4 | 10.2958 | 14.6368 | 15 | 92 | 92 | 0 | 0 | 1.9362 | 59.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 6 | 3342 | 9.7 | 9.7 | 10.2958 | 14.6368 | 15 | 90 | 90 | 85.0358 | 47.0804 | 10.2783 | 70.7633 | 43.3671 | 82.3475 | 73.0899 | 21.0172 | 0 | 0 | 0 | 0 | 8.9196 | 100.557 | 173.9799 | 156.5424 | 58.4593 | 18.8716 | 18.8716 | 18.8716 | 18.8716 | 47.0804 | 143.9241 | 256.3274 | 229.6323 | 79.4765 | 18.8716 | 18.8716 | 18.8716 | 18.8716 | 56 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 7 | 3343 | 10.3 | 10.3 | 10.2958 | 14.6368 | 15 | 87 | 87 | 78.4643 | 113.1171 | 19.2198 | 82.0549 | 25.4369 | 69.5308 | 72.8945 | 33.5576 | 0 | 0 | 0 | 0 | 19.8829 | 97.4613 | 178.2424 | 184.4047 | 112.3386 | 50.8603 | 50.8603 | 50.8603 | 50.8603 | 113.1171 | 122.8982 | 247.7731 | 257.2992 | 145.8961 | 50.8603 | 50.8603 | 50.8603 | 50.8603 | 133 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 20 | 8 | 3344 | 10.4 | 10.4 | 10.2958 | 14.6368 | 15 | 84 | 84 | 4.839 | 106.0503 | 28.4115 | 93.7684 | 0.63159 | 3.6466 | 4.5254 | 2.7534 | 0 | 0 | 0 | 0 | 1.9497 | 53.2028 | 64.5366 | 67.8404 | 61.1789 | 50.8286 | 50.8286 | 50.8286 | 50.8286 | 106.0503 | 53.8344 | 68.1832 | 72.3658 | 63.9323 | 50.8286 | 50.8286 | 50.8286 | 50.8286 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 9 | 3345 | 10.9 | 10.9 | 10.2958 | 14.6368 | 15 | 78 | 78 | 1.8076 | 88.018 | 37.4642 | 106.6907 | 0 | 1.0479 | 1.5864 | 1.1957 | 0.10449 | 0 | 0 | 0 | 0.98197 | 43.2657 | 43.2657 | 43.2657 | 43.2657 | 43.2657 | 43.2657 | 43.2657 | 43.2657 | 88.018 | 43.2657 | 44.3136 | 44.8521 | 44.4614 | 43.3702 | 43.2657 | 43.2657 | 43.2657 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 10 | 3346 | 13.5 | 13.5 | 10.2958 | 14.6368 | 15 | 69 | 69 | 101.8288 | 301.2955 | 45.8532 | 121.929 | 0 | 38.3297 | 77.4197 | 71.1583 | 23.2134 | 0 | 0 | 0 | 67.7045 | 136.3254 | 185.388 | 235.4239 | 227.4093 | 166.0389 | 136.3254 | 136.3254 | 136.3254 | 301.2955 | 136.3254 | 223.7177 | 312.8437 | 298.5676 | 189.2522 | 136.3254 | 136.3254 | 136.3254 | 369 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 11 | 3347 | 13.5 | 13.5 | 10.2958 | 14.6368 | 15 | 62 | 62 | 618.1859 | 205.4803 | 52.7715 | 140.8864 | 0 | 97.3762 | 365.4233 | 419.4104 | 227.7126 | 0 | 0 | 0 | 469.5197 | 132.6286 | 155.0528 | 216.7799 | 229.2123 | 185.0673 | 132.6286 | 132.6286 | 132.6286 | 205.4803 | 132.6286 | 252.429 | 582.2031 | 648.6226 | 412.7798 | 132.6286 | 132.6286 | 132.6286 | 675 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 12 | 3348 | 13.8 | 13.8 | 10.2958 | 14.6368 | 15 | 65 | 65 | 574.4712 | 239.5696 | 57.0261 | 164.4174 | 0 | 0 | 219.2568 | 345.7199 | 269.665 | 35.644 | 0 | 0 | 471.4304 | 141.5617 | 141.5617 | 202.2671 | 237.2808 | 216.2235 | 151.4304 | 141.5617 | 141.5617 | 239.5696 | 141.5617 | 141.5617 | 421.5238 | 583.0007 | 485.8885 | 187.0744 | 141.5617 | 141.5617 | 711 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 13 | 3349 | 14.6 | 14.6 | 10.2958 | 14.6368 | 15 | 57 | 57 | 345.4103 | 336.4752 | 57.4282 | 190.6211 | 0 | 0 | 50.4998 | 163.753 | 181.082 | 92.3356 | 0 | 0 | 291.5248 | 159.0096 | 159.0096 | 190.431 | 260.8983 | 271.6806 | 216.4617 | 159.0096 | 159.0096 | 336.4752 | 159.0096 | 159.0096 | 240.9308 | 424.6513 | 452.7626 | 308.7973 | 159.0096 | 159.0096 | 628 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 14 | 3350 | 14.4 | 14.4 | 10.2958 | 14.6368 | 15 | 59 | 59 | 134.8645 | 377.3392 | 53.8395 | 214.9353 | 0 | 0 | 0 | 40.9974 | 71.3611 | 59.9225 | 13.3821 | 0 | 111.6608 | 163.8839 | 163.8839 | 163.8839 | 220.5877 | 262.584 | 246.7631 | 182.3927 | 163.8839 | 377.3392 | 163.8839 | 163.8839 | 163.8839 | 261.585 | 333.9451 | 306.6856 | 195.7748 | 163.8839 | 489 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 15 | 3351 | 14.1 | 14.1 | 10.2958 | 14.6368 | 15 | 58 | 58 | 426.9537 | 280.6977 | 47.3305 | 234.7556 | 0 | 0 | 0 | 44.0263 | 206.5269 | 248.0469 | 144.2644 | 0 | 330.3023 | 143.0103 | 143.0103 | 143.0103 | 163.5239 | 239.2396 | 258.5855 | 210.229 | 143.0103 | 280.6977 | 143.0103 | 143.0103 | 143.0103 | 207.5502 | 445.7665 | 506.6324 | 354.4933 | 143.0103 | 611 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 16 | 3352 | 13.4 | 13.4 | 10.2958 | 14.6368 | 15 | 57 | 57 | 149.4061 | 311.6834 | 39.1503 | 250.597 | 0 | 0 | 0 | 0 | 58.4352 | 99.7984 | 82.701 | 17.1585 | 102.3166 | 142.3006 | 142.3006 | 142.3006 | 142.3006 | 202.9615 | 245.9002 | 228.1516 | 160.1127 | 311.6834 | 142.3006 | 142.3006 | 142.3006 | 142.3006 | 261.3967 | 345.6986 | 310.8526 | 177.2712 | 414 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 17 | 3353 | 13.3 | 13.3 | 10.2958 | 14.6368 | 15 | 60 | 60 | 43.5348 | 239.2876 | 30.1782 | 263.8675 | 0 | 0 | 0 | 0 | 11.2157 | 30.4475 | 31.8435 | 14.586 | 24.7124 | 109.9788 | 109.9788 | 109.9788 | 109.9788 | 131.7843 | 169.1746 | 171.8888 | 138.3369 | 239.2876 | 109.9788 | 109.9788 | 109.9788 | 109.9788 | 143.0001 | 199.6221 | 203.7323 | 152.9229 | 264 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 18 | 3354 | 13.4 | 13.4 | 10.2958 | 14.6368 | 15 | 60 | 60 | 242.8501 | 187.55 | 20.9804 | 275.7442 | 0 | 0 | 0 | 0 | 22.4269 | 163.4557 | 208.7343 | 131.7392 | 104.45 | 95.8532 | 95.8532 | 95.8532 | 95.8532 | 108.5426 | 188.3385 | 213.9577 | 170.3929 | 187.55 | 95.8532 | 95.8532 | 95.8532 | 95.8532 | 130.9696 | 351.7941 | 422.6919 | 302.132 | 292 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 19 | 3355 | 13.3 | 13.3 | 10.2958 | 14.6368 | 15 | 57 | 57 | 561.0279 | 84.0472 | 11.9634 | 287.0671 | 52.4295 | 0 | 0 | 0 | 0 | 331.4729 | 521.2029 | 405.6194 | 157.9528 | 66.1669 | 57.7438 | 57.7438 | 57.7438 | 57.7438 | 110.9968 | 141.478 | 122.9089 | 84.0472 | 118.5965 | 57.7438 | 57.7438 | 57.7438 | 57.7438 | 442.4696 | 662.6809 | 528.5283 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 20 | 3356 | 11.4 | 11.4 | 10.2958 | 14.6368 | 15 | 66 | 66 | 427.6908 | 38.9642 | 3.4787 | 298.4454 | 122.7969 | 0 | 0 | 0 | 0 | 195.9951 | 399.9759 | 369.6562 | 75.0358 | 48.1563 | 28.4739 | 28.4739 | 28.4739 | 28.4739 | 59.8888 | 92.5838 | 87.724 | 38.9642 | 170.9533 | 28.4739 | 28.4739 | 28.4739 | 28.4739 | 255.8839 | 492.5597 | 457.3802 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 21 | 3357 | 9.5 | 9.5 | 10.2958 | 14.6368 | 15 | 79 | 79 | 0 | 14 | -4.1166 | 310.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 14 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 6.7762 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 22 | 3358 | 7.2 | 7.2 | 10.2958 | 14.6368 | 15 | 90 | 90 | 0 | 0 | -10.4326 | 323.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 23 | 3359 | 6.4 | 6.4 | 10.2958 | 14.6368 | 15 | 95 | 95 | 0 | 0 | -15.0553 | 336.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 20 | 24 | 3360 | 5.5 | 5.5 | 10.9667 | 13.4716 | 15 | 97 | 97 | 0 | 0 | -17.6042 | 351.1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 1 | 3361 | 6.2 | 6.2 | 10.9667 | 13.4716 | 15 | 96 | 96 | 0 | 0 | -17.8328 | 5.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 2 | 3362 | 5.9 | 5.9 | 10.9667 | 13.4716 | 15 | 97 | 97 | 0 | 0 | -15.517 | 20.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 3 | 3363 | 6 | 6 | 10.9667 | 13.4716 | 15 | 97 | 97 | 0 | 0 | -11.2777 | 34.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 4 | 3364 | 7.4 | 7.4 | 10.9667 | 13.4716 | 15 | 97 | 97 | 0 | 0 | -5.2679 | 47.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 5 | 3365 | 7.9 | 7.9 | 10.9667 | 13.4716 | 15 | 92 | 92 | 0 | 0 | 2.101 | 59.1881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 6 | 3366 | 8.5 | 8.5 | 10.9667 | 13.4716 | 15 | 90 | 90 | 2.0927 | 18.7744 | 10.4338 | 70.6205 | 1.0712 | 2.0275 | 1.7961 | 0.51258 | 0 | 0 | 0 | 0 | 0.22561 | 19.2455 | 28.7157 | 26.4243 | 13.7135 | 8.6373 | 8.6373 | 8.6373 | 8.6373 | 18.7744 | 20.3167 | 30.7432 | 28.2204 | 14.2261 | 8.6373 | 8.6373 | 8.6373 | 8.6373 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 7 | 3367 | 9.1 | 9.1 | 10.9667 | 13.4716 | 15 | 91 | 91 | 0.49711 | 21.8727 | 19.3697 | 81.8996 | 0.16222 | 0.44082 | 0.46119 | 0.2114 | 0 | 0 | 0 | 0 | 0.12732 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 21.8727 | 10.5769 | 10.8555 | 10.8759 | 10.6261 | 10.4147 | 10.4147 | 10.4147 | 10.4147 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 21 | 8 | 3368 | 9.9 | 9.9 | 10.9667 | 13.4716 | 15 | 90 | 90 | 1.84 | 66.254 | 28.5605 | 93.6006 | 0.24459 | 1.3881 | 1.7185 | 1.0422 | 0 | 0 | 0 | 0 | 0.74597 | 32.496 | 32.496 | 32.496 | 32.496 | 32.496 | 32.496 | 32.496 | 32.496 | 66.254 | 32.7406 | 33.8841 | 34.2145 | 33.5382 | 32.496 | 32.496 | 32.496 | 32.496 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 9 | 3369 | 10.5 | 10.5 | 10.9667 | 13.4716 | 15 | 91 | 91 | 4.1863 | 133.716 | 37.618 | 106.5112 | 0 | 2.4316 | 3.6697 | 2.7581 | 0.23091 | 0 | 0 | 0 | 2.284 | 65.9113 | 69.8169 | 71.8055 | 70.3414 | 66.2822 | 65.9113 | 65.9113 | 65.9113 | 133.716 | 65.9113 | 72.2484 | 75.4752 | 73.0995 | 66.5131 | 65.9113 | 65.9113 | 65.9113 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 10 | 3370 | 11.1 | 11.1 | 10.9667 | 13.4716 | 15 | 89 | 89 | 3.2718 | 144.8175 | 46.0189 | 121.7445 | 0 | 1.2362 | 2.4847 | 2.2778 | 0.73654 | 0 | 0 | 0 | 2.1825 | 72.7092 | 72.7092 | 72.7092 | 72.7092 | 72.7092 | 72.7092 | 72.7092 | 72.7092 | 144.8175 | 72.7092 | 73.9454 | 75.194 | 74.987 | 73.4458 | 72.7092 | 72.7092 | 72.7092 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 11 | 3371 | 11.2 | 11.2 | 10.9667 | 13.4716 | 15 | 90 | 90 | 2.4088 | 142.1656 | 52.9559 | 140.7213 | 0 | 0.38354 | 1.4225 | 1.6281 | 0.88007 | 0 | 0 | 0 | 1.8344 | 70.9856 | 70.9856 | 70.9856 | 70.9856 | 70.9856 | 70.9856 | 70.9856 | 70.9856 | 142.1656 | 70.9856 | 71.3691 | 72.408 | 72.6137 | 71.8656 | 70.9856 | 70.9856 | 70.9856 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 12 | 3372 | 11.6 | 11.6 | 10.9667 | 13.4716 | 15 | 86 | 86 | 6.22 | 241.8834 | 57.2294 | 164.323 | 0 | 0 | 2.3723 | 3.7285 | 2.9006 | 0.37355 | 0 | 0 | 5.1166 | 119.4086 | 119.4086 | 124.7245 | 127.7635 | 125.9083 | 120.2457 | 119.4086 | 119.4086 | 241.8834 | 119.4086 | 119.4086 | 127.0968 | 131.492 | 128.8089 | 120.6192 | 119.4086 | 119.4086 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 13 | 3373 | 12.2 | 12.2 | 10.9667 | 13.4716 | 15 | 85 | 85 | 28.2843 | 337.0731 | 57.6376 | 190.641 | 0 | 0 | 4.1369 | 13.3481 | 14.7401 | 7.4976 | 0 | 0 | 23.9269 | 146.9547 | 146.9547 | 163.8868 | 201.5879 | 207.2856 | 177.6423 | 146.9547 | 146.9547 | 337.0731 | 146.9547 | 146.9547 | 168.0237 | 214.936 | 222.0258 | 185.1399 | 146.9547 | 146.9547 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 14 | 3374 | 11.7 | 11.7 | 10.9667 | 13.4716 | 15 | 85 | 85 | 2.0284 | 142.3166 | 54.0388 | 215.0454 | 0 | 0 | 0 | 0.61276 | 1.0671 | 0.89629 | 0.20049 | 0 | 1.6834 | 71.0377 | 71.0377 | 71.0377 | 71.0377 | 71.0377 | 71.0377 | 71.0377 | 71.0377 | 142.3166 | 71.0377 | 71.0377 | 71.0377 | 71.6505 | 72.1048 | 71.934 | 71.2382 | 71.0377 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 15 | 3375 | 11.9 | 11.9 | 10.9667 | 13.4716 | 15 | 86 | 86 | 0.9478 | 91.2648 | 47.5151 | 234.9024 | 0 | 0 | 0 | 0.096216 | 0.45568 | 0.54821 | 0.31961 | 0 | 0.73517 | 44.7263 | 44.7263 | 44.7263 | 44.7263 | 44.7263 | 44.7263 | 44.7263 | 44.7263 | 91.2648 | 44.7263 | 44.7263 | 44.7263 | 44.8225 | 45.182 | 45.2745 | 45.0459 | 44.7263 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 16 | 3376 | 10.4 | 10.4 | 10.9667 | 13.4716 | 15 | 92 | 92 | 0.67968 | 68.5331 | 39.3239 | 250.7487 | 0 | 0 | 0 | 0 | 0.26394 | 0.45222 | 0.37559 | 0.078944 | 0.46692 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 68.5331 | 33.2461 | 33.2461 | 33.2461 | 33.2461 | 33.5101 | 33.6983 | 33.6217 | 33.3251 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 17 | 3377 | 11.1 | 11.1 | 10.9667 | 13.4716 | 15 | 89 | 89 | 4.4817 | 144.4456 | 30.3467 | 264.012 | 0 | 0 | 0 | 0 | 1.1431 | 3.1227 | 3.2731 | 1.5061 | 2.5544 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 144.4456 | 72.4615 | 72.4615 | 72.4615 | 72.4615 | 73.6046 | 75.5842 | 75.7346 | 73.9676 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 21 | 18 | 3378 | 11.1 | 11.1 | 10.9667 | 13.4716 | 15 | 92 | 92 | 3.1813 | 92.6238 | 21.1488 | 275.878 | 0 | 0 | 0 | 0 | 0.2864 | 2.1332 | 2.7304 | 1.7282 | 1.3762 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 92.6238 | 45.6045 | 45.6045 | 45.6045 | 45.6045 | 45.8909 | 47.7377 | 48.3349 | 47.3326 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 19 | 3379 | 10.7 | 10.7 | 10.9667 | 13.4716 | 15 | 95 | 95 | 1.4712 | 41.5819 | 12.1358 | 287.1889 | 0.14052 | 0 | 0 | 0 | 0 | 0.86576 | 1.3649 | 1.0645 | 0.41814 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 41.5819 | 20.0846 | 19.9441 | 19.9441 | 19.9441 | 19.9441 | 20.8099 | 21.309 | 21.0086 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 20 | 3380 | 10.7 | 10.7 | 10.9667 | 13.4716 | 15 | 94 | 94 | 0.72513 | 13.9021 | 3.6582 | 298.5538 | 0.2095 | 0 | 0 | 0 | 0 | 0.33075 | 0.67726 | 0.62704 | 0.097854 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 13.9021 | 6.7388 | 6.5293 | 6.5293 | 6.5293 | 6.5293 | 6.8601 | 7.2066 | 7.1564 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 21 | 3381 | 10.4 | 10.4 | 10.9667 | 13.4716 | 15 | 94 | 94 | 0 | 3 | -3.928 | 310.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 3 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 1.3886 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 22 | 3382 | 10.2 | 10.2 | 10.9667 | 13.4716 | 15 | 95 | 95 | 0 | 0 | -10.2346 | 323.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 23 | 3383 | 10.1 | 10.1 | 10.9667 | 13.4716 | 15 | 97 | 97 | 0 | 0 | -14.8495 | 336.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 21 | 24 | 3384 | 10.3 | 10.3 | 9.8375 | 12.185 | 15 | 97 | 97 | 0 | 0 | -17.3947 | 351.1835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 1 | 3385 | 10.3 | 10.3 | 9.8375 | 12.185 | 15 | 97 | 97 | 0 | 0 | -17.6251 | 5.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 2 | 3386 | 10.3 | 10.3 | 9.8375 | 12.185 | 15 | 97 | 97 | 0 | 0 | -15.3228 | 20.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 3 | 3387 | 9.8 | 9.8 | 9.8375 | 12.185 | 15 | 96 | 96 | 0 | 0 | -11.0947 | 34.2042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 4 | 3388 | 9.6 | 9.6 | 9.8375 | 12.185 | 15 | 97 | 97 | 0 | 0 | -5.0974 | 47.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 5 | 3389 | 8.8 | 8.8 | 9.8375 | 12.185 | 15 | 96 | 96 | 0 | 0 | 2.2599 | 59.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 6 | 3390 | 9.1 | 9.1 | 9.8375 | 12.185 | 15 | 97 | 97 | 2.6649 | 21.7052 | 10.5836 | 70.4796 | 1.3691 | 2.583 | 2.2839 | 0.6469 | 0 | 0 | 0 | 0 | 0.29484 | 26.2545 | 40.8868 | 37.2814 | 17.5502 | 9.753 | 9.753 | 9.753 | 9.753 | 21.7052 | 27.6235 | 43.4699 | 39.5653 | 18.1971 | 9.753 | 9.753 | 9.753 | 9.753 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 7 | 3391 | 10.7 | 10.7 | 9.8375 | 12.185 | 15 | 97 | 97 | 4.1231 | 62.9331 | 19.5139 | 81.7466 | 1.3543 | 3.6587 | 3.82 | 1.7435 | 0 | 0 | 0 | 0 | 1.0669 | 37.439 | 50.5564 | 51.4742 | 39.6548 | 29.7304 | 29.7304 | 29.7304 | 29.7304 | 62.9331 | 38.7933 | 54.2152 | 55.2942 | 41.3984 | 29.7304 | 29.7304 | 29.7304 | 29.7304 | 64 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 22 | 8 | 3392 | 11 | 11 | 9.8375 | 12.185 | 15 | 94 | 94 | 1.3629 | 57.4441 | 28.7036 | 93.435 | 0.1844 | 1.0293 | 1.2713 | 0.76854 | 0 | 0 | 0 | 0 | 0.55588 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 57.4441 | 28.1397 | 28.9846 | 29.2265 | 28.7238 | 27.9553 | 27.9553 | 27.9553 | 27.9553 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 9 | 3393 | 11.7 | 11.7 | 9.8375 | 12.185 | 15 | 92 | 92 | 1.2631 | 74.308 | 37.7659 | 106.3335 | 0 | 0.73506 | 1.1059 | 0.82894 | 0.06638 | 0 | 0 | 0 | 0.69201 | 36.2189 | 36.2189 | 36.2189 | 36.2189 | 36.2189 | 36.2189 | 36.2189 | 36.2189 | 74.308 | 36.2189 | 36.954 | 37.3248 | 37.0479 | 36.2853 | 36.2189 | 36.2189 | 36.2189 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 10 | 3394 | 13.1 | 13.1 | 9.8375 | 12.185 | 15 | 81 | 81 | 38.1977 | 277.4392 | 46.1786 | 121.5613 | 0 | 14.4853 | 28.9773 | 26.4948 | 8.492 | 0 | 0 | 0 | 25.5608 | 123.8616 | 166.4321 | 209.0223 | 201.7264 | 148.8185 | 123.8616 | 123.8616 | 123.8616 | 277.4392 | 123.8616 | 180.9175 | 237.9996 | 228.2212 | 157.3104 | 123.8616 | 123.8616 | 123.8616 | 303 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 11 | 3395 | 14.3 | 14.3 | 9.8375 | 12.185 | 15 | 67 | 67 | 96.9268 | 344.9912 | 53.134 | 140.5558 | 0 | 15.5974 | 57.186 | 65.2758 | 35.1279 | 0 | 0 | 0 | 74.0088 | 154.0382 | 175.898 | 234.1845 | 245.5223 | 203.27 | 154.0382 | 154.0382 | 154.0382 | 344.9912 | 154.0382 | 191.4955 | 291.3705 | 310.7981 | 238.3979 | 154.0382 | 154.0382 | 154.0382 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 12 | 3396 | 14.6 | 14.6 | 9.8375 | 12.185 | 15 | 65 | 65 | 72.1979 | 365.4715 | 57.4266 | 164.226 | 0 | 0 | 27.519 | 43.1113 | 33.4496 | 4.1936 | 0 | 0 | 59.5285 | 160.379 | 160.379 | 212.215 | 241.5853 | 223.3861 | 168.2781 | 160.379 | 160.379 | 365.4715 | 160.379 | 160.379 | 239.734 | 284.6966 | 256.8357 | 172.4717 | 160.379 | 160.379 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 13 | 3397 | 14.8 | 14.8 | 9.8375 | 12.185 | 15 | 67 | 67 | 30.4464 | 341.1869 | 57.8414 | 190.6563 | 0 | 0 | 4.456 | 14.3051 | 15.7745 | 8.0034 | 0 | 0 | 25.8131 | 148.5924 | 148.5924 | 165.8368 | 203.9521 | 209.6385 | 179.5649 | 148.5924 | 148.5924 | 341.1869 | 148.5924 | 148.5924 | 170.2928 | 218.2572 | 225.413 | 187.5683 | 148.5924 | 148.5924 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 14 | 3398 | 14.5 | 14.5 | 9.8375 | 12.185 | 15 | 71 | 71 | 4.1336 | 202.5616 | 54.2335 | 215.1498 | 0 | 0 | 0 | 1.2412 | 2.1622 | 1.8166 | 0.40685 | 0 | 3.4384 | 103.1616 | 103.1616 | 103.1616 | 103.1616 | 103.1616 | 103.1616 | 103.1616 | 103.1616 | 202.5616 | 103.1616 | 103.1616 | 103.1616 | 104.4028 | 105.3238 | 104.9782 | 103.5684 | 103.1616 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 15 | 3399 | 13.3 | 13.3 | 9.8375 | 12.185 | 15 | 84 | 84 | 0.94337 | 91.2664 | 47.6957 | 235.0433 | 0 | 0 | 0 | 0.094326 | 0.45084 | 0.54325 | 0.31744 | 0 | 0.73359 | 44.7299 | 44.7299 | 44.7299 | 44.7299 | 44.7299 | 44.7299 | 44.7299 | 44.7299 | 91.2664 | 44.7299 | 44.7299 | 44.7299 | 44.8243 | 45.1808 | 45.2732 | 45.0474 | 44.7299 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 16 | 3400 | 13.3 | 13.3 | 9.8375 | 12.185 | 15 | 82 | 82 | 0.93135 | 80.3582 | 39.494 | 250.8945 | 0 | 0 | 0 | 0 | 0.35916 | 0.61726 | 0.51377 | 0.10932 | 0.64175 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 80.3582 | 39.1675 | 39.1675 | 39.1675 | 39.1675 | 39.5267 | 39.7848 | 39.6813 | 39.2768 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 17 | 3401 | 12.9 | 12.9 | 9.8375 | 12.185 | 15 | 92 | 92 | 0.36314 | 41.7922 | 30.5118 | 264.1509 | 0 | 0 | 0 | 0 | 0.091723 | 0.2521 | 0.2648 | 0.12238 | 0.20778 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 41.7922 | 20.0017 | 20.0017 | 20.0017 | 20.0017 | 20.0935 | 20.2538 | 20.2665 | 20.1241 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 22 | 18 | 3402 | 15.2 | 15.2 | 9.8375 | 12.185 | 15 | 69 | 69 | 375.407 | 167.6994 | 21.3139 | 276.0066 | 0 | 0 | 0 | 0 | 32.9594 | 250.8093 | 321.7386 | 204.1977 | 163.3006 | 92.9607 | 92.9607 | 92.9607 | 92.9607 | 104.7966 | 183.0278 | 208.4989 | 166.2893 | 167.6994 | 92.9607 | 92.9607 | 92.9607 | 92.9607 | 137.756 | 433.8371 | 530.2375 | 370.487 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 19 | 3403 | 14.7 | 14.7 | 9.8375 | 12.185 | 15 | 67 | 67 | 331.8289 | 115.8229 | 12.3049 | 287.3057 | 32.3484 | 0 | 0 | 0 | 0 | 194.516 | 307.4355 | 240.2635 | 95.1771 | 76.2956 | 65.5356 | 65.5356 | 65.5356 | 65.5356 | 130.2375 | 167.7979 | 145.4545 | 115.8229 | 108.644 | 65.5356 | 65.5356 | 65.5356 | 65.5356 | 324.7535 | 475.2335 | 385.718 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 20 | 3404 | 12.8 | 12.8 | 9.8375 | 12.185 | 15 | 68 | 68 | 457.8481 | 47.9338 | 3.8342 | 298.6573 | 133.0676 | 0 | 0 | 0 | 0 | 207.8981 | 427.0799 | 396.0841 | 63.0662 | 53.7086 | 31.5048 | 31.5048 | 31.5048 | 31.5048 | 66.1949 | 102.7679 | 97.5959 | 47.9338 | 186.7762 | 31.5048 | 31.5048 | 31.5048 | 31.5048 | 274.0931 | 529.8478 | 493.68 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 21 | 3405 | 10.3 | 10.3 | 9.8375 | 12.185 | 15 | 86 | 86 | 0 | 11 | -3.7434 | 310.5149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 11 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 5.2461 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 22 | 3406 | 8.4 | 8.4 | 9.8375 | 12.185 | 15 | 93 | 93 | 0 | 0 | -10.041 | 323.1896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 23 | 3407 | 7.4 | 7.4 | 9.8375 | 12.185 | 15 | 96 | 96 | 0 | 0 | -14.6487 | 336.7984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 22 | 24 | 3408 | 7.2 | 7.2 | 11.5875 | 11.5766 | 15 | 97 | 97 | 0 | 0 | -17.1908 | 351.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 1 | 3409 | 6.8 | 6.8 | 11.5875 | 11.5766 | 15 | 97 | 97 | 0 | 0 | -17.4234 | 5.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 2 | 3410 | 7.8 | 7.8 | 11.5875 | 11.5766 | 15 | 97 | 97 | 0 | 0 | -15.1347 | 20.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 3 | 3411 | 7.4 | 7.4 | 11.5875 | 11.5766 | 15 | 97 | 97 | 0 | 0 | -10.9178 | 34.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 4 | 3412 | 8.5 | 8.5 | 11.5875 | 11.5766 | 15 | 98 | 98 | 0 | 0 | -4.9329 | 46.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 5 | 3413 | 9.2 | 9.2 | 11.5875 | 11.5766 | 15 | 96 | 96 | 0 | 0 | 2.413 | 58.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 6 | 3414 | 9.7 | 9.7 | 11.5875 | 11.5766 | 15 | 95 | 95 | 10.0269 | 37.8631 | 10.7276 | 70.3407 | 5.1696 | 9.7232 | 8.5811 | 2.4123 | 0 | 0 | 0 | 0 | 1.1369 | 93.8314 | 163.9582 | 146.3697 | 51.3693 | 14.2191 | 14.2191 | 14.2191 | 14.2191 | 37.8631 | 99.001 | 173.6814 | 154.9509 | 53.7816 | 14.2191 | 14.2191 | 14.2191 | 14.2191 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 7 | 3415 | 10.8 | 10.8 | 11.5875 | 11.5766 | 15 | 93 | 93 | 16.4309 | 95.7063 | 19.6523 | 81.5957 | 5.4312 | 14.5904 | 15.2027 | 6.9095 | 0 | 0 | 0 | 0 | 4.2937 | 76.0228 | 134.9045 | 138.8412 | 85.5267 | 41.1075 | 41.1075 | 41.1075 | 41.1075 | 95.7063 | 81.454 | 149.4949 | 154.0439 | 92.4363 | 41.1075 | 41.1075 | 41.1075 | 41.1075 | 100 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 23 | 8 | 3416 | 12.3 | 12.3 | 11.5875 | 11.5766 | 15 | 92 | 92 | 5.2063 | 111.8641 | 28.841 | 93.2716 | 0.71662 | 3.9365 | 4.8504 | 2.923 | 0 | 0 | 0 | 0 | 2.1359 | 56.2981 | 69.7381 | 73.5529 | 65.5078 | 53.3069 | 53.3069 | 53.3069 | 53.3069 | 111.8641 | 57.0147 | 73.6746 | 78.4033 | 68.4309 | 53.3069 | 53.3069 | 53.3069 | 53.3069 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 9 | 3417 | 13.8 | 13.8 | 11.5875 | 11.5766 | 15 | 83 | 83 | 75.3627 | 244.5471 | 37.9079 | 106.158 | 0 | 43.9395 | 65.9072 | 49.2674 | 3.7674 | 0 | 0 | 0 | 41.4529 | 110.7032 | 181.8086 | 217.3581 | 190.4306 | 116.7998 | 110.7032 | 110.7032 | 110.7032 | 244.5471 | 110.7032 | 225.7481 | 283.2654 | 239.698 | 120.5672 | 110.7032 | 110.7032 | 110.7032 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 10 | 3418 | 15.7 | 15.7 | 11.5875 | 11.5766 | 15 | 77 | 77 | 128.8003 | 305.5479 | 46.3321 | 121.3795 | 0 | 49.0227 | 97.6091 | 89.0174 | 28.2805 | 0 | 0 | 0 | 86.4521 | 137.855 | 202.5223 | 266.6141 | 255.2805 | 175.1607 | 137.855 | 137.855 | 137.855 | 305.5479 | 137.855 | 251.545 | 364.2231 | 344.2979 | 203.4412 | 137.855 | 137.855 | 137.855 | 392 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 11 | 3419 | 17.4 | 17.4 | 11.5875 | 11.5766 | 15 | 72 | 72 | 198.1295 | 342.3369 | 53.3058 | 140.3902 | 0 | 32.2159 | 116.7946 | 132.9566 | 71.2345 | 0 | 0 | 0 | 151.6631 | 157.408 | 186.1433 | 261.5842 | 276.0001 | 220.9464 | 157.408 | 157.408 | 157.408 | 342.3369 | 157.408 | 218.3592 | 378.3788 | 408.9567 | 292.1808 | 157.408 | 157.408 | 157.408 | 494 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 12 | 3420 | 16.5 | 16.5 | 11.5875 | 11.5766 | 15 | 71 | 71 | 20.6099 | 313.9687 | 57.6176 | 164.1265 | 0 | 0 | 7.8517 | 12.2609 | 9.4878 | 1.1569 | 0 | 0 | 17.0313 | 148.5088 | 148.5088 | 166.1243 | 176.0164 | 169.7949 | 151.1043 | 148.5088 | 148.5088 | 313.9687 | 148.5088 | 148.5088 | 173.976 | 188.2772 | 179.2827 | 152.2612 | 148.5088 | 148.5088 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 13 | 3421 | 17.3 | 17.3 | 11.5875 | 11.5766 | 15 | 70 | 70 | 58.3925 | 369.3874 | 58.0398 | 190.6669 | 0 | 0 | 8.5537 | 27.3185 | 30.0806 | 15.2218 | 0 | 0 | 49.6126 | 160.8104 | 160.8104 | 180.3099 | 223.0876 | 229.3841 | 195.5111 | 160.8104 | 160.8104 | 369.3874 | 160.8104 | 160.8104 | 188.8636 | 250.4061 | 259.4647 | 210.733 | 160.8104 | 160.8104 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 14 | 3422 | 16.6 | 16.6 | 11.5875 | 11.5766 | 15 | 76 | 76 | 3.5764 | 189.0185 | 54.4233 | 215.2485 | 0 | 0 | 0 | 1.0677 | 1.8604 | 1.5633 | 0.35041 | 0 | 2.9815 | 95.8363 | 95.8363 | 95.8363 | 95.8363 | 95.8363 | 95.8363 | 95.8363 | 95.8363 | 189.0185 | 95.8363 | 95.8363 | 95.8363 | 96.904 | 97.6966 | 97.3995 | 96.1867 | 95.8363 | 192 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 15 | 3423 | 18.3 | 18.3 | 11.5875 | 11.5766 | 15 | 72 | 72 | 9.3972 | 256.6745 | 47.8721 | 235.1782 | 0 | 0 | 0 | 0.92602 | 4.4649 | 5.3882 | 3.1553 | 0 | 7.3255 | 126.116 | 126.116 | 126.116 | 127.8737 | 134.5908 | 136.3434 | 132.105 | 126.116 | 256.6745 | 126.116 | 126.116 | 126.116 | 128.7997 | 139.0556 | 141.7317 | 135.2603 | 126.116 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 16 | 3424 | 16.8 | 16.8 | 11.5875 | 11.5766 | 15 | 76 | 76 | 0.63375 | 66.562 | 39.6605 | 251.0345 | 0 | 0 | 0 | 0 | 0.24275 | 0.41842 | 0.34899 | 0.075121 | 0.43796 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 66.562 | 32.2684 | 32.2684 | 32.2684 | 32.2684 | 32.5111 | 32.6868 | 32.6173 | 32.3435 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 17 | 3425 | 17.9 | 17.9 | 11.5875 | 11.5766 | 15 | 68 | 68 | 7.1874 | 176.8719 | 30.6736 | 264.2843 | 0 | 0 | 0 | 0 | 1.7983 | 4.9717 | 5.2328 | 2.4286 | 4.1281 | 87.9374 | 87.9374 | 87.9374 | 87.9374 | 89.5737 | 92.4613 | 92.6989 | 90.1472 | 176.8719 | 87.9374 | 87.9374 | 87.9374 | 87.9374 | 91.372 | 97.4331 | 97.9317 | 92.5758 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 23 | 18 | 3426 | 18.2 | 18.2 | 11.5875 | 11.5766 | 15 | 68 | 68 | 9.9087 | 145.6666 | 21.4758 | 276.1298 | 0 | 0 | 0 | 0 | 0.84876 | 6.5964 | 8.48 | 5.3961 | 4.3334 | 71.8294 | 71.8294 | 71.8294 | 71.8294 | 72.545 | 77.3913 | 78.9795 | 76.3792 | 145.6666 | 71.8294 | 71.8294 | 71.8294 | 71.8294 | 73.3938 | 83.9877 | 87.4595 | 81.7753 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 19 | 3427 | 15.8 | 15.8 | 11.5875 | 11.5766 | 15 | 80 | 80 | 0.15784 | 13.9543 | 12.4705 | 287.4175 | 0.015684 | 0 | 0 | 0 | 0 | 0.092177 | 0.14604 | 0.11436 | 0.045671 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 13.9543 | 6.5564 | 6.5407 | 6.5407 | 6.5407 | 6.5407 | 6.6329 | 6.6867 | 6.6551 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 20 | 3428 | 14.5 | 14.5 | 11.5875 | 11.5766 | 15 | 87 | 87 | 0.21872 | 7.9693 | 4.0064 | 298.756 | 0.063924 | 0 | 0 | 0 | 0 | 0.098882 | 0.20376 | 0.18928 | 0.030721 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 7.9693 | 3.7743 | 3.7104 | 3.7104 | 3.7104 | 3.7104 | 3.8092 | 3.9141 | 3.8997 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 21 | 3429 | 13.9 | 13.9 | 11.5875 | 11.5766 | 15 | 92 | 92 | 0 | 0 | -3.5629 | 310.5974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 22 | 3430 | 13.4 | 13.4 | 11.5875 | 11.5766 | 15 | 96 | 96 | 0 | 0 | -9.8521 | 323.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 23 | 3431 | 13.4 | 13.4 | 11.5875 | 11.5766 | 15 | 96 | 96 | 0 | 0 | -14.4531 | 336.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 23 | 24 | 3432 | 13.4 | 13.4 | 13.5583 | 11.7274 | 15 | 97 | 97 | 0 | 0 | -16.9924 | 351.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 1 | 3433 | 13.5 | 13.5 | 13.5583 | 11.7274 | 15 | 97 | 97 | 0 | 0 | -17.2275 | 5.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 2 | 3434 | 13.5 | 13.5 | 13.5583 | 11.7274 | 15 | 97 | 97 | 0 | 0 | -14.9527 | 20.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 3 | 3435 | 13.5 | 13.5 | 13.5583 | 11.7274 | 15 | 97 | 97 | 0 | 0 | -10.747 | 34.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 4 | 3436 | 13.6 | 13.6 | 13.5583 | 11.7274 | 15 | 97 | 97 | 0 | 0 | -4.7743 | 46.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 5 | 3437 | 13.4 | 13.4 | 13.5583 | 11.7274 | 15 | 96 | 96 | 0 | 0 | 2.5602 | 58.8092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 6 | 3438 | 13.2 | 13.2 | 13.5583 | 11.7274 | 15 | 96 | 96 | 0.18027 | 5.9791 | 10.8658 | 70.204 | 0.093268 | 0.17489 | 0.15406 | 0.042986 | 0 | 0 | 0 | 0 | 0.020922 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 5.9791 | 2.9124 | 2.994 | 2.9732 | 2.8621 | 2.8192 | 2.8192 | 2.8192 | 2.8192 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 7 | 3439 | 11.8 | 11.8 | 13.5583 | 11.7274 | 15 | 95 | 95 | 0.34988 | 18.9077 | 19.7849 | 81.4472 | 0.11637 | 0.3109 | 0.3233 | 0.14632 | 0 | 0 | 0 | 0 | 0.092299 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 18.9077 | 9.0697 | 9.2643 | 9.2767 | 9.0997 | 8.9534 | 8.9534 | 8.9534 | 8.9534 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 24 | 8 | 3440 | 11.8 | 11.8 | 13.5583 | 11.7274 | 15 | 94 | 94 | 1.6233 | 63.3303 | 28.9725 | 93.1107 | 0.22716 | 1.2287 | 1.5105 | 0.90743 | 0 | 0 | 0 | 0 | 0.66967 | 30.961 | 30.961 | 30.961 | 30.961 | 30.961 | 30.961 | 30.961 | 30.961 | 63.3303 | 31.1882 | 32.1897 | 32.4715 | 31.8685 | 30.961 | 30.961 | 30.961 | 30.961 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 9 | 3441 | 13.3 | 13.3 | 13.5583 | 11.7274 | 15 | 88 | 88 | 30.5247 | 222.1452 | 38.0438 | 105.9847 | 0 | 17.8305 | 26.6653 | 19.8799 | 1.4491 | 0 | 0 | 0 | 16.8548 | 100.0506 | 145.433 | 167.9194 | 150.6491 | 103.7389 | 100.0506 | 100.0506 | 100.0506 | 222.1452 | 100.0506 | 163.2636 | 194.5847 | 170.529 | 105.188 | 100.0506 | 100.0506 | 100.0506 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 10 | 3442 | 14.5 | 14.5 | 13.5583 | 11.7274 | 15 | 74 | 74 | 344.5091 | 268.0827 | 46.4794 | 121.1993 | 0 | 131.5991 | 260.8242 | 237.262 | 74.715 | 0 | 0 | 0 | 231.9173 | 137.4965 | 204.2723 | 269.8436 | 257.8877 | 175.4083 | 137.4965 | 137.4965 | 137.4965 | 268.0827 | 137.4965 | 335.8714 | 530.6678 | 495.1497 | 250.1233 | 137.4965 | 137.4965 | 137.4965 | 500 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 11 | 3443 | 16 | 16 | 13.5583 | 11.7274 | 15 | 72 | 72 | 553.6096 | 231.1988 | 53.4714 | 140.2247 | 0 | 90.9391 | 326.0877 | 370.2187 | 197.4805 | 0 | 0 | 0 | 424.8012 | 138.7927 | 166.6871 | 238.8159 | 252.3525 | 199.3673 | 138.7927 | 138.7927 | 138.7927 | 231.1988 | 138.7927 | 257.6261 | 564.9037 | 622.5711 | 396.8478 | 138.7927 | 138.7927 | 138.7927 | 656 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 12 | 3444 | 16 | 16 | 13.5583 | 11.7274 | 15 | 66 | 66 | 520.5722 | 262.8905 | 57.8025 | 164.0245 | 0 | 0 | 198.2401 | 308.57 | 238.1437 | 28.2161 | 0 | 0 | 431.1095 | 147.3415 | 147.3415 | 219.6146 | 259.838 | 234.1624 | 157.6283 | 147.3415 | 147.3415 | 262.8905 | 147.3415 | 147.3415 | 417.8547 | 568.4079 | 472.3062 | 185.8445 | 147.3415 | 147.3415 | 694 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 13 | 3445 | 16.5 | 16.5 | 13.5583 | 11.7274 | 15 | 64 | 64 | 277.0915 | 361.0865 | 58.2325 | 190.6729 | 0 | 0 | 40.6358 | 129.1027 | 141.9431 | 71.6351 | 0 | 0 | 235.9135 | 160.7605 | 160.7605 | 194.1412 | 266.8136 | 277.3615 | 219.6061 | 160.7605 | 160.7605 | 361.0865 | 160.7605 | 160.7605 | 234.777 | 395.9163 | 419.3046 | 291.2412 | 160.7605 | 160.7605 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 14 | 3446 | 16.4 | 16.4 | 13.5583 | 11.7274 | 15 | 61 | 61 | 151.4011 | 379.516 | 54.6084 | 215.3413 | 0 | 0 | 0 | 44.9491 | 78.3298 | 65.826 | 14.7622 | 0 | 126.484 | 165.8639 | 165.8639 | 165.8639 | 221.5252 | 262.8611 | 247.3774 | 184.1442 | 165.8639 | 379.516 | 165.8639 | 165.8639 | 165.8639 | 266.4743 | 341.1909 | 313.2034 | 198.9064 | 165.8639 | 506 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 15 | 3447 | 17.5 | 17.5 | 13.5583 | 11.7274 | 15 | 58 | 58 | 388.5055 | 296.4324 | 48.0445 | 235.307 | 0 | 0 | 0 | 37.7514 | 183.5434 | 221.8181 | 130.1548 | 0 | 303.5676 | 144.9944 | 144.9944 | 144.9944 | 165.1039 | 242.7645 | 263.1527 | 214.3254 | 144.9944 | 296.4324 | 144.9944 | 144.9944 | 144.9944 | 202.8553 | 426.3079 | 484.9708 | 344.4802 | 144.9944 | 600 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 16 | 3448 | 17.1 | 17.1 | 13.5583 | 11.7274 | 15 | 65 | 65 | 27.5762 | 274.8892 | 39.8233 | 251.1685 | 0 | 0 | 0 | 0 | 10.4935 | 18.1387 | 15.1585 | 3.2986 | 19.1108 | 123.6193 | 123.6193 | 123.6193 | 123.6193 | 158.491 | 183.8974 | 173.9936 | 134.5812 | 274.8892 | 123.6193 | 123.6193 | 123.6193 | 123.6193 | 168.9845 | 202.036 | 189.1521 | 137.8799 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 17 | 3449 | 16.1 | 16.1 | 13.5583 | 11.7274 | 15 | 59 | 59 | 3.0212 | 120.2585 | 30.832 | 264.4121 | 0 | 0 | 0 | 0 | 0.74898 | 2.0825 | 2.1962 | 1.0233 | 1.7415 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 120.2585 | 59.6626 | 59.6626 | 59.6626 | 59.6626 | 60.4116 | 61.7452 | 61.8588 | 60.686 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 24 | 18 | 3450 | 15.1 | 15.1 | 13.5583 | 11.7274 | 15 | 64 | 64 | 1.4296 | 63.3715 | 21.6343 | 276.2477 | 0 | 0 | 0 | 0 | 0.11953 | 0.94843 | 1.2217 | 0.77938 | 0.62846 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 63.3715 | 30.6732 | 30.6732 | 30.6732 | 30.6732 | 30.7927 | 31.6216 | 31.8949 | 31.4526 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 19 | 3451 | 13 | 13 | 13.5583 | 11.7274 | 15 | 78 | 78 | 0.86264 | 32.7483 | 12.6327 | 287.5242 | 0.087265 | 0 | 0 | 0 | 0 | 0.50194 | 0.79711 | 0.62535 | 0.25172 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 32.7483 | 15.6764 | 15.5892 | 15.5892 | 15.5892 | 15.5892 | 16.0911 | 16.3863 | 16.2145 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 20 | 3452 | 12.2 | 12.2 | 13.5583 | 11.7274 | 15 | 90 | 90 | 2.0588 | 24.7054 | 4.1749 | 298.8498 | 0.6049 | 0 | 0 | 0 | 0 | 0.92686 | 1.9157 | 1.7823 | 0.2946 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 24.7054 | 12.3788 | 11.7739 | 11.7739 | 11.7739 | 11.7739 | 12.7007 | 13.6896 | 13.5562 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 21 | 3453 | 11.8 | 11.8 | 13.5583 | 11.7274 | 15 | 92 | 92 | 1.3141 | 1.1467 | -3.3866 | 310.6754 | 0.63238 | 0 | 0 | 0 | 0 | 0.36455 | 1.1479 | 1.2589 | 1.8533 | 1.3108 | 0.83248 | 0.83248 | 0.83248 | 0.83248 | 1.1082 | 1.7008 | 1.7847 | 1.1467 | 1.9432 | 0.83248 | 0.83248 | 0.83248 | 0.83248 | 1.4728 | 2.8488 | 3.0436 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 22 | 3454 | 12 | 12 | 13.5583 | 11.7274 | 15 | 95 | 95 | 0 | 0 | -9.6678 | 323.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 23 | 3455 | 12.3 | 12.3 | 13.5583 | 11.7274 | 15 | 95 | 95 | 0 | 0 | -14.2627 | 336.8635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 24 | 24 | 3456 | 12.3 | 12.3 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | -16.7996 | 351.1882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 1 | 3457 | 12.2 | 12.2 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | -17.0377 | 5.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 2 | 3458 | 13.1 | 13.1 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | -14.7769 | 20.2231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 3 | 3459 | 13.7 | 13.7 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | -10.5824 | 33.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 4 | 3460 | 14 | 14 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | -4.6219 | 46.7311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 5 | 3461 | 13.9 | 13.9 | 14.0167 | 12.2386 | 15 | 96 | 96 | 0 | 0 | 2.7014 | 58.6865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 6 | 3462 | 13.9 | 13.9 | 14.0167 | 12.2386 | 15 | 97 | 97 | 0.043142 | 2.9949 | 10.9982 | 70.0694 | 0.022397 | 0.041871 | 0.036817 | 0.010196 | 0 | 0 | 0 | 0 | 0.0051184 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 2.9949 | 1.4122 | 1.4317 | 1.4266 | 1.4 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 7 | 3463 | 14.1 | 14.1 | 14.0167 | 12.2386 | 15 | 97 | 97 | 0.18662 | 13.9503 | 19.9118 | 81.3011 | 0.062446 | 0.16593 | 0.17222 | 0.07762 | 0 | 0 | 0 | 0 | 0.049678 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 13.9503 | 6.617 | 6.7205 | 6.7268 | 6.6322 | 6.5546 | 6.5546 | 6.5546 | 6.5546 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 25 | 8 | 3464 | 14.1 | 14.1 | 14.0167 | 12.2386 | 15 | 97 | 97 | 0.3075 | 27.8725 | 29.0982 | 92.9523 | 0.043726 | 0.233 | 0.28579 | 0.17116 | 0 | 0 | 0 | 0 | 0.12754 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 27.8725 | 13.2609 | 13.4502 | 13.503 | 13.3884 | 13.2172 | 13.2172 | 13.2172 | 13.2172 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 9 | 3465 | 14 | 14 | 14.0167 | 12.2386 | 15 | 91 | 91 | 4.9425 | 147.2608 | 38.1738 | 105.8139 | 0 | 2.8924 | 4.3129 | 3.207 | 0.22243 | 0 | 0 | 0 | 2.7392 | 71.6923 | 79.3498 | 83.1105 | 80.1826 | 72.2812 | 71.6923 | 71.6923 | 71.6923 | 147.2608 | 71.6923 | 82.2423 | 87.4235 | 83.3896 | 72.5036 | 71.6923 | 71.6923 | 71.6923 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 10 | 3466 | 12.6 | 12.6 | 14.0167 | 12.2386 | 15 | 88 | 88 | 21.2885 | 257.6285 | 46.6205 | 121.0209 | 0 | 8.1611 | 16.1023 | 14.6109 | 4.5607 | 0 | 0 | 0 | 14.3715 | 119.0453 | 140.9414 | 162.2472 | 158.246 | 131.2815 | 119.0453 | 119.0453 | 119.0453 | 257.6285 | 119.0453 | 149.1025 | 178.3495 | 172.8569 | 135.8422 | 119.0453 | 119.0453 | 119.0453 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 11 | 3467 | 12.9 | 12.9 | 14.0167 | 12.2386 | 15 | 80 | 80 | 5.0781 | 207.0943 | 53.6305 | 140.0594 | 0 | 0.84253 | 2.9889 | 3.3845 | 1.7974 | 0 | 0 | 0 | 3.9057 | 102.8171 | 104.279 | 108.003 | 108.6893 | 105.9357 | 102.8171 | 102.8171 | 102.8171 | 207.0943 | 102.8171 | 105.1215 | 110.992 | 112.0738 | 107.7331 | 102.8171 | 102.8171 | 102.8171 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 12 | 3468 | 13.2 | 13.2 | 14.0167 | 12.2386 | 15 | 78 | 78 | 10.1367 | 277.5879 | 57.9811 | 163.9203 | 0 | 0 | 3.859 | 5.9876 | 4.6087 | 0.5301 | 0 | 0 | 8.4121 | 134.1663 | 134.1663 | 144.7063 | 150.5199 | 146.7538 | 135.6141 | 134.1663 | 134.1663 | 277.5879 | 134.1663 | 134.1663 | 148.5653 | 156.5075 | 151.3625 | 136.1442 | 134.1663 | 134.1663 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 13 | 3469 | 13.8 | 13.8 | 14.0167 | 12.2386 | 15 | 70 | 70 | 28.4344 | 339.7431 | 58.4195 | 190.6742 | 0 | 0 | 4.1756 | 13.1958 | 14.4861 | 7.2906 | 0 | 0 | 24.2569 | 147.875 | 147.875 | 165.0169 | 202.0466 | 207.3434 | 177.8044 | 147.875 | 147.875 | 339.7431 | 147.875 | 147.875 | 169.1925 | 215.2424 | 221.8294 | 185.095 | 147.875 | 147.875 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 14 | 3470 | 13.3 | 13.3 | 14.0167 | 12.2386 | 15 | 69 | 69 | 17.6896 | 310.1915 | 54.7885 | 215.4283 | 0 | 0 | 0 | 5.2239 | 9.1037 | 7.6506 | 1.7159 | 0 | 14.8085 | 149.2458 | 149.2458 | 149.2458 | 159.6318 | 167.3453 | 164.4564 | 152.6573 | 149.2458 | 310.1915 | 149.2458 | 149.2458 | 149.2458 | 164.8557 | 176.449 | 172.107 | 154.3732 | 149.2458 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 15 | 3471 | 13.8 | 13.8 | 14.0167 | 12.2386 | 15 | 67 | 67 | 12.5285 | 273.1884 | 48.2127 | 235.4296 | 0 | 0 | 0 | 1.2012 | 5.8863 | 7.1233 | 4.1876 | 0 | 9.8116 | 133.0496 | 133.0496 | 133.0496 | 135.3582 | 144.3625 | 146.7399 | 141.0977 | 133.0496 | 273.1884 | 133.0496 | 133.0496 | 133.0496 | 136.5594 | 150.2488 | 153.8632 | 145.2852 | 133.0496 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 16 | 3472 | 14.3 | 14.3 | 14.0167 | 12.2386 | 15 | 63 | 63 | 75.2522 | 308.7075 | 39.9825 | 251.2966 | 0 | 0 | 0 | 0 | 28.4536 | 49.3171 | 41.2914 | 9.0777 | 52.2925 | 139.3966 | 139.3966 | 139.3966 | 139.3966 | 181.0011 | 211.5075 | 199.7723 | 152.6699 | 308.7075 | 139.3966 | 139.3966 | 139.3966 | 139.3966 | 209.4546 | 260.8246 | 241.0637 | 161.7476 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 17 | 3473 | 14.7 | 14.7 | 14.0167 | 12.2386 | 15 | 58 | 58 | 372.9036 | 223.2903 | 30.9869 | 264.5341 | 0 | 0 | 0 | 0 | 91.6261 | 256.1643 | 270.6449 | 126.5854 | 215.7097 | 117.2557 | 117.2557 | 117.2557 | 117.2557 | 157.3036 | 229.2197 | 235.5489 | 172.5835 | 223.2903 | 117.2557 | 117.2557 | 117.2557 | 117.2557 | 248.9297 | 485.384 | 506.1937 | 299.1689 | 439 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 25 | 18 | 3474 | 14.8 | 14.8 | 14.0167 | 12.2386 | 15 | 57 | 57 | 225.3169 | 194.4589 | 21.7894 | 276.3602 | 0 | 0 | 0 | 0 | 18.3991 | 148.9743 | 192.2825 | 122.9541 | 99.5411 | 97.9627 | 97.9627 | 97.9627 | 97.9627 | 109.4381 | 190.8771 | 217.8882 | 174.6485 | 194.4589 | 97.9627 | 97.9627 | 97.9627 | 97.9627 | 127.8371 | 339.8515 | 410.1706 | 297.6026 | 294 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 19 | 3475 | 14.2 | 14.2 | 14.0167 | 12.2386 | 15 | 65 | 65 | 245.6077 | 127.7504 | 12.7913 | 287.6258 | 25.2643 | 0 | 0 | 0 | 0 | 142.4058 | 226.6565 | 178.1349 | 72.2496 | 79.9688 | 68.5813 | 68.5813 | 68.5813 | 68.5813 | 132.7688 | 170.7436 | 148.8732 | 127.7504 | 105.2331 | 68.5813 | 68.5813 | 68.5813 | 68.5813 | 275.1746 | 397.4002 | 327.0081 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 20 | 3476 | 12.6 | 12.6 | 14.0167 | 12.2386 | 15 | 71 | 71 | 286.6748 | 61.2474 | 4.3395 | 298.9388 | 84.6506 | 0 | 0 | 0 | 0 | 128.5419 | 266.4363 | 248.2559 | 41.7526 | 60.7096 | 35.6793 | 35.6793 | 35.6793 | 35.6793 | 73.6877 | 114.4616 | 109.0858 | 61.2474 | 145.3601 | 35.6793 | 35.6793 | 35.6793 | 35.6793 | 202.2296 | 380.8978 | 357.3417 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 21 | 3477 | 11.5 | 11.5 | 14.0167 | 12.2386 | 15 | 78 | 78 | 2.5553 | 3.63 | -3.2146 | 310.7489 | 1.2329 | 0 | 0 | 0 | 0 | 0.70494 | 2.2299 | 2.4485 | 18.37 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 3.63 | 5.0041 | 3.7712 | 3.7712 | 3.7712 | 3.7712 | 4.4761 | 6.001 | 6.2197 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 22 | 3478 | 11.5 | 11.5 | 14.0167 | 12.2386 | 15 | 82 | 82 | 0 | 0 | -9.4884 | 323.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 23 | 3479 | 10.8 | 10.8 | 14.0167 | 12.2386 | 15 | 84 | 84 | 0 | 0 | -14.0776 | 336.8909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 25 | 24 | 3480 | 10.8 | 10.8 | 13.2417 | 12.5442 | 15 | 83 | 83 | 0 | 0 | -16.6126 | 351.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 1 | 3481 | 10.4 | 10.4 | 13.2417 | 12.5442 | 15 | 87 | 87 | 0 | 0 | -16.8538 | 5.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 2 | 3482 | 9.8 | 9.8 | 13.2417 | 12.5442 | 15 | 90 | 90 | 0 | 0 | -14.6073 | 20.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 3 | 3483 | 9.1 | 9.1 | 13.2417 | 12.5442 | 15 | 94 | 94 | 0 | 0 | -10.424 | 33.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 4 | 3484 | 8.5 | 8.5 | 13.2417 | 12.5442 | 15 | 95 | 95 | 0 | 0 | -4.4755 | 46.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 5 | 3485 | 8.5 | 8.5 | 13.2417 | 12.5442 | 15 | 95 | 95 | 0 | 0 | 2.8367 | 58.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 6 | 3486 | 9.2 | 9.2 | 13.2417 | 12.5442 | 15 | 94 | 94 | 6.075 | 35.2641 | 11.1248 | 69.9372 | 3.1643 | 5.8982 | 5.177 | 1.4232 | 0 | 0 | 0 | 0 | 0.73591 | 70.1821 | 118.4841 | 105.7421 | 39.4202 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 35.2641 | 73.3464 | 124.3823 | 110.9191 | 40.8434 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 7 | 3487 | 10.5 | 10.5 | 13.2417 | 12.5442 | 15 | 89 | 89 | 12.5231 | 93.6372 | 20.0329 | 81.1576 | 4.2153 | 11.1422 | 11.5422 | 5.1808 | 0 | 0 | 0 | 0 | 3.3628 | 70.7973 | 120.0327 | 122.8753 | 77.66 | 40.8353 | 40.8353 | 40.8353 | 40.8353 | 93.6372 | 75.0127 | 131.1749 | 134.4175 | 82.8408 | 40.8353 | 40.8353 | 40.8353 | 40.8353 | 97 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 26 | 8 | 3488 | 11.4 | 11.4 | 13.2417 | 12.5442 | 15 | 86 | 86 | 24.0179 | 161.9868 | 29.218 | 92.7965 | 3.4686 | 18.2187 | 22.2965 | 13.3133 | 0 | 0 | 0 | 0 | 10.0132 | 83.9811 | 136.0128 | 150.3975 | 118.7089 | 71.7454 | 71.7454 | 71.7454 | 71.7454 | 161.9868 | 87.4496 | 154.2314 | 172.694 | 132.0223 | 71.7454 | 71.7454 | 71.7454 | 71.7454 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 9 | 3489 | 11.9 | 11.9 | 13.2417 | 12.5442 | 15 | 84 | 84 | 25.9465 | 218.5687 | 38.2978 | 105.6456 | 0 | 15.2123 | 22.6183 | 16.7748 | 1.1048 | 0 | 0 | 0 | 14.4313 | 98.8613 | 141.1051 | 161.6712 | 145.4441 | 101.9294 | 98.8613 | 98.8613 | 98.8613 | 218.5687 | 98.8613 | 156.3174 | 184.2895 | 162.2189 | 103.0342 | 98.8613 | 98.8613 | 98.8613 | 233 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 10 | 3490 | 13.2 | 13.2 | 13.2417 | 12.5442 | 15 | 78 | 78 | 177.102 | 305.1162 | 46.7555 | 120.8444 | 0 | 68.1342 | 133.8398 | 121.1439 | 37.4835 | 0 | 0 | 0 | 119.8838 | 141.109 | 205.9439 | 268.4679 | 256.3867 | 176.7774 | 141.109 | 141.109 | 141.109 | 305.1162 | 141.109 | 274.0781 | 402.3076 | 377.5305 | 214.2609 | 141.109 | 141.109 | 141.109 | 425 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 11 | 3491 | 15.2 | 15.2 | 13.2417 | 12.5442 | 15 | 67 | 67 | 774.9644 | 152.6235 | 53.7833 | 139.8945 | 0 | 129.844 | 455.844 | 514.8168 | 272.2169 | 0 | 0 | 0 | 597.3765 | 127.6069 | 142.5782 | 180.1666 | 186.9663 | 158.994 | 127.6069 | 127.6069 | 127.6069 | 152.6235 | 127.6069 | 272.4221 | 636.0106 | 701.7831 | 431.2109 | 127.6069 | 127.6069 | 127.6069 | 750 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 12 | 3492 | 15.6 | 15.6 | 13.2417 | 12.5442 | 15 | 58 | 58 | 360.4935 | 325.2439 | 58.1535 | 163.814 | 0 | 0 | 137.2104 | 212.2177 | 162.9108 | 18.173 | 0 | 0 | 299.7561 | 157.897 | 157.897 | 236.733 | 279.8294 | 251.4995 | 168.3385 | 157.897 | 157.897 | 325.2439 | 157.897 | 157.897 | 373.9433 | 492.0471 | 414.4103 | 186.5115 | 157.897 | 157.897 | 625 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 13 | 3493 | 15.5 | 15.5 | 13.2417 | 12.5442 | 15 | 58 | 58 | 139.7209 | 388.5794 | 58.6007 | 190.6709 | 0 | 0 | 20.5509 | 64.5954 | 70.8009 | 35.5321 | 0 | 0 | 119.4206 | 168.004 | 168.004 | 196.423 | 257.3307 | 265.912 | 217.1401 | 168.004 | 168.004 | 388.5794 | 168.004 | 168.004 | 216.9739 | 321.9262 | 336.7129 | 252.6723 | 168.004 | 168.004 | 508 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 14 | 3494 | 16.6 | 16.6 | 13.2417 | 12.5442 | 15 | 57 | 57 | 128.2639 | 381.4151 | 54.9637 | 215.5092 | 0 | 0 | 0 | 37.6859 | 65.6697 | 55.1851 | 12.3738 | 0 | 107.5849 | 164.4829 | 164.4829 | 164.4829 | 219.8654 | 260.99 | 245.582 | 182.6673 | 164.4829 | 381.4151 | 164.4829 | 164.4829 | 164.4829 | 257.5513 | 326.6597 | 300.7671 | 195.0411 | 164.4829 | 489 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 15 | 3495 | 16.7 | 16.7 | 13.2417 | 12.5442 | 15 | 54 | 54 | 78.2619 | 349.5759 | 48.3766 | 235.5459 | 0 | 0 | 0 | 7.4084 | 36.5739 | 44.3148 | 26.0967 | 0 | 61.4241 | 155.1041 | 155.1041 | 155.1041 | 166.9089 | 213.3823 | 225.7171 | 196.6877 | 155.1041 | 349.5759 | 155.1041 | 155.1041 | 155.1041 | 174.3174 | 249.9562 | 270.0319 | 222.7844 | 155.1041 | 411 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 16 | 3496 | 17 | 17 | 13.2417 | 12.5442 | 15 | 53 | 53 | 28.3404 | 277.255 | 40.1378 | 251.4186 | 0 | 0 | 0 | 0 | 10.6499 | 18.5066 | 15.5224 | 3.4453 | 19.745 | 124.5708 | 124.5708 | 124.5708 | 124.5708 | 159.353 | 185.0126 | 175.2662 | 135.8231 | 277.255 | 124.5708 | 124.5708 | 124.5708 | 124.5708 | 170.003 | 203.5192 | 190.7886 | 139.2685 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 17 | 3497 | 17.1 | 17.1 | 13.2417 | 12.5442 | 15 | 49 | 49 | 12.8994 | 203.5131 | 31.1383 | 264.6505 | 0 | 0 | 0 | 0 | 3.1424 | 8.8317 | 9.3475 | 4.3876 | 7.4869 | 99.3368 | 99.3368 | 99.3368 | 99.3368 | 103.5851 | 111.2768 | 111.9742 | 105.2687 | 203.5131 | 99.3368 | 99.3368 | 99.3368 | 99.3368 | 106.7275 | 120.1085 | 121.3216 | 109.6563 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 18 | 3498 | 16.6 | 16.6 | 13.2417 | 12.5442 | 15 | 51 | 51 | 11.0524 | 151.0939 | 21.9409 | 276.4674 | 0 | 0 | 0 | 0 | 0.88196 | 7.2837 | 9.4188 | 6.0364 | 4.9061 | 74.2805 | 74.2805 | 74.2805 | 74.2805 | 75.096 | 81.0149 | 82.9889 | 79.8617 | 151.0939 | 74.2805 | 74.2805 | 74.2805 | 74.2805 | 75.9779 | 88.2986 | 92.4077 | 85.8981 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 19 | 3499 | 16.4 | 16.4 | 13.2417 | 12.5442 | 15 | 53 | 53 | 13.0273 | 104.138 | 12.9463 | 287.7223 | 1.3611 | 0 | 0 | 0 | 0 | 7.5277 | 12.0069 | 9.4526 | 3.862 | 52.032 | 51.3762 | 51.3762 | 51.3762 | 51.3762 | 55.0036 | 57.162 | 55.9311 | 104.138 | 53.3931 | 51.3762 | 51.3762 | 51.3762 | 51.3762 | 62.5313 | 69.1688 | 65.3837 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 20 | 3500 | 15.4 | 15.4 | 13.2417 | 12.5442 | 15 | 60 | 60 | 0.3723 | 10.9449 | 4.5002 | 299.023 | 0.11045 | 0 | 0 | 0 | 0 | 0.16629 | 0.34561 | 0.32248 | 0.055141 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 10.9449 | 5.2268 | 5.1163 | 5.1163 | 5.1163 | 5.1163 | 5.2826 | 5.4619 | 5.4388 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 21 | 3501 | 13 | 13 | 13.2417 | 12.5442 | 15 | 84 | 84 | 0 | 0 | -3.0469 | 310.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 22 | 3502 | 13.4 | 13.4 | 13.2417 | 12.5442 | 15 | 88 | 88 | 0 | 0 | -9.3137 | 323.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 23 | 3503 | 13.8 | 13.8 | 13.2417 | 12.5442 | 15 | 92 | 92 | 0 | 0 | -13.8979 | 336.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 26 | 24 | 3504 | 15 | 15 | 13.325 | 12.865 | 15 | 90 | 90 | 0 | 0 | -16.4315 | 351.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 1 | 3505 | 16 | 16 | 13.325 | 12.865 | 15 | 89 | 89 | 0 | 0 | -16.6761 | 5.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 2 | 3506 | 16.7 | 16.7 | 13.325 | 12.865 | 15 | 82 | 82 | 0 | 0 | -14.4439 | 20.0906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 3 | 3507 | 13.3 | 13.3 | 13.325 | 12.865 | 15 | 81 | 81 | 0 | 0 | -10.2717 | 33.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 4 | 3508 | 11.6 | 11.6 | 13.325 | 12.865 | 15 | 81 | 81 | 0 | 0 | -4.3352 | 46.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 5 | 3509 | 11.3 | 11.3 | 13.325 | 12.865 | 15 | 76 | 76 | 0 | 0 | 2.9661 | 58.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 6 | 3510 | 10.6 | 10.6 | 13.325 | 12.865 | 15 | 74 | 74 | 1.5967 | 18.8027 | 11.2454 | 69.8073 | 0.83443 | 1.5509 | 1.3588 | 0.37082 | 0 | 0 | 0 | 0 | 0.19728 | 13.3037 | 16.9841 | 15.9976 | 10.9221 | 9.0173 | 9.0173 | 9.0173 | 9.0173 | 18.8027 | 14.1382 | 18.535 | 17.3564 | 11.293 | 9.0173 | 9.0173 | 9.0173 | 9.0173 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 7 | 3511 | 10.7 | 10.7 | 13.325 | 12.865 | 15 | 70 | 70 | 5.1803 | 73.5974 | 20.1481 | 81.0167 | 1.7538 | 4.612 | 4.7685 | 2.1318 | 0 | 0 | 0 | 0 | 1.4026 | 46.5385 | 66.8301 | 67.9415 | 49.2218 | 34.0875 | 34.0875 | 34.0875 | 34.0875 | 73.5974 | 48.2923 | 71.442 | 72.7101 | 51.3535 | 34.0875 | 34.0875 | 34.0875 | 34.0875 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 27 | 8 | 3512 | 10.9 | 10.9 | 13.325 | 12.865 | 15 | 73 | 73 | 4.4864 | 106.1203 | 29.332 | 92.6436 | 0.65766 | 3.4067 | 4.1601 | 2.4766 | 0 | 0 | 0 | 0 | 1.8797 | 53.3343 | 62.0168 | 64.3964 | 59.0792 | 51.2571 | 51.2571 | 51.2571 | 51.2571 | 106.1203 | 53.9919 | 65.4235 | 68.5566 | 61.5559 | 51.2571 | 51.2571 | 51.2571 | 51.2571 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 9 | 3513 | 10.7 | 10.7 | 13.325 | 12.865 | 15 | 75 | 75 | 0.80659 | 60.5498 | 38.4159 | 105.48 | 0 | 0.47376 | 0.70243 | 0.51963 | 0.032433 | 0 | 0 | 0 | 0.45016 | 29.2627 | 29.2627 | 29.2627 | 29.2627 | 29.2627 | 29.2627 | 29.2627 | 29.2627 | 60.5498 | 29.2627 | 29.7365 | 29.9652 | 29.7824 | 29.2952 | 29.2627 | 29.2627 | 29.2627 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 10 | 3514 | 12.6 | 12.6 | 13.325 | 12.865 | 15 | 70 | 70 | 30.7794 | 273.1104 | 46.8842 | 120.6701 | 0 | 11.8828 | 23.2415 | 20.9856 | 6.4367 | 0 | 0 | 0 | 20.8896 | 125.0796 | 151.5042 | 176.7633 | 171.7468 | 139.3933 | 125.0796 | 125.0796 | 125.0796 | 273.1104 | 125.0796 | 163.387 | 200.0049 | 192.7325 | 145.83 | 125.0796 | 125.0796 | 125.0796 | 294 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 11 | 3515 | 12 | 12 | 13.325 | 12.865 | 15 | 73 | 73 | 42.0145 | 323.5437 | 53.9296 | 139.7303 | 0 | 7.1073 | 24.6991 | 27.8224 | 14.6478 | 0 | 0 | 0 | 32.4563 | 142.5388 | 163.012 | 213.6865 | 222.6836 | 184.7331 | 142.5388 | 142.5388 | 142.5388 | 323.5437 | 142.5388 | 170.1193 | 238.3855 | 250.5061 | 199.3809 | 142.5388 | 142.5388 | 142.5388 | 356 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 12 | 3516 | 13.7 | 13.7 | 13.325 | 12.865 | 15 | 68 | 68 | 201.1007 | 371.4619 | 58.3194 | 163.7056 | 0 | 0 | 76.5347 | 118.0005 | 90.3433 | 9.7642 | 0 | 0 | 167.5381 | 168.012 | 168.012 | 238.6928 | 276.9871 | 251.4453 | 177.0294 | 168.012 | 168.012 | 371.4619 | 168.012 | 168.012 | 315.2275 | 394.9876 | 341.7886 | 186.7936 | 168.012 | 168.012 | 539 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 13 | 3517 | 13.5 | 13.5 | 13.325 | 12.865 | 15 | 64 | 64 | 339.5297 | 342.2701 | 58.7762 | 190.6629 | 0 | 0 | 50.0304 | 156.4002 | 171.1529 | 85.6465 | 0 | 0 | 290.7299 | 159.9788 | 159.9788 | 192.201 | 260.7086 | 270.2101 | 215.1396 | 159.9788 | 159.9788 | 342.2701 | 159.9788 | 159.9788 | 242.2314 | 417.1088 | 441.363 | 300.7861 | 159.9788 | 159.9788 | 633 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 14 | 3518 | 12.8 | 12.8 | 13.325 | 12.865 | 15 | 70 | 70 | 162.5497 | 380.3999 | 55.1339 | 215.5841 | 0 | 0 | 0 | 47.5294 | 82.808 | 69.5787 | 15.5912 | 0 | 136.6001 | 167.0179 | 167.0179 | 167.0179 | 221.9277 | 262.6842 | 247.4007 | 185.03 | 167.0179 | 380.3999 | 167.0179 | 167.0179 | 167.0179 | 269.4571 | 345.4922 | 316.9794 | 200.6212 | 167.0179 | 517 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 15 | 3519 | 12.8 | 12.8 | 13.325 | 12.865 | 15 | 63 | 63 | 778.9257 | 154.3779 | 48.5362 | 235.6559 | 0 | 0 | 0 | 72.8477 | 362.1305 | 439.2821 | 259.1083 | 0 | 612.6221 | 127.2278 | 127.2278 | 127.2278 | 135.5955 | 168.8242 | 177.6863 | 156.9905 | 127.2278 | 154.3779 | 127.2278 | 127.2278 | 127.2278 | 208.4432 | 530.9546 | 616.9684 | 416.0988 | 127.2278 | 767 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 16 | 3520 | 15.4 | 15.4 | 13.325 | 12.865 | 15 | 55 | 55 | 721.8456 | 153.8254 | 40.2894 | 251.5345 | 0 | 0 | 0 | 0 | 269.6512 | 469.7254 | 394.6408 | 88.381 | 504.1746 | 117.379 | 117.379 | 117.379 | 117.379 | 161.3109 | 193.9072 | 181.6743 | 131.7781 | 153.8254 | 117.379 | 117.379 | 117.379 | 117.379 | 430.9621 | 663.6326 | 576.3151 | 220.1591 | 658 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 17 | 3521 | 14.9 | 14.9 | 13.325 | 12.865 | 15 | 54 | 54 | 442.7947 | 206.1663 | 31.2861 | 264.7611 | 0 | 0 | 0 | 0 | 106.9795 | 302.181 | 320.369 | 150.8892 | 257.8337 | 115.0455 | 115.0455 | 115.0455 | 115.0455 | 152.5166 | 220.8887 | 227.2593 | 167.8966 | 206.1663 | 115.0455 | 115.0455 | 115.0455 | 115.0455 | 259.4961 | 523.0697 | 547.6283 | 318.7858 | 464 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 18 | 3522 | 13.3 | 13.3 | 13.325 | 12.865 | 15 | 67 | 67 | 124.1128 | 202.6541 | 22.0889 | 276.5691 | 0 | 0 | 0 | 0 | 9.6846 | 81.534 | 105.6218 | 67.8378 | 55.3459 | 97.3298 | 97.3298 | 97.3298 | 97.3298 | 106.054 | 170.7787 | 192.478 | 158.4407 | 202.6541 | 97.3298 | 97.3298 | 97.3298 | 97.3298 | 115.7387 | 252.3127 | 298.0998 | 226.2786 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 19 | 3523 | 11.5 | 11.5 | 13.325 | 12.865 | 15 | 75 | 75 | 18.5485 | 111.4602 | 13.0975 | 287.8137 | 1.9662 | 0 | 0 | 0 | 0 | 10.683 | 17.0742 | 13.4636 | 5.5398 | 55.7583 | 54.5969 | 54.5969 | 54.5969 | 54.5969 | 60.9072 | 64.6825 | 62.5498 | 111.4602 | 57.7245 | 54.5969 | 54.5969 | 54.5969 | 54.5969 | 71.5902 | 81.7568 | 76.0134 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 20 | 3524 | 11.5 | 11.5 | 13.325 | 12.865 | 15 | 72 | 72 | 282.7986 | 63.441 | 4.6568 | 299.1023 | 84.2638 | 0 | 0 | 0 | 0 | 125.8455 | 262.2362 | 245.0125 | 42.559 | 62.3826 | 36.794 | 36.794 | 36.794 | 36.794 | 75.0098 | 116.4279 | 111.1975 | 63.441 | 146.6464 | 36.794 | 36.794 | 36.794 | 36.794 | 200.8553 | 378.6641 | 356.21 | 106 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 21 | 3525 | 11.6 | 11.6 | 13.325 | 12.865 | 15 | 71 | 71 | 4.4079 | 2.31 | -2.8836 | 310.8823 | 2.1368 | 0 | 0 | 0 | 0 | 1.2034 | 3.8387 | 4.2254 | 11.69 | 3.5009 | 2.4658 | 2.4658 | 2.4658 | 2.4658 | 3.0487 | 4.3253 | 4.5126 | 2.31 | 5.6377 | 2.4658 | 2.4658 | 2.4658 | 2.4658 | 4.2522 | 8.1641 | 8.738 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 22 | 3526 | 11 | 11 | 13.325 | 12.865 | 15 | 76 | 76 | 0 | 0 | -9.144 | 323.4562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 23 | 3527 | 11.4 | 11.4 | 13.325 | 12.865 | 15 | 72 | 72 | 0 | 0 | -13.7235 | 336.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 27 | 24 | 3528 | 11.5 | 11.5 | 12.5542 | 12.9038 | 15 | 72 | 72 | 0 | 0 | -16.2561 | 351.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 1 | 3529 | 11.2 | 11.2 | 12.5542 | 12.9038 | 15 | 74 | 74 | 0 | 0 | -16.5046 | 5.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 2 | 3530 | 10.8 | 10.8 | 12.5542 | 12.9038 | 15 | 80 | 80 | 0 | 0 | -14.2869 | 20.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 3 | 3531 | 9.9 | 9.9 | 12.5542 | 12.9038 | 15 | 89 | 89 | 0 | 0 | -10.1258 | 33.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 4 | 3532 | 9.6 | 9.6 | 12.5542 | 12.9038 | 15 | 91 | 91 | 0 | 0 | -4.201 | 46.4139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 5 | 3533 | 9.7 | 9.7 | 12.5542 | 12.9038 | 15 | 92 | 92 | 0 | 0 | 3.0894 | 58.3303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 6 | 3534 | 9.8 | 9.8 | 12.5542 | 12.9038 | 15 | 92 | 92 | 0 | 0 | 11.3603 | 69.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 7 | 3535 | 9.9 | 9.9 | 12.5542 | 12.9038 | 15 | 93 | 93 | 0.10971 | 10.9701 | 20.2576 | 80.8785 | 0.037353 | 0.097739 | 0.10087 | 0.044913 | 0 | 0 | 0 | 0 | 0.029944 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 10.9701 | 5.1669 | 5.2273 | 5.2304 | 5.1744 | 5.1295 | 5.1295 | 5.1295 | 5.1295 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 28 | 8 | 3536 | 10.3 | 10.3 | 12.5542 | 12.9038 | 15 | 90 | 90 | 0.13759 | 18.9421 | 29.4402 | 92.4935 | 0.020462 | 0.10459 | 0.12744 | 0.075648 | 0 | 0 | 0 | 0 | 0.05792 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 18.9421 | 8.9333 | 9.0174 | 9.0403 | 8.9885 | 8.9129 | 8.9129 | 8.9129 | 8.9129 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 9 | 3537 | 11 | 11 | 12.5542 | 12.9038 | 15 | 90 | 90 | 0.38 | 41.7872 | 38.5279 | 105.3172 | 0 | 0.2236 | 0.33062 | 0.24396 | 0.014398 | 0 | 0 | 0 | 0.21278 | 19.9696 | 19.9696 | 19.9696 | 19.9696 | 19.9696 | 19.9696 | 19.9696 | 19.9696 | 41.7872 | 19.9696 | 20.1932 | 20.3003 | 20.2136 | 19.984 | 19.9696 | 19.9696 | 19.9696 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 10 | 3538 | 12.2 | 12.2 | 12.5542 | 12.9038 | 15 | 88 | 88 | 2.6986 | 134.1639 | 47.0067 | 120.4982 | 0 | 1.0454 | 2.0361 | 1.8341 | 0.55768 | 0 | 0 | 0 | 1.8361 | 66.9974 | 66.9974 | 66.9974 | 66.9974 | 66.9974 | 66.9974 | 66.9974 | 66.9974 | 134.1639 | 66.9974 | 68.0428 | 69.0335 | 68.8315 | 67.5551 | 66.9974 | 66.9974 | 66.9974 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 11 | 3539 | 12.4 | 12.4 | 12.5542 | 12.9038 | 15 | 72 | 72 | 44.6383 | 326.4457 | 54.0695 | 139.5669 | 0 | 7.6224 | 26.228 | 29.4696 | 15.4483 | 0 | 0 | 0 | 34.5543 | 143.7721 | 164.7074 | 215.8088 | 224.7121 | 186.2018 | 143.7721 | 143.7721 | 143.7721 | 326.4457 | 143.7721 | 172.3298 | 242.0368 | 254.1817 | 201.6502 | 143.7721 | 143.7721 | 143.7721 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 12 | 3540 | 10.4 | 10.4 | 12.5542 | 12.9038 | 15 | 78 | 78 | 1.373 | 117.8541 | 58.479 | 163.5954 | 0 | 0 | 0.52253 | 0.80312 | 0.61325 | 0.06415 | 0 | 0 | 1.1459 | 58.3043 | 58.3043 | 58.3043 | 58.3043 | 58.3043 | 58.3043 | 58.3043 | 58.3043 | 117.8541 | 58.3043 | 58.3043 | 58.8268 | 59.1074 | 58.9175 | 58.3684 | 58.3043 | 58.3043 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 13 | 3541 | 9.6 | 9.6 | 12.5542 | 12.9038 | 15 | 82 | 82 | 1.504 | 126.7099 | 58.9457 | 190.6503 | 0 | 0 | 0.22206 | 0.69038 | 0.75429 | 0.37634 | 0 | 0 | 1.2901 | 62.9297 | 62.9297 | 62.9297 | 62.9297 | 62.9297 | 62.9297 | 62.9297 | 62.9297 | 126.7099 | 62.9297 | 62.9297 | 63.1518 | 63.6201 | 63.684 | 63.3061 | 62.9297 | 62.9297 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 14 | 3542 | 9.1 | 9.1 | 12.5542 | 12.9038 | 15 | 88 | 88 | 2.0592 | 145.2664 | 55.2989 | 215.653 | 0 | 0 | 0 | 0.59936 | 1.0439 | 0.877 | 0.19632 | 0 | 1.7336 | 72.6043 | 72.6043 | 72.6043 | 72.6043 | 72.6043 | 72.6043 | 72.6043 | 72.6043 | 145.2664 | 72.6043 | 72.6043 | 72.6043 | 73.2037 | 73.6482 | 73.4813 | 72.8006 | 72.6043 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 15 | 3543 | 8.4 | 8.4 | 12.5542 | 12.9038 | 15 | 92 | 92 | 2.35 | 145.148 | 48.6914 | 235.7595 | 0 | 0 | 0 | 0.21728 | 1.0871 | 1.3201 | 0.77979 | 0 | 1.852 | 72.5182 | 72.5182 | 72.5182 | 72.5182 | 72.5182 | 72.5182 | 72.5182 | 72.5182 | 145.148 | 72.5182 | 72.5182 | 72.5182 | 72.7355 | 73.6053 | 73.8383 | 73.298 | 72.5182 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 16 | 3544 | 8.4 | 8.4 | 12.5542 | 12.9038 | 15 | 90 | 90 | 2.7783 | 140.0548 | 40.437 | 251.6442 | 0 | 0 | 0 | 0 | 1.0319 | 1.8018 | 1.5162 | 0.34239 | 1.9452 | 69.869 | 69.869 | 69.869 | 69.869 | 69.869 | 69.869 | 69.869 | 69.869 | 140.0548 | 69.869 | 69.869 | 69.869 | 69.869 | 70.901 | 71.6708 | 71.3852 | 70.2114 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 17 | 3545 | 8.8 | 8.8 | 12.5542 | 12.9038 | 15 | 90 | 90 | 1.9797 | 98.8437 | 31.4303 | 264.8659 | 0 | 0 | 0 | 0 | 0.47451 | 1.3468 | 1.4301 | 0.67572 | 1.1563 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 98.8437 | 48.5624 | 48.5624 | 48.5624 | 48.5624 | 49.0369 | 49.9092 | 49.9925 | 49.2381 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 28 | 18 | 3546 | 8.8 | 8.8 | 12.5542 | 12.9038 | 15 | 89 | 89 | 0.5939 | 41.734 | 22.2332 | 276.6654 | 0 | 0 | 0 | 0 | 0.045348 | 0.38896 | 0.50473 | 0.32483 | 0.266 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 41.734 | 19.9492 | 19.9492 | 19.9492 | 19.9492 | 19.9945 | 20.3382 | 20.4539 | 20.274 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 19 | 3547 | 9.4 | 9.4 | 12.5542 | 12.9038 | 15 | 82 | 82 | 2.5113 | 57.2446 | 13.2449 | 287.8999 | 0.26981 | 0 | 0 | 0 | 0 | 1.4418 | 2.3088 | 1.8234 | 0.75536 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 57.2446 | 28.0451 | 27.7753 | 27.7753 | 27.7753 | 27.7753 | 29.2171 | 30.0841 | 29.5987 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 20 | 3548 | 9.5 | 9.5 | 12.5542 | 12.9038 | 15 | 80 | 80 | 5.6013 | 43.1442 | 4.8094 | 299.1769 | 1.6758 | 0 | 0 | 0 | 0 | 2.4838 | 5.1884 | 4.8537 | 0.85582 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 43.1442 | 22.7154 | 21.0396 | 21.0396 | 21.0396 | 21.0396 | 23.5234 | 26.228 | 25.8933 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 21 | 3549 | 7.8 | 7.8 | 12.5542 | 12.9038 | 15 | 91 | 91 | 3.127 | 2.9564 | -2.7249 | 310.9423 | 1.5191 | 0 | 0 | 0 | 0 | 0.84965 | 2.7207 | 2.998 | 0.043598 | 3.0238 | 1.6597 | 1.6597 | 1.6597 | 1.6597 | 2.4227 | 4.1029 | 4.3519 | 2.9564 | 4.5429 | 1.6597 | 1.6597 | 1.6597 | 1.6597 | 3.2723 | 6.8236 | 7.3499 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 22 | 3550 | 7.4 | 7.4 | 12.5542 | 12.9038 | 15 | 93 | 93 | 0 | 0 | -8.9793 | 323.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 23 | 3551 | 7 | 7 | 12.5542 | 12.9038 | 15 | 95 | 95 | 0 | 0 | -13.5547 | 336.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 28 | 24 | 3552 | 8.4 | 8.4 | 9.575 | 12.1647 | 15 | 86 | 86 | 0 | 0 | -16.0868 | 351.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 1 | 3553 | 7.4 | 7.4 | 9.575 | 12.1647 | 15 | 92 | 92 | 0 | 0 | -16.3392 | 5.7017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 2 | 3554 | 7 | 7 | 9.575 | 12.1647 | 15 | 93 | 93 | 0 | 0 | -14.1363 | 19.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 3 | 3555 | 6.8 | 6.8 | 9.575 | 12.1647 | 15 | 96 | 96 | 0 | 0 | -9.9861 | 33.5782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 4 | 3556 | 7.6 | 7.6 | 9.575 | 12.1647 | 15 | 95 | 95 | 0 | 0 | -4.073 | 46.3114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 5 | 3557 | 7.4 | 7.4 | 9.575 | 12.1647 | 15 | 96 | 96 | 0 | 0 | 3.2068 | 58.2158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 6 | 3558 | 8.2 | 8.2 | 9.575 | 12.1647 | 15 | 95 | 95 | 3.9556 | 30.4932 | 11.4692 | 69.5551 | 2.0802 | 3.8448 | 3.3571 | 0.90291 | 0 | 0 | 0 | 0 | 0.50678 | 44.3021 | 70.5833 | 63.3201 | 26.7673 | 13.3195 | 13.3195 | 13.3195 | 13.3195 | 30.4932 | 46.3823 | 74.4281 | 66.6772 | 27.6702 | 13.3195 | 13.3195 | 13.3195 | 13.3195 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 7 | 3559 | 9.6 | 9.6 | 9.575 | 12.1647 | 15 | 90 | 90 | 34.8025 | 112.4292 | 20.3613 | 80.7432 | 11.914 | 31.023 | 31.9591 | 14.174 | 0 | 0 | 0 | 0 | 9.5708 | 90.5527 | 154.5026 | 157.6355 | 98.1162 | 50.6815 | 50.6815 | 50.6815 | 50.6815 | 112.4292 | 102.4667 | 185.5256 | 189.5946 | 112.2902 | 50.6815 | 50.6815 | 50.6815 | 50.6815 | 122 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 29 | 8 | 3560 | 9.8 | 9.8 | 9.575 | 12.1647 | 15 | 91 | 91 | 6.0039 | 122.4611 | 29.5425 | 92.3465 | 0.90544 | 4.5685 | 5.5554 | 3.2881 | 0 | 0 | 0 | 0 | 2.5389 | 62.0717 | 79.6244 | 84.3534 | 73.4887 | 57.7331 | 57.7331 | 57.7331 | 57.7331 | 122.4611 | 62.9772 | 84.1929 | 89.9089 | 76.7767 | 57.7331 | 57.7331 | 57.7331 | 57.7331 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 9 | 3561 | 9.9 | 9.9 | 9.575 | 12.1647 | 15 | 95 | 95 | 2.783 | 112.4368 | 38.634 | 105.1575 | 0 | 1.6405 | 2.4191 | 1.7807 | 0.09913 | 0 | 0 | 0 | 1.5632 | 56.0043 | 56.0043 | 56.0043 | 56.0043 | 56.0043 | 56.0043 | 56.0043 | 56.0043 | 112.4368 | 56.0043 | 57.6448 | 58.4234 | 57.785 | 56.1034 | 56.0043 | 56.0043 | 56.0043 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 10 | 3562 | 12.3 | 12.3 | 9.575 | 12.1647 | 15 | 80 | 80 | 182.6428 | 306.435 | 47.123 | 120.3287 | 0 | 70.9958 | 137.708 | 123.7527 | 37.3048 | 0 | 0 | 0 | 124.565 | 142.0483 | 207.5951 | 269.1871 | 256.3029 | 176.4899 | 142.0483 | 142.0483 | 142.0483 | 306.435 | 142.0483 | 278.5909 | 406.8951 | 380.0556 | 213.7947 | 142.0483 | 142.0483 | 142.0483 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 11 | 3563 | 12.2 | 12.2 | 9.575 | 12.1647 | 15 | 70 | 70 | 350.3002 | 306.2987 | 54.2029 | 139.4046 | 0 | 60.3686 | 205.7333 | 230.5822 | 120.3592 | 0 | 0 | 0 | 271.7013 | 151.8315 | 185.3884 | 266.1917 | 280.0044 | 218.7351 | 151.8315 | 151.8315 | 151.8315 | 306.2987 | 151.8315 | 245.757 | 471.9251 | 510.5866 | 339.0943 | 151.8315 | 151.8315 | 151.8315 | 578 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 12 | 3564 | 13.6 | 13.6 | 9.575 | 12.1647 | 15 | 70 | 70 | 162.3877 | 378.2284 | 58.632 | 163.4835 | 0 | 0 | 61.8069 | 94.7028 | 72.123 | 7.2946 | 0 | 0 | 135.7716 | 166.9253 | 166.9253 | 239.1697 | 277.6207 | 251.2279 | 175.4517 | 166.9253 | 166.9253 | 378.2284 | 166.9253 | 166.9253 | 300.9766 | 372.3234 | 323.3509 | 182.7463 | 166.9253 | 166.9253 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 13 | 3565 | 13.4 | 13.4 | 9.575 | 12.1647 | 15 | 66 | 66 | 241.2937 | 373.6775 | 59.1093 | 190.6331 | 0 | 0 | 35.7073 | 110.3976 | 120.4186 | 59.8999 | 0 | 0 | 207.3225 | 161.2393 | 161.2393 | 195.9219 | 268.4687 | 278.202 | 219.4202 | 161.2393 | 161.2393 | 373.6775 | 161.2393 | 161.2393 | 231.6291 | 378.8663 | 398.6206 | 279.3201 | 161.2393 | 161.2393 | 581 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 14 | 3566 | 12.9 | 12.9 | 9.575 | 12.1647 | 15 | 69 | 69 | 175.5724 | 379.934 | 55.4589 | 215.7156 | 0 | 0 | 0 | 50.8826 | 88.5913 | 74.4045 | 16.6325 | 0 | 148.066 | 167.9294 | 167.9294 | 167.9294 | 222.2308 | 262.4732 | 247.3331 | 185.6794 | 167.9294 | 379.934 | 167.9294 | 167.9294 | 167.9294 | 273.1134 | 351.0645 | 321.7376 | 202.3119 | 167.9294 | 528 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 15 | 3567 | 14.3 | 14.3 | 9.575 | 12.1647 | 15 | 60 | 60 | 729.6262 | 170.8964 | 48.8423 | 235.8566 | 0 | 0 | 0 | 66.7435 | 335.8903 | 408.277 | 241.5007 | 0 | 576.1036 | 128.7565 | 128.7565 | 128.7565 | 140.3988 | 187.347 | 199.9737 | 170.8823 | 128.7565 | 170.8964 | 128.7565 | 128.7565 | 128.7565 | 207.1423 | 523.2373 | 608.2507 | 412.383 | 128.7565 | 747 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 16 | 3568 | 14.1 | 14.1 | 9.575 | 12.1647 | 15 | 59 | 59 | 502.8774 | 228.1123 | 40.5807 | 251.7478 | 0 | 0 | 0 | 0 | 185.7572 | 325.0373 | 273.915 | 62.3369 | 352.8877 | 129.5307 | 129.5307 | 129.5307 | 129.5307 | 192.0161 | 238.8674 | 221.6708 | 150.4997 | 228.1123 | 129.5307 | 129.5307 | 129.5307 | 129.5307 | 377.7733 | 563.9047 | 495.5857 | 212.8367 | 581 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 17 | 3569 | 13.1 | 13.1 | 9.575 | 12.1647 | 15 | 65 | 65 | 164.0503 | 264.8945 | 31.5707 | 264.965 | 0 | 0 | 0 | 0 | 39.0232 | 111.2626 | 118.3259 | 56.0755 | 96.1055 | 125.1924 | 125.1924 | 125.1924 | 125.1924 | 157.3618 | 216.9135 | 222.7363 | 171.4192 | 264.8945 | 125.1924 | 125.1924 | 125.1924 | 125.1924 | 196.3849 | 328.1761 | 341.0622 | 227.4947 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 29 | 18 | 3570 | 10.2 | 10.2 | 9.575 | 12.1647 | 15 | 88 | 88 | 13.1291 | 158.0948 | 22.3739 | 276.7563 | 0 | 0 | 0 | 0 | 0.98173 | 8.5733 | 11.1427 | 7.1849 | 5.9052 | 77.3859 | 77.3859 | 77.3859 | 77.3859 | 78.3616 | 85.9069 | 88.4607 | 84.527 | 158.0948 | 77.3859 | 77.3859 | 77.3859 | 77.3859 | 79.3434 | 94.4802 | 99.6035 | 91.7119 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 19 | 3571 | 11.7 | 11.7 | 9.575 | 12.1647 | 15 | 83 | 83 | 193.3815 | 135.4367 | 13.3885 | 287.981 | 21.0379 | 0 | 0 | 0 | 0 | 110.6933 | 177.5819 | 140.4454 | 58.5633 | 82.9151 | 70.4505 | 70.4505 | 70.4505 | 70.4505 | 136.0343 | 175.6646 | 153.6619 | 135.4367 | 103.953 | 70.4505 | 70.4505 | 70.4505 | 70.4505 | 246.7276 | 353.2465 | 294.1073 | 194 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 20 | 3572 | 10.1 | 10.1 | 9.575 | 12.1647 | 15 | 89 | 89 | 19.0279 | 58.0507 | 4.9578 | 299.2466 | 5.7143 | 0 | 0 | 0 | 0 | 8.4092 | 17.6067 | 16.4905 | 2.9493 | 36.0016 | 29.0876 | 29.0876 | 29.0876 | 29.0876 | 39.2622 | 50.3906 | 49.0401 | 58.0507 | 41.7159 | 29.0876 | 29.0876 | 29.0876 | 29.0876 | 47.6714 | 67.9973 | 65.5305 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 21 | 3573 | 9.6 | 9.6 | 9.575 | 12.1647 | 15 | 90 | 90 | 17.4633 | 4.8243 | -2.5708 | 310.9979 | 8.5001 | 0 | 0 | 0 | 0 | 4.7235 | 15.1801 | 16.7444 | 9.1757 | 11.6088 | 3.6547 | 3.6547 | 3.6547 | 3.6547 | 8.0748 | 17.8597 | 19.3235 | 4.8243 | 20.1089 | 3.6547 | 3.6547 | 3.6547 | 3.6547 | 12.7983 | 33.0398 | 36.068 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 22 | 3574 | 8.6 | 8.6 | 9.575 | 12.1647 | 15 | 91 | 91 | 0 | 0 | -8.8197 | 323.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 23 | 3575 | 7.9 | 7.9 | 9.575 | 12.1647 | 15 | 92 | 92 | 0 | 0 | -13.3915 | 336.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 29 | 24 | 3576 | 6.9 | 6.9 | 10.1917 | 11.6474 | 15 | 96 | 96 | 0 | 0 | -15.9234 | 351.1477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 1 | 3577 | 5.9 | 5.9 | 10.1917 | 11.6474 | 15 | 97 | 97 | 0 | 0 | -16.1801 | 5.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 2 | 3578 | 4.9 | 4.9 | 10.1917 | 11.6474 | 15 | 97 | 97 | 0 | 0 | -13.992 | 19.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 3 | 3579 | 4.3 | 4.3 | 10.1917 | 11.6474 | 15 | 98 | 98 | 0 | 0 | -9.8528 | 33.4922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 4 | 3580 | 4.1 | 4.1 | 10.1917 | 11.6474 | 15 | 99 | 99 | 0 | 0 | -3.9512 | 46.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 5 | 3581 | 5.1 | 5.1 | 10.1917 | 11.6474 | 15 | 98 | 98 | 0 | 3 | 3.3182 | 58.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 6 | 3582 | 7.1 | 7.1 | 10.1917 | 11.6474 | 15 | 99 | 99 | 35.4844 | 53.3775 | 11.5723 | 69.4329 | 18.718 | 34.5025 | 30.0759 | 8.0313 | 0 | 0 | 0 | 0 | 4.6225 | 109.2922 | 182.6631 | 162.087 | 59.6172 | 22.2857 | 22.2857 | 22.2857 | 22.2857 | 53.3775 | 128.0102 | 217.1656 | 192.163 | 67.6485 | 22.2857 | 22.2857 | 22.2857 | 22.2857 | 58 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 7 | 3583 | 8.9 | 8.9 | 10.1917 | 11.6474 | 15 | 98 | 98 | 137.9742 | 125.7814 | 20.4591 | 80.6109 | 47.4855 | 123.0645 | 126.554 | 55.9099 | 0 | 0 | 0 | 0 | 38.2186 | 113.503 | 200.629 | 204.6517 | 123.2145 | 58.7627 | 58.7627 | 58.7627 | 58.7627 | 125.7814 | 160.9885 | 323.6936 | 331.2057 | 179.1244 | 58.7627 | 58.7627 | 58.7627 | 58.7627 | 164 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 30 | 8 | 3584 | 10.5 | 10.5 | 10.1917 | 11.6474 | 15 | 92 | 92 | 120.655 | 192.7558 | 29.639 | 92.2027 | 18.4418 | 91.9039 | 111.5298 | 65.8232 | 0 | 0 | 0 | 0 | 51.2442 | 108.5586 | 186.2635 | 207.023 | 158.6765 | 89.0516 | 89.0516 | 89.0516 | 89.0516 | 192.7558 | 127.0004 | 278.1674 | 318.5529 | 224.4996 | 89.0516 | 89.0516 | 89.0516 | 89.0516 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 9 | 3585 | 11 | 11 | 10.1917 | 11.6474 | 15 | 89 | 89 | 15.9926 | 204.99 | 38.7341 | 105.001 | 0 | 9.4438 | 13.8898 | 10.1993 | 0.53425 | 0 | 0 | 0 | 9.01 | 94.1058 | 127.0159 | 142.5096 | 129.6489 | 95.9675 | 94.1058 | 94.1058 | 94.1058 | 204.99 | 94.1058 | 136.4597 | 156.3993 | 139.8482 | 96.5018 | 94.1058 | 94.1058 | 94.1058 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 10 | 3586 | 11.9 | 11.9 | 10.1917 | 11.6474 | 15 | 87 | 87 | 5.1664 | 185.4683 | 47.233 | 120.162 | 0 | 2.015 | 3.8928 | 3.4902 | 1.0431 | 0 | 0 | 0 | 3.5317 | 91.0796 | 95.6708 | 99.9493 | 99.0321 | 93.4564 | 91.0796 | 91.0796 | 91.0796 | 185.4683 | 91.0796 | 97.6858 | 103.8421 | 102.5223 | 94.4995 | 91.0796 | 91.0796 | 91.0796 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 11 | 3587 | 13.5 | 13.5 | 10.1917 | 11.6474 | 15 | 78 | 78 | 139.1894 | 352.8377 | 54.3298 | 139.2435 | 0 | 24.2033 | 81.716 | 91.3605 | 47.4873 | 0 | 0 | 0 | 108.1623 | 156.386 | 188.1007 | 263.4621 | 276.0998 | 218.6107 | 156.386 | 156.386 | 156.386 | 352.8377 | 156.386 | 212.3041 | 345.1781 | 367.4603 | 266.098 | 156.386 | 156.386 | 156.386 | 461 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 12 | 3588 | 14.6 | 14.6 | 10.1917 | 11.6474 | 15 | 65 | 65 | 609.727 | 228.3562 | 58.7786 | 163.3701 | 0 | 0 | 232.1147 | 354.5684 | 269.3208 | 26.3086 | 0 | 0 | 510.6438 | 141.4797 | 141.4797 | 200.5481 | 231.71 | 210.0163 | 148.1747 | 141.4797 | 141.4797 | 228.3562 | 141.4797 | 141.4797 | 432.6628 | 586.2784 | 479.337 | 174.4834 | 141.4797 | 141.4797 | 739 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 13 | 3589 | 10 | 10 | 10.1917 | 11.6474 | 15 | 87 | 87 | 4.297 | 213.302 | 59.2669 | 190.6114 | 0 | 0 | 0.63744 | 1.9598 | 2.1342 | 1.0584 | 0 | 0 | 3.698 | 108.6159 | 108.6159 | 108.7552 | 109.0443 | 109.0824 | 108.8472 | 108.6159 | 108.6159 | 213.302 | 108.6159 | 108.6159 | 109.3927 | 111.0041 | 111.2166 | 109.9056 | 108.6159 | 108.6159 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 14 | 3590 | 9.9 | 9.9 | 10.1917 | 11.6474 | 15 | 90 | 90 | 2.4551 | 158.9261 | 55.6136 | 215.7721 | 0 | 0 | 0 | 0.70862 | 1.2332 | 1.0354 | 0.23104 | 0 | 2.0739 | 79.7977 | 79.7977 | 79.7977 | 79.7977 | 79.7977 | 79.7977 | 79.7977 | 79.7977 | 158.9261 | 79.7977 | 79.7977 | 79.7977 | 80.5063 | 81.0308 | 80.833 | 80.0287 | 79.7977 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 15 | 3591 | 11.9 | 11.9 | 10.1917 | 11.6474 | 15 | 82 | 82 | 73.1708 | 350.1192 | 48.9886 | 235.9472 | 0 | 0 | 0 | 6.6269 | 33.5288 | 40.79 | 24.157 | 0 | 57.8808 | 154.9078 | 154.9078 | 154.9078 | 166.1779 | 211.929 | 224.2779 | 195.9906 | 154.9078 | 350.1192 | 154.9078 | 154.9078 | 154.9078 | 172.8048 | 245.4578 | 265.0679 | 220.1476 | 154.9078 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 16 | 3592 | 13.4 | 13.4 | 10.1917 | 11.6474 | 15 | 68 | 68 | 970.0218 | 134.805 | 40.7204 | 251.845 | 0 | 0 | 0 | 0 | 356.4336 | 624.9543 | 527.3852 | 120.8811 | 682.195 | 129.973 | 129.973 | 129.973 | 129.973 | 149.0231 | 163.3745 | 158.1598 | 136.4337 | 134.805 | 129.973 | 129.973 | 129.973 | 129.973 | 505.4566 | 788.3287 | 685.545 | 257.3148 | 817 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 17 | 3593 | 13.1 | 13.1 | 10.1917 | 11.6474 | 15 | 62 | 62 | 585.0674 | 167.2769 | 31.7073 | 265.0581 | 0 | 0 | 0 | 0 | 138.1657 | 395.6367 | 421.3491 | 200.2409 | 343.7231 | 107.9196 | 107.9196 | 107.9196 | 107.9196 | 137.4239 | 192.4049 | 197.8956 | 150.6796 | 167.2769 | 107.9196 | 107.9196 | 107.9196 | 107.9196 | 275.5896 | 588.0416 | 619.2447 | 350.9205 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 30 | 18 | 3594 | 12.9 | 12.9 | 10.1917 | 11.6474 | 15 | 66 | 66 | 14.0526 | 160.654 | 22.5107 | 276.8417 | 0 | 0 | 0 | 0 | 1.0299 | 9.1504 | 11.9107 | 7.6939 | 6.346 | 78.5134 | 78.5134 | 78.5134 | 78.5134 | 79.551 | 87.7328 | 90.514 | 86.2653 | 160.654 | 78.5134 | 78.5134 | 78.5134 | 78.5134 | 80.5809 | 96.8832 | 102.4247 | 93.9592 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 19 | 3595 | 12.5 | 12.5 | 10.1917 | 11.6474 | 15 | 73 | 73 | 1.8186 | 49.4457 | 13.5281 | 288.057 | 0.20014 | 0 | 0 | 0 | 0 | 1.038 | 1.6681 | 1.321 | 0.55432 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 49.4457 | 24.0394 | 23.8393 | 23.8393 | 23.8393 | 23.8393 | 24.8773 | 25.5074 | 25.1603 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 20 | 3596 | 11.5 | 11.5 | 10.1917 | 11.6474 | 15 | 83 | 83 | 0.79117 | 16.8757 | 5.1019 | 299.3115 | 0.23843 | 0 | 0 | 0 | 0 | 0.34854 | 0.73133 | 0.68573 | 0.12431 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 16.8757 | 8.1871 | 7.9487 | 7.9487 | 7.9487 | 7.9487 | 8.2972 | 8.68 | 8.6344 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 21 | 3597 | 10.8 | 10.8 | 10.1917 | 11.6474 | 15 | 87 | 87 | 28.8354 | 4.5012 | -2.4213 | 311.049 | 14.0606 | 0 | 0 | 0 | 0 | 7.7664 | 25.044 | 27.6512 | 12.4988 | 12.972 | 3.8451 | 3.8451 | 3.8451 | 3.8451 | 8.8864 | 20.1015 | 21.7938 | 4.5012 | 27.0327 | 3.8451 | 3.8451 | 3.8451 | 3.8451 | 16.6528 | 45.1455 | 49.445 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 22 | 3598 | 10 | 10 | 10.1917 | 11.6474 | 15 | 83 | 83 | 0 | 0 | -8.6652 | 323.5683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 23 | 3599 | 8.8 | 8.8 | 10.1917 | 11.6474 | 15 | 88 | 88 | 0 | 0 | -13.2339 | 336.9788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 30 | 24 | 3600 | 7.3 | 7.3 | 9.7458 | 11.0598 | 15 | 95 | 95 | 0 | 0 | -15.7661 | 351.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 1 | 3601 | 6.4 | 6.4 | 9.7458 | 11.0598 | 15 | 96 | 96 | 0 | 0 | -16.0274 | 5.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 2 | 3602 | 5.2 | 5.2 | 9.7458 | 11.0598 | 15 | 97 | 97 | 0 | 0 | -13.8542 | 19.8252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 3 | 3603 | 4.8 | 4.8 | 9.7458 | 11.0598 | 15 | 97 | 97 | 0 | 0 | -9.7259 | 33.4072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 4 | 3604 | 4.3 | 4.3 | 9.7458 | 11.0598 | 15 | 98 | 98 | 0 | 0 | -3.8356 | 46.1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 5 | 3605 | 4.4 | 4.4 | 9.7458 | 11.0598 | 15 | 98 | 98 | 0 | 3 | 3.4235 | 57.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 6 | 3606 | 6.3 | 6.3 | 9.7458 | 11.0598 | 15 | 98 | 98 | 32.8226 | 53.6565 | 11.6695 | 69.3135 | 17.3653 | 31.9251 | 27.7836 | 7.3668 | 0 | 0 | 0 | 0 | 4.3435 | 108.5882 | 180.7687 | 160.2369 | 59.0199 | 22.4987 | 22.4987 | 22.4987 | 22.4987 | 53.6565 | 125.9535 | 212.6938 | 188.0204 | 66.3867 | 22.4987 | 22.4987 | 22.4987 | 22.4987 | 58 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 7 | 3607 | 10.2 | 10.2 | 9.7458 | 11.0598 | 15 | 97 | 97 | 213.9483 | 123.3278 | 20.5511 | 80.4816 | 74.016 | 190.9425 | 196.0175 | 86.2681 | 0 | 0 | 0 | 0 | 59.6722 | 112.9708 | 196.3069 | 199.924 | 121.7032 | 60.218 | 60.218 | 60.218 | 60.218 | 123.3278 | 186.9868 | 387.2494 | 395.9415 | 207.9713 | 60.218 | 60.218 | 60.218 | 60.218 | 183 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2000 | 5 | 31 | 8 | 3608 | 12.5 | 12.5 | 9.7458 | 11.0598 | 15 | 73 | 73 | 440.4362 | 151.1645 | 29.7297 | 92.0622 | 68.197 | 335.8232 | 406.7288 | 239.3781 | 0 | 0 | 0 | 0 | 187.8355 | 107.7762 | 181.2348 | 200.6971 | 154.7623 | 89.0574 | 89.0574 | 89.0574 | 89.0574 | 151.1645 | 175.9732 | 517.0581 | 607.4259 | 394.1404 | 89.0574 | 89.0574 | 89.0574 | 89.0574 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 9 | 3609 | 13.9 | 13.9 | 9.7458 | 11.0598 | 15 | 64 | 64 | 604.6892 | 155.3484 | 38.8283 | 104.8477 | 0 | 357.6984 | 524.7569 | 384.4198 | 18.8949 | 0 | 0 | 0 | 341.6516 | 105.9357 | 182.0773 | 217.6382 | 187.7653 | 109.9578 | 105.9357 | 105.9357 | 105.9357 | 155.3484 | 105.9357 | 539.7757 | 742.3951 | 572.1852 | 128.8527 | 105.9357 | 105.9357 | 105.9357 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 10 | 3610 | 14.8 | 14.8 | 9.7458 | 11.0598 | 15 | 60 | 60 | 762.85 | 138.3944 | 47.3369 | 119.9982 | 0 | 298.5077 | 574.4392 | 513.8719 | 152.2855 | 0 | 0 | 0 | 522.6056 | 115.3614 | 158.7258 | 198.8106 | 190.0119 | 137.484 | 115.3614 | 115.3614 | 115.3614 | 138.3944 | 115.3614 | 457.2336 | 773.2498 | 703.8839 | 289.7695 | 115.3614 | 115.3614 | 115.3614 | 661 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 11 | 3611 | 15.9 | 15.9 | 9.7458 | 11.0598 | 15 | 54 | 54 | 893.4718 | 137.445 | 54.4502 | 139.084 | 0 | 156.7321 | 524.3829 | 584.8574 | 302.7303 | 0 | 0 | 0 | 695.555 | 131.7722 | 146.3342 | 180.4927 | 186.1114 | 159.8989 | 131.7722 | 131.7722 | 131.7722 | 137.445 | 131.7722 | 303.0663 | 704.8757 | 770.9688 | 462.6292 | 131.7722 | 131.7722 | 131.7722 | 833 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 12 | 3612 | 16.5 | 16.5 | 9.7458 | 11.0598 | 15 | 47 | 47 | 502.386 | 272.5818 | 58.9186 | 163.2554 | 0 | 0 | 191.3065 | 291.3506 | 220.7254 | 20.8022 | 0 | 0 | 421.4182 | 149.0708 | 149.0708 | 223.419 | 262.2996 | 234.8522 | 157.1552 | 149.0708 | 149.0708 | 272.5818 | 149.0708 | 149.0708 | 414.7256 | 553.6501 | 455.5776 | 177.9575 | 149.0708 | 149.0708 | 694 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 13 | 3613 | 16.5 | 16.5 | 9.7458 | 11.0598 | 15 | 44 | 44 | 490.9769 | 284.8254 | 59.4184 | 190.5852 | 0 | 0 | 73.0261 | 223.2673 | 242.7216 | 119.9928 | 0 | 0 | 423.1746 | 150.8007 | 150.8007 | 181.3351 | 244.1554 | 252.2897 | 200.9732 | 150.8007 | 150.8007 | 284.8254 | 150.8007 | 150.8007 | 254.3612 | 467.4227 | 495.0113 | 320.966 | 150.8007 | 150.8007 | 708 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 14 | 3614 | 17.8 | 17.8 | 9.7458 | 11.0598 | 15 | 39 | 39 | 618.0146 | 227.1249 | 55.763 | 215.8224 | 0 | 0 | 0 | 177.706 | 309.0734 | 259.3898 | 57.7592 | 0 | 522.8751 | 140.4043 | 140.4043 | 140.4043 | 185.6007 | 219.0117 | 206.3755 | 155.0943 | 140.4043 | 227.1249 | 140.4043 | 140.4043 | 140.4043 | 363.3067 | 528.0851 | 465.7653 | 212.8535 | 140.4043 | 750 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 15 | 3615 | 17.8 | 17.8 | 9.7458 | 11.0598 | 15 | 43 | 43 | 604.578 | 217.92 | 49.1303 | 236.0312 | 0 | 0 | 0 | 54.2518 | 275.8026 | 335.792 | 199.079 | 0 | 479.08 | 134.5699 | 134.5699 | 134.5699 | 148.1387 | 203.5502 | 218.5539 | 184.361 | 134.5699 | 217.92 | 134.5699 | 134.5699 | 134.5699 | 202.3905 | 479.3527 | 554.3459 | 383.44 | 134.5699 | 697 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 16 | 3616 | 17.8 | 17.8 | 9.7458 | 11.0598 | 15 | 47 | 47 | 855.1771 | 122.3126 | 40.856 | 251.936 | 0 | 0 | 0 | 0 | 312.6587 | 549.2377 | 464.0807 | 107.0716 | 602.6874 | 116.2944 | 116.2944 | 116.2944 | 116.2944 | 144.0149 | 164.9901 | 157.4401 | 125.7875 | 122.3126 | 116.2944 | 116.2944 | 116.2944 | 116.2944 | 456.6736 | 714.2278 | 621.5208 | 232.859 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 17 | 3617 | 17.2 | 17.2 | 9.7458 | 11.0598 | 15 | 49 | 49 | 245.7956 | 255.2055 | 31.8401 | 265.1454 | 0 | 0 | 0 | 0 | 57.6465 | 165.7404 | 176.7457 | 84.2159 | 144.7945 | 123.341 | 123.341 | 123.341 | 123.341 | 162.9387 | 237.1889 | 244.7486 | 181.1893 | 255.2055 | 123.341 | 123.341 | 123.341 | 123.341 | 220.5853 | 402.9293 | 421.4943 | 265.4052 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2000 | 5 | 31 | 18 | 3618 | 16.6 | 16.6 | 9.7458 | 11.0598 | 15 | 52 | 52 | 115.783 | 205.5135 | 22.6437 | 276.9216 | 0 | 0 | 0 | 0 | 8.324 | 75.1878 | 98.0076 | 63.4159 | 52.4865 | 98.1827 | 98.1827 | 98.1827 | 98.1827 | 106.275 | 171.2774 | 193.462 | 159.8332 | 205.5135 | 98.1827 | 98.1827 | 98.1827 | 98.1827 | 114.599 | 246.4652 | 291.4696 | 223.2491 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 19 | 3619 | 15.4 | 15.4 | 9.7458 | 11.0598 | 15 | 52 | 52 | 79.6659 | 136.5676 | 13.6637 | 288.1279 | 8.8605 | 0 | 0 | 0 | 0 | 45.3458 | 72.9891 | 57.8765 | 24.4324 | 72.8304 | 66.4327 | 66.4327 | 66.4327 | 66.4327 | 99.1746 | 119.1345 | 108.2224 | 136.5676 | 81.691 | 66.4327 | 66.4327 | 66.4327 | 66.4327 | 144.5203 | 192.1236 | 166.0988 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 20 | 3620 | 13.9 | 13.9 | 9.7458 | 11.0598 | 15 | 60 | 60 | 68.714 | 70.0637 | 5.2417 | 299.3716 | 20.7746 | 0 | 0 | 0 | 0 | 30.1797 | 63.4551 | 59.5594 | 10.9363 | 52.4765 | 35.8906 | 35.8906 | 35.8906 | 35.8906 | 59.9853 | 86.5515 | 83.4413 | 70.0637 | 73.2511 | 35.8906 | 35.8906 | 35.8906 | 35.8906 | 90.165 | 150.0067 | 143.0007 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 21 | 3621 | 11.4 | 11.4 | 9.7458 | 11.0598 | 15 | 75 | 75 | 83.2977 | 9.271 | -2.2765 | 311.0958 | 40.6844 | 0 | 0 | 0 | 0 | 22.3463 | 72.2868 | 79.8827 | 1.729 | 24.9464 | 5.592 | 5.592 | 5.592 | 5.592 | 16.2226 | 39.9804 | 43.594 | 9.271 | 65.6308 | 5.592 | 5.592 | 5.592 | 5.592 | 38.5689 | 112.2673 | 123.4767 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 22 | 3622 | 10.7 | 10.7 | 9.7458 | 11.0598 | 15 | 79 | 79 | 0 | 0 | -8.516 | 323.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 23 | 3623 | 10.3 | 10.3 | 9.7458 | 11.0598 | 15 | 84 | 84 | 0 | 0 | -13.082 | 336.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2000 | 5 | 31 | 24 | 3624 | 10.1 | 10.1 | 12.1125 | 11.1787 | 15 | 82 | 82 | 0 | 0 | -15.6149 | 351.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 1 | 3625 | 9.5 | 9.5 | 12.1125 | 11.1787 | 15 | 86 | 86 | 0 | 0 | -15.881 | 5.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 2 | 3626 | 9 | 9 | 12.1125 | 11.1787 | 15 | 94 | 94 | 0 | 0 | -13.7228 | 19.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 3 | 3627 | 6.8 | 6.8 | 12.1125 | 11.1787 | 15 | 95 | 95 | 0 | 0 | -9.6053 | 33.3233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 4 | 3628 | 7.5 | 7.5 | 12.1125 | 11.1787 | 15 | 96 | 96 | 0 | 0 | -3.7262 | 46.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 5 | 3629 | 6 | 6 | 12.1125 | 11.1787 | 15 | 97 | 97 | 0 | 8 | 3.5228 | 57.8862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 8 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 3.8967 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 6 | 3630 | 9.3 | 9.3 | 12.1125 | 11.1787 | 15 | 89 | 89 | 254.737 | 57.787 | 11.7608 | 69.1969 | 135.163 | 247.8523 | 215.353 | 56.7029 | 0 | 0 | 0 | 0 | 34.213 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 57.787 | 162.5213 | 275.2106 | 242.7113 | 84.0612 | 27.3583 | 27.3583 | 27.3583 | 27.3583 | 92 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 7 | 3631 | 12.3 | 12.3 | 12.1125 | 11.1787 | 15 | 72 | 72 | 413.2821 | 102.9762 | 20.6374 | 80.3556 | 143.6986 | 369.0581 | 378.2284 | 165.8376 | 0 | 0 | 0 | 0 | 116.0238 | 91.9284 | 141.121 | 143.1228 | 96.761 | 60.5611 | 60.5611 | 60.5611 | 60.5611 | 102.9762 | 235.627 | 510.1792 | 521.3512 | 262.5986 | 60.5611 | 60.5611 | 60.5611 | 60.5611 | 219 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 1 | 8 | 3632 | 13.5 | 13.5 | 12.1125 | 11.1787 | 15 | 66 | 66 | 683.1201 | 101.517 | 29.8145 | 91.925 | 107.1015 | 521.3853 | 630.2486 | 369.9209 | 0 | 0 | 0 | 0 | 292.483 | 93.7098 | 153.4306 | 169.1238 | 131.5964 | 78.2706 | 78.2706 | 78.2706 | 78.2706 | 101.517 | 200.8113 | 674.816 | 799.3724 | 501.5172 | 78.2706 | 78.2706 | 78.2706 | 78.2706 | 394 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 9 | 3633 | 14.4 | 14.4 | 12.1125 | 11.1787 | 15 | 62 | 62 | 721.0406 | 124.4962 | 38.9165 | 104.698 | 0 | 427.2588 | 625.2502 | 456.9785 | 21.015 | 0 | 0 | 0 | 408.5038 | 99.4093 | 162.4962 | 191.7306 | 166.8845 | 102.5123 | 99.4093 | 99.4093 | 99.4093 | 124.4962 | 99.4093 | 589.755 | 816.9809 | 623.863 | 123.5273 | 99.4093 | 99.4093 | 99.4093 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 10 | 3634 | 16.3 | 16.3 | 12.1125 | 11.1787 | 15 | 54 | 54 | 786.0864 | 132.3555 | 47.4345 | 119.8374 | 0 | 308.6 | 591.6101 | 528.063 | 155.1838 | 0 | 0 | 0 | 539.6445 | 114.699 | 156.8814 | 195.566 | 186.8797 | 135.911 | 114.699 | 114.699 | 114.699 | 132.3555 | 114.699 | 465.4814 | 787.1761 | 714.9428 | 291.0948 | 114.699 | 114.699 | 114.699 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 11 | 3635 | 17 | 17 | 12.1125 | 11.1787 | 15 | 42 | 42 | 793.4584 | 148.2458 | 54.5641 | 138.9261 | 0 | 140.384 | 465.5739 | 518.0369 | 267.0409 | 0 | 0 | 0 | 618.7542 | 127.9895 | 143.4679 | 179.3226 | 185.1071 | 157.4328 | 127.9895 | 127.9895 | 127.9895 | 148.2458 | 127.9895 | 283.8519 | 644.8965 | 703.1439 | 424.4737 | 127.9895 | 127.9895 | 127.9895 | 767 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 12 | 3636 | 17.5 | 17.5 | 12.1125 | 11.1787 | 15 | 42 | 42 | 872.5377 | 144.9735 | 59.0521 | 163.1394 | 0 | 0 | 332.386 | 504.7029 | 381.3716 | 34.6381 | 0 | 0 | 733.0265 | 136.1498 | 136.1498 | 168.6843 | 185.551 | 173.4791 | 139.5402 | 136.1498 | 136.1498 | 144.9735 | 136.1498 | 136.1498 | 501.0703 | 690.2539 | 554.8508 | 174.1783 | 136.1498 | 136.1498 | 878 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 13 | 3637 | 18.3 | 18.3 | 12.1125 | 11.1787 | 15 | 43 | 43 | 884.4922 | 150.5448 | 59.5638 | 190.5546 | 0 | 0 | 131.9287 | 401.0949 | 435.3051 | 214.5196 | 0 | 0 | 763.4552 | 139.6083 | 139.6083 | 152.7022 | 179.417 | 182.8124 | 160.8994 | 139.6083 | 139.6083 | 150.5448 | 139.6083 | 139.6083 | 284.6309 | 580.5118 | 618.1175 | 375.4189 | 139.6083 | 139.6083 | 914 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 14 | 3638 | 18.7 | 18.7 | 12.1125 | 11.1787 | 15 | 40 | 40 | 886.941 | 148.4731 | 55.9071 | 215.8664 | 0 | 0 | 0 | 254.1365 | 441.7038 | 370.5271 | 82.3006 | 0 | 751.5269 | 137.5208 | 137.5208 | 137.5208 | 162.4136 | 180.786 | 173.8142 | 145.5822 | 137.5208 | 148.4731 | 137.5208 | 137.5208 | 137.5208 | 416.5501 | 622.4898 | 544.3413 | 227.8828 | 137.5208 | 900 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 15 | 3639 | 19.4 | 19.4 | 12.1125 | 11.1787 | 15 | 38 | 38 | 858.7734 | 137.3565 | 49.2675 | 236.1086 | 0 | 0 | 0 | 76.412 | 390.0987 | 475.2708 | 282.0358 | 0 | 681.6435 | 127.8529 | 127.8529 | 127.8529 | 135.1405 | 165.0572 | 173.1802 | 154.7511 | 127.8529 | 137.3565 | 127.8529 | 127.8529 | 127.8529 | 211.5525 | 555.1558 | 648.451 | 436.7868 | 127.8529 | 819 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 16 | 3640 | 19.4 | 19.4 | 12.1125 | 11.1787 | 15 | 38 | 38 | 827.6598 | 126.5416 | 40.9874 | 252.0206 | 0 | 0 | 0 | 0 | 301.1548 | 529.9525 | 448.3113 | 104.0554 | 584.4584 | 116.0569 | 116.0569 | 116.0569 | 116.0569 | 144.3537 | 165.8518 | 158.1807 | 125.8341 | 126.5416 | 116.0569 | 116.0569 | 116.0569 | 116.0569 | 445.5085 | 695.8044 | 606.492 | 229.8895 | 711 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 17 | 3641 | 19.3 | 19.3 | 12.1125 | 11.1787 | 15 | 46 | 46 | 769.179 | 117.7186 | 31.9689 | 265.2268 | 0 | 0 | 0 | 0 | 179.2218 | 517.239 | 552.2647 | 263.7811 | 454.2814 | 101.4897 | 101.4897 | 101.4897 | 101.4897 | 119.1823 | 152.5512 | 156.0089 | 127.53 | 117.7186 | 101.4897 | 101.4897 | 101.4897 | 101.4897 | 298.4041 | 669.7902 | 708.2736 | 391.3111 | 572 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 1 | 18 | 3642 | 18.8 | 18.8 | 12.1125 | 11.1787 | 15 | 46 | 46 | 638.3255 | 117.5793 | 22.7728 | 276.996 | 0 | 0 | 0 | 0 | 45.0606 | 413.443 | 539.6362 | 349.7177 | 290.4207 | 84.7312 | 84.7312 | 84.7312 | 84.7312 | 91.9304 | 150.7863 | 170.948 | 140.605 | 117.5793 | 84.7312 | 84.7312 | 84.7312 | 84.7312 | 136.991 | 564.2293 | 710.5841 | 490.3227 | 408 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 19 | 3643 | 17.9 | 17.9 | 12.1125 | 11.1787 | 15 | 48 | 48 | 520.2054 | 97.5233 | 13.7952 | 288.1937 | 58.4219 | 0 | 0 | 0 | 0 | 295.3309 | 476.0828 | 377.9519 | 160.4767 | 74.4865 | 63.6957 | 63.6957 | 63.6957 | 63.6957 | 118.2445 | 151.6301 | 133.5049 | 97.5233 | 132.9083 | 63.6957 | 63.6957 | 63.6957 | 63.6957 | 413.5754 | 627.7129 | 511.4568 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 20 | 3644 | 16.3 | 16.3 | 12.1125 | 11.1787 | 15 | 57 | 57 | 289.1729 | 67.4128 | 5.3771 | 299.427 | 87.684 | 0 | 0 | 0 | 0 | 126.6483 | 266.7918 | 250.6522 | 46.5872 | 65.6453 | 39.0653 | 39.0653 | 39.0653 | 39.0653 | 77.4566 | 119.9388 | 115.0464 | 67.4128 | 153.3293 | 39.0653 | 39.0653 | 39.0653 | 39.0653 | 204.1049 | 386.7306 | 365.6986 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 21 | 3645 | 14.7 | 14.7 | 12.1125 | 11.1787 | 15 | 63 | 63 | 10.9558 | 7.7497 | -2.1366 | 311.1382 | 5.3591 | 0 | 0 | 0 | 0 | 2.9283 | 9.5003 | 10.5072 | 0.25026 | 8.1721 | 4.2906 | 4.2906 | 4.2906 | 4.2906 | 6.4115 | 11.1716 | 11.9009 | 7.7497 | 13.5312 | 4.2906 | 4.2906 | 4.2906 | 4.2906 | 9.3399 | 20.6719 | 22.408 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 22 | 3646 | 13.1 | 13.1 | 12.1125 | 11.1787 | 15 | 66 | 66 | 0 | 0 | -8.372 | 323.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 23 | 3647 | 10.7 | 10.7 | 12.1125 | 11.1787 | 15 | 79 | 79 | 0 | 0 | -12.9359 | 336.9919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 1 | 24 | 3648 | 7.9 | 7.9 | 13.9 | 11.788 | 15 | 97 | 97 | 0 | 0 | -15.4698 | 351.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 1 | 3649 | 6.8 | 6.8 | 13.9 | 11.788 | 15 | 98 | 98 | 0 | 0 | -15.741 | 5.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 2 | 3650 | 6.4 | 6.4 | 13.9 | 11.788 | 15 | 99 | 99 | 0 | 0 | -13.598 | 19.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 3 | 3651 | 5.9 | 5.9 | 13.9 | 11.788 | 15 | 99 | 99 | 0 | 0 | -9.4912 | 33.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 4 | 3652 | 5.6 | 5.6 | 13.9 | 11.788 | 15 | 99 | 99 | 0 | 0 | -3.6231 | 45.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 5 | 3653 | 5.6 | 5.6 | 13.9 | 11.788 | 15 | 99 | 99 | 4.3407 | 1.32 | 3.616 | 57.7812 | 3.0137 | 4.3315 | 3.1119 | 0.069485 | 0 | 0 | 0 | 0 | 6.68 | 2.079 | 2.4705 | 2.1082 | 1.2042 | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 1.32 | 5.0926 | 6.802 | 5.2201 | 1.2737 | 1.1836 | 1.1836 | 1.1836 | 1.1836 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 6 | 3654 | 9.2 | 9.2 | 13.9 | 11.788 | 15 | 78 | 78 | 210.8238 | 60.2876 | 11.8463 | 69.0833 | 112.1778 | 205.1907 | 178.0057 | 46.5474 | 0 | 0 | 0 | 0 | 28.7124 | 53.0782 | 72.3937 | 66.7483 | 39.449 | 29.7827 | 29.7827 | 29.7827 | 29.7827 | 60.2876 | 165.2559 | 277.5844 | 244.754 | 85.9963 | 29.7827 | 29.7827 | 29.7827 | 29.7827 | 89 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 7 | 3655 | 13.7 | 13.7 | 13.9 | 11.788 | 15 | 58 | 58 | 444.1024 | 99.5491 | 20.7179 | 80.2327 | 155.1724 | 396.8096 | 406.001 | 177.3626 | 0 | 0 | 0 | 0 | 125.4509 | 92.364 | 142.426 | 144.3303 | 96.9613 | 60.2155 | 60.2155 | 60.2155 | 60.2155 | 99.5491 | 247.5364 | 539.2356 | 550.3314 | 274.3239 | 60.2155 | 60.2155 | 60.2155 | 60.2155 | 225 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 2 | 8 | 3656 | 16.2 | 16.2 | 13.9 | 11.788 | 15 | 54 | 54 | 627.8606 | 113.1701 | 29.8936 | 91.7914 | 99.6265 | 479.6824 | 578.7469 | 338.7893 | 0 | 0 | 0 | 0 | 269.8299 | 96.649 | 158.3824 | 174.4737 | 135.4968 | 80.4664 | 80.4664 | 80.4664 | 80.4664 | 113.1701 | 196.2754 | 638.0649 | 753.2207 | 474.2861 | 80.4664 | 80.4664 | 80.4664 | 80.4664 | 383 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 9 | 3657 | 17 | 17 | 13.9 | 11.788 | 15 | 46 | 46 | 690.9908 | 132.5042 | 38.9987 | 104.5519 | 0 | 410.1477 | 598.7635 | 436.6318 | 18.7271 | 0 | 0 | 0 | 392.4958 | 100.8956 | 166.2549 | 196.3118 | 170.4752 | 103.8799 | 100.8956 | 100.8956 | 100.8956 | 132.5042 | 100.8956 | 576.4025 | 795.0753 | 607.107 | 122.607 | 100.8956 | 100.8956 | 100.8956 | 525 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 10 | 3658 | 18.1 | 18.1 | 13.9 | 11.788 | 15 | 42 | 42 | 749.2655 | 142.6159 | 47.5259 | 119.68 | 0 | 295.0849 | 563.6194 | 501.9933 | 146.3063 | 0 | 0 | 0 | 515.3841 | 116.2274 | 160.7321 | 201.2324 | 191.938 | 138.2933 | 116.2274 | 116.2274 | 116.2274 | 142.6159 | 116.2274 | 455.817 | 764.8518 | 693.9313 | 284.5996 | 116.2274 | 116.2274 | 116.2274 | 658 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 11 | 3659 | 18.9 | 18.9 | 13.9 | 11.788 | 15 | 38 | 38 | 785.0932 | 150.7727 | 54.6715 | 138.7702 | 0 | 140.068 | 460.5877 | 511.3014 | 262.5016 | 0 | 0 | 0 | 613.2273 | 128.307 | 144.0919 | 180.2126 | 185.9277 | 157.8894 | 128.307 | 128.307 | 128.307 | 150.7727 | 128.307 | 284.1599 | 640.8003 | 697.2291 | 420.3911 | 128.307 | 128.307 | 128.307 | 764 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 12 | 3660 | 20 | 20 | 13.9 | 11.788 | 15 | 38 | 38 | 822.7374 | 151.8133 | 59.1789 | 163.0225 | 0 | 0 | 313.5642 | 474.7298 | 357.8052 | 31.2831 | 0 | 0 | 692.1867 | 134.4283 | 134.4283 | 168.101 | 185.4082 | 172.852 | 137.7877 | 134.4283 | 134.4283 | 151.8133 | 134.4283 | 134.4283 | 481.6652 | 660.138 | 530.6571 | 169.0708 | 134.4283 | 134.4283 | 844 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 13 | 3661 | 21.1 | 21.1 | 13.9 | 11.788 | 15 | 40 | 40 | 825.7923 | 155.2278 | 59.7029 | 190.5196 | 0 | 0 | 123.5442 | 373.4994 | 404.6637 | 198.7815 | 0 | 0 | 713.7722 | 136.183 | 136.183 | 149.6233 | 176.8158 | 180.2061 | 157.8083 | 136.183 | 136.183 | 155.2278 | 136.183 | 136.183 | 273.1676 | 550.3152 | 584.8698 | 356.5898 | 136.183 | 136.183 | 869 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 14 | 3662 | 21.3 | 21.3 | 13.9 | 11.788 | 15 | 45 | 45 | 820.6956 | 153.6144 | 56.0457 | 215.9041 | 0 | 0 | 0 | 234.3909 | 407.0686 | 341.2911 | 75.5899 | 0 | 696.3856 | 133.7067 | 133.7067 | 133.7067 | 159.1695 | 177.9282 | 170.7826 | 141.9183 | 133.7067 | 153.6144 | 133.7067 | 133.7067 | 133.7067 | 393.5604 | 584.9969 | 512.0737 | 217.5082 | 133.7067 | 850 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 15 | 3663 | 21.5 | 21.5 | 13.9 | 11.788 | 15 | 46 | 46 | 785.8871 | 153.222 | 49.4 | 236.1794 | 0 | 0 | 0 | 69.3911 | 355.543 | 433.4225 | 257.4091 | 0 | 624.778 | 127.7117 | 127.7117 | 127.7117 | 135.5633 | 167.9413 | 176.7533 | 156.8375 | 127.7117 | 153.222 | 127.7117 | 127.7117 | 127.7117 | 204.9545 | 523.4842 | 610.1759 | 414.2465 | 127.7117 | 778 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 16 | 3664 | 22.1 | 22.1 | 13.9 | 11.788 | 15 | 47 | 47 | 737.4468 | 150.2589 | 41.1147 | 252.0989 | 0 | 0 | 0 | 0 | 267.1162 | 470.8052 | 398.7029 | 93.0458 | 521.7411 | 118.4627 | 118.4627 | 118.4627 | 118.4627 | 150.3616 | 174.686 | 166.0756 | 129.5742 | 150.2589 | 118.4627 | 118.4627 | 118.4627 | 118.4627 | 417.4778 | 645.4912 | 564.7785 | 222.62 | 672 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 17 | 3665 | 21 | 21 | 13.9 | 11.788 | 15 | 51 | 51 | 699.7296 | 135.7222 | 32.0937 | 265.3022 | 0 | 0 | 0 | 0 | 162.0396 | 469.3005 | 501.6515 | 240.1419 | 414.2778 | 103.1017 | 103.1017 | 103.1017 | 103.1017 | 128.2677 | 175.9877 | 181.012 | 140.3976 | 135.7222 | 103.1017 | 103.1017 | 103.1017 | 103.1017 | 290.3073 | 645.2882 | 682.6636 | 380.5395 | 550 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 18 | 3666 | 21.1 | 21.1 | 13.9 | 11.788 | 15 | 52 | 52 | 585.6094 | 129.6397 | 22.8978 | 277.0649 | 0 | 0 | 0 | 0 | 40.6317 | 378.3598 | 494.4499 | 320.8979 | 267.3603 | 87.1916 | 87.1916 | 87.1916 | 87.1916 | 94.7036 | 157.1435 | 178.6065 | 146.5198 | 129.6397 | 87.1916 | 87.1916 | 87.1916 | 87.1916 | 135.3354 | 535.5034 | 673.0564 | 467.4177 | 397 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 19 | 3667 | 20 | 20 | 13.9 | 11.788 | 15 | 59 | 59 | 443.6068 | 109.3909 | 13.9225 | 288.2543 | 50.2615 | 0 | 0 | 0 | 0 | 251.2254 | 405.5479 | 322.306 | 137.6091 | 78.9595 | 66.9378 | 66.9378 | 66.9378 | 66.9378 | 127.0268 | 163.9383 | 144.0281 | 109.3909 | 129.2211 | 66.9378 | 66.9378 | 66.9378 | 66.9378 | 378.2522 | 569.4862 | 466.3341 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 20 | 3668 | 19 | 19 | 13.9 | 11.788 | 15 | 66 | 66 | 183.463 | 73.1021 | 5.508 | 299.4776 | 55.7788 | 0 | 0 | 0 | 0 | 80.1386 | 169.1118 | 159.0217 | 29.8979 | 66.0238 | 39.9727 | 39.9727 | 39.9727 | 39.9727 | 77.4008 | 118.9551 | 114.2426 | 73.1021 | 121.8025 | 39.9727 | 39.9727 | 39.9727 | 39.9727 | 157.5394 | 288.0669 | 273.2643 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 21 | 3669 | 18 | 18 | 13.9 | 11.788 | 15 | 73 | 73 | 33.8401 | 9.406 | -2.0016 | 311.1762 | 16.5752 | 0 | 0 | 0 | 0 | 9.0143 | 29.3234 | 32.4553 | 9.594 | 19.9887 | 6.2232 | 6.2232 | 6.2232 | 6.2232 | 13.7095 | 30.5759 | 33.1769 | 9.406 | 36.564 | 6.2232 | 6.2232 | 6.2232 | 6.2232 | 22.7238 | 59.8993 | 65.6321 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 22 | 3670 | 17 | 17 | 13.9 | 11.788 | 15 | 76 | 76 | 0 | 0 | -8.2334 | 323.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 23 | 3671 | 16.2 | 16.2 | 13.9 | 11.788 | 15 | 76 | 76 | 0 | 0 | -12.7956 | 336.9939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 2 | 24 | 3672 | 14.8 | 14.8 | 15.6875 | 12.7389 | 15 | 83 | 83 | 0 | 0 | -15.331 | 351.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 1 | 3673 | 14.1 | 14.1 | 15.6875 | 12.7389 | 15 | 88 | 88 | 0 | 0 | -15.6075 | 5.4876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 2 | 3674 | 13 | 13 | 15.6875 | 12.7389 | 15 | 93 | 93 | 0 | 0 | -13.4797 | 19.6278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 3 | 3675 | 12.6 | 12.6 | 15.6875 | 12.7389 | 15 | 94 | 94 | 0 | 0 | -9.3834 | 33.1592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 4 | 3676 | 12.3 | 12.3 | 15.6875 | 12.7389 | 15 | 96 | 96 | 0 | 0 | -3.5262 | 45.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 5 | 3677 | 12.3 | 12.3 | 15.6875 | 12.7389 | 15 | 95 | 95 | 1.0399 | 0.99 | 3.7032 | 57.6788 | 0.7233 | 1.0379 | 0.74445 | 0.01496 | 0 | 0 | 0 | 0 | 5.01 | 1.5633 | 1.8704 | 1.584 | 0.87182 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.99 | 2.2866 | 2.9083 | 2.3284 | 0.88678 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 6 | 3678 | 13.2 | 13.2 | 15.6875 | 12.7389 | 15 | 92 | 92 | 112.6097 | 62.4614 | 11.9258 | 68.9726 | 60.0828 | 109.6344 | 94.9637 | 24.6645 | 0 | 0 | 0 | 0 | 15.5386 | 131.5409 | 217.9416 | 192.3609 | 69.7836 | 26.7773 | 26.7773 | 26.7773 | 26.7773 | 62.4614 | 191.6237 | 327.5761 | 287.3246 | 94.4481 | 26.7773 | 26.7773 | 26.7773 | 26.7773 | 78 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 7 | 3679 | 14.8 | 14.8 | 15.6875 | 12.7389 | 15 | 84 | 84 | 347.1832 | 112.3507 | 20.7925 | 80.1133 | 121.8853 | 310.3878 | 317.0693 | 138.016 | 0 | 0 | 0 | 0 | 98.6493 | 101.5097 | 161.0261 | 163.1356 | 106.6027 | 63.0266 | 63.0266 | 63.0266 | 63.0266 | 112.3507 | 223.3949 | 471.4138 | 480.205 | 244.6187 | 63.0266 | 63.0266 | 63.0266 | 63.0266 | 211 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 3 | 8 | 3680 | 16.6 | 16.6 | 15.6875 | 12.7389 | 15 | 75 | 75 | 585.7843 | 122.3597 | 29.9669 | 91.6615 | 94.029 | 447.973 | 539.5005 | 314.9959 | 0 | 0 | 0 | 0 | 252.6403 | 102.1479 | 170.4661 | 188.1327 | 144.7989 | 83.9984 | 83.9984 | 83.9984 | 83.9984 | 122.3597 | 196.1769 | 618.4391 | 727.6332 | 459.7948 | 83.9984 | 83.9984 | 83.9984 | 83.9984 | 375 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 9 | 3681 | 17.9 | 17.9 | 15.6875 | 12.7389 | 15 | 74 | 74 | 677.134 | 136.4282 | 39.0751 | 104.4095 | 0 | 402.5957 | 586.3644 | 426.6488 | 17.0081 | 0 | 0 | 0 | 385.5718 | 101.6852 | 168.1333 | 198.4642 | 172.1032 | 104.4923 | 101.6852 | 101.6852 | 101.6852 | 136.4282 | 101.6852 | 570.7289 | 784.8285 | 598.752 | 121.5005 | 101.6852 | 101.6852 | 101.6852 | 522 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 10 | 3682 | 19.5 | 19.5 | 15.6875 | 12.7389 | 15 | 68 | 68 | 741.362 | 145.0965 | 47.6111 | 119.526 | 0 | 292.8888 | 557.4295 | 495.4356 | 143.2222 | 0 | 0 | 0 | 510.9035 | 116.7085 | 161.8528 | 202.6277 | 193.0723 | 138.784 | 116.7085 | 116.7085 | 116.7085 | 145.0965 | 116.7085 | 454.7416 | 760.0573 | 688.5079 | 282.0062 | 116.7085 | 116.7085 | 116.7085 | 656 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 11 | 3683 | 21.5 | 21.5 | 15.6875 | 12.7389 | 15 | 60 | 60 | 776.6971 | 153.3949 | 54.7723 | 138.6164 | 0 | 139.7014 | 455.6163 | 504.6374 | 258.0487 | 0 | 0 | 0 | 607.6051 | 128.642 | 144.7383 | 181.1376 | 186.7858 | 158.3741 | 128.642 | 128.642 | 128.642 | 153.3949 | 128.642 | 284.4396 | 636.754 | 691.4232 | 416.4228 | 128.642 | 128.642 | 128.642 | 761 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 12 | 3684 | 22.2 | 22.2 | 15.6875 | 12.7389 | 15 | 60 | 60 | 743.5251 | 176.6004 | 59.299 | 162.9048 | 0 | 0 | 283.5354 | 428.0318 | 321.7929 | 27.0521 | 0 | 0 | 626.3996 | 135.9744 | 135.9744 | 185.651 | 210.9673 | 192.3538 | 140.714 | 135.9744 | 135.9744 | 176.6004 | 135.9744 | 135.9744 | 469.1864 | 638.9991 | 514.1468 | 167.7661 | 135.9744 | 135.9744 | 803 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 13 | 3685 | 22 | 22 | 15.6875 | 12.7389 | 15 | 59 | 59 | 649.8085 | 218.6044 | 59.8358 | 190.4803 | 0 | 0 | 97.5257 | 293.1895 | 317.1068 | 155.2673 | 0 | 0 | 562.3956 | 141.7682 | 141.7682 | 164.7384 | 210.8229 | 216.4561 | 178.3382 | 141.7682 | 141.7682 | 218.6044 | 141.7682 | 141.7682 | 262.264 | 504.0123 | 533.5629 | 333.6055 | 141.7682 | 141.7682 | 781 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 14 | 3686 | 22.8 | 22.8 | 15.6875 | 12.7389 | 15 | 59 | 59 | 745.8494 | 177.2699 | 56.179 | 215.9355 | 0 | 0 | 0 | 212.3804 | 368.5218 | 308.7882 | 68.1706 | 0 | 633.7301 | 135.1008 | 135.1008 | 135.1008 | 163.3007 | 184.0333 | 176.1018 | 144.1525 | 135.1008 | 177.2699 | 135.1008 | 135.1008 | 135.1008 | 375.6811 | 552.5551 | 484.89 | 212.3231 | 135.1008 | 811 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 15 | 3687 | 24.1 | 24.1 | 15.6875 | 12.7389 | 15 | 53 | 53 | 777.6831 | 155.8168 | 49.5277 | 236.2434 | 0 | 0 | 0 | 68.195 | 350.4763 | 427.4533 | 254.034 | 0 | 619.1832 | 127.9916 | 127.9916 | 127.9916 | 135.8853 | 168.5601 | 177.4704 | 157.3967 | 127.9916 | 155.8168 | 127.9916 | 127.9916 | 127.9916 | 204.0804 | 519.0364 | 604.9237 | 411.4306 | 127.9916 | 775 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 16 | 3688 | 24.6 | 24.6 | 15.6875 | 12.7389 | 15 | 50 | 50 | 706.7107 | 160.106 | 41.2377 | 252.1708 | 0 | 0 | 0 | 0 | 254.8903 | 449.9079 | 381.3756 | 89.4386 | 500.894 | 119.0799 | 119.0799 | 119.0799 | 119.0799 | 162.7118 | 196.0948 | 184.3635 | 134.3899 | 160.106 | 119.0799 | 119.0799 | 119.0799 | 119.0799 | 417.6022 | 646.0027 | 565.7391 | 223.8285 | 661 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 17 | 3689 | 24.6 | 24.6 | 15.6875 | 12.7389 | 15 | 49 | 49 | 686.5959 | 139.5528 | 32.2145 | 265.3718 | 0 | 0 | 0 | 0 | 158.0834 | 459.3327 | 491.5111 | 235.7689 | 407.4472 | 103.8766 | 103.8766 | 103.8766 | 103.8766 | 129.3839 | 177.9914 | 183.1835 | 141.9187 | 139.5528 | 103.8766 | 103.8766 | 103.8766 | 103.8766 | 287.4673 | 637.3241 | 674.6945 | 377.6876 | 547 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 18 | 3690 | 23.9 | 23.9 | 15.6875 | 12.7389 | 15 | 51 | 51 | 354.1618 | 179.7758 | 23.0188 | 277.1283 | 0 | 0 | 0 | 0 | 24.1781 | 228.2841 | 298.6644 | 194.0911 | 162.2242 | 97.2827 | 97.2827 | 97.2827 | 97.2827 | 106.8684 | 187.7889 | 215.6921 | 174.2327 | 179.7758 | 97.2827 | 97.2827 | 97.2827 | 97.2827 | 131.0465 | 416.0731 | 514.3565 | 368.3238 | 342 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 19 | 3691 | 22.6 | 22.6 | 15.6875 | 12.7389 | 15 | 57 | 57 | 436.0771 | 111.0137 | 14.0456 | 288.3098 | 49.8051 | 0 | 0 | 0 | 0 | 246.3898 | 398.2528 | 316.8248 | 135.9863 | 79.6874 | 67.4704 | 67.4704 | 67.4704 | 67.4704 | 127.9086 | 165.1598 | 145.1859 | 111.0137 | 129.4925 | 67.4704 | 67.4704 | 67.4704 | 67.4704 | 374.2984 | 563.4127 | 462.0107 | 247 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 20 | 3692 | 21.3 | 21.3 | 15.6875 | 12.7389 | 15 | 60 | 60 | 154.5158 | 74.5459 | 5.6344 | 299.5234 | 47.0906 | 0 | 0 | 0 | 0 | 67.3283 | 142.3073 | 133.9246 | 25.4541 | 66.5791 | 40.1955 | 40.1955 | 40.1955 | 40.1955 | 77.9177 | 119.9262 | 115.2296 | 74.5459 | 113.6697 | 40.1955 | 40.1955 | 40.1955 | 40.1955 | 145.246 | 262.2335 | 249.1542 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 21 | 3693 | 19.9 | 19.9 | 15.6875 | 12.7389 | 15 | 65 | 65 | 13.3527 | 11.8874 | -1.8715 | 311.2099 | 6.5482 | 0 | 0 | 0 | 0 | 3.5459 | 11.5628 | 12.8064 | 2.1126 | 12.9533 | 6.6657 | 6.6657 | 6.6657 | 6.6657 | 10.0705 | 17.7683 | 18.9624 | 11.8874 | 19.5014 | 6.6657 | 6.6657 | 6.6657 | 6.6657 | 13.6164 | 29.3311 | 31.7688 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 22 | 3694 | 18.7 | 18.7 | 15.6875 | 12.7389 | 15 | 70 | 70 | 0 | 0 | -8.1003 | 323.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 23 | 3695 | 17.6 | 17.6 | 15.6875 | 12.7389 | 15 | 76 | 76 | 0 | 0 | -12.6613 | 336.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 3 | 24 | 3696 | 16.9 | 16.9 | 18.7083 | 14.3488 | 15 | 81 | 81 | 0 | 0 | -15.1985 | 351.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 1 | 3697 | 16.4 | 16.4 | 18.7083 | 14.3488 | 15 | 85 | 85 | 0 | 0 | -15.4805 | 5.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 2 | 3698 | 15.9 | 15.9 | 18.7083 | 14.3488 | 15 | 87 | 87 | 0 | 0 | -13.368 | 19.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 3 | 3699 | 15.8 | 15.8 | 18.7083 | 14.3488 | 15 | 87 | 87 | 0 | 0 | -9.2822 | 33.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 4 | 3700 | 15.4 | 15.4 | 18.7083 | 14.3488 | 15 | 90 | 90 | 0 | 0 | -3.4355 | 45.7346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 5 | 3701 | 15.1 | 15.1 | 18.7083 | 14.3488 | 15 | 91 | 91 | 0.92998 | 1.32 | 3.7844 | 57.579 | 0.64794 | 0.92823 | 0.66478 | 0.011902 | 0 | 0 | 0 | 0 | 6.68 | 1.9522 | 2.2966 | 1.9729 | 1.1707 | 1.1561 | 1.1561 | 1.1561 | 1.1561 | 1.32 | 2.6002 | 3.2248 | 2.6377 | 1.1826 | 1.1561 | 1.1561 | 1.1561 | 1.1561 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 6 | 3702 | 16.4 | 16.4 | 18.7083 | 14.3488 | 15 | 83 | 83 | 88.9221 | 62.5785 | 11.9995 | 68.8651 | 47.5704 | 86.5984 | 74.8983 | 19.3237 | 0 | 0 | 0 | 0 | 12.4215 | 130.8942 | 216.415 | 190.7768 | 68.9981 | 26.6547 | 26.6547 | 26.6547 | 26.6547 | 62.5785 | 178.4647 | 303.0135 | 265.6751 | 88.3218 | 26.6547 | 26.6547 | 26.6547 | 26.6547 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 7 | 3703 | 18.3 | 18.3 | 18.7083 | 14.3488 | 15 | 77 | 77 | 294.4161 | 118.8802 | 20.8615 | 79.9973 | 103.8366 | 263.3606 | 268.6115 | 116.5135 | 0 | 0 | 0 | 0 | 84.1198 | 103.2533 | 163.3874 | 165.3668 | 108.032 | 64.1111 | 64.1111 | 64.1111 | 64.1111 | 118.8802 | 207.0899 | 426.748 | 433.9783 | 224.5455 | 64.1111 | 64.1111 | 64.1111 | 64.1111 | 203 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 4 | 8 | 3704 | 20.6 | 20.6 | 18.7083 | 14.3488 | 15 | 69 | 69 | 494.6201 | 141.9621 | 30.0344 | 91.5353 | 80.2806 | 378.6203 | 455.1693 | 265.0863 | 0 | 0 | 0 | 0 | 214.0379 | 107.5013 | 179.5803 | 198.0746 | 152.1504 | 88.1054 | 88.1054 | 88.1054 | 88.1054 | 141.9621 | 187.7819 | 558.2006 | 653.2439 | 417.2368 | 88.1054 | 88.1054 | 88.1054 | 88.1054 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 9 | 3705 | 22.1 | 22.1 | 18.7083 | 14.3488 | 15 | 63 | 63 | 598.9371 | 158.1611 | 39.1455 | 104.2711 | 0 | 356.6905 | 518.3288 | 376.3372 | 13.8923 | 0 | 0 | 0 | 341.8389 | 107.035 | 184.4742 | 219.5666 | 188.7396 | 110.0511 | 107.035 | 107.035 | 107.035 | 158.1611 | 107.035 | 541.1647 | 737.8955 | 565.0768 | 123.9434 | 107.035 | 107.035 | 107.035 | 500 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 10 | 3706 | 24.3 | 24.3 | 18.7083 | 14.3488 | 15 | 56 | 56 | 677.7635 | 165.0972 | 47.6901 | 119.3757 | 0 | 268.588 | 509.4154 | 451.8341 | 129.5745 | 0 | 0 | 0 | 467.9028 | 119.779 | 168.8603 | 212.8686 | 202.3463 | 143.4572 | 119.779 | 119.779 | 119.779 | 165.0972 | 119.779 | 437.4483 | 722.2839 | 654.1804 | 273.0317 | 119.779 | 119.779 | 119.779 | 633 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 11 | 3707 | 25.3 | 25.3 | 18.7083 | 14.3488 | 15 | 52 | 52 | 733.1655 | 167.613 | 54.8665 | 138.4649 | 0 | 132.9195 | 430.0667 | 475.2866 | 242.0901 | 0 | 0 | 0 | 574.387 | 129.6128 | 152.276 | 202.9405 | 210.6507 | 170.8899 | 129.6128 | 129.6128 | 129.6128 | 167.613 | 129.6128 | 285.1955 | 633.0072 | 685.9373 | 412.98 | 129.6128 | 129.6128 | 129.6128 | 742 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 12 | 3708 | 26.3 | 26.3 | 18.7083 | 14.3488 | 15 | 49 | 49 | 763.9792 | 169.5363 | 59.4124 | 162.7865 | 0 | 0 | 291.527 | 438.8532 | 329.1051 | 26.5717 | 0 | 0 | 644.4637 | 135.5629 | 135.5629 | 172.0276 | 190.4554 | 176.7279 | 138.8865 | 135.5629 | 135.5629 | 169.5363 | 135.5629 | 135.5629 | 463.5546 | 629.3086 | 505.833 | 165.4583 | 135.5629 | 135.5629 | 814 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 13 | 3709 | 27.2 | 27.2 | 18.7083 | 14.3488 | 15 | 47 | 47 | 769.4032 | 172.2745 | 59.9624 | 190.4368 | 0 | 0 | 115.8622 | 346.3695 | 373.9783 | 182.5157 | 0 | 0 | 666.7255 | 136.9825 | 136.9825 | 151.5863 | 180.6407 | 184.1207 | 159.9877 | 136.9825 | 136.9825 | 172.2745 | 136.9825 | 136.9825 | 267.4485 | 527.0102 | 558.099 | 342.5034 | 136.9825 | 136.9825 | 839 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 14 | 3710 | 27.2 | 27.2 | 18.7083 | 14.3488 | 15 | 45 | 45 | 697.4002 | 195.6805 | 56.3066 | 215.9607 | 0 | 0 | 0 | 198.0475 | 343.3206 | 287.4812 | 63.2392 | 0 | 593.3195 | 137.2963 | 137.2963 | 137.2963 | 177.5371 | 207.0549 | 195.709 | 150.1457 | 137.2963 | 195.6805 | 137.2963 | 137.2963 | 137.2963 | 375.5846 | 550.3755 | 483.1902 | 213.3849 | 137.2963 | 789 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 15 | 3711 | 26.6 | 26.6 | 18.7083 | 14.3488 | 15 | 47 | 47 | 358.0868 | 311.4908 | 49.6507 | 236.3008 | 0 | 0 | 0 | 31.2101 | 160.7897 | 196.1808 | 116.6519 | 0 | 285.5092 | 150.5374 | 150.5374 | 150.5374 | 168.0995 | 241.0144 | 260.9292 | 216.1779 | 150.5374 | 311.4908 | 150.5374 | 150.5374 | 150.5374 | 199.3096 | 401.8041 | 457.11 | 332.8299 | 150.5374 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 16 | 3712 | 27 | 27 | 18.7083 | 14.3488 | 15 | 44 | 44 | 419.7403 | 257.9959 | 41.3563 | 252.2362 | 0 | 0 | 0 | 0 | 150.7811 | 266.4903 | 226.0931 | 53.2537 | 298.0041 | 134.1092 | 134.1092 | 134.1092 | 134.1092 | 200.3897 | 251.2533 | 233.4955 | 157.5185 | 257.9959 | 134.1092 | 134.1092 | 134.1092 | 134.1092 | 351.1708 | 517.7436 | 459.5886 | 210.7721 | 556 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 17 | 3713 | 26.4 | 26.4 | 18.7083 | 14.3488 | 15 | 45 | 45 | 300.9742 | 245.9999 | 32.3312 | 265.4353 | 0 | 0 | 0 | 0 | 68.9253 | 200.8678 | 215.1447 | 103.3927 | 179.0001 | 123.2192 | 123.2192 | 123.2192 | 123.2192 | 160.8215 | 232.8029 | 240.5917 | 179.6252 | 245.9999 | 123.2192 | 123.2192 | 123.2192 | 123.2192 | 229.7468 | 433.6707 | 455.7363 | 283.0179 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 4 | 18 | 3714 | 24.8 | 24.8 | 18.7083 | 14.3488 | 15 | 54 | 54 | 436.6162 | 163.3861 | 23.1357 | 277.1863 | 0 | 0 | 0 | 0 | 29.3608 | 280.8052 | 367.7577 | 239.2828 | 200.6139 | 94.6377 | 94.6377 | 94.6377 | 94.6377 | 103.5562 | 179.9341 | 206.3465 | 167.3214 | 163.3861 | 94.6377 | 94.6377 | 94.6377 | 94.6377 | 132.917 | 460.7393 | 574.1042 | 406.6042 | 364 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 19 | 3715 | 23.5 | 23.5 | 18.7083 | 14.3488 | 15 | 56 | 56 | 382.5022 | 119.1272 | 14.1644 | 288.3602 | 44.001 | 0 | 0 | 0 | 0 | 215.6506 | 348.9771 | 277.8775 | 119.8728 | 82.1442 | 69.3329 | 69.3329 | 69.3329 | 69.3329 | 132.1217 | 170.941 | 150.2397 | 119.1272 | 126.1453 | 69.3329 | 69.3329 | 69.3329 | 69.3329 | 347.7723 | 519.9181 | 428.1171 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 20 | 3716 | 21.7 | 21.7 | 18.7083 | 14.3488 | 15 | 58 | 58 | 282.7439 | 69.9472 | 5.7562 | 299.5646 | 86.3538 | 0 | 0 | 0 | 0 | 122.9224 | 260.1923 | 245.0451 | 47.0528 | 67.436 | 40.2914 | 40.2914 | 40.2914 | 40.2914 | 78.931 | 122.0807 | 117.3193 | 69.9472 | 153.7898 | 40.2914 | 40.2914 | 40.2914 | 40.2914 | 201.8534 | 382.273 | 362.3644 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 21 | 3717 | 20 | 20 | 18.7083 | 14.3488 | 15 | 62 | 62 | 12.201 | 12.4942 | -1.7465 | 311.2394 | 5.9897 | 0 | 0 | 0 | 0 | 3.2309 | 10.5589 | 11.7016 | 6.5058 | 8.267 | 7.2274 | 7.2274 | 7.2274 | 7.2274 | 7.7882 | 9.0601 | 9.2584 | 12.4942 | 14.2567 | 7.2274 | 7.2274 | 7.2274 | 7.2274 | 11.0191 | 19.619 | 20.96 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 22 | 3718 | 18.2 | 18.2 | 18.7083 | 14.3488 | 15 | 65 | 65 | 0 | 0 | -7.9727 | 323.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 23 | 3719 | 16.7 | 16.7 | 18.7083 | 14.3488 | 15 | 72 | 72 | 0 | 0 | -12.5329 | 336.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 4 | 24 | 3720 | 15.2 | 15.2 | 21.1 | 16.378 | 15 | 78 | 78 | 0 | 0 | -15.0723 | 351.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 1 | 3721 | 13.8 | 13.8 | 21.1 | 16.378 | 15 | 85 | 85 | 0 | 0 | -15.36 | 5.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 2 | 3722 | 13.3 | 13.3 | 21.1 | 16.378 | 15 | 89 | 89 | 0 | 0 | -13.2629 | 19.4979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 3 | 3723 | 13.4 | 13.4 | 21.1 | 16.378 | 15 | 90 | 90 | 0 | 0 | -9.1874 | 33.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 4 | 3724 | 13.5 | 13.5 | 21.1 | 16.378 | 15 | 92 | 92 | 0 | 0 | -3.3512 | 45.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 5 | 3725 | 13.6 | 13.6 | 21.1 | 16.378 | 15 | 91 | 91 | 1.316 | 1.3215 | 3.8595 | 57.4819 | 0.91845 | 1.3137 | 0.93939 | 0.014802 | 0 | 0 | 0 | 0 | 4.6785 | 1.8889 | 2.2958 | 1.9105 | 0.95852 | 0.94328 | 0.94328 | 0.94328 | 0.94328 | 1.3215 | 2.8074 | 3.6095 | 2.8499 | 0.97332 | 0.94328 | 0.94328 | 0.94328 | 0.94328 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 6 | 3726 | 14 | 14 | 21.1 | 16.378 | 15 | 89 | 89 | 1.224 | 18.827 | 12.0674 | 68.7607 | 0.6565 | 1.1924 | 1.0298 | 0.26395 | 0 | 0 | 0 | 0 | 0.17296 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 18.827 | 9.9136 | 10.4494 | 10.2868 | 9.521 | 9.2571 | 9.2571 | 9.2571 | 9.2571 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 7 | 3727 | 14.4 | 14.4 | 21.1 | 16.378 | 15 | 89 | 89 | 2.0518 | 49.4107 | 20.9246 | 79.8849 | 0.72686 | 1.8364 | 1.8702 | 0.80843 | 0 | 0 | 0 | 0 | 0.58929 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 49.4107 | 25.0804 | 26.1899 | 26.2237 | 25.162 | 24.3535 | 24.3535 | 24.3535 | 24.3535 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 5 | 8 | 3728 | 14.3 | 14.3 | 21.1 | 16.378 | 15 | 95 | 95 | 0.54643 | 38.7628 | 30.0961 | 91.413 | 0.089638 | 0.41868 | 0.50246 | 0.29191 | 0 | 0 | 0 | 0 | 0.2372 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 38.7628 | 18.6312 | 18.9603 | 19.0441 | 18.8335 | 18.5416 | 18.5416 | 18.5416 | 18.5416 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 9 | 3729 | 14.7 | 14.7 | 21.1 | 16.378 | 15 | 96 | 96 | 0.92885 | 66.4687 | 39.2101 | 104.1367 | 0 | 0.55407 | 0.80339 | 0.58209 | 0.019816 | 0 | 0 | 0 | 0.5313 | 32.2273 | 32.2273 | 32.2273 | 32.2273 | 32.2273 | 32.2273 | 32.2273 | 32.2273 | 66.4687 | 32.2273 | 32.7814 | 33.0307 | 32.8094 | 32.2471 | 32.2273 | 32.2273 | 32.2273 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 10 | 3730 | 15.1 | 15.1 | 21.1 | 16.378 | 15 | 96 | 96 | 1.3321 | 96.0789 | 47.763 | 119.2292 | 0 | 0.52947 | 1.0009 | 0.88596 | 0.25208 | 0 | 0 | 0 | 0.92114 | 47.1438 | 47.1438 | 47.1438 | 47.1438 | 47.1438 | 47.1438 | 47.1438 | 47.1438 | 96.0789 | 47.1438 | 47.6733 | 48.1447 | 48.0298 | 47.3959 | 47.1438 | 47.1438 | 47.1438 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 11 | 3731 | 16.8 | 16.8 | 21.1 | 16.378 | 15 | 93 | 93 | 10.5205 | 263.7466 | 54.9543 | 138.3161 | 0 | 1.922 | 6.1714 | 6.8056 | 3.4532 | 0 | 0 | 0 | 8.2534 | 126.166 | 132.021 | 144.9656 | 146.8976 | 136.6853 | 126.166 | 126.166 | 126.166 | 263.7466 | 126.166 | 133.9431 | 151.137 | 153.7033 | 140.1386 | 126.166 | 126.166 | 126.166 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 12 | 3732 | 18.1 | 18.1 | 21.1 | 16.378 | 15 | 88 | 88 | 160.4844 | 381.4566 | 59.5191 | 162.6678 | 0 | 0 | 61.285 | 92.0006 | 68.8236 | 5.3306 | 0 | 0 | 135.5434 | 167.7611 | 167.7611 | 240.8046 | 277.4135 | 249.7896 | 174.1145 | 167.7611 | 167.7611 | 381.4566 | 167.7611 | 167.7611 | 302.0895 | 369.4142 | 318.6132 | 179.4451 | 167.7611 | 167.7611 | 517 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 13 | 3733 | 19.4 | 19.4 | 21.1 | 16.378 | 15 | 82 | 82 | 142.8058 | 393.1077 | 60.0826 | 190.3892 | 0 | 0 | 21.5802 | 64.1554 | 69.1493 | 33.6364 | 0 | 0 | 123.8923 | 169.4978 | 169.4978 | 199.034 | 257.3053 | 264.1402 | 215.5348 | 169.4978 | 169.4978 | 393.1077 | 169.4978 | 169.4978 | 220.6142 | 321.4607 | 333.2894 | 249.1712 | 169.4978 | 169.4978 | 517 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 14 | 3734 | 20.6 | 20.6 | 21.1 | 16.378 | 15 | 74 | 74 | 607.9446 | 232.1644 | 56.4288 | 215.9795 | 0 | 0 | 0 | 172.2246 | 298.2418 | 249.5529 | 54.6794 | 0 | 517.8356 | 141.1239 | 141.1239 | 141.1239 | 186.3926 | 219.5158 | 206.7181 | 155.4962 | 141.1239 | 232.1644 | 141.1239 | 141.1239 | 141.1239 | 358.6172 | 517.7576 | 456.2711 | 210.1756 | 141.1239 | 750 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 15 | 3735 | 20.2 | 20.2 | 21.1 | 16.378 | 15 | 76 | 76 | 40.2478 | 331.8668 | 49.7688 | 236.3513 | 0 | 0 | 0 | 3.4895 | 18.0102 | 21.9807 | 13.0753 | 0 | 32.1332 | 145.8212 | 145.8212 | 145.8212 | 155.6985 | 196.8005 | 208.0396 | 182.8319 | 145.8212 | 331.8668 | 145.8212 | 145.8212 | 145.8212 | 159.188 | 214.8107 | 230.0203 | 195.9072 | 145.8212 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 16 | 3736 | 20.9 | 20.9 | 21.1 | 16.378 | 15 | 75 | 75 | 65.5658 | 311.3755 | 41.4706 | 252.2953 | 0 | 0 | 0 | 0 | 23.4645 | 41.5188 | 35.252 | 8.335 | 46.6245 | 139.8157 | 139.8157 | 139.8157 | 139.8157 | 179.0504 | 209.2388 | 198.76 | 153.7525 | 311.3755 | 139.8157 | 139.8157 | 139.8157 | 139.8157 | 202.515 | 250.7577 | 234.012 | 162.0875 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 17 | 3737 | 20.6 | 20.6 | 21.1 | 16.378 | 15 | 75 | 75 | 9.1677 | 194.5363 | 32.4437 | 265.493 | 0 | 0 | 0 | 0 | 2.089 | 6.1045 | 6.544 | 3.1501 | 5.4637 | 95.9679 | 95.9679 | 95.9679 | 95.9679 | 98.5315 | 103.459 | 103.9983 | 99.8336 | 194.5363 | 95.9679 | 95.9679 | 95.9679 | 95.9679 | 100.6205 | 109.5634 | 110.5423 | 102.9837 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 5 | 18 | 3738 | 20.1 | 20.1 | 21.1 | 16.378 | 15 | 77 | 77 | 18.9942 | 172.2471 | 23.2484 | 277.2387 | 0 | 0 | 0 | 0 | 1.2596 | 12.1903 | 15.98 | 10.4089 | 8.7529 | 83.6618 | 83.6618 | 83.6618 | 83.6618 | 84.9264 | 95.9005 | 99.7053 | 94.112 | 172.2471 | 83.6618 | 83.6618 | 83.6618 | 83.6618 | 86.186 | 108.0908 | 115.6854 | 104.5209 | 181 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 19 | 3739 | 19.1 | 19.1 | 21.1 | 16.378 | 15 | 77 | 77 | 157.8598 | 142.2965 | 14.2788 | 288.4055 | 18.2757 | 0 | 0 | 0 | 0 | 88.8198 | 143.8859 | 114.6656 | 49.7035 | 82.0329 | 71.8637 | 71.8637 | 71.8637 | 71.8637 | 121.2861 | 151.9267 | 135.6675 | 142.2965 | 100.3086 | 71.8637 | 71.8637 | 71.8637 | 71.8637 | 210.1059 | 295.8127 | 250.3331 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 20 | 3740 | 18.2 | 18.2 | 21.1 | 16.378 | 15 | 82 | 82 | 107.6787 | 75.9094 | 5.8732 | 299.601 | 32.9482 | 0 | 0 | 0 | 0 | 46.7157 | 99.0141 | 93.3115 | 18.0906 | 57.2132 | 39.2692 | 39.2692 | 39.2692 | 39.2692 | 64.7111 | 93.1934 | 90.0877 | 75.9094 | 90.1614 | 39.2692 | 39.2692 | 39.2692 | 39.2692 | 111.4268 | 192.2076 | 183.3992 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 21 | 3741 | 16.9 | 16.9 | 21.1 | 16.378 | 15 | 89 | 89 | 14.9624 | 12.2548 | -1.6266 | 311.2647 | 7.352 | 0 | 0 | 0 | 0 | 3.9523 | 12.9414 | 14.3496 | 9.7452 | 13.9108 | 7.6258 | 7.6258 | 7.6258 | 7.6258 | 11.0045 | 18.689 | 19.8928 | 12.2548 | 21.2628 | 7.6258 | 7.6258 | 7.6258 | 7.6258 | 14.9567 | 31.6303 | 34.2424 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 22 | 3742 | 16 | 16 | 21.1 | 16.378 | 15 | 92 | 92 | 0 | 0 | -7.8506 | 323.6896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 23 | 3743 | 15.5 | 15.5 | 21.1 | 16.378 | 15 | 93 | 93 | 0 | 0 | -12.4105 | 336.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 5 | 24 | 3744 | 15.4 | 15.4 | 16.5792 | 16.7555 | 15 | 93 | 93 | 0 | 0 | -14.9525 | 351.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 1 | 3745 | 15 | 15 | 16.5792 | 16.7555 | 15 | 96 | 96 | 0 | 0 | -15.2461 | 5.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 2 | 3746 | 14.3 | 14.3 | 16.5792 | 16.7555 | 15 | 98 | 98 | 0 | 0 | -13.1644 | 19.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 3 | 3747 | 14.6 | 14.6 | 16.5792 | 16.7555 | 15 | 97 | 97 | 0 | 0 | -9.0991 | 32.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 4 | 3748 | 14.6 | 14.6 | 16.5792 | 16.7555 | 15 | 97 | 97 | 0 | 0 | -3.2731 | 45.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 5 | 3749 | 14.9 | 14.9 | 16.5792 | 16.7555 | 15 | 95 | 95 | 2.3633 | 3.0459 | 3.9285 | 57.3877 | 1.652 | 2.3593 | 1.6845 | 0.023009 | 0 | 0 | 0 | 0 | 2.9541 | 3.2629 | 4.0516 | 3.2992 | 1.4466 | 1.4209 | 1.4209 | 1.4209 | 1.4209 | 3.0459 | 4.9149 | 6.4109 | 4.9838 | 1.4696 | 1.4209 | 1.4209 | 1.4209 | 1.4209 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 6 | 3750 | 14.8 | 14.8 | 16.5792 | 16.7555 | 15 | 93 | 93 | 0.95939 | 16.863 | 12.1294 | 68.6597 | 0.51585 | 0.93485 | 0.80623 | 0.20533 | 0 | 0 | 0 | 0 | 0.13702 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 16.863 | 8.7403 | 9.1593 | 9.0307 | 8.4298 | 8.2245 | 8.2245 | 8.2245 | 8.2245 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 7 | 3751 | 15.1 | 15.1 | 16.5792 | 16.7555 | 15 | 93 | 93 | 3.3298 | 63.039 | 20.9821 | 79.7762 | 1.1847 | 2.9819 | 3.0323 | 1.3064 | 0 | 0 | 0 | 0 | 0.96103 | 34.411 | 40.3989 | 40.5669 | 34.8166 | 30.4637 | 30.4637 | 30.4637 | 30.4637 | 63.039 | 35.5957 | 43.3807 | 43.5992 | 36.1231 | 30.4637 | 30.4637 | 30.4637 | 30.4637 | 64 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 6 | 8 | 3752 | 15.6 | 15.6 | 16.5792 | 16.7555 | 15 | 90 | 90 | 4.1667 | 106.1859 | 30.1522 | 91.2947 | 0.69052 | 3.1955 | 3.8286 | 2.219 | 0 | 0 | 0 | 0 | 1.8141 | 53.4547 | 60.1501 | 61.8423 | 57.54 | 51.6091 | 51.6091 | 51.6091 | 51.6091 | 106.1859 | 54.1453 | 63.3456 | 65.6709 | 59.759 | 51.6091 | 51.6091 | 51.6091 | 51.6091 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 9 | 3753 | 16 | 16 | 16.5792 | 16.7555 | 15 | 88 | 88 | 2.8216 | 115.3827 | 39.2688 | 104.0065 | 0 | 1.6858 | 2.4392 | 1.7637 | 0.055126 | 0 | 0 | 0 | 1.6173 | 57.5309 | 57.5309 | 57.5309 | 57.5309 | 57.5309 | 57.5309 | 57.5309 | 57.5309 | 115.3827 | 57.5309 | 59.2167 | 59.9701 | 59.2947 | 57.586 | 57.5309 | 57.5309 | 57.5309 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 10 | 3754 | 15.6 | 15.6 | 16.5792 | 16.7555 | 15 | 97 | 97 | 0.31183 | 46.784 | 47.8297 | 119.0868 | 0 | 0.12431 | 0.23424 | 0.20695 | 0.058431 | 0 | 0 | 0 | 0.21598 | 22.4395 | 22.4395 | 22.4395 | 22.4395 | 22.4395 | 22.4395 | 22.4395 | 22.4395 | 46.784 | 22.4395 | 22.5639 | 22.6738 | 22.6465 | 22.498 | 22.4395 | 22.4395 | 22.4395 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 11 | 3755 | 16.4 | 16.4 | 16.5792 | 16.7555 | 15 | 95 | 95 | 3.2466 | 169.4497 | 55.0355 | 138.17 | 0 | 0.5976 | 1.9047 | 2.096 | 1.0596 | 0 | 0 | 0 | 2.5503 | 85.4832 | 85.4832 | 85.4832 | 85.4832 | 85.4832 | 85.4832 | 85.4832 | 85.4832 | 169.4497 | 85.4832 | 86.0808 | 87.3879 | 87.5793 | 86.5428 | 85.4832 | 85.4832 | 85.4832 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 12 | 3756 | 17.8 | 17.8 | 16.5792 | 16.7555 | 15 | 88 | 88 | 17.8708 | 312.8892 | 59.619 | 162.5489 | 0 | 0 | 6.8301 | 10.2256 | 7.631 | 0.56633 | 0 | 0 | 15.1108 | 148.6477 | 148.6477 | 164.9497 | 173.054 | 166.8613 | 149.9994 | 148.6477 | 148.6477 | 312.8892 | 148.6477 | 148.6477 | 171.7798 | 183.2795 | 174.4924 | 150.5658 | 148.6477 | 148.6477 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 13 | 3757 | 19.1 | 19.1 | 16.5792 | 16.7555 | 15 | 86 | 86 | 36.8549 | 356.9913 | 60.1964 | 190.3375 | 0 | 0 | 5.5898 | 16.5259 | 17.7814 | 8.6208 | 0 | 0 | 32.0087 | 154.5653 | 154.5653 | 173.5295 | 210.6322 | 214.8917 | 183.8127 | 154.5653 | 154.5653 | 356.9913 | 154.5653 | 154.5653 | 179.1193 | 227.1581 | 232.673 | 192.4335 | 154.5653 | 154.5653 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 14 | 3758 | 20.6 | 20.6 | 16.5792 | 16.7555 | 15 | 79 | 79 | 82.1549 | 379.9431 | 56.5452 | 215.992 | 0 | 0 | 0 | 23.2236 | 40.1705 | 33.5861 | 7.3274 | 0 | 70.0569 | 166.2562 | 166.2562 | 166.2562 | 205.0418 | 233.3447 | 222.3481 | 178.4937 | 166.2562 | 379.9431 | 166.2562 | 166.2562 | 166.2562 | 228.2653 | 273.5152 | 255.9342 | 185.8211 | 166.2562 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 15 | 3759 | 21 | 21 | 16.5792 | 16.7555 | 15 | 79 | 79 | 321.3105 | 324.1488 | 49.882 | 236.3951 | 0 | 0 | 0 | 27.7339 | 143.3171 | 174.947 | 104.0954 | 0 | 256.8512 | 151.6989 | 151.6989 | 151.6989 | 169.6625 | 244.527 | 265.0141 | 219.1227 | 151.6989 | 324.1488 | 151.6989 | 151.6989 | 151.6989 | 197.3965 | 387.8441 | 439.9611 | 323.2181 | 151.6989 | 581 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 16 | 3760 | 19.8 | 19.8 | 16.5792 | 16.7555 | 15 | 82 | 82 | 5.1814 | 193.3099 | 41.5804 | 252.3478 | 0 | 0 | 0 | 0 | 1.8478 | 3.2729 | 2.7807 | 0.65964 | 3.6901 | 97.7897 | 97.7897 | 97.7897 | 97.7897 | 98.3239 | 98.736 | 98.5937 | 97.9804 | 193.3099 | 97.7897 | 97.7897 | 97.7897 | 97.7897 | 100.1718 | 102.0088 | 101.3744 | 98.64 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 17 | 3761 | 18.3 | 18.3 | 16.5792 | 16.7555 | 15 | 86 | 86 | 0.70667 | 60.578 | 32.5519 | 265.5446 | 0 | 0 | 0 | 0 | 0.16029 | 0.46953 | 0.50372 | 0.24284 | 0.42197 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 60.578 | 29.2588 | 29.2588 | 29.2588 | 29.2588 | 29.4191 | 29.7284 | 29.7626 | 29.5017 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 6 | 18 | 3762 | 17.2 | 17.2 | 16.5792 | 16.7555 | 15 | 87 | 87 | 5.4424 | 128.4852 | 23.3568 | 277.2856 | 0 | 0 | 0 | 0 | 0.35636 | 3.486 | 4.5735 | 2.982 | 2.5148 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 128.4852 | 64.3968 | 64.3968 | 64.3968 | 64.3968 | 64.7531 | 67.8827 | 68.9703 | 67.3788 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 19 | 3763 | 16 | 16 | 16.5792 | 16.7555 | 15 | 93 | 93 | 0.081929 | 10.9741 | 14.3887 | 288.4457 | 0.0095385 | 0 | 0 | 0 | 0 | 0.046011 | 0.074608 | 0.059501 | 0.025909 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 10.9741 | 5.144 | 5.1345 | 5.1345 | 5.1345 | 5.1345 | 5.1805 | 5.2091 | 5.194 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 20 | 3764 | 15.8 | 15.8 | 16.5792 | 16.7555 | 15 | 93 | 93 | 2.2649 | 30.6161 | 5.9855 | 299.6328 | 0.69415 | 0 | 0 | 0 | 0 | 0.98076 | 2.0812 | 1.9624 | 0.38391 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 30.6161 | 15.3499 | 14.6558 | 14.6558 | 14.6558 | 14.6558 | 15.6365 | 16.7369 | 16.6182 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 21 | 3765 | 15.5 | 15.5 | 16.5792 | 16.7555 | 15 | 95 | 95 | 2.4033 | 5.9235 | -1.5118 | 311.2857 | 1.1818 | 0 | 0 | 0 | 0 | 0.6334 | 2.0776 | 2.3047 | 0.076542 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 5.9235 | 4.3531 | 3.1713 | 3.1713 | 3.1713 | 3.1713 | 3.8047 | 5.2488 | 5.476 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 22 | 3766 | 14.4 | 14.4 | 16.5792 | 16.7555 | 15 | 94 | 94 | 0 | 0 | -7.7342 | 323.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 23 | 3767 | 13.4 | 13.4 | 16.5792 | 16.7555 | 15 | 94 | 94 | 0 | 0 | -12.2942 | 336.9731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 6 | 24 | 3768 | 12 | 12 | 16.1583 | 16.9219 | 15 | 96 | 96 | 0 | 0 | -14.8391 | 350.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 1 | 3769 | 11.6 | 11.6 | 16.1583 | 16.9219 | 15 | 96 | 96 | 0 | 0 | -15.1388 | 5.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 2 | 3770 | 11.5 | 11.5 | 16.1583 | 16.9219 | 15 | 96 | 96 | 0 | 0 | -13.0725 | 19.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 3 | 3771 | 11.7 | 11.7 | 16.1583 | 16.9219 | 15 | 93 | 93 | 0 | 0 | -9.0174 | 32.8474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 4 | 3772 | 11.8 | 11.8 | 16.1583 | 16.9219 | 15 | 92 | 92 | 0 | 0 | -3.2013 | 45.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 5 | 3773 | 11.9 | 11.9 | 16.1583 | 16.9219 | 15 | 89 | 89 | 0 | 0 | 3.9916 | 57.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 6 | 3774 | 12.2 | 12.2 | 16.1583 | 16.9219 | 15 | 90 | 90 | 1.1751 | 18.8305 | 12.1855 | 68.5619 | 0.63335 | 1.1453 | 0.9864 | 0.24965 | 0 | 0 | 0 | 0 | 0.16951 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 18.8305 | 9.8766 | 10.3886 | 10.2296 | 9.4929 | 9.2432 | 9.2432 | 9.2432 | 9.2432 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 7 | 3775 | 12.7 | 12.7 | 16.1583 | 16.9219 | 15 | 83 | 83 | 2.9982 | 60.1307 | 21.0338 | 79.6712 | 1.0712 | 2.6864 | 2.7279 | 1.1715 | 0 | 0 | 0 | 0 | 0.86929 | 31.8318 | 35.654 | 35.7524 | 32.0693 | 29.2971 | 29.2971 | 29.2971 | 29.2971 | 60.1307 | 32.903 | 38.3404 | 38.4803 | 33.2409 | 29.2971 | 29.2971 | 29.2971 | 29.2971 | 61 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 7 | 8 | 3776 | 13.4 | 13.4 | 16.1583 | 16.9219 | 15 | 80 | 80 | 113.443 | 197.4711 | 30.2025 | 91.1805 | 18.9847 | 87.0823 | 104.1683 | 60.2339 | 0 | 0 | 0 | 0 | 49.5289 | 112.3048 | 189.3485 | 208.6791 | 158.9731 | 90.8262 | 90.8262 | 90.8262 | 90.8262 | 197.4711 | 131.2895 | 276.4308 | 312.8475 | 219.207 | 90.8262 | 90.8262 | 90.8262 | 90.8262 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 9 | 3777 | 13.8 | 13.8 | 16.1583 | 16.9219 | 15 | 78 | 78 | 15.7235 | 207.9703 | 39.3216 | 103.8807 | 0 | 9.4089 | 13.5862 | 9.8049 | 0.27997 | 0 | 0 | 0 | 9.0297 | 95.5034 | 128.7512 | 143.5121 | 130.1502 | 96.4927 | 95.5034 | 95.5034 | 95.5034 | 207.9703 | 95.5034 | 138.1601 | 157.0983 | 139.9551 | 96.7727 | 95.5034 | 95.5034 | 95.5034 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 10 | 3778 | 14.5 | 14.5 | 16.1583 | 16.9219 | 15 | 75 | 75 | 16.2901 | 252.7009 | 47.8903 | 118.9485 | 0 | 6.513 | 12.234 | 10.7885 | 3.0232 | 0 | 0 | 0 | 11.2991 | 117.6976 | 137.4324 | 154.7675 | 150.3875 | 126.8582 | 117.6976 | 117.6976 | 117.6976 | 252.7009 | 117.6976 | 143.9454 | 167.0015 | 161.176 | 129.8815 | 117.6976 | 117.6976 | 117.6976 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 11 | 3779 | 15.3 | 15.3 | 16.1583 | 16.9219 | 15 | 76 | 76 | 19.6836 | 295.5194 | 55.1101 | 138.027 | 0 | 3.6495 | 11.5497 | 12.6843 | 6.3886 | 0 | 0 | 0 | 15.4806 | 138.5947 | 147.7875 | 167.6878 | 170.5456 | 154.6871 | 138.5947 | 138.5947 | 138.5947 | 295.5194 | 138.5947 | 151.437 | 179.2375 | 183.2299 | 161.0756 | 138.5947 | 138.5947 | 138.5947 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 12 | 3780 | 15.8 | 15.8 | 16.1583 | 16.9219 | 15 | 72 | 72 | 32.1875 | 341.7545 | 59.7121 | 162.43 | 0 | 0 | 12.3131 | 18.3856 | 13.6881 | 0.97223 | 0 | 0 | 27.2455 | 148.8491 | 148.8491 | 194.9302 | 217.6562 | 200.0759 | 152.4876 | 148.8491 | 148.8491 | 341.7545 | 148.8491 | 148.8491 | 207.2433 | 236.0418 | 213.7639 | 153.4599 | 148.8491 | 148.8491 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 13 | 3781 | 16.8 | 16.8 | 16.1583 | 16.9219 | 15 | 69 | 69 | 134.6129 | 393.9681 | 60.3037 | 190.2819 | 0 | 0 | 20.4944 | 60.2586 | 64.7241 | 31.2752 | 0 | 0 | 117.0319 | 169.0224 | 169.0224 | 198.851 | 256.726 | 263.2254 | 214.542 | 169.0224 | 169.0224 | 393.9681 | 169.0224 | 169.0224 | 219.3454 | 316.9845 | 327.9495 | 245.8171 | 169.0224 | 169.0224 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 14 | 3782 | 17.5 | 17.5 | 16.1583 | 16.9219 | 15 | 66 | 66 | 234.3996 | 371.9067 | 56.656 | 215.9982 | 0 | 0 | 0 | 66.136 | 114.2573 | 95.4482 | 20.7269 | 0 | 200.0933 | 158.8462 | 158.8462 | 158.8462 | 225.1492 | 273.3919 | 254.5354 | 179.6254 | 158.8462 | 371.9067 | 158.8462 | 158.8462 | 158.8462 | 291.2851 | 387.6492 | 349.9836 | 200.3523 | 158.8462 | 572 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 15 | 3783 | 18.6 | 18.6 | 16.1583 | 16.9219 | 15 | 65 | 65 | 657.6178 | 198.6918 | 49.9902 | 236.4322 | 0 | 0 | 0 | 56.5573 | 292.4415 | 357.0175 | 212.4575 | 0 | 526.3082 | 132.7713 | 132.7713 | 132.7713 | 145.0001 | 196.0027 | 209.9652 | 178.7086 | 132.7713 | 198.6918 | 132.7713 | 132.7713 | 132.7713 | 201.5574 | 488.4442 | 566.9827 | 391.1661 | 132.7713 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 16 | 3784 | 19.1 | 19.1 | 16.1583 | 16.9219 | 15 | 63 | 63 | 419.1876 | 259.0423 | 41.6857 | 252.394 | 0 | 0 | 0 | 0 | 149.0149 | 264.1566 | 224.559 | 53.4178 | 298.9577 | 134.3972 | 134.3972 | 134.3972 | 134.3972 | 200.2323 | 251.1022 | 233.6079 | 157.9973 | 259.0423 | 134.3972 | 134.3972 | 134.3972 | 134.3972 | 349.2471 | 515.2588 | 458.1669 | 211.415 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 17 | 3785 | 19.2 | 19.2 | 16.1583 | 16.9219 | 15 | 61 | 61 | 364.8658 | 231.7307 | 32.6558 | 265.5903 | 0 | 0 | 0 | 0 | 82.4181 | 241.9279 | 259.7197 | 125.3711 | 218.2693 | 119.9814 | 119.9814 | 119.9814 | 119.9814 | 157.7964 | 230.9826 | 239.1458 | 177.5041 | 231.7307 | 119.9814 | 119.9814 | 119.9814 | 119.9814 | 240.2145 | 472.9106 | 498.8655 | 302.8753 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 7 | 18 | 3786 | 18.8 | 18.8 | 16.1583 | 16.9219 | 15 | 66 | 66 | 58.8491 | 200.7366 | 23.4609 | 277.327 | 0 | 0 | 0 | 0 | 3.8095 | 37.6248 | 49.4 | 32.2373 | 27.2634 | 94.2795 | 94.2795 | 94.2795 | 94.2795 | 99.1187 | 142.0739 | 157.0318 | 135.2303 | 200.7366 | 94.2795 | 94.2795 | 94.2795 | 94.2795 | 102.9282 | 179.6987 | 206.4318 | 167.4676 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 19 | 3787 | 19 | 19 | 16.1583 | 16.9219 | 15 | 64 | 64 | 159.4101 | 143.3808 | 14.4942 | 288.4809 | 18.6493 | 0 | 0 | 0 | 0 | 89.3703 | 145.0379 | 115.7444 | 50.6192 | 82.7301 | 72.4259 | 72.4259 | 72.4259 | 72.4259 | 121.8054 | 152.5633 | 136.3778 | 143.3808 | 101.3795 | 72.4259 | 72.4259 | 72.4259 | 72.4259 | 211.1756 | 297.6013 | 252.1222 | 194 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 20 | 3788 | 17.7 | 17.7 | 16.1583 | 16.9219 | 15 | 73 | 73 | 11.9978 | 58.9494 | 6.093 | 299.6599 | 3.6821 | 0 | 0 | 0 | 0 | 5.1865 | 11.0169 | 10.3938 | 2.0506 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 58.9494 | 32.9225 | 29.2404 | 29.2404 | 29.2404 | 29.2404 | 34.4269 | 40.2574 | 39.6342 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 21 | 3789 | 16.3 | 16.3 | 16.1583 | 16.9219 | 15 | 80 | 80 | 2.1909 | 5.9269 | -1.4023 | 311.3026 | 1.078 | 0 | 0 | 0 | 0 | 0.57631 | 1.8931 | 2.1009 | 0.07309 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 5.9269 | 4.2512 | 3.1731 | 3.1731 | 3.1731 | 3.1731 | 3.7495 | 5.0662 | 5.274 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 22 | 3790 | 16.8 | 16.8 | 16.1583 | 16.9219 | 15 | 77 | 77 | 0 | 0 | -7.6234 | 323.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 23 | 3791 | 16.3 | 16.3 | 16.1583 | 16.9219 | 15 | 82 | 82 | 0 | 0 | -12.184 | 336.9609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 7 | 24 | 3792 | 14.3 | 14.3 | 15.275 | 16.7549 | 15 | 95 | 95 | 0 | 0 | -14.7322 | 350.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 1 | 3793 | 13.2 | 13.2 | 15.275 | 16.7549 | 15 | 95 | 95 | 0 | 0 | -15.0382 | 5.2534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 2 | 3794 | 11.9 | 11.9 | 15.275 | 16.7549 | 15 | 93 | 93 | 0 | 0 | -12.9874 | 19.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 3 | 3795 | 11.6 | 11.6 | 15.275 | 16.7549 | 15 | 93 | 93 | 0 | 0 | -8.9421 | 32.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 4 | 3796 | 11.2 | 11.2 | 15.275 | 16.7549 | 15 | 94 | 94 | 0 | 0 | -3.1358 | 45.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 5 | 3797 | 11.3 | 11.3 | 15.275 | 16.7549 | 15 | 95 | 95 | 0 | 0 | 4.0486 | 57.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 6 | 3798 | 12 | 12 | 15.275 | 16.7549 | 15 | 94 | 94 | 0.62648 | 13.9088 | 12.2358 | 68.4677 | 0.33845 | 0.61079 | 0.52533 | 0.13215 | 0 | 0 | 0 | 0 | 0.091208 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 13.9088 | 7.0409 | 7.3132 | 7.2278 | 6.8346 | 6.7024 | 6.7024 | 6.7024 | 6.7024 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 7 | 3799 | 12.7 | 12.7 | 15.275 | 16.7549 | 15 | 90 | 90 | 1.5471 | 43.5495 | 21.0798 | 79.5701 | 0.55494 | 1.3869 | 1.4065 | 0.60212 | 0 | 0 | 0 | 0 | 0.45047 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 43.5495 | 21.8372 | 22.6692 | 22.6888 | 21.8844 | 21.2823 | 21.2823 | 21.2823 | 21.2823 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 8 | 8 | 3800 | 13.3 | 13.3 | 15.275 | 16.7549 | 15 | 82 | 82 | 15.101 | 157.3899 | 30.2472 | 91.0705 | 2.5508 | 11.6025 | 13.8576 | 7.9951 | 0 | 0 | 0 | 0 | 6.6101 | 82.1188 | 122.0624 | 132.0138 | 106.1435 | 70.8625 | 70.8625 | 70.8625 | 70.8625 | 157.3899 | 84.6697 | 133.6649 | 145.8714 | 114.1386 | 70.8625 | 70.8625 | 70.8625 | 70.8625 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 9 | 3801 | 14 | 14 | 15.275 | 16.7549 | 15 | 80 | 80 | 56.7632 | 248.3433 | 39.3687 | 103.7594 | 0 | 34.0194 | 49.0269 | 35.3151 | 0.91615 | 0 | 0 | 0 | 32.6567 | 111.6689 | 182.7435 | 214.0977 | 185.4504 | 113.583 | 111.6689 | 111.6689 | 111.6689 | 248.3433 | 111.6689 | 216.763 | 263.1246 | 220.7655 | 114.4992 | 111.6689 | 111.6689 | 111.6689 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 10 | 3802 | 14.3 | 14.3 | 15.275 | 16.7549 | 15 | 65 | 65 | 38.6905 | 287.1268 | 47.9448 | 118.8146 | 0 | 15.5128 | 29.0525 | 25.5737 | 7.1141 | 0 | 0 | 0 | 26.8732 | 127.7037 | 173.7392 | 213.9195 | 203.5958 | 148.8155 | 127.7037 | 127.7037 | 127.7037 | 287.1268 | 127.7037 | 189.252 | 242.972 | 229.1695 | 155.9297 | 127.7037 | 127.7037 | 127.7037 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 11 | 3803 | 15.5 | 15.5 | 15.275 | 16.7549 | 15 | 66 | 66 | 80.9124 | 350.2929 | 55.1782 | 137.8872 | 0 | 15.1078 | 47.4882 | 52.0507 | 26.1226 | 0 | 0 | 0 | 63.7071 | 154.9432 | 180.3252 | 234.7264 | 242.3916 | 198.8308 | 154.9432 | 154.9432 | 154.9432 | 350.2929 | 154.9432 | 195.4329 | 282.2146 | 294.4424 | 224.9535 | 154.9432 | 154.9432 | 154.9432 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 12 | 3804 | 15.4 | 15.4 | 15.275 | 16.7549 | 15 | 59 | 59 | 46.2528 | 357.8098 | 59.7985 | 162.3114 | 0 | 0 | 17.7114 | 26.378 | 19.5928 | 1.3303 | 0 | 0 | 39.1902 | 155.6405 | 155.6405 | 205.1896 | 229.4353 | 210.4529 | 159.3622 | 155.6405 | 155.6405 | 357.8098 | 155.6405 | 155.6405 | 222.901 | 255.8132 | 230.0457 | 160.6926 | 155.6405 | 155.6405 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 13 | 3805 | 16.9 | 16.9 | 15.275 | 16.7549 | 15 | 50 | 50 | 204.7418 | 385.8286 | 60.4045 | 190.2226 | 0 | 0 | 31.2941 | 91.5128 | 98.1246 | 47.2563 | 0 | 0 | 178.1714 | 172.5677 | 172.5677 | 201.7355 | 257.8627 | 264.0252 | 216.6132 | 172.5677 | 172.5677 | 385.8286 | 172.5677 | 172.5677 | 233.0296 | 349.3755 | 362.1499 | 263.8696 | 172.5677 | 172.5677 | 564 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 14 | 3806 | 17 | 17 | 15.275 | 16.7549 | 15 | 46 | 46 | 403.2194 | 316.4565 | 56.761 | 215.9982 | 0 | 0 | 0 | 113.587 | 195.978 | 163.5677 | 35.3417 | 0 | 344.5435 | 151.8531 | 151.8531 | 151.8531 | 214.51 | 259.9585 | 242.0803 | 171.3483 | 151.8531 | 316.4565 | 151.8531 | 151.8531 | 151.8531 | 328.097 | 455.9365 | 405.648 | 206.69 | 151.8531 | 661 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 15 | 3807 | 17.2 | 17.2 | 15.275 | 16.7549 | 15 | 50 | 50 | 519.622 | 252.6781 | 50.0934 | 236.4624 | 0 | 0 | 0 | 44.5647 | 230.4311 | 281.3141 | 167.4071 | 0 | 416.3219 | 140.7132 | 140.7132 | 140.7132 | 156.704 | 223.3971 | 241.6551 | 200.7827 | 140.7132 | 252.6781 | 140.7132 | 140.7132 | 140.7132 | 201.2687 | 453.8282 | 522.9692 | 368.1898 | 140.7132 | 669 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 16 | 3808 | 17.3 | 17.3 | 15.275 | 16.7549 | 15 | 47 | 47 | 470.1569 | 242.2515 | 41.7865 | 252.4336 | 0 | 0 | 0 | 0 | 166.6421 | 295.6079 | 251.4106 | 59.9404 | 335.7485 | 132.2393 | 132.2393 | 132.2393 | 132.2393 | 194.956 | 243.493 | 226.8591 | 154.7982 | 242.2515 | 132.2393 | 132.2393 | 132.2393 | 132.2393 | 361.5981 | 539.1009 | 478.2697 | 214.7386 | 578 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 17 | 3809 | 17.9 | 17.9 | 15.275 | 16.7549 | 15 | 48 | 48 | 404.5899 | 221.5556 | 32.7553 | 265.63 | 0 | 0 | 0 | 0 | 91.049 | 267.7509 | 287.6079 | 138.9881 | 242.4444 | 118.6819 | 118.6819 | 118.6819 | 118.6819 | 155.3214 | 226.429 | 234.4198 | 174.6129 | 221.5556 | 118.6819 | 118.6819 | 118.6819 | 118.6819 | 246.3704 | 494.1799 | 522.0277 | 313.601 | 464 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 8 | 18 | 3810 | 17.8 | 17.8 | 15.275 | 16.7549 | 15 | 52 | 52 | 478.9377 | 155.5868 | 23.5606 | 277.363 | 0 | 0 | 0 | 0 | 30.6905 | 305.6828 | 401.6103 | 262.2799 | 222.4132 | 93.5905 | 93.5905 | 93.5905 | 93.5905 | 101.8217 | 175.5748 | 201.3027 | 163.9341 | 155.5868 | 93.5905 | 93.5905 | 93.5905 | 93.5905 | 132.5121 | 481.2576 | 602.9129 | 426.2141 | 378 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 19 | 3811 | 17.2 | 17.2 | 15.275 | 16.7549 | 15 | 56 | 56 | 202.3425 | 141.5024 | 14.5951 | 288.511 | 23.7695 | 0 | 0 | 0 | 0 | 113.2615 | 183.9455 | 146.8766 | 64.4976 | 87.2676 | 73.5456 | 73.5456 | 73.5456 | 73.5456 | 138.9309 | 179.7363 | 158.3367 | 141.5024 | 111.0371 | 73.5456 | 73.5456 | 73.5456 | 73.5456 | 252.1924 | 363.6818 | 305.2133 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 20 | 3812 | 16.2 | 16.2 | 15.275 | 16.7549 | 15 | 57 | 57 | 178.3226 | 77.2873 | 6.1956 | 299.6824 | 54.7882 | 0 | 0 | 0 | 0 | 76.9698 | 163.64 | 154.4521 | 30.7127 | 68.8937 | 42.0008 | 42.0008 | 42.0008 | 42.0008 | 79.7816 | 122.3239 | 117.814 | 77.2873 | 123.682 | 42.0008 | 42.0008 | 42.0008 | 42.0008 | 156.7515 | 285.964 | 272.2661 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 21 | 3813 | 14.7 | 14.7 | 15.275 | 16.7549 | 15 | 58 | 58 | 27.3175 | 14.2632 | -1.2981 | 311.3153 | 13.4484 | 0 | 0 | 0 | 0 | 7.1743 | 23.5944 | 26.1932 | 10.7368 | 16.0122 | 8.7738 | 8.7738 | 8.7738 | 8.7738 | 12.6353 | 21.4732 | 22.872 | 14.2632 | 29.4607 | 8.7738 | 8.7738 | 8.7738 | 8.7738 | 19.8096 | 45.0676 | 49.0652 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 22 | 3814 | 13.8 | 13.8 | 15.275 | 16.7549 | 15 | 63 | 63 | 0 | 0 | -7.5184 | 323.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 23 | 3815 | 13.2 | 13.2 | 15.275 | 16.7549 | 15 | 72 | 72 | 0 | 0 | -12.08 | 336.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 8 | 24 | 3816 | 12.7 | 12.7 | 14.5125 | 16.2913 | 15 | 74 | 74 | 0 | 0 | -14.6318 | 350.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 1 | 3817 | 12.3 | 12.3 | 14.5125 | 16.2913 | 15 | 72 | 72 | 0 | 0 | -14.9443 | 5.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 2 | 3818 | 11.8 | 11.8 | 14.5125 | 16.2913 | 15 | 74 | 74 | 0 | 0 | -12.9089 | 19.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 3 | 3819 | 11.3 | 11.3 | 14.5125 | 16.2913 | 15 | 80 | 80 | 0 | 0 | -8.8734 | 32.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 4 | 3820 | 10.6 | 10.6 | 14.5125 | 16.2913 | 15 | 85 | 85 | 0 | 0 | -3.0765 | 45.3123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 5 | 3821 | 10.8 | 10.8 | 14.5125 | 16.2913 | 15 | 87 | 87 | 58.2578 | 5.288 | 4.0995 | 57.1226 | 40.9103 | 58.173 | 41.3587 | 0.31712 | 0 | 0 | 0 | 0 | 0.71198 | 3.8729 | 4.3665 | 3.8858 | 2.7123 | 2.7033 | 2.7033 | 2.7033 | 2.7033 | 5.288 | 44.7832 | 62.5395 | 45.2445 | 3.0295 | 2.7033 | 2.7033 | 2.7033 | 2.7033 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 6 | 3822 | 11.7 | 11.7 | 14.5125 | 16.2913 | 15 | 86 | 86 | 70.5581 | 64.6399 | 12.2804 | 68.3769 | 38.204 | 68.8082 | 59.1055 | 14.7796 | 0 | 0 | 0 | 0 | 10.3601 | 134.7574 | 220.6299 | 193.4049 | 69.0304 | 27.5603 | 27.5603 | 27.5603 | 27.5603 | 64.6399 | 172.9614 | 289.4381 | 252.5104 | 83.81 | 27.5603 | 27.5603 | 27.5603 | 27.5603 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 7 | 3823 | 13.1 | 13.1 | 14.5125 | 16.2913 | 15 | 83 | 83 | 216.4694 | 128.7235 | 21.1202 | 79.4729 | 77.9436 | 194.1539 | 196.6315 | 83.925 | 0 | 0 | 0 | 0 | 63.2765 | 117.8722 | 199.8443 | 201.5919 | 122.0913 | 62.8925 | 62.8925 | 62.8925 | 62.8925 | 128.7235 | 195.8157 | 393.9982 | 398.2234 | 206.0164 | 62.8925 | 62.8925 | 62.8925 | 62.8925 | 192 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 9 | 8 | 3824 | 14.1 | 14.1 | 14.5125 | 16.2913 | 15 | 78 | 78 | 282.0042 | 184.263 | 30.2863 | 90.9649 | 48.0612 | 216.8657 | 258.6333 | 148.8969 | 0 | 0 | 0 | 0 | 123.737 | 119.6765 | 202.0587 | 222.4426 | 168.8877 | 96.2211 | 96.2211 | 96.2211 | 96.2211 | 184.263 | 167.7377 | 418.9245 | 481.0759 | 317.7846 | 96.2211 | 96.2211 | 96.2211 | 96.2211 | 308 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 9 | 3825 | 15.1 | 15.1 | 14.5125 | 16.2913 | 15 | 70 | 70 | 201.528 | 255.8646 | 39.41 | 103.6426 | 0 | 120.963 | 173.998 | 125.1074 | 2.9306 | 0 | 0 | 0 | 116.1354 | 121.9854 | 216.5832 | 258.0587 | 219.8243 | 124.2772 | 121.9854 | 121.9854 | 121.9854 | 255.8646 | 121.9854 | 337.5462 | 432.0568 | 344.9318 | 127.2078 | 121.9854 | 121.9854 | 121.9854 | 372 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 10 | 3826 | 17.1 | 17.1 | 14.5125 | 16.2913 | 15 | 50 | 50 | 534.7563 | 214.1029 | 47.9932 | 118.6852 | 0 | 215.0004 | 401.5076 | 352.8171 | 97.4511 | 0 | 0 | 0 | 371.8971 | 129.6107 | 193.2639 | 248.4815 | 234.0661 | 158.4622 | 129.6107 | 129.6107 | 129.6107 | 214.1029 | 129.6107 | 408.2643 | 649.989 | 586.8832 | 255.9133 | 129.6107 | 129.6107 | 129.6107 | 586 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 11 | 3827 | 13.6 | 13.6 | 14.5125 | 16.2913 | 15 | 69 | 69 | 1.5447 | 117.7825 | 55.2398 | 137.7509 | 0 | 0.29039 | 0.90687 | 0.99211 | 0.49619 | 0 | 0 | 0 | 1.2175 | 58.2529 | 58.2529 | 58.2529 | 58.2529 | 58.2529 | 58.2529 | 58.2529 | 58.2529 | 117.7825 | 58.2529 | 58.5433 | 59.1597 | 59.245 | 58.7491 | 58.2529 | 58.2529 | 58.2529 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 12 | 3828 | 14.4 | 14.4 | 14.5125 | 16.2913 | 15 | 66 | 66 | 6.7403 | 255.2836 | 59.878 | 162.1932 | 0 | 0 | 2.5838 | 3.8385 | 2.8446 | 0.18443 | 0 | 0 | 5.7164 | 125.5593 | 125.5593 | 131.9871 | 135.1084 | 132.636 | 126.0181 | 125.5593 | 125.5593 | 255.2836 | 125.5593 | 125.5593 | 134.5709 | 138.9469 | 135.4806 | 126.2025 | 125.5593 | 125.5593 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 13 | 3829 | 17.3 | 17.3 | 14.5125 | 16.2913 | 15 | 49 | 49 | 688.4734 | 203.3439 | 60.4988 | 190.1595 | 0 | 0 | 105.6585 | 307.3173 | 328.9537 | 157.8935 | 0 | 0 | 599.6561 | 140.4256 | 140.4256 | 162.7749 | 205.4305 | 210.0072 | 173.8238 | 140.4256 | 140.4256 | 203.3439 | 140.4256 | 140.4256 | 268.4334 | 512.7478 | 538.9609 | 331.7174 | 140.4256 | 140.4256 | 803 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 14 | 3830 | 17 | 17 | 14.5125 | 16.2913 | 15 | 53 | 53 | 69.8932 | 376.2231 | 56.8601 | 215.992 | 0 | 0 | 0 | 19.663 | 33.8787 | 28.2487 | 6.071 | 0 | 59.7769 | 163.9236 | 163.9236 | 163.9236 | 201.896 | 229.3489 | 218.4765 | 175.6477 | 163.9236 | 376.2231 | 163.9236 | 163.9236 | 163.9236 | 221.559 | 263.2276 | 246.7252 | 181.7188 | 163.9236 | 436 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 15 | 3831 | 18 | 18 | 14.5125 | 16.2913 | 15 | 47 | 47 | 593.9366 | 223.6541 | 50.1915 | 236.4859 | 0 | 0 | 0 | 50.8385 | 262.7113 | 320.6914 | 190.8148 | 0 | 476.3459 | 135.6361 | 135.6361 | 135.6361 | 148.834 | 203.8374 | 218.8894 | 185.1727 | 135.6361 | 223.6541 | 135.6361 | 135.6361 | 135.6361 | 199.6725 | 466.5487 | 539.5808 | 375.9875 | 135.6361 | 700 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 16 | 3832 | 17.9 | 17.9 | 14.5125 | 16.2913 | 15 | 48 | 48 | 536.2244 | 219.605 | 41.8826 | 252.4668 | 0 | 0 | 0 | 0 | 189.5524 | 336.4287 | 286.2297 | 68.3612 | 383.395 | 127.3012 | 127.3012 | 127.3012 | 127.3012 | 180.1161 | 221.0402 | 207.0533 | 146.3487 | 219.605 | 127.3012 | 127.3012 | 127.3012 | 127.3012 | 369.6685 | 557.469 | 493.283 | 214.7099 | 603 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 17 | 3833 | 17.9 | 17.9 | 14.5125 | 16.2913 | 15 | 46 | 46 | 571.5933 | 173.9412 | 32.8504 | 265.6638 | 0 | 0 | 0 | 0 | 128.2035 | 377.5898 | 405.7891 | 196.2826 | 343.0588 | 109.9833 | 109.9833 | 109.9833 | 109.9833 | 138.662 | 194.449 | 200.7571 | 153.8911 | 173.9412 | 109.9833 | 109.9833 | 109.9833 | 109.9833 | 266.8656 | 572.0388 | 606.5461 | 350.1738 | 517 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 18 | 3834 | 18.1 | 18.1 | 14.5125 | 16.2913 | 15 | 46 | 46 | 208.7148 | 205.8596 | 23.6558 | 277.3934 | 0 | 0 | 0 | 0 | 13.2572 | 133.0028 | 174.8372 | 114.2544 | 97.1404 | 102.8721 | 102.8721 | 102.8721 | 102.8721 | 109.8926 | 173.3055 | 195.4595 | 163.377 | 205.8596 | 102.8721 | 102.8721 | 102.8721 | 102.8721 | 123.1497 | 306.3083 | 370.2967 | 277.6314 | 303 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 19 | 3835 | 17.1 | 17.1 | 14.5125 | 16.2913 | 15 | 48 | 48 | 501.0274 | 103.7295 | 14.6913 | 288.5361 | 59.0557 | 0 | 0 | 0 | 0 | 280.0538 | 455.1117 | 363.5713 | 160.2705 | 77.8535 | 66.2301 | 66.2301 | 66.2301 | 66.2301 | 121.3504 | 155.8054 | 137.7884 | 103.7295 | 136.9093 | 66.2301 | 66.2301 | 66.2301 | 66.2301 | 401.4043 | 610.917 | 501.3596 | 264 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 20 | 3836 | 16.1 | 16.1 | 14.5125 | 16.2913 | 15 | 48 | 48 | 311.789 | 70.9181 | 6.2932 | 299.7004 | 95.878 | 0 | 0 | 0 | 0 | 134.401 | 285.9498 | 269.993 | 54.0819 | 68.7933 | 41.4625 | 41.4625 | 41.4625 | 41.4625 | 79.7746 | 122.9747 | 118.4261 | 70.9181 | 164.6714 | 41.4625 | 41.4625 | 41.4625 | 41.4625 | 214.1756 | 408.9245 | 388.4192 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 21 | 3837 | 14 | 14 | 14.5125 | 16.2913 | 15 | 62 | 62 | 81.4339 | 16.0609 | -1.1992 | 311.324 | 40.1044 | 0 | 0 | 0 | 0 | 21.3582 | 70.3096 | 78.0745 | 2.9391 | 32.9869 | 9.2283 | 9.2283 | 9.2283 | 9.2283 | 21.8813 | 50.8809 | 55.481 | 16.0609 | 73.0913 | 9.2283 | 9.2283 | 9.2283 | 9.2283 | 43.2395 | 121.1905 | 133.5555 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 22 | 3838 | 11 | 11 | 14.5125 | 16.2913 | 15 | 80 | 80 | 0 | 0 | -7.4193 | 323.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 23 | 3839 | 9 | 9 | 14.5125 | 16.2913 | 15 | 93 | 93 | 0 | 0 | -11.9823 | 336.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 9 | 24 | 3840 | 8.1 | 8.1 | 14.0583 | 15.6884 | 15 | 97 | 97 | 0 | 0 | -14.538 | 350.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 1 | 3841 | 7.3 | 7.3 | 14.0583 | 15.6884 | 15 | 97 | 97 | 0 | 0 | -14.8571 | 5.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 2 | 3842 | 6.6 | 6.6 | 14.0583 | 15.6884 | 15 | 99 | 99 | 0 | 0 | -12.8372 | 19.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 3 | 3843 | 6.1 | 6.1 | 14.0583 | 15.6884 | 15 | 99 | 99 | 0 | 0 | -8.8112 | 32.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 4 | 3844 | 6.1 | 6.1 | 14.0583 | 15.6884 | 15 | 99 | 99 | 0 | 0 | -3.0236 | 45.2351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 5 | 3845 | 7.2 | 7.2 | 14.0583 | 15.6884 | 15 | 99 | 99 | 13.2011 | 4.4553 | 4.1445 | 57.0403 | 9.2833 | 13.1826 | 9.3598 | 0.054095 | 0 | 0 | 0 | 0 | 6.5447 | 5.4439 | 6.7266 | 5.4691 | 2.408 | 2.3902 | 2.3902 | 2.3902 | 2.3902 | 4.4553 | 14.7272 | 19.9093 | 14.8289 | 2.4621 | 2.3902 | 2.3902 | 2.3902 | 2.3902 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 6 | 3846 | 9.6 | 9.6 | 14.0583 | 15.6884 | 15 | 95 | 95 | 18.8827 | 55.2057 | 12.3191 | 68.2898 | 10.2463 | 18.419 | 15.8022 | 3.9286 | 0 | 0 | 0 | 0 | 2.7943 | 103.9967 | 167.9727 | 147.4882 | 54.5427 | 23.7895 | 23.7895 | 23.7895 | 23.7895 | 55.2057 | 114.243 | 186.3918 | 163.2904 | 58.4713 | 23.7895 | 23.7895 | 23.7895 | 23.7895 | 58 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 7 | 3847 | 10.7 | 10.7 | 14.0583 | 15.6884 | 15 | 92 | 92 | 1.0206 | 35.7006 | 21.155 | 79.3798 | 0.36885 | 0.91587 | 0.92639 | 0.39424 | 0 | 0 | 0 | 0 | 0.29942 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 35.7006 | 17.628 | 18.175 | 18.1855 | 17.6534 | 17.2592 | 17.2592 | 17.2592 | 17.2592 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 10 | 8 | 3848 | 13.5 | 13.5 | 14.0583 | 15.6884 | 15 | 77 | 77 | 13.5444 | 155.0439 | 30.3197 | 90.8637 | 2.328 | 10.4251 | 12.4153 | 7.1328 | 0 | 0 | 0 | 0 | 5.9561 | 80.8598 | 118.3498 | 127.5647 | 103.1064 | 70.081 | 70.081 | 70.081 | 70.081 | 155.0439 | 83.1877 | 128.7749 | 139.98 | 110.2392 | 70.081 | 70.081 | 70.081 | 70.081 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 9 | 3849 | 15.7 | 15.7 | 14.0583 | 15.6884 | 15 | 60 | 60 | 182.9613 | 258.4018 | 39.4456 | 103.5306 | 0 | 109.9817 | 157.9183 | 113.3486 | 2.3808 | 0 | 0 | 0 | 105.5982 | 121.7812 | 217.7531 | 259.5835 | 220.6911 | 123.8587 | 121.7812 | 121.7812 | 121.7812 | 258.4018 | 121.7812 | 327.7348 | 417.5018 | 334.0397 | 126.2395 | 121.7812 | 121.7812 | 121.7812 | 364 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 10 | 3850 | 16.2 | 16.2 | 14.0583 | 15.6884 | 15 | 54 | 54 | 289.4953 | 290.4342 | 48.0356 | 118.5605 | 0 | 116.706 | 217.3516 | 190.6756 | 52.3043 | 0 | 0 | 0 | 201.5658 | 141.8786 | 216.3402 | 280.5548 | 263.5348 | 175.2502 | 141.8786 | 141.8786 | 141.8786 | 290.4342 | 141.8786 | 333.0463 | 497.9064 | 454.2103 | 227.5545 | 141.8786 | 141.8786 | 141.8786 | 492 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 11 | 3851 | 17.6 | 17.6 | 14.0583 | 15.6884 | 15 | 52 | 52 | 242.7412 | 341.4919 | 55.2949 | 137.6182 | 0 | 45.9351 | 142.562 | 155.6781 | 77.6 | 0 | 0 | 0 | 191.5081 | 155.0519 | 194.9956 | 279.0194 | 290.4247 | 222.5305 | 155.0519 | 155.0519 | 155.0519 | 341.4919 | 155.0519 | 240.9306 | 421.5814 | 446.1028 | 300.1305 | 155.0519 | 155.0519 | 155.0519 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 12 | 3852 | 17.8 | 17.8 | 14.0583 | 15.6884 | 15 | 44 | 44 | 658.5179 | 210.0418 | 59.9506 | 162.0757 | 0 | 0 | 252.7274 | 374.5372 | 276.9482 | 17.1267 | 0 | 0 | 558.9582 | 140.1791 | 140.1791 | 196.687 | 223.9228 | 202.1026 | 144.0085 | 140.1791 | 140.1791 | 210.0418 | 140.1791 | 140.1791 | 449.4144 | 598.46 | 479.0508 | 161.1351 | 140.1791 | 140.1791 | 769 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 13 | 3853 | 18.4 | 18.4 | 14.0583 | 15.6884 | 15 | 44 | 44 | 507.0129 | 280.0351 | 60.5864 | 190.0929 | 0 | 0 | 78.1357 | 226.0605 | 241.5621 | 115.5599 | 0 | 0 | 441.9649 | 150.5139 | 150.5139 | 181.8913 | 241.2941 | 247.5192 | 196.9199 | 150.5139 | 150.5139 | 280.0351 | 150.5139 | 150.5139 | 260.027 | 467.3546 | 489.0812 | 312.4798 | 150.5139 | 150.5139 | 722 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 14 | 3854 | 18.9 | 18.9 | 14.0583 | 15.6884 | 15 | 49 | 49 | 42.4121 | 357.6961 | 56.9534 | 215.9796 | 0 | 0 | 0 | 11.9194 | 20.5067 | 17.0815 | 3.6502 | 0 | 36.3039 | 155.16 | 155.16 | 155.16 | 190.2537 | 215.5371 | 205.4524 | 165.9071 | 155.16 | 357.6961 | 155.16 | 155.16 | 155.16 | 202.1731 | 236.0438 | 222.5339 | 169.5573 | 155.16 | 394 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 15 | 3855 | 18.9 | 18.9 | 14.0583 | 15.6884 | 15 | 46 | 46 | 387.9065 | 302.6021 | 50.2844 | 236.5026 | 0 | 0 | 0 | 33.1656 | 171.1784 | 208.9172 | 124.2752 | 0 | 311.3979 | 146.3265 | 146.3265 | 146.3265 | 164.4444 | 239.8388 | 260.4549 | 214.2162 | 146.3265 | 302.6021 | 146.3265 | 146.3265 | 146.3265 | 197.61 | 411.0172 | 469.3722 | 338.4914 | 146.3265 | 614 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 16 | 3856 | 16.8 | 16.8 | 14.0583 | 15.6884 | 15 | 60 | 60 | 6.6257 | 214.2574 | 41.974 | 252.4935 | 0 | 0 | 0 | 0 | 2.3366 | 4.1487 | 3.5305 | 0.84425 | 4.7426 | 106.9579 | 106.9579 | 106.9579 | 106.9579 | 109.6278 | 111.6984 | 110.9921 | 107.9226 | 214.2574 | 106.9579 | 106.9579 | 106.9579 | 106.9579 | 111.9644 | 115.847 | 114.5226 | 108.7669 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 17 | 3857 | 17.8 | 17.8 | 14.0583 | 15.6884 | 15 | 56 | 56 | 22.5176 | 230.4658 | 32.941 | 265.6916 | 0 | 0 | 0 | 0 | 5.0358 | 14.85 | 15.9653 | 7.7283 | 13.5342 | 111.2161 | 111.2161 | 111.2161 | 111.2161 | 117.3908 | 129.4247 | 130.7922 | 120.6922 | 230.4658 | 111.2161 | 111.2161 | 111.2161 | 111.2161 | 122.4266 | 144.2747 | 146.7574 | 128.4205 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 18 | 3858 | 13.2 | 13.2 | 14.0583 | 15.6884 | 15 | 85 | 85 | 3.5013 | 104.3671 | 23.7465 | 277.4185 | 0 | 0 | 0 | 0 | 0.22075 | 2.228 | 2.9301 | 1.9158 | 1.6329 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 104.3671 | 51.6225 | 51.6225 | 51.6225 | 51.6225 | 51.8433 | 53.8505 | 54.5526 | 53.5383 | 106 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 19 | 3859 | 12.8 | 12.8 | 14.0583 | 15.6884 | 15 | 92 | 92 | 0.51594 | 27.8344 | 14.7828 | 288.5562 | 0.060975 | 0 | 0 | 0 | 0 | 0.28802 | 0.4683 | 0.37426 | 0.16558 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 27.8344 | 13.2535 | 13.1925 | 13.1925 | 13.1925 | 13.1925 | 13.4805 | 13.6608 | 13.5667 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 20 | 3860 | 12.6 | 12.6 | 14.0583 | 15.6884 | 15 | 91 | 91 | 0.64262 | 16.8878 | 6.3858 | 299.7137 | 0.19773 | 0 | 0 | 0 | 0 | 0.2767 | 0.58904 | 0.55634 | 0.11219 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 16.8878 | 8.1453 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 8.2242 | 8.5366 | 8.5039 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 21 | 3861 | 12.3 | 12.3 | 14.0583 | 15.6884 | 15 | 94 | 94 | 0.43822 | 2.9837 | -1.1058 | 311.3286 | 0.21586 | 0 | 0 | 0 | 0 | 0.11482 | 0.37824 | 0.42009 | 0.01635 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 2.9837 | 1.5951 | 1.3793 | 1.3793 | 1.3793 | 1.3793 | 1.4941 | 1.7575 | 1.7994 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 22 | 3862 | 12.4 | 12.4 | 14.0583 | 15.6884 | 15 | 94 | 94 | 0 | 0 | -7.3259 | 323.6914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 23 | 3863 | 10.8 | 10.8 | 14.0583 | 15.6884 | 15 | 91 | 91 | 0 | 0 | -11.8908 | 336.9087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 10 | 24 | 3864 | 10.5 | 10.5 | 12.9083 | 14.7782 | 15 | 94 | 94 | 0 | 0 | -14.4507 | 350.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 1 | 3865 | 9.5 | 9.5 | 12.9083 | 14.7782 | 15 | 95 | 95 | 0 | 0 | -14.7766 | 5.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 2 | 3866 | 9.1 | 9.1 | 12.9083 | 14.7782 | 15 | 96 | 96 | 0 | 0 | -12.7721 | 19.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 3 | 3867 | 9 | 9 | 12.9083 | 14.7782 | 15 | 95 | 95 | 0 | 0 | -8.7555 | 32.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 4 | 3868 | 8.8 | 8.8 | 12.9083 | 14.7782 | 15 | 96 | 96 | 0 | 0 | -2.9769 | 45.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 5 | 3869 | 8.7 | 8.7 | 12.9083 | 14.7782 | 15 | 95 | 95 | 15.1158 | 6.5591 | 4.1834 | 56.9613 | 10.6441 | 15.0953 | 10.7039 | 0.042278 | 0 | 0 | 0 | 0 | 1.4409 | 7.1896 | 9.0692 | 7.2149 | 2.7129 | 2.695 | 2.695 | 2.695 | 2.695 | 6.5591 | 17.8338 | 24.1645 | 17.9188 | 2.7552 | 2.695 | 2.695 | 2.695 | 2.695 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 6 | 3870 | 9.3 | 9.3 | 12.9083 | 14.7782 | 15 | 92 | 92 | 94.6863 | 66.8884 | 12.3521 | 68.2063 | 51.486 | 92.3837 | 79.1642 | 19.5715 | 0 | 0 | 0 | 0 | 14.1116 | 141.7155 | 231.5238 | 202.4949 | 71.6335 | 28.656 | 28.656 | 28.656 | 28.656 | 66.8884 | 193.2015 | 323.9074 | 281.6591 | 91.205 | 28.656 | 28.656 | 28.656 | 28.656 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 7 | 3871 | 10.8 | 10.8 | 12.9083 | 14.7782 | 15 | 88 | 88 | 339.8041 | 116.9803 | 21.1841 | 79.2908 | 123.2373 | 305.0817 | 308.2134 | 130.7979 | 0 | 0 | 0 | 0 | 100.0197 | 105.4162 | 164.8384 | 165.8617 | 107.8869 | 65.1454 | 65.1454 | 65.1454 | 65.1454 | 116.9803 | 228.6535 | 469.9201 | 474.0751 | 238.6847 | 65.1454 | 65.1454 | 65.1454 | 65.1454 | 217 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 11 | 8 | 3872 | 12.1 | 12.1 | 12.9083 | 14.7782 | 15 | 85 | 85 | 468.0482 | 149.7596 | 30.3476 | 90.7671 | 81.0972 | 360.5648 | 428.8184 | 245.876 | 0 | 0 | 0 | 0 | 206.2404 | 111.4696 | 184.0626 | 201.7918 | 154.2717 | 90.4042 | 90.4042 | 90.4042 | 90.4042 | 149.7596 | 192.5669 | 544.6274 | 630.6102 | 400.1476 | 90.4042 | 90.4042 | 90.4042 | 90.4042 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 9 | 3873 | 13.8 | 13.8 | 12.9083 | 14.7782 | 15 | 71 | 71 | 432.2632 | 206.1625 | 39.4755 | 103.4235 | 0 | 260.2193 | 372.9996 | 267.2818 | 4.9939 | 0 | 0 | 0 | 249.8375 | 116.2356 | 205.7294 | 244.5164 | 208.1583 | 117.9531 | 116.2356 | 116.2356 | 116.2356 | 206.1625 | 116.2356 | 465.9487 | 617.516 | 475.4401 | 122.947 | 116.2356 | 116.2356 | 116.2356 | 456 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 10 | 3874 | 11.8 | 11.8 | 12.9083 | 14.7782 | 15 | 76 | 76 | 14.2807 | 248.0462 | 48.0719 | 118.4407 | 0 | 5.7722 | 10.7221 | 9.3911 | 2.559 | 0 | 0 | 0 | 9.9538 | 115.985 | 134.444 | 150.2735 | 146.0172 | 124.1685 | 115.985 | 115.985 | 115.985 | 248.0462 | 115.985 | 140.2162 | 160.9956 | 155.4084 | 126.7275 | 115.985 | 115.985 | 115.985 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 11 | 3875 | 12.7 | 12.7 | 12.9083 | 14.7782 | 15 | 73 | 73 | 32.1955 | 318.5773 | 55.3436 | 137.4894 | 0 | 6.1313 | 18.9165 | 20.6207 | 10.2455 | 0 | 0 | 0 | 25.4227 | 140.1117 | 162.2628 | 208.4528 | 214.6095 | 177.1264 | 140.1117 | 140.1117 | 140.1117 | 318.5773 | 140.1117 | 168.3942 | 227.3693 | 235.2302 | 187.3719 | 140.1117 | 140.1117 | 140.1117 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 12 | 3876 | 14.2 | 14.2 | 12.9083 | 14.7782 | 15 | 64 | 64 | 371.9145 | 326.0679 | 60.0164 | 161.959 | 0 | 0 | 142.9101 | 211.2912 | 155.9008 | 9.1858 | 0 | 0 | 315.9321 | 158.8664 | 158.8664 | 238.897 | 277.1909 | 246.1719 | 164.0106 | 158.8664 | 158.8664 | 326.0679 | 158.8664 | 158.8664 | 381.8071 | 488.4821 | 402.0727 | 173.1964 | 158.8664 | 158.8664 | 642 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 13 | 3877 | 10.4 | 10.4 | 12.9083 | 14.7782 | 15 | 82 | 82 | 4.6309 | 223.9602 | 60.6674 | 190.0229 | 0 | 0 | 0.71674 | 2.0628 | 2.2005 | 1.0492 | 0 | 0 | 4.0398 | 113.5304 | 113.5304 | 114.0105 | 114.9121 | 115.0043 | 114.2332 | 113.5304 | 113.5304 | 223.9602 | 113.5304 | 113.5304 | 114.7272 | 116.9749 | 117.2048 | 115.2824 | 113.5304 | 113.5304 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 14 | 3878 | 14.3 | 14.3 | 12.9083 | 14.7782 | 15 | 71 | 71 | 290.9113 | 356.7941 | 57.0408 | 215.961 | 0 | 0 | 0 | 81.6945 | 140.3364 | 116.7711 | 24.8029 | 0 | 249.2059 | 158.8579 | 158.8579 | 158.8579 | 222.8235 | 268.7392 | 250.288 | 178.2783 | 158.8579 | 356.7941 | 158.8579 | 158.8579 | 158.8579 | 304.518 | 409.0756 | 367.0591 | 203.0812 | 158.8579 | 606 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 15 | 3879 | 15.6 | 15.6 | 12.9083 | 14.7782 | 15 | 57 | 57 | 343.3437 | 318.1393 | 50.3721 | 236.5126 | 0 | 0 | 0 | 29.3464 | 151.1936 | 184.4736 | 109.6915 | 0 | 275.8607 | 151.3362 | 151.3362 | 151.3362 | 168.884 | 241.7432 | 261.6431 | 216.9268 | 151.3362 | 318.1393 | 151.3362 | 151.3362 | 151.3362 | 198.2304 | 392.9367 | 446.1168 | 326.6183 | 151.3362 | 594 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 16 | 3880 | 15.3 | 15.3 | 12.9083 | 14.7782 | 15 | 55 | 55 | 25.0344 | 279.0621 | 42.0606 | 252.5138 | 0 | 0 | 0 | 0 | 8.8098 | 15.6457 | 13.3165 | 3.1867 | 17.9379 | 125.0313 | 125.0313 | 125.0313 | 125.0313 | 157.3057 | 182.3486 | 173.8159 | 136.7058 | 279.0621 | 125.0313 | 125.0313 | 125.0313 | 125.0313 | 166.1155 | 197.9943 | 187.1324 | 139.8925 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 17 | 3881 | 15.7 | 15.7 | 12.9083 | 14.7782 | 15 | 46 | 46 | 296.8144 | 249.3613 | 33.027 | 265.7135 | 0 | 0 | 0 | 0 | 66.2147 | 195.4423 | 210.1825 | 101.8006 | 178.6387 | 124.1756 | 124.1756 | 124.1756 | 124.1756 | 161.1669 | 233.3608 | 241.5955 | 181.0472 | 249.3613 | 124.1756 | 124.1756 | 124.1756 | 124.1756 | 227.3817 | 428.8032 | 451.778 | 282.8478 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 11 | 18 | 3882 | 15.6 | 15.6 | 12.9083 | 14.7782 | 15 | 52 | 52 | 490.6336 | 153.75 | 23.8326 | 277.4381 | 0 | 0 | 0 | 0 | 30.746 | 311.7983 | 410.2033 | 268.3168 | 229.25 | 93.4713 | 93.4713 | 93.4713 | 93.4713 | 101.4532 | 174.417 | 199.9638 | 163.1288 | 153.75 | 93.4713 | 93.4713 | 93.4713 | 93.4713 | 132.1993 | 486.2152 | 610.1671 | 431.4456 | 383 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 19 | 3883 | 14.9 | 14.9 | 12.9083 | 14.7782 | 15 | 52 | 52 | 409.5451 | 118.1732 | 14.8695 | 288.5714 | 48.4967 | 0 | 0 | 0 | 0 | 228.3772 | 371.4708 | 296.9618 | 131.8268 | 83.1609 | 70.0726 | 70.0726 | 70.0726 | 70.0726 | 131.707 | 170.3251 | 150.2166 | 118.1732 | 131.6576 | 70.0726 | 70.0726 | 70.0726 | 70.0726 | 360.0842 | 541.7959 | 447.1785 | 250 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 20 | 3884 | 13.9 | 13.9 | 12.9083 | 14.7782 | 15 | 56 | 56 | 117.1427 | 79.4261 | 6.4733 | 299.7226 | 36.0589 | 0 | 0 | 0 | 0 | 50.3922 | 107.3243 | 101.3872 | 20.5739 | 59.6083 | 41.149 | 41.149 | 41.149 | 41.149 | 66.9458 | 96.0905 | 93.0512 | 79.4261 | 95.6673 | 41.149 | 41.149 | 41.149 | 41.149 | 117.338 | 203.4148 | 194.4385 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 21 | 3885 | 10.9 | 10.9 | 12.9083 | 14.7782 | 15 | 83 | 83 | 60.3943 | 16.6791 | -1.0179 | 311.3292 | 29.7527 | 0 | 0 | 0 | 0 | 15.812 | 52.1142 | 57.8886 | 2.3209 | 29.7262 | 9.3955 | 9.3955 | 9.3955 | 9.3955 | 20.2002 | 45.0064 | 48.9522 | 16.6791 | 59.4789 | 9.3955 | 9.3955 | 9.3955 | 9.3955 | 36.0122 | 97.1205 | 106.8408 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 22 | 3886 | 8.6 | 8.6 | 12.9083 | 14.7782 | 15 | 95 | 95 | 0 | 0 | -7.2385 | 323.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 23 | 3887 | 7.3 | 7.3 | 12.9083 | 14.7782 | 15 | 98 | 98 | 0 | 0 | -11.8056 | 336.8862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 11 | 24 | 3888 | 6.5 | 6.5 | 11.6167 | 13.66 | 15 | 98 | 98 | 0 | 0 | -14.3701 | 350.8064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 1 | 3889 | 5.9 | 5.9 | 11.6167 | 13.66 | 15 | 99 | 99 | 0 | 0 | -14.7029 | 5.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 2 | 3890 | 5.5 | 5.5 | 11.6167 | 13.66 | 15 | 99 | 99 | 0 | 0 | -12.7138 | 19.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 3 | 3891 | 5.2 | 5.2 | 11.6167 | 13.66 | 15 | 99 | 99 | 0 | 0 | -8.7064 | 32.4942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 4 | 3892 | 4.8 | 4.8 | 11.6167 | 13.66 | 15 | 99 | 99 | 0 | 0 | -2.9364 | 45.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 5 | 3893 | 5 | 5 | 11.6167 | 13.66 | 15 | 100 | 100 | 17.1348 | 5.7324 | 4.2164 | 56.8854 | 12.0815 | 17.1123 | 12.1189 | 0.026425 | 0 | 0 | 0 | 0 | 0.26758 | 6.1934 | 7.8322 | 6.2056 | 2.2663 | 2.2577 | 2.2577 | 2.2577 | 2.2577 | 5.7324 | 18.2749 | 24.9445 | 18.3245 | 2.2927 | 2.2577 | 2.2577 | 2.2577 | 2.2577 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 6 | 3894 | 8.3 | 8.3 | 11.6167 | 13.66 | 15 | 95 | 95 | 91.9661 | 67.2054 | 12.3793 | 68.1266 | 50.1065 | 89.7509 | 76.8205 | 18.8897 | 0 | 0 | 0 | 0 | 13.7946 | 142.5306 | 232.5421 | 203.184 | 71.6539 | 28.7654 | 28.7654 | 28.7654 | 28.7654 | 67.2054 | 192.6371 | 322.293 | 280.0045 | 90.5435 | 28.7654 | 28.7654 | 28.7654 | 28.7654 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 7 | 3895 | 11.7 | 11.7 | 11.6167 | 13.66 | 15 | 75 | 75 | 286.5369 | 123.4052 | 21.2076 | 79.206 | 104.2694 | 257.3839 | 259.7265 | 109.9248 | 0 | 0 | 0 | 0 | 84.5948 | 106.9156 | 166.9103 | 167.8282 | 109.1316 | 66.0599 | 66.0599 | 66.0599 | 66.0599 | 123.4052 | 211.185 | 424.2943 | 427.5547 | 219.0564 | 66.0599 | 66.0599 | 66.0599 | 66.0599 | 208 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 12 | 8 | 3896 | 13.6 | 13.6 | 11.6167 | 13.66 | 15 | 67 | 67 | 535.5639 | 135.5752 | 30.3699 | 90.675 | 93.5066 | 412.9261 | 490.4592 | 280.6879 | 0 | 0 | 0 | 0 | 236.4248 | 108.3849 | 178.714 | 195.7851 | 149.5981 | 87.7968 | 87.7968 | 87.7968 | 87.7968 | 135.5752 | 201.8914 | 591.6401 | 686.2442 | 430.286 | 87.7968 | 87.7968 | 87.7968 | 87.7968 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 9 | 3897 | 14.9 | 14.9 | 11.6167 | 13.66 | 15 | 62 | 62 | 697.0221 | 132.6223 | 39.4997 | 103.3213 | 0 | 420.198 | 601.3347 | 430.2178 | 7.0851 | 0 | 0 | 0 | 403.3777 | 101.9937 | 168.2878 | 196.8655 | 169.8686 | 103.1115 | 101.9937 | 101.9937 | 101.9937 | 132.6223 | 101.9937 | 588.4857 | 798.2002 | 600.0863 | 110.1966 | 101.9937 | 101.9937 | 101.9937 | 536 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 10 | 3898 | 15.7 | 15.7 | 11.6167 | 13.66 | 15 | 50 | 50 | 762.5649 | 139.9639 | 48.1023 | 118.3259 | 0 | 309.01 | 572.584 | 500.7461 | 135.5779 | 0 | 0 | 0 | 532.0361 | 116.7729 | 161.9068 | 200.4043 | 189.9117 | 136.5753 | 116.7729 | 116.7729 | 116.7729 | 139.9639 | 116.7729 | 470.9167 | 772.9883 | 690.6577 | 272.1532 | 116.7729 | 116.7729 | 116.7729 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 11 | 3899 | 15.9 | 15.9 | 11.6167 | 13.66 | 15 | 51 | 51 | 817.4025 | 143.0335 | 55.3857 | 137.3646 | 0 | 156.6229 | 480.5032 | 522.9113 | 259.005 | 0 | 0 | 0 | 645.9665 | 128.6245 | 144.9463 | 178.6979 | 183.1173 | 155.6155 | 128.6245 | 128.6245 | 128.6245 | 143.0335 | 128.6245 | 301.5692 | 659.2012 | 706.0285 | 414.6205 | 128.6245 | 128.6245 | 128.6245 | 789 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 12 | 3900 | 17.1 | 17.1 | 11.6167 | 13.66 | 15 | 49 | 49 | 753.054 | 173.8456 | 60.0754 | 161.8435 | 0 | 0 | 289.7428 | 427.4074 | 314.7026 | 17.6492 | 0 | 0 | 640.1544 | 136.3185 | 136.3185 | 173.7153 | 191.4836 | 176.9368 | 138.5964 | 136.3185 | 136.3185 | 173.8456 | 136.3185 | 136.3185 | 463.4581 | 618.891 | 491.6394 | 156.2456 | 136.3185 | 136.3185 | 814 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 13 | 3901 | 17.9 | 17.9 | 11.6167 | 13.66 | 15 | 42 | 42 | 606.0414 | 237.9591 | 60.7417 | 189.9496 | 0 | 0 | 94.2102 | 269.7519 | 287.2765 | 136.5185 | 0 | 0 | 529.0409 | 143.9392 | 143.9392 | 169.1736 | 216.1929 | 220.8869 | 180.506 | 143.9392 | 143.9392 | 237.9591 | 143.9392 | 143.9392 | 263.3839 | 485.9448 | 508.1634 | 317.0245 | 143.9392 | 143.9392 | 767 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 14 | 3902 | 17.6 | 17.6 | 11.6167 | 13.66 | 15 | 42 | 42 | 376.5105 | 327.241 | 57.1222 | 215.9364 | 0 | 0 | 0 | 105.6813 | 181.2512 | 150.6466 | 31.7952 | 0 | 322.759 | 152.6857 | 152.6857 | 152.6857 | 216.6478 | 262.3853 | 243.8623 | 171.9293 | 152.6857 | 327.241 | 152.6857 | 152.6857 | 152.6857 | 322.3291 | 443.6365 | 394.5089 | 203.7246 | 152.6857 | 650 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 15 | 3903 | 17.4 | 17.4 | 11.6167 | 13.66 | 15 | 43 | 43 | 361.8591 | 312.0366 | 50.4546 | 236.5158 | 0 | 0 | 0 | 30.9444 | 159.0472 | 193.9822 | 115.2851 | 0 | 290.9634 | 147.1149 | 147.1149 | 147.1149 | 165.6234 | 242.2443 | 263.1397 | 216.0693 | 147.1149 | 312.0366 | 147.1149 | 147.1149 | 147.1149 | 196.5679 | 401.2915 | 457.1219 | 331.3545 | 147.1149 | 603 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 16 | 3904 | 17.8 | 17.8 | 11.6167 | 13.66 | 15 | 42 | 42 | 144.4614 | 324.3924 | 42.1425 | 252.5276 | 0 | 0 | 0 | 0 | 50.7444 | 90.1256 | 76.7124 | 18.3622 | 103.6076 | 146.3908 | 146.3908 | 146.3908 | 146.3908 | 202.5014 | 246.0473 | 231.2157 | 166.6948 | 324.3924 | 146.3908 | 146.3908 | 146.3908 | 146.3908 | 253.2458 | 336.1728 | 307.9281 | 185.057 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 17 | 3905 | 17.6 | 17.6 | 11.6167 | 13.66 | 15 | 42 | 42 | 59.5259 | 261.1307 | 33.1084 | 265.7295 | 0 | 0 | 0 | 0 | 13.252 | 39.1404 | 42.1008 | 20.3992 | 35.8693 | 119.5944 | 119.5944 | 119.5944 | 119.5944 | 140.1926 | 180.4319 | 185.0335 | 151.3017 | 261.1307 | 119.5944 | 119.5944 | 119.5944 | 119.5944 | 153.4446 | 219.5723 | 227.1343 | 171.7008 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 12 | 18 | 3906 | 17.2 | 17.2 | 11.6167 | 13.66 | 15 | 43 | 43 | 20.2634 | 176.5157 | 23.9141 | 277.4523 | 0 | 0 | 0 | 0 | 1.2639 | 12.8624 | 16.9263 | 11.0749 | 9.4843 | 85.6933 | 85.6933 | 85.6933 | 85.6933 | 86.935 | 98.3292 | 102.3215 | 96.5732 | 176.5157 | 85.6933 | 85.6933 | 85.6933 | 85.6933 | 88.1989 | 111.1916 | 119.2477 | 107.6481 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 19 | 3907 | 17.1 | 17.1 | 11.6167 | 13.66 | 15 | 44 | 44 | 5.5092 | 90.2219 | 14.9514 | 288.5816 | 0.6532 | 0 | 0 | 0 | 0 | 3.0692 | 4.9937 | 3.993 | 1.7781 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 90.2219 | 45.4159 | 44.7627 | 44.7627 | 44.7627 | 44.7627 | 47.8319 | 49.7564 | 48.7557 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 20 | 3908 | 16.7 | 16.7 | 11.6167 | 13.66 | 15 | 46 | 46 | 34.5555 | 71.8982 | 6.5557 | 299.727 | 10.6385 | 0 | 0 | 0 | 0 | 14.854 | 31.6453 | 29.8991 | 6.1018 | 45.0704 | 35.79 | 35.79 | 35.79 | 35.79 | 48.7478 | 63.3954 | 61.8722 | 71.8982 | 55.7089 | 35.79 | 35.79 | 35.79 | 35.79 | 63.6018 | 95.0407 | 91.7713 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 21 | 3909 | 15.5 | 15.5 | 11.6167 | 13.66 | 15 | 57 | 57 | 11.7387 | 13.5369 | -0.93544 | 311.3259 | 5.7828 | 0 | 0 | 0 | 0 | 3.072 | 10.1272 | 11.2501 | 0.46306 | 8.2222 | 7.1717 | 7.1717 | 7.1717 | 7.1717 | 7.7298 | 9.0115 | 9.2154 | 13.5369 | 14.005 | 7.1717 | 7.1717 | 7.1717 | 7.1717 | 10.8017 | 19.1387 | 20.4655 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 22 | 3910 | 15 | 15 | 11.6167 | 13.66 | 15 | 57 | 57 | 0 | 0 | -7.1571 | 323.6684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 23 | 3911 | 14.9 | 14.9 | 11.6167 | 13.66 | 15 | 55 | 55 | 0 | 0 | -11.7269 | 336.8613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 12 | 24 | 3912 | 14.9 | 14.9 | 13.4667 | 13.4614 | 15 | 56 | 56 | 0 | 0 | -14.2962 | 350.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 1 | 3913 | 15 | 15 | 13.4667 | 13.4614 | 15 | 58 | 58 | 0 | 0 | -14.6359 | 5.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 2 | 3914 | 15.2 | 15.2 | 13.4667 | 13.4614 | 15 | 59 | 59 | 0 | 0 | -12.6623 | 19.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 3 | 3915 | 15.3 | 15.3 | 13.4667 | 13.4614 | 15 | 62 | 62 | 0 | 0 | -8.6638 | 32.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 4 | 3916 | 14.8 | 14.8 | 13.4667 | 13.4614 | 15 | 67 | 67 | 0 | 0 | -2.9023 | 45.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 5 | 3917 | 14.2 | 14.2 | 13.4667 | 13.4614 | 15 | 74 | 74 | 0 | 0 | 4.2434 | 56.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 6 | 3918 | 14.6 | 14.6 | 13.4667 | 13.4614 | 15 | 73 | 73 | 2.8635 | 30.568 | 12.4008 | 68.0507 | 1.5631 | 2.7952 | 2.3899 | 0.58461 | 0 | 0 | 0 | 0 | 0.432 | 32.826 | 47.608 | 42.7452 | 21.0862 | 14.0723 | 14.0723 | 14.0723 | 14.0723 | 30.568 | 34.3891 | 50.4032 | 45.135 | 21.6708 | 14.0723 | 14.0723 | 14.0723 | 14.0723 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 7 | 3919 | 14.5 | 14.5 | 13.4667 | 13.4614 | 15 | 78 | 78 | 3.1698 | 63.0616 | 21.2256 | 79.1255 | 1.1572 | 2.8487 | 2.8715 | 1.2122 | 0 | 0 | 0 | 0 | 0.93837 | 34.0484 | 39.1271 | 39.1955 | 34.2135 | 30.574 | 30.574 | 30.574 | 30.574 | 63.0616 | 35.2056 | 41.9758 | 42.067 | 35.4257 | 30.574 | 30.574 | 30.574 | 30.574 | 64 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 13 | 8 | 3920 | 14.6 | 14.6 | 13.4667 | 13.4614 | 15 | 81 | 81 | 2.3895 | 81.9434 | 30.3867 | 90.5877 | 0.42022 | 1.8439 | 2.1874 | 1.2496 | 0 | 0 | 0 | 0 | 1.0566 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 81.9434 | 40.9863 | 42.4099 | 42.7535 | 41.8156 | 40.5661 | 40.5661 | 40.5661 | 40.5661 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 9 | 3921 | 15.9 | 15.9 | 13.4667 | 13.4614 | 15 | 77 | 77 | 11.8447 | 199.1374 | 39.5183 | 103.2242 | 0 | 7.1505 | 10.2171 | 7.2987 | 0.10481 | 0 | 0 | 0 | 6.8626 | 92.3195 | 120.5464 | 132.6521 | 121.1315 | 92.7333 | 92.3195 | 92.3195 | 92.3195 | 199.1374 | 92.3195 | 127.6969 | 142.8692 | 128.4302 | 92.8381 | 92.3195 | 92.3195 | 92.3195 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 10 | 3922 | 17 | 17 | 13.4667 | 13.4614 | 15 | 76 | 76 | 33.2133 | 282.807 | 48.1267 | 118.2163 | 0 | 13.4922 | 24.942 | 21.7812 | 5.8612 | 0 | 0 | 0 | 23.193 | 125.8114 | 171.1446 | 209.6157 | 198.9954 | 145.5049 | 125.8114 | 125.8114 | 125.8114 | 282.807 | 125.8114 | 184.6367 | 234.5577 | 220.7766 | 151.3662 | 125.8114 | 125.8114 | 125.8114 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 11 | 3923 | 17.1 | 17.1 | 13.4667 | 13.4614 | 15 | 76 | 76 | 10.7207 | 266.5216 | 55.4214 | 137.2441 | 0 | 2.0663 | 6.3056 | 6.8511 | 3.3833 | 0 | 0 | 0 | 8.4784 | 127.3648 | 133.7052 | 146.713 | 148.3869 | 137.7463 | 127.3648 | 127.3648 | 127.3648 | 266.5216 | 127.3648 | 135.7715 | 153.0186 | 155.238 | 141.1296 | 127.3648 | 127.3648 | 127.3648 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 12 | 3924 | 17.1 | 17.1 | 13.4667 | 13.4614 | 15 | 78 | 78 | 5.2204 | 231.5594 | 60.1275 | 161.7292 | 0 | 0 | 2.0113 | 2.9605 | 2.1754 | 0.11601 | 0 | 0 | 4.4406 | 115.6748 | 115.6748 | 118.9363 | 120.4753 | 119.2023 | 115.8629 | 115.6748 | 115.6748 | 231.5594 | 115.6748 | 115.6748 | 120.9476 | 123.4358 | 121.3777 | 115.9789 | 115.6748 | 115.6748 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 13 | 3925 | 17.3 | 17.3 | 13.4667 | 13.4614 | 15 | 79 | 79 | 13.024 | 305.6238 | 60.8092 | 189.8733 | 0 | 0 | 2.0337 | 5.7937 | 6.1599 | 2.9176 | 0 | 0 | 11.3762 | 147.6871 | 147.6871 | 152.5735 | 161.6078 | 162.4875 | 154.6974 | 147.6871 | 147.6871 | 305.6238 | 147.6871 | 147.6871 | 154.6072 | 167.4015 | 168.6474 | 157.615 | 147.6871 | 147.6871 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 14 | 3926 | 17.4 | 17.4 | 13.4667 | 13.4614 | 15 | 82 | 82 | 3.9114 | 202.6449 | 57.1976 | 215.9058 | 0 | 0 | 0 | 1.0977 | 1.8794 | 1.5603 | 0.32711 | 0 | 3.3551 | 103.24 | 103.24 | 103.24 | 103.24 | 103.24 | 103.24 | 103.24 | 103.24 | 202.6449 | 103.24 | 103.24 | 103.24 | 104.3377 | 105.1195 | 104.8003 | 103.5671 | 103.24 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 15 | 3927 | 17.4 | 17.4 | 13.4667 | 13.4614 | 15 | 85 | 85 | 6.4636 | 238.7991 | 50.5317 | 236.5124 | 0 | 0 | 0 | 0.55346 | 2.8362 | 3.4576 | 2.0535 | 0 | 5.2009 | 119.2849 | 119.2849 | 119.2849 | 120.0787 | 123.3528 | 124.2439 | 122.2302 | 119.2849 | 238.7991 | 119.2849 | 119.2849 | 119.2849 | 120.6322 | 126.189 | 127.7015 | 124.2837 | 119.2849 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 16 | 3928 | 17.5 | 17.5 | 13.4667 | 13.4614 | 15 | 88 | 88 | 1.9591 | 120.5937 | 42.2195 | 252.535 | 0 | 0 | 0 | 0 | 0.68711 | 1.2203 | 1.0386 | 0.24854 | 1.4063 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 120.5937 | 59.7256 | 59.7256 | 59.7256 | 59.7256 | 60.4127 | 60.9458 | 60.7642 | 59.9741 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 17 | 3929 | 19.4 | 19.4 | 13.4667 | 13.4614 | 15 | 77 | 77 | 31.1473 | 242.2108 | 33.1851 | 265.7396 | 0 | 0 | 0 | 0 | 6.9229 | 20.4541 | 22.0036 | 10.6636 | 18.7892 | 110.7162 | 110.7162 | 110.7162 | 110.7162 | 128.8846 | 164.3958 | 168.4622 | 138.7018 | 242.2108 | 110.7162 | 110.7162 | 110.7162 | 110.7162 | 135.8075 | 184.8499 | 190.4658 | 149.3654 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 13 | 18 | 3930 | 18.4 | 18.4 | 13.4667 | 13.4614 | 15 | 89 | 89 | 2.4446 | 87.854 | 23.9908 | 277.4611 | 0 | 0 | 0 | 0 | 0.15199 | 1.5502 | 2.0403 | 1.3352 | 1.146 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 87.854 | 43.0665 | 43.0665 | 43.0665 | 43.0665 | 43.2185 | 44.6167 | 45.1068 | 44.4018 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 19 | 3931 | 18.6 | 18.6 | 13.4667 | 13.4614 | 15 | 84 | 84 | 2.6536 | 63.1414 | 15.0284 | 288.5869 | 0.31481 | 0 | 0 | 0 | 0 | 1.4772 | 2.4039 | 1.9224 | 0.85857 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 63.1414 | 31.031 | 30.7162 | 30.7162 | 30.7162 | 30.7162 | 32.1933 | 33.12 | 32.6385 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 20 | 3932 | 18.1 | 18.1 | 13.4667 | 13.4614 | 15 | 81 | 81 | 2.0701 | 30.6327 | 6.6328 | 299.727 | 0.63727 | 0 | 0 | 0 | 0 | 0.88938 | 1.895 | 1.7906 | 0.36731 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 30.6327 | 15.2862 | 14.6489 | 14.6489 | 14.6489 | 14.6489 | 15.5383 | 16.544 | 16.4395 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 21 | 3933 | 17.5 | 17.5 | 13.4667 | 13.4614 | 15 | 80 | 80 | 10.5975 | 13.5722 | -0.85862 | 311.3186 | 5.2198 | 0 | 0 | 0 | 0 | 2.7729 | 9.1413 | 10.1548 | 0.42779 | 8.2231 | 7.1879 | 7.1879 | 7.1879 | 7.1879 | 7.7378 | 9.0007 | 9.2017 | 13.5722 | 13.4428 | 7.1879 | 7.1879 | 7.1879 | 7.1879 | 10.5107 | 18.142 | 19.3565 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 22 | 3934 | 16.2 | 16.2 | 13.4667 | 13.4614 | 15 | 86 | 86 | 0 | 0 | -7.0817 | 323.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 23 | 3935 | 15.1 | 15.1 | 13.4667 | 13.4614 | 15 | 90 | 90 | 0 | 0 | -11.6545 | 336.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 13 | 24 | 3936 | 14.6 | 14.6 | 16.3667 | 14.1043 | 15 | 90 | 90 | 0 | 0 | -14.2289 | 350.7297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 1 | 3937 | 14.3 | 14.3 | 16.3667 | 14.1043 | 15 | 91 | 91 | 0 | 0 | -14.5758 | 4.9571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 2 | 3938 | 14.9 | 14.9 | 16.3667 | 14.1043 | 15 | 90 | 90 | 0 | 0 | -12.6175 | 18.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 3 | 3939 | 14.9 | 14.9 | 16.3667 | 14.1043 | 15 | 90 | 90 | 0 | 0 | -8.6278 | 32.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 4 | 3940 | 15.1 | 15.1 | 16.3667 | 14.1043 | 15 | 88 | 88 | 0 | 0 | -2.8744 | 44.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 5 | 3941 | 13.9 | 13.9 | 16.3667 | 14.1043 | 15 | 94 | 94 | 10.4052 | 5.8192 | 4.2645 | 56.7439 | 7.3544 | 10.3921 | 7.3423 | 0 | 0 | 0 | 0 | 0.0085769 | 0.18079 | 6.3138 | 8.0516 | 6.3069 | 2.1067 | 2.1067 | 2.1067 | 2.1067 | 2.1116 | 5.8192 | 13.6682 | 18.4437 | 13.6492 | 2.1067 | 2.1067 | 2.1067 | 2.1067 | 2.1202 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 6 | 3942 | 14.8 | 14.8 | 16.3667 | 14.1043 | 15 | 91 | 91 | 34.6534 | 61.7453 | 12.4167 | 67.9788 | 18.9507 | 33.8341 | 28.8979 | 7.0337 | 0 | 0 | 0 | 0 | 5.2547 | 126.3652 | 205.1099 | 178.9937 | 63.315 | 26.1011 | 26.1011 | 26.1011 | 26.1011 | 61.7453 | 145.3159 | 238.944 | 207.8916 | 70.3488 | 26.1011 | 26.1011 | 26.1011 | 26.1011 | 67 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 7 | 3943 | 15.8 | 15.8 | 16.3667 | 14.1043 | 15 | 76 | 76 | 178.7114 | 132.9686 | 21.2381 | 79.0494 | 65.4405 | 160.6822 | 161.7984 | 68.1353 | 0 | 0 | 0 | 0 | 53.0314 | 121.3763 | 205.8275 | 206.8172 | 123.7658 | 63.35 | 63.35 | 63.35 | 63.35 | 132.9686 | 186.8169 | 366.5096 | 368.6156 | 191.9011 | 63.35 | 63.35 | 63.35 | 63.35 | 186 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 14 | 8 | 3944 | 16.4 | 16.4 | 16.3667 | 14.1043 | 15 | 69 | 69 | 448.2005 | 154.5223 | 30.398 | 90.5053 | 79.3585 | 346.1371 | 410.1533 | 233.9072 | 0 | 0 | 0 | 0 | 198.4777 | 113.1592 | 186.0688 | 203.5641 | 155.3968 | 91.4709 | 91.4709 | 91.4709 | 91.4709 | 154.5223 | 192.5178 | 532.2059 | 613.7174 | 389.304 | 91.4709 | 91.4709 | 91.4709 | 91.4709 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 9 | 3945 | 17.5 | 17.5 | 16.3667 | 14.1043 | 15 | 59 | 59 | 637.9995 | 148.9749 | 39.5313 | 103.1324 | 0 | 385.6703 | 550.273 | 392.5332 | 4.8528 | 0 | 0 | 0 | 370.0251 | 104.7268 | 175.1165 | 205.1586 | 176.3691 | 105.6125 | 104.7268 | 104.7268 | 104.7268 | 148.9749 | 104.7268 | 560.7868 | 755.4316 | 568.9023 | 110.4654 | 104.7268 | 104.7268 | 104.7268 | 519 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 10 | 3946 | 17.7 | 17.7 | 16.3667 | 14.1043 | 15 | 61 | 61 | 215.1489 | 307.6432 | 48.1453 | 118.112 | 0 | 87.6091 | 161.5997 | 140.9274 | 37.7017 | 0 | 0 | 0 | 150.3568 | 145.074 | 213.2179 | 270.769 | 254.6897 | 174.399 | 145.074 | 145.074 | 145.074 | 307.6432 | 145.074 | 300.827 | 432.3687 | 395.6171 | 212.1007 | 145.074 | 145.074 | 145.074 | 458 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 11 | 3947 | 18.4 | 18.4 | 16.3667 | 14.1043 | 15 | 55 | 55 | 475.0832 | 266.0459 | 55.4507 | 137.1281 | 0 | 92.0881 | 279.6 | 303.3259 | 149.3677 | 0 | 0 | 0 | 375.9541 | 145.2631 | 181.5046 | 255.3004 | 264.6378 | 204.0471 | 145.2631 | 145.2631 | 145.2631 | 266.0459 | 145.2631 | 273.5927 | 534.9003 | 567.9637 | 353.4148 | 145.2631 | 145.2631 | 145.2631 | 642 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 12 | 3948 | 19.7 | 19.7 | 16.3667 | 14.1043 | 15 | 48 | 48 | 403.6142 | 314.4828 | 60.1727 | 161.6166 | 0 | 0 | 155.7318 | 228.7379 | 167.7525 | 8.4999 | 0 | 0 | 343.5172 | 154.0826 | 154.0826 | 237.2503 | 276.2388 | 243.6698 | 158.6219 | 154.0826 | 154.0826 | 314.4828 | 154.0826 | 154.0826 | 392.9821 | 504.9767 | 411.4223 | 167.1218 | 154.0826 | 154.0826 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 13 | 3949 | 20.2 | 20.2 | 16.3667 | 14.1043 | 15 | 47 | 47 | 231.2326 | 380.9141 | 60.87 | 189.794 | 0 | 0 | 36.2719 | 102.8238 | 109.1429 | 51.5275 | 0 | 0 | 202.0859 | 161.8229 | 161.8229 | 199.3388 | 268.173 | 274.7087 | 215.1175 | 161.8229 | 161.8229 | 380.9141 | 161.8229 | 161.8229 | 235.6107 | 370.9968 | 383.8516 | 266.645 | 161.8229 | 161.8229 | 583 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 14 | 3950 | 20.1 | 20.1 | 16.3667 | 14.1043 | 15 | 46 | 46 | 476.6794 | 287.8866 | 57.2668 | 215.8693 | 0 | 0 | 0 | 133.7777 | 228.6622 | 189.5995 | 39.472 | 0 | 409.1134 | 149.1699 | 149.1699 | 149.1699 | 207.6989 | 249.2117 | 232.1215 | 166.4393 | 149.1699 | 287.8866 | 149.1699 | 149.1699 | 149.1699 | 341.4766 | 477.874 | 421.721 | 205.9113 | 149.1699 | 697 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 15 | 3951 | 20.4 | 20.4 | 16.3667 | 14.1043 | 15 | 42 | 42 | 602.9831 | 220.5116 | 50.6035 | 236.5023 | 0 | 0 | 0 | 51.7399 | 264.2161 | 321.9181 | 191.0448 | 0 | 485.4884 | 135.4066 | 135.4066 | 135.4066 | 148.5256 | 202.4005 | 217.0312 | 183.8474 | 135.4066 | 220.5116 | 135.4066 | 135.4066 | 135.4066 | 200.2655 | 466.6166 | 538.9493 | 374.8922 | 135.4066 | 706 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 16 | 3952 | 20.1 | 20.1 | 16.3667 | 14.1043 | 15 | 43 | 43 | 619.5939 | 190.9209 | 42.2915 | 252.5361 | 0 | 0 | 0 | 0 | 217.0342 | 385.3487 | 327.9311 | 78.4159 | 445.0791 | 123.9814 | 123.9814 | 123.9814 | 123.9814 | 171.9059 | 209.0723 | 196.3936 | 141.2968 | 190.9209 | 123.9814 | 123.9814 | 123.9814 | 123.9814 | 388.9401 | 594.421 | 524.3247 | 219.7128 | 636 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 17 | 3953 | 19.9 | 19.9 | 16.3667 | 14.1043 | 15 | 44 | 44 | 795.9441 | 113.3906 | 33.257 | 265.7438 | 0 | 0 | 0 | 0 | 176.6972 | 522.087 | 561.6453 | 272.1994 | 480.6094 | 102.1119 | 102.1119 | 102.1119 | 102.1119 | 118.4072 | 150.2595 | 153.9076 | 127.2145 | 113.3906 | 102.1119 | 102.1119 | 102.1119 | 102.1119 | 295.1044 | 672.3464 | 715.5529 | 399.4139 | 594 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 14 | 18 | 3954 | 19.7 | 19.7 | 16.3667 | 14.1043 | 15 | 45 | 45 | 554.4989 | 139.7125 | 24.0628 | 277.4645 | 0 | 0 | 0 | 0 | 34.4129 | 351.3023 | 462.4036 | 302.6351 | 260.2875 | 90.2438 | 90.2438 | 90.2438 | 90.2438 | 97.2371 | 161.6351 | 184.213 | 151.745 | 139.7125 | 90.2438 | 90.2438 | 90.2438 | 90.2438 | 131.6501 | 512.9374 | 646.6165 | 454.38 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 19 | 3955 | 19 | 19 | 16.3667 | 14.1043 | 15 | 47 | 47 | 366.7395 | 125.086 | 15.1004 | 288.5873 | 43.5037 | 0 | 0 | 0 | 0 | 204.0201 | 332.0318 | 265.5437 | 118.914 | 85.2301 | 71.6968 | 71.6968 | 71.6968 | 71.6968 | 135.1645 | 174.9871 | 154.3036 | 125.086 | 128.7339 | 71.6968 | 71.6968 | 71.6968 | 71.6968 | 339.1846 | 507.0188 | 419.8473 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 20 | 3956 | 18.3 | 18.3 | 16.3667 | 14.1043 | 15 | 49 | 49 | 336.7803 | 70.9869 | 6.7047 | 299.7225 | 103.6416 | 0 | 0 | 0 | 0 | 144.6385 | 308.1914 | 291.2099 | 60.0131 | 69.3078 | 42.1013 | 42.1013 | 42.1013 | 42.1013 | 80.0698 | 123.0034 | 118.5457 | 70.9869 | 172.9494 | 42.1013 | 42.1013 | 42.1013 | 42.1013 | 224.7083 | 431.1948 | 409.7556 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 21 | 3957 | 14.9 | 14.9 | 16.3667 | 14.1043 | 15 | 75 | 75 | 24.5645 | 15.9883 | -0.78744 | 311.3075 | 12.0958 | 0 | 0 | 0 | 0 | 6.4283 | 21.1868 | 23.5343 | 1.0117 | 16.4505 | 8.7034 | 8.7034 | 8.7034 | 8.7034 | 12.8206 | 22.2732 | 23.7767 | 15.9883 | 28.5463 | 8.7034 | 8.7034 | 8.7034 | 8.7034 | 19.249 | 43.46 | 47.3111 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 22 | 3958 | 12.5 | 12.5 | 16.3667 | 14.1043 | 15 | 90 | 90 | 0 | 0 | -7.0123 | 323.6324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 23 | 3959 | 11.6 | 11.6 | 16.3667 | 14.1043 | 15 | 94 | 94 | 0 | 0 | -11.5885 | 336.8044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 14 | 24 | 3960 | 10.8 | 10.8 | 16.7042 | 14.7287 | 15 | 97 | 97 | 0 | 0 | -14.1683 | 350.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 1 | 3961 | 10.3 | 10.3 | 16.7042 | 14.7287 | 15 | 97 | 97 | 0 | 0 | -14.5225 | 4.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 2 | 3962 | 10.1 | 10.1 | 16.7042 | 14.7287 | 15 | 97 | 97 | 0 | 0 | -12.5795 | 18.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 3 | 3963 | 11.4 | 11.4 | 16.7042 | 14.7287 | 15 | 96 | 96 | 0 | 0 | -8.5983 | 32.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 4 | 3964 | 11 | 11 | 16.7042 | 14.7287 | 15 | 94 | 94 | 0 | 0 | -2.8527 | 44.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 5 | 3965 | 10.3 | 10.3 | 16.7042 | 14.7287 | 15 | 97 | 97 | 8.7775 | 5.8411 | 4.2796 | 56.6783 | 6.2109 | 8.7666 | 6.1869 | 0 | 0 | 0 | 0 | 0.016972 | 0.15889 | 6.34 | 8.0796 | 6.3237 | 2.1123 | 2.1123 | 2.1123 | 2.1123 | 2.1239 | 5.8411 | 12.5509 | 16.8462 | 12.5106 | 2.1123 | 2.1123 | 2.1123 | 2.1123 | 2.1409 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 6 | 3966 | 13 | 13 | 16.7042 | 14.7287 | 15 | 88 | 88 | 26.8997 | 59.9028 | 12.4269 | 67.9108 | 14.7359 | 26.2694 | 22.4147 | 5.4298 | 0 | 0 | 0 | 0 | 4.0972 | 119.3692 | 192.8525 | 168.2931 | 60.0775 | 25.4831 | 25.4831 | 25.4831 | 25.4831 | 59.9028 | 134.1051 | 219.122 | 190.7078 | 65.5072 | 25.4831 | 25.4831 | 25.4831 | 25.4831 | 64 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 7 | 3967 | 15.9 | 15.9 | 16.7042 | 14.7287 | 15 | 74 | 74 | 136.109 | 134.5256 | 21.2451 | 78.9778 | 49.9846 | 122.4344 | 123.1638 | 51.7455 | 0 | 0 | 0 | 0 | 40.4744 | 121.8089 | 207.6365 | 208.5006 | 123.895 | 62.5948 | 62.5948 | 62.5948 | 62.5948 | 134.5256 | 171.7935 | 330.0709 | 331.6643 | 175.6405 | 62.5948 | 62.5948 | 62.5948 | 62.5948 | 175 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 15 | 8 | 3968 | 18.2 | 18.2 | 16.7042 | 14.7287 | 15 | 71 | 71 | 282.0741 | 185.9274 | 30.4039 | 90.4277 | 50.2645 | 218.0142 | 258.0541 | 146.9294 | 0 | 0 | 0 | 0 | 125.0726 | 121.6067 | 203.774 | 223.3864 | 168.9552 | 96.9861 | 96.9861 | 96.9861 | 96.9861 | 185.9274 | 171.8713 | 421.7882 | 481.4405 | 315.8846 | 96.9861 | 96.9861 | 96.9861 | 96.9861 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 9 | 3969 | 19.8 | 19.8 | 16.7042 | 14.7287 | 15 | 67 | 67 | 118.2144 | 262.3768 | 39.5388 | 103.0458 | 0 | 71.5546 | 101.9545 | 72.6309 | 0.76111 | 0 | 0 | 0 | 68.6232 | 120.1184 | 198.9607 | 232.4569 | 200.1467 | 120.957 | 120.1184 | 120.1184 | 120.1184 | 262.3768 | 120.1184 | 270.5153 | 334.4115 | 272.7777 | 121.7181 | 120.1184 | 120.1184 | 120.1184 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 10 | 3970 | 20.2 | 20.2 | 16.7042 | 14.7287 | 15 | 67 | 67 | 18.2427 | 259.2424 | 48.1579 | 118.0131 | 0 | 7.4457 | 13.7055 | 11.9368 | 3.1757 | 0 | 0 | 0 | 12.7576 | 120.2334 | 142.0448 | 160.3824 | 155.2012 | 129.5364 | 120.2334 | 120.2334 | 120.2334 | 259.2424 | 120.2334 | 149.4905 | 174.0879 | 167.1381 | 132.7121 | 120.2334 | 120.2334 | 120.2334 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 11 | 3971 | 20.1 | 20.1 | 16.7042 | 14.7287 | 15 | 72 | 72 | 3.018 | 164.6104 | 55.4736 | 137.0168 | 0 | 0.58817 | 1.7774 | 1.9254 | 0.94557 | 0 | 0 | 0 | 2.3896 | 82.8894 | 82.8894 | 82.8894 | 82.8894 | 82.8894 | 82.8894 | 82.8894 | 82.8894 | 164.6104 | 82.8894 | 83.4776 | 84.6668 | 84.8148 | 83.835 | 82.8894 | 82.8894 | 82.8894 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 12 | 3972 | 21 | 21 | 16.7042 | 14.7287 | 15 | 66 | 66 | 55.7998 | 366.4851 | 60.211 | 161.5056 | 0 | 0 | 21.5625 | 31.607 | 23.1365 | 1.113 | 0 | 0 | 47.5149 | 159.4188 | 159.4188 | 211.2553 | 235.4023 | 215.0393 | 162.0944 | 159.4188 | 159.4188 | 366.4851 | 159.4188 | 159.4188 | 232.8178 | 267.0093 | 238.1758 | 163.2074 | 159.4188 | 159.4188 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 13 | 3973 | 21.7 | 21.7 | 16.7042 | 14.7287 | 15 | 66 | 66 | 51.9761 | 373.5539 | 60.924 | 189.7119 | 0 | 0 | 8.1911 | 23.108 | 24.4885 | 11.524 | 0 | 0 | 45.4461 | 161.5575 | 161.5575 | 182.6414 | 221.0377 | 224.5913 | 191.2206 | 161.5575 | 161.5575 | 373.5539 | 161.5575 | 161.5575 | 190.8325 | 244.1456 | 249.0798 | 202.7446 | 161.5575 | 161.5575 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 14 | 3974 | 22.6 | 22.6 | 16.7042 | 14.7287 | 15 | 61 | 61 | 56.8022 | 370.2252 | 57.33 | 215.8269 | 0 | 0 | 0 | 15.9466 | 27.2085 | 22.5321 | 4.6566 | 0 | 48.7748 | 160.7073 | 160.7073 | 160.7073 | 197.6206 | 223.6899 | 212.8648 | 171.4865 | 160.7073 | 370.2252 | 160.7073 | 160.7073 | 160.7073 | 213.5672 | 250.8985 | 235.3969 | 176.1432 | 160.7073 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 15 | 3975 | 22 | 22 | 16.7042 | 14.7287 | 15 | 65 | 65 | 24.0219 | 311.6484 | 50.6698 | 236.4855 | 0 | 0 | 0 | 2.0672 | 10.5135 | 12.8012 | 7.5901 | 0 | 19.3516 | 149.6102 | 149.6102 | 149.6102 | 152.8947 | 166.3152 | 169.9501 | 161.6701 | 149.6102 | 311.6484 | 149.6102 | 149.6102 | 149.6102 | 154.9619 | 176.8287 | 182.7512 | 169.2602 | 149.6102 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 16 | 3976 | 21.4 | 21.4 | 16.7042 | 14.7287 | 15 | 66 | 66 | 12.3859 | 249.0969 | 42.3585 | 252.5308 | 0 | 0 | 0 | 0 | 4.3344 | 7.6928 | 6.5449 | 1.5631 | 8.9031 | 121.7411 | 121.7411 | 121.7411 | 121.7411 | 128.8386 | 134.3379 | 132.4583 | 124.3007 | 249.0969 | 121.7411 | 121.7411 | 121.7411 | 121.7411 | 133.1729 | 142.0308 | 139.0032 | 125.8638 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 17 | 3977 | 21.3 | 21.3 | 16.7042 | 14.7287 | 15 | 68 | 68 | 3.7456 | 139.7364 | 33.3242 | 265.7422 | 0 | 0 | 0 | 0 | 0.83087 | 2.4544 | 2.6401 | 1.2793 | 2.2636 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 139.7364 | 69.8607 | 69.8607 | 69.8607 | 69.8607 | 70.6916 | 72.3151 | 72.5008 | 71.1401 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 15 | 18 | 3978 | 20.3 | 20.3 | 16.7042 | 14.7287 | 15 | 65 | 65 | 99.439 | 211.2665 | 24.1299 | 277.4627 | 0 | 0 | 0 | 0 | 6.1689 | 62.9526 | 82.8594 | 54.2284 | 46.7335 | 99.9088 | 99.9088 | 99.9088 | 99.9088 | 106.9391 | 171.6518 | 194.3384 | 161.7094 | 211.2665 | 99.9088 | 99.9088 | 99.9088 | 99.9088 | 113.108 | 234.6043 | 277.1978 | 215.9378 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 19 | 3979 | 19.6 | 19.6 | 16.7042 | 14.7287 | 15 | 60 | 60 | 692.5271 | 75.0247 | 15.1674 | 288.5828 | 82.0862 | 0 | 0 | 0 | 0 | 385.0728 | 626.6614 | 501.1602 | 224.9753 | 69.7586 | 62.1281 | 62.1281 | 62.1281 | 62.1281 | 97.9237 | 120.3813 | 108.7149 | 75.0247 | 151.8448 | 62.1281 | 62.1281 | 62.1281 | 62.1281 | 482.9965 | 747.0426 | 609.8751 | 300 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 20 | 3980 | 18.6 | 18.6 | 16.7042 | 14.7287 | 15 | 57 | 57 | 252.8622 | 76.7718 | 6.7713 | 299.7137 | 77.7739 | 0 | 0 | 0 | 0 | 108.5804 | 231.3298 | 218.5693 | 45.2282 | 71.5731 | 43.2541 | 43.2541 | 43.2541 | 43.2541 | 82.7903 | 127.4857 | 122.8394 | 76.7718 | 149.347 | 43.2541 | 43.2541 | 43.2541 | 43.2541 | 191.3706 | 358.8154 | 341.4087 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 21 | 3981 | 17.3 | 17.3 | 16.7042 | 14.7287 | 15 | 65 | 65 | 80.7376 | 18.6167 | -0.72196 | 311.2926 | 39.7398 | 0 | 0 | 0 | 0 | 21.1374 | 69.6325 | 77.3379 | 3.3833 | 35.9956 | 10.6294 | 10.6294 | 10.6294 | 10.6294 | 24.1216 | 55.0764 | 59.9948 | 18.6167 | 75.7354 | 10.6294 | 10.6294 | 10.6294 | 10.6294 | 45.2589 | 124.709 | 137.3327 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 22 | 3982 | 16.5 | 16.5 | 16.7042 | 14.7287 | 15 | 71 | 71 | 0 | 0 | -6.949 | 323.6097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 23 | 3983 | 15.6 | 15.6 | 16.7042 | 14.7287 | 15 | 81 | 81 | 0 | 0 | -11.5291 | 336.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 15 | 24 | 3984 | 15.4 | 15.4 | 17.2333 | 15.3897 | 15 | 81 | 81 | 0 | 0 | -14.1145 | 350.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 1 | 3985 | 15.1 | 15.1 | 17.2333 | 15.3897 | 15 | 82 | 82 | 0 | 0 | -14.4761 | 4.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 2 | 3986 | 14.2 | 14.2 | 17.2333 | 15.3897 | 15 | 85 | 85 | 0 | 0 | -12.5482 | 18.8336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 3 | 3987 | 14.6 | 14.6 | 17.2333 | 15.3897 | 15 | 84 | 84 | 0 | 0 | -8.5753 | 32.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 4 | 3988 | 15 | 15 | 17.2333 | 15.3897 | 15 | 84 | 84 | 0 | 0 | -2.8372 | 44.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 5 | 3989 | 15.7 | 15.7 | 17.2333 | 15.3897 | 15 | 83 | 83 | 1.7411 | 2.9674 | 4.2889 | 56.6162 | 1.2333 | 1.739 | 1.226 | 0 | 0 | 0 | 0 | 0.0052095 | 0.032608 | 2.9183 | 3.6639 | 2.9074 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 1.1075 | 2.9674 | 4.1516 | 5.4028 | 4.1334 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 1.1127 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 6 | 3990 | 16.3 | 16.3 | 17.2333 | 15.3897 | 15 | 83 | 83 | 0.56889 | 13.913 | 12.4314 | 67.8469 | 0.31215 | 0.55568 | 0.47369 | 0.11423 | 0 | 0 | 0 | 0 | 0.086982 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 13.913 | 7.0029 | 7.2464 | 7.1644 | 6.805 | 6.6908 | 6.6908 | 6.6908 | 6.6908 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 7 | 3991 | 15.8 | 15.8 | 17.2333 | 15.3897 | 15 | 93 | 93 | 0.47786 | 24.8576 | 21.2467 | 78.9106 | 0.17597 | 0.43004 | 0.4322 | 0.18119 | 0 | 0 | 0 | 0 | 0.14236 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 24.8576 | 12.0158 | 12.2698 | 12.272 | 12.021 | 11.8398 | 11.8398 | 11.8398 | 11.8398 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 16 | 8 | 3992 | 16.1 | 16.1 | 17.2333 | 15.3897 | 15 | 95 | 95 | 1.1584 | 57.4858 | 30.4045 | 90.3552 | 0.20767 | 0.89604 | 1.0595 | 0.60236 | 0 | 0 | 0 | 0 | 0.51422 | 27.911 | 27.911 | 27.911 | 27.911 | 27.911 | 27.911 | 27.911 | 27.911 | 57.4858 | 28.1187 | 28.8071 | 28.9706 | 28.5134 | 27.911 | 27.911 | 27.911 | 27.911 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 9 | 3993 | 15.4 | 15.4 | 17.2333 | 15.3897 | 15 | 89 | 89 | 0.95719 | 68.4439 | 39.5407 | 102.9647 | 0 | 0.58012 | 0.82554 | 0.58736 | 0.0051172 | 0 | 0 | 0 | 0.55608 | 33.2207 | 33.2207 | 33.2207 | 33.2207 | 33.2207 | 33.2207 | 33.2207 | 33.2207 | 68.4439 | 33.2207 | 33.8008 | 34.0462 | 33.808 | 33.2258 | 33.2207 | 33.2207 | 33.2207 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 10 | 3994 | 15.3 | 15.3 | 17.2333 | 15.3897 | 15 | 93 | 93 | 1.0977 | 88.2319 | 48.1647 | 117.9199 | 0 | 0.44902 | 0.82493 | 0.71761 | 0.18992 | 0 | 0 | 0 | 0.7681 | 43.1394 | 43.1394 | 43.1394 | 43.1394 | 43.1394 | 43.1394 | 43.1394 | 43.1394 | 88.2319 | 43.1394 | 43.5884 | 43.9643 | 43.857 | 43.3293 | 43.1394 | 43.1394 | 43.1394 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 11 | 3995 | 15.4 | 15.4 | 17.2333 | 15.3897 | 15 | 96 | 96 | 0.30373 | 52.7594 | 55.4901 | 136.9102 | 0 | 0.059501 | 0.179 | 0.19365 | 0.094858 | 0 | 0 | 0 | 0.24061 | 25.4401 | 25.4401 | 25.4401 | 25.4401 | 25.4401 | 25.4401 | 25.4401 | 25.4401 | 52.7594 | 25.4401 | 25.4996 | 25.6191 | 25.6337 | 25.5349 | 25.4401 | 25.4401 | 25.4401 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 12 | 3996 | 16.1 | 16.1 | 17.2333 | 15.3897 | 15 | 91 | 91 | 3.4467 | 189.0638 | 60.2425 | 161.3967 | 0 | 0 | 1.334 | 1.9517 | 1.4261 | 0.065092 | 0 | 0 | 2.9362 | 95.9015 | 95.9015 | 95.9015 | 95.9015 | 95.9015 | 95.9015 | 95.9015 | 95.9015 | 189.0638 | 95.9015 | 95.9015 | 97.2355 | 97.8532 | 97.3276 | 95.9666 | 95.9015 | 95.9015 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 13 | 3997 | 15.6 | 15.6 | 17.2333 | 15.3897 | 15 | 94 | 94 | 2.7159 | 172.6244 | 60.9712 | 189.6272 | 0 | 0 | 0.43002 | 1.2074 | 1.2775 | 0.59928 | 0 | 0 | 2.3756 | 87.0881 | 87.0881 | 87.0881 | 87.0881 | 87.0881 | 87.0881 | 87.0881 | 87.0881 | 172.6244 | 87.0881 | 87.0881 | 87.5181 | 88.2955 | 88.3656 | 87.6874 | 87.0881 | 87.0881 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 14 | 3998 | 17.3 | 17.3 | 17.2333 | 15.3897 | 15 | 81 | 81 | 65.0594 | 375.1115 | 57.3869 | 215.7788 | 0 | 0 | 0 | 18.2757 | 31.1254 | 25.7423 | 5.2797 | 0 | 55.8885 | 163.0892 | 163.0892 | 163.0892 | 200.7707 | 227.2647 | 216.1655 | 173.975 | 163.0892 | 375.1115 | 163.0892 | 163.0892 | 163.0892 | 219.0464 | 258.3901 | 241.9078 | 179.2546 | 163.0892 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 15 | 3999 | 14.7 | 14.7 | 17.2333 | 15.3897 | 15 | 91 | 91 | 1.7926 | 129.5552 | 50.7306 | 236.4622 | 0 | 0 | 0 | 0.15482 | 0.78382 | 0.95367 | 0.56487 | 0 | 1.4448 | 64.4114 | 64.4114 | 64.4114 | 64.4114 | 64.4114 | 64.4114 | 64.4114 | 64.4114 | 129.5552 | 64.4114 | 64.4114 | 64.4114 | 64.5662 | 65.1952 | 65.365 | 64.9762 | 64.4114 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 16 | 4000 | 15 | 15 | 17.2333 | 15.3897 | 15 | 92 | 92 | 0.58885 | 66.5765 | 42.4205 | 252.5192 | 0 | 0 | 0 | 0 | 0.20592 | 0.36529 | 0.31067 | 0.074068 | 0.42351 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 66.5765 | 32.3084 | 32.3084 | 32.3084 | 32.3084 | 32.5143 | 32.6737 | 32.6191 | 32.3825 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 17 | 4001 | 16 | 16 | 17.2333 | 15.3897 | 15 | 88 | 88 | 11.6101 | 206.9785 | 33.3865 | 265.7347 | 0 | 0 | 0 | 0 | 2.5745 | 7.601 | 8.1749 | 3.9601 | 7.0215 | 101.5044 | 101.5044 | 101.5044 | 101.5044 | 104.882 | 111.4762 | 112.2292 | 106.6997 | 206.9785 | 101.5044 | 101.5044 | 101.5044 | 101.5044 | 107.4565 | 119.0773 | 120.4041 | 110.6597 | 214 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 18 | 4002 | 17.1 | 17.1 | 17.2333 | 15.3897 | 15 | 80 | 80 | 223.1128 | 206.0355 | 24.1922 | 277.4555 | 0 | 0 | 0 | 0 | 13.8555 | 141.1624 | 185.7783 | 121.5678 | 104.9645 | 102.583 | 102.583 | 102.583 | 102.583 | 111.6059 | 194.5106 | 223.5653 | 181.7502 | 206.0355 | 102.583 | 102.583 | 102.583 | 102.583 | 125.4614 | 335.673 | 409.3436 | 303.318 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 19 | 4003 | 14.4 | 14.4 | 17.2333 | 15.3897 | 15 | 92 | 92 | 0.6979 | 32.7729 | 15.2294 | 288.5736 | 0.082604 | 0 | 0 | 0 | 0 | 0.38793 | 0.63122 | 0.50475 | 0.22709 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 32.7729 | 15.6723 | 15.5897 | 15.5897 | 15.5897 | 15.5897 | 15.9776 | 16.2209 | 16.0945 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 20 | 4004 | 14.6 | 14.6 | 17.2333 | 15.3897 | 15 | 88 | 88 | 12.0374 | 61.84 | 6.8325 | 299.7006 | 3.6995 | 0 | 0 | 0 | 0 | 5.1691 | 11.0097 | 10.401 | 2.16 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 61.84 | 34.3942 | 30.6947 | 30.6947 | 30.6947 | 30.6947 | 35.8638 | 41.7044 | 41.0957 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 21 | 4005 | 13.6 | 13.6 | 17.2333 | 15.3897 | 15 | 86 | 86 | 4.5404 | 10.8069 | -0.66222 | 311.274 | 2.2337 | 0 | 0 | 0 | 0 | 1.1895 | 3.9159 | 4.3484 | 0.19308 | 6.1437 | 5.7557 | 5.7557 | 5.7557 | 5.7557 | 5.9624 | 6.436 | 6.5111 | 10.8069 | 8.3774 | 5.7557 | 5.7557 | 5.7557 | 5.7557 | 7.1519 | 10.3519 | 10.8595 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 22 | 4006 | 13.6 | 13.6 | 17.2333 | 15.3897 | 15 | 87 | 87 | 0 | 0 | -6.8919 | 323.5839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 23 | 4007 | 13.6 | 13.6 | 17.2333 | 15.3897 | 15 | 85 | 85 | 0 | 0 | -11.4761 | 336.7384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 16 | 24 | 4008 | 12.9 | 12.9 | 15.1417 | 15.4178 | 15 | 83 | 83 | 0 | 0 | -14.0675 | 350.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 1 | 4009 | 12.6 | 12.6 | 15.1417 | 15.4178 | 15 | 79 | 79 | 0 | 0 | -14.4365 | 4.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 2 | 4010 | 12 | 12 | 15.1417 | 15.4178 | 15 | 84 | 84 | 0 | 0 | -12.5236 | 18.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 3 | 4011 | 11.6 | 11.6 | 15.1417 | 15.4178 | 15 | 86 | 86 | 0 | 0 | -8.5588 | 32.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 4 | 4012 | 11.3 | 11.3 | 15.1417 | 15.4178 | 15 | 89 | 89 | 0 | 0 | -2.8279 | 44.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 5 | 4013 | 11.4 | 11.4 | 15.1417 | 15.4178 | 15 | 89 | 89 | 8.3388 | 8.7003 | 4.2923 | 56.5577 | 5.9127 | 8.3285 | 5.8656 | 0 | 0 | 0 | 0 | 0.033341 | 2.2997 | 9.6488 | 12.2231 | 9.5985 | 3.348 | 3.348 | 3.348 | 3.348 | 3.3835 | 8.7003 | 15.5615 | 20.5516 | 15.4641 | 3.348 | 3.348 | 3.348 | 3.348 | 3.4169 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 6 | 4014 | 12 | 12 | 15.1417 | 15.4178 | 15 | 88 | 88 | 57.4452 | 66.1888 | 12.4304 | 67.7871 | 31.5691 | 56.1226 | 47.8002 | 11.4772 | 0 | 0 | 0 | 0 | 8.8112 | 143.8945 | 234.2671 | 203.6356 | 69.9435 | 27.7002 | 27.7002 | 27.7002 | 27.7002 | 66.1888 | 175.4635 | 290.3896 | 251.4358 | 81.4207 | 27.7002 | 27.7002 | 27.7002 | 27.7002 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 7 | 4015 | 13 | 13 | 15.1417 | 15.4178 | 15 | 85 | 85 | 236.1606 | 129.5406 | 21.2429 | 78.8481 | 87.1875 | 212.6244 | 213.5089 | 89.3227 | 0 | 0 | 0 | 0 | 70.4594 | 108.673 | 168.7045 | 169.1278 | 109.6949 | 66.9468 | 66.9468 | 66.9468 | 66.9468 | 129.5406 | 195.8605 | 381.3289 | 382.6366 | 199.0176 | 66.9468 | 66.9468 | 66.9468 | 66.9468 | 200 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 17 | 8 | 4016 | 14.3 | 14.3 | 15.1417 | 15.4178 | 15 | 80 | 80 | 319.7828 | 179.919 | 30.3997 | 90.2877 | 57.6468 | 247.5393 | 292.4265 | 166.0143 | 0 | 0 | 0 | 0 | 142.081 | 120.9503 | 201.7286 | 220.8232 | 167.0487 | 96.4279 | 96.4279 | 96.4279 | 96.4279 | 179.919 | 178.5971 | 449.2679 | 513.2498 | 333.063 | 96.4279 | 96.4279 | 96.4279 | 96.4279 | 322 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 9 | 4017 | 15.3 | 15.3 | 15.1417 | 15.4178 | 15 | 72 | 72 | 550.44 | 174.0184 | 39.5373 | 102.8891 | 0 | 334.0188 | 474.7576 | 337.3898 | 2.3837 | 0 | 0 | 0 | 319.9816 | 111.0557 | 194.2813 | 229.3485 | 195.1213 | 111.6497 | 111.0557 | 111.0557 | 111.0557 | 174.0184 | 111.0557 | 528.3001 | 704.106 | 532.5111 | 114.0333 | 111.0557 | 111.0557 | 111.0557 | 494 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 10 | 4018 | 16.3 | 16.3 | 15.1417 | 15.4178 | 15 | 64 | 64 | 355.181 | 273.3446 | 48.1658 | 117.8323 | 0 | 145.6044 | 267.0177 | 232.0156 | 61.1019 | 0 | 0 | 0 | 248.6554 | 140.5531 | 213.1563 | 273.697 | 256.2437 | 171.0205 | 140.5531 | 140.5531 | 140.5531 | 273.3446 | 140.5531 | 358.7607 | 540.7146 | 488.2593 | 232.1224 | 140.5531 | 140.5531 | 140.5531 | 522 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 11 | 4019 | 16.6 | 16.6 | 15.1417 | 15.4178 | 15 | 58 | 58 | 650.2634 | 198.6739 | 55.5003 | 136.8087 | 0 | 128.0181 | 383.5384 | 414.3871 | 202.4934 | 0 | 0 | 0 | 515.3261 | 134.2655 | 161.7864 | 216.7172 | 223.349 | 177.7968 | 134.2655 | 134.2655 | 134.2655 | 198.6739 | 134.2655 | 289.8045 | 600.2556 | 637.736 | 380.2902 | 134.2655 | 134.2655 | 134.2655 | 714 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 12 | 4020 | 17 | 17 | 15.1417 | 15.4178 | 15 | 55 | 55 | 141.7054 | 385.2398 | 60.2671 | 161.29 | 0 | 0 | 54.9343 | 80.2222 | 58.517 | 2.5333 | 0 | 0 | 120.7602 | 167.3129 | 167.3129 | 242.2628 | 276.7644 | 247.1508 | 170.7693 | 167.3129 | 167.3129 | 385.2398 | 167.3129 | 167.3129 | 297.1971 | 356.9866 | 305.6678 | 173.3026 | 167.3129 | 167.3129 | 506 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 13 | 4021 | 16.9 | 16.9 | 15.1417 | 15.4178 | 15 | 53 | 53 | 50.6402 | 372.6889 | 61.0115 | 189.5401 | 0 | 0 | 8.0565 | 22.5175 | 23.7881 | 11.1239 | 0 | 0 | 44.3111 | 161.1357 | 161.1357 | 182.3416 | 220.4055 | 223.7499 | 190.4157 | 161.1357 | 161.1357 | 372.6889 | 161.1357 | 161.1357 | 190.3981 | 242.923 | 247.538 | 201.5397 | 161.1357 | 161.1357 | 417 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 14 | 4022 | 17.3 | 17.3 | 15.1417 | 15.4178 | 15 | 55 | 55 | 11.9547 | 295.7269 | 57.4376 | 215.7251 | 0 | 0 | 0 | 3.3611 | 5.7135 | 4.7191 | 0.96023 | 0 | 10.2731 | 144.0448 | 144.0448 | 144.0448 | 151.3951 | 156.5396 | 154.3648 | 146.1447 | 144.0448 | 295.7269 | 144.0448 | 144.0448 | 144.0448 | 154.7562 | 162.2531 | 159.0839 | 147.1049 | 144.0448 | 306 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 15 | 4023 | 17.3 | 17.3 | 15.1417 | 15.4178 | 15 | 52 | 52 | 16.7096 | 294.5274 | 50.7859 | 236.4324 | 0 | 0 | 0 | 1.4495 | 7.3011 | 8.8758 | 5.2512 | 0 | 13.4726 | 142.5779 | 142.5779 | 142.5779 | 145.1921 | 155.7454 | 158.5855 | 152.0485 | 142.5779 | 294.5274 | 142.5779 | 142.5779 | 142.5779 | 146.6415 | 163.0465 | 167.4613 | 157.2997 | 142.5779 | 308 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 16 | 4024 | 17.3 | 17.3 | 15.1417 | 15.4178 | 15 | 56 | 56 | 4.8318 | 188.5232 | 42.4774 | 252.5013 | 0 | 0 | 0 | 0 | 1.6891 | 2.9942 | 2.5454 | 0.6055 | 3.4768 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 188.5232 | 95.7434 | 95.7434 | 95.7434 | 95.7434 | 97.4325 | 98.7376 | 98.2888 | 96.3489 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 17 | 4025 | 16.6 | 16.6 | 15.1417 | 15.4178 | 15 | 62 | 62 | 2.4084 | 112.5426 | 33.4438 | 265.7216 | 0 | 0 | 0 | 0 | 0.53411 | 1.5756 | 1.6941 | 0.82024 | 1.4574 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 112.5426 | 55.6122 | 55.6122 | 55.6122 | 55.6122 | 56.1463 | 57.1877 | 57.3063 | 56.4324 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 18 | 4026 | 13.3 | 13.3 | 15.1417 | 15.4178 | 15 | 93 | 93 | 0.53995 | 41.7458 | 24.2495 | 277.4431 | 0 | 0 | 0 | 0 | 0.033613 | 0.34147 | 0.44929 | 0.29393 | 0.25424 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 41.7458 | 19.9596 | 19.9596 | 19.9596 | 19.9596 | 19.9932 | 20.301 | 20.4088 | 20.2535 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 19 | 4027 | 13.5 | 13.5 | 15.1417 | 15.4178 | 15 | 94 | 94 | 2.1503 | 57.2994 | 15.2862 | 288.5596 | 0.25398 | 0 | 0 | 0 | 0 | 1.1951 | 1.9441 | 1.5543 | 0.70065 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 57.2994 | 28.0038 | 27.7498 | 27.7498 | 27.7498 | 27.7498 | 28.9449 | 29.6939 | 29.3041 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 20 | 4028 | 13.4 | 13.4 | 15.1417 | 15.4178 | 15 | 95 | 95 | 4.0586 | 43.2698 | 6.8883 | 299.6832 | 1.2461 | 0 | 0 | 0 | 0 | 1.7432 | 3.7114 | 3.5055 | 0.73023 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 43.2698 | 22.2314 | 20.9853 | 20.9853 | 20.9853 | 20.9853 | 22.7285 | 24.6967 | 24.4908 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 21 | 4029 | 13.1 | 13.1 | 15.1417 | 15.4178 | 15 | 94 | 94 | 19.7198 | 16.1512 | -0.60827 | 311.2516 | 9.6948 | 0 | 0 | 0 | 0 | 5.1715 | 17.0084 | 18.8821 | 0.84876 | 16.4079 | 8.7762 | 8.7762 | 8.7762 | 8.7762 | 12.8472 | 22.165 | 23.6399 | 16.1512 | 26.1027 | 8.7762 | 8.7762 | 8.7762 | 8.7762 | 18.0186 | 39.1734 | 42.5219 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 22 | 4030 | 13.1 | 13.1 | 15.1417 | 15.4178 | 15 | 91 | 91 | 0 | 0 | -6.841 | 323.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 23 | 4031 | 13 | 13 | 15.1417 | 15.4178 | 15 | 92 | 92 | 0 | 0 | -11.4297 | 336.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 17 | 24 | 4032 | 13.3 | 13.3 | 14.2292 | 15.2486 | 15 | 89 | 89 | 0 | 0 | -14.0272 | 350.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 1 | 4033 | 13.1 | 13.1 | 14.2292 | 15.2486 | 15 | 90 | 90 | 0 | 0 | -14.4038 | 4.7569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 2 | 4034 | 13 | 13 | 14.2292 | 15.2486 | 15 | 91 | 91 | 0 | 0 | -12.5059 | 18.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 3 | 4035 | 13.5 | 13.5 | 14.2292 | 15.2486 | 15 | 92 | 92 | 0 | 0 | -8.5489 | 32.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 4 | 4036 | 13.8 | 13.8 | 14.2292 | 15.2486 | 15 | 92 | 92 | 0 | 0 | -2.8248 | 44.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 5 | 4037 | 14 | 14 | 14.2292 | 15.2486 | 15 | 91 | 91 | 1.5784 | 2.9689 | 4.2898 | 56.5029 | 1.1202 | 1.5764 | 1.1092 | 0 | 0 | 0 | 0 | 0.0078154 | 0.031051 | 2.9232 | 3.6656 | 2.9052 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.1129 | 2.9689 | 4.0435 | 5.2421 | 4.0144 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.1207 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 6 | 4038 | 13.6 | 13.6 | 14.2292 | 15.2486 | 15 | 92 | 92 | 0.34729 | 10.9466 | 12.4238 | 67.7315 | 0.19113 | 0.33936 | 0.2888 | 0.069063 | 0 | 0 | 0 | 0 | 0.053406 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 10.9466 | 5.4009 | 5.5491 | 5.4986 | 5.2788 | 5.2098 | 5.2098 | 5.2098 | 5.2098 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 7 | 4039 | 13.7 | 13.7 | 14.2292 | 15.2486 | 15 | 92 | 92 | 1.9016 | 49.432 | 21.2337 | 78.7903 | 0.70374 | 1.7128 | 1.7186 | 0.7176 | 0 | 0 | 0 | 0 | 0.56804 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 49.432 | 25.0333 | 26.0424 | 26.0481 | 25.0471 | 24.3295 | 24.3295 | 24.3295 | 24.3295 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 18 | 8 | 4040 | 14 | 14 | 14.2292 | 15.2486 | 15 | 85 | 85 | 3.4331 | 98.4735 | 30.3896 | 90.2253 | 0.62209 | 2.6595 | 3.139 | 1.7797 | 0 | 0 | 0 | 0 | 1.5265 | 49.3846 | 52.3068 | 52.9945 | 51.045 | 48.4923 | 48.4923 | 48.4923 | 48.4923 | 98.4735 | 50.0067 | 54.9663 | 56.1335 | 52.8247 | 48.4923 | 48.4923 | 48.4923 | 48.4923 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 9 | 4041 | 13.4 | 13.4 | 14.2292 | 15.2486 | 15 | 85 | 85 | 2.3403 | 106.6389 | 39.5284 | 102.8191 | 0 | 1.4218 | 2.0187 | 1.4331 | 0.0079395 | 0 | 0 | 0 | 1.3611 | 52.9008 | 52.9008 | 52.9008 | 52.9008 | 52.9008 | 52.9008 | 52.9008 | 52.9008 | 106.6389 | 52.9008 | 54.3226 | 54.9195 | 54.3338 | 52.9087 | 52.9008 | 52.9008 | 52.9008 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 10 | 4042 | 14.6 | 14.6 | 14.2292 | 15.2486 | 15 | 72 | 72 | 10.8404 | 236.4079 | 48.1611 | 117.7506 | 0 | 4.4532 | 8.1529 | 7.0768 | 1.8552 | 0 | 0 | 0 | 7.5921 | 111.5343 | 127.1199 | 140.0686 | 136.3022 | 118.0272 | 111.5343 | 111.5343 | 111.5343 | 236.4079 | 111.5343 | 131.5731 | 148.2215 | 143.379 | 119.8823 | 111.5343 | 111.5343 | 111.5343 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 11 | 4043 | 15.8 | 15.8 | 14.2292 | 15.2486 | 15 | 67 | 67 | 52.8225 | 339.1253 | 55.5042 | 136.7124 | 0 | 10.4482 | 31.182 | 33.6499 | 16.4061 | 0 | 0 | 0 | 41.8747 | 148.9189 | 174.3694 | 224.8746 | 230.886 | 188.8822 | 148.9189 | 148.9189 | 148.9189 | 339.1253 | 148.9189 | 184.8175 | 256.0566 | 264.5359 | 205.2882 | 148.9189 | 148.9189 | 148.9189 | 381 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 12 | 4044 | 14.3 | 14.3 | 14.2292 | 15.2486 | 15 | 80 | 80 | 10.843 | 287.757 | 60.2849 | 161.1856 | 0 | 0 | 4.2106 | 6.1382 | 4.4701 | 0.1835 | 0 | 0 | 9.243 | 138.7749 | 138.7749 | 150.4085 | 155.7344 | 151.1256 | 139.282 | 138.7749 | 138.7749 | 287.757 | 138.7749 | 138.7749 | 154.6191 | 161.8725 | 155.5957 | 139.4655 | 138.7749 | 138.7749 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 13 | 4045 | 12.9 | 12.9 | 14.2292 | 15.2486 | 15 | 84 | 84 | 17.1286 | 321.008 | 61.045 | 189.4508 | 0 | 0 | 2.7382 | 7.6191 | 8.0368 | 3.7467 | 0 | 0 | 14.992 | 153.9108 | 153.9108 | 160.0005 | 170.8556 | 171.7846 | 162.2434 | 153.9108 | 153.9108 | 321.008 | 153.9108 | 153.9108 | 162.7387 | 178.4747 | 179.8214 | 165.99 | 153.9108 | 153.9108 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 14 | 4046 | 13.9 | 13.9 | 14.2292 | 15.2486 | 15 | 82 | 82 | 12.8757 | 299.9323 | 57.4821 | 215.6658 | 0 | 0 | 0 | 3.6241 | 6.1488 | 5.0716 | 1.0235 | 0 | 11.0677 | 145.7723 | 145.7723 | 145.7723 | 153.6078 | 159.0663 | 156.7373 | 147.9852 | 145.7723 | 299.9323 | 145.7723 | 145.7723 | 145.7723 | 157.2319 | 165.2151 | 161.8089 | 149.0087 | 145.7723 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 15 | 4047 | 16.3 | 16.3 | 14.2292 | 15.2486 | 15 | 64 | 64 | 407.5417 | 296.3052 | 50.8355 | 236.3962 | 0 | 0 | 0 | 35.533 | 177.9869 | 216.1786 | 127.7357 | 0 | 328.6948 | 145.7447 | 145.7447 | 145.7447 | 163.9988 | 237.1808 | 256.8007 | 211.3655 | 145.7447 | 296.3052 | 145.7447 | 145.7447 | 145.7447 | 199.5318 | 415.1677 | 472.9793 | 339.1013 | 145.7447 | 625 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 16 | 4048 | 15.1 | 15.1 | 14.2292 | 15.2486 | 15 | 71 | 71 | 45.7257 | 303.0854 | 42.5291 | 252.4772 | 0 | 0 | 0 | 0 | 15.9824 | 28.3087 | 24.0521 | 5.7061 | 32.9146 | 135.422 | 135.422 | 135.422 | 135.422 | 171.758 | 199.7816 | 190.1042 | 148.3947 | 303.0854 | 135.422 | 135.422 | 135.422 | 135.422 | 187.7404 | 228.0902 | 214.1563 | 154.1008 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 17 | 4049 | 16.7 | 16.7 | 14.2292 | 15.2486 | 15 | 60 | 60 | 434.5147 | 214.9271 | 33.4962 | 265.7026 | 0 | 0 | 0 | 0 | 96.4102 | 284.0873 | 305.3498 | 147.7426 | 263.0729 | 118.0511 | 118.0511 | 118.0511 | 118.0511 | 153.5124 | 222.5431 | 230.3638 | 172.3933 | 214.9271 | 118.0511 | 118.0511 | 118.0511 | 118.0511 | 249.9226 | 506.6304 | 535.7137 | 320.1359 | 478 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 18 | 18 | 4050 | 16.1 | 16.1 | 14.2292 | 15.2486 | 15 | 63 | 63 | 54.6151 | 202.2662 | 24.3018 | 277.4255 | 0 | 0 | 0 | 0 | 3.4128 | 34.5277 | 45.4167 | 29.7013 | 25.7338 | 94.8413 | 94.8413 | 94.8413 | 94.8413 | 99.4618 | 141.5876 | 156.33 | 135.0532 | 202.2662 | 94.8413 | 94.8413 | 94.8413 | 94.8413 | 102.8746 | 176.1152 | 201.7467 | 164.7544 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 19 | 4051 | 15.6 | 15.6 | 14.2292 | 15.2486 | 15 | 63 | 63 | 216.5046 | 143.3787 | 15.3379 | 288.5409 | 25.5012 | 0 | 0 | 0 | 0 | 120.3243 | 195.6655 | 156.3885 | 70.6213 | 88.6993 | 74.9023 | 74.9023 | 74.9023 | 74.9023 | 140.0014 | 180.7633 | 159.5132 | 143.3787 | 114.2005 | 74.9023 | 74.9023 | 74.9023 | 74.9023 | 260.3257 | 376.4288 | 315.9017 | 214 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 20 | 4052 | 14.3 | 14.3 | 14.2292 | 15.2486 | 15 | 73 | 73 | 37.7599 | 74.1916 | 6.9387 | 299.6616 | 11.5793 | 0 | 0 | 0 | 0 | 16.225 | 34.5249 | 32.6006 | 6.8084 | 46.4099 | 36.9272 | 36.9272 | 36.9272 | 36.9272 | 50.2144 | 65.2009 | 63.625 | 74.1916 | 57.9893 | 36.9272 | 36.9272 | 36.9272 | 36.9272 | 66.4394 | 99.7258 | 96.2256 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 21 | 4053 | 13.2 | 13.2 | 14.2292 | 15.2486 | 15 | 83 | 83 | 2.3001 | 7.9 | -0.56016 | 311.2256 | 1.1299 | 0 | 0 | 0 | 0 | 0.60396 | 1.9841 | 2.2019 | 0.099957 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 7.9 | 5.3653 | 4.2354 | 4.2354 | 4.2354 | 4.2354 | 4.8393 | 6.2194 | 6.4373 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 22 | 4054 | 13.6 | 13.6 | 14.2292 | 15.2486 | 15 | 78 | 78 | 0 | 0 | -6.7963 | 323.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 23 | 4055 | 11.2 | 11.2 | 14.2292 | 15.2486 | 15 | 87 | 87 | 0 | 0 | -11.3899 | 336.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 18 | 24 | 4056 | 12.5 | 12.5 | 14.0917 | 15.1215 | 15 | 89 | 89 | 0 | 0 | -13.9938 | 350.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 1 | 4057 | 12.6 | 12.6 | 14.0917 | 15.1215 | 15 | 90 | 90 | 0 | 0 | -14.3779 | 4.7072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 2 | 4058 | 12.7 | 12.7 | 14.0917 | 15.1215 | 15 | 91 | 91 | 0 | 0 | -12.4949 | 18.6746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 3 | 4059 | 12.4 | 12.4 | 14.0917 | 15.1215 | 15 | 89 | 89 | 0 | 0 | -8.5454 | 32.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 4 | 4060 | 11.8 | 11.8 | 14.0917 | 15.1215 | 15 | 95 | 95 | 0 | 0 | -2.8278 | 44.6644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 5 | 4061 | 12.1 | 12.1 | 14.0917 | 15.1215 | 15 | 92 | 92 | 1.5286 | 2.9694 | 4.2816 | 56.4519 | 1.0859 | 1.5267 | 1.0732 | 0 | 0 | 0 | 0 | 0.0089429 | 0.03056 | 2.9253 | 3.6662 | 2.904 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.1154 | 2.9694 | 4.0112 | 5.1929 | 3.9773 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.1243 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 6 | 4062 | 12.8 | 12.8 | 14.0917 | 15.1215 | 15 | 92 | 92 | 6.5874 | 45.9851 | 12.4117 | 67.6801 | 3.6303 | 6.4382 | 5.4748 | 1.3042 | 0 | 0 | 0 | 0 | 1.0149 | 91.0304 | 146.8174 | 127.6755 | 44.8179 | 18.9059 | 18.9059 | 18.9059 | 18.9059 | 45.9851 | 94.6607 | 153.2556 | 133.1503 | 46.1222 | 18.9059 | 18.9059 | 18.9059 | 18.9059 | 47 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 7 | 4063 | 13.5 | 13.5 | 14.0917 | 15.1215 | 15 | 87 | 87 | 11.729 | 102.4932 | 21.2192 | 78.7371 | 4.3503 | 10.5691 | 10.5967 | 4.4168 | 0 | 0 | 0 | 0 | 3.5068 | 76.7243 | 122.3227 | 122.5248 | 77.2122 | 44.8264 | 44.8264 | 44.8264 | 44.8264 | 102.4932 | 81.0746 | 132.8918 | 133.1215 | 81.6291 | 44.8264 | 44.8264 | 44.8264 | 44.8264 | 106 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 19 | 8 | 4064 | 13.8 | 13.8 | 14.0917 | 15.1215 | 15 | 80 | 80 | 4.0004 | 106.2203 | 30.3743 | 90.1682 | 0.72835 | 3.1012 | 3.6574 | 2.0711 | 0 | 0 | 0 | 0 | 1.7797 | 53.6037 | 59.8188 | 61.2757 | 57.1208 | 51.6959 | 51.6959 | 51.6959 | 51.6959 | 106.2203 | 54.332 | 62.92 | 64.9331 | 59.192 | 51.6959 | 51.6959 | 51.6959 | 51.6959 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 9 | 4065 | 13.2 | 13.2 | 14.0917 | 15.1215 | 15 | 87 | 87 | 1.8866 | 95.9023 | 39.5141 | 102.7549 | 0 | 1.1475 | 1.6276 | 1.1543 | 0.0047794 | 0 | 0 | 0 | 1.0977 | 47.2872 | 47.2872 | 47.2872 | 47.2872 | 47.2872 | 47.2872 | 47.2872 | 47.2872 | 95.9023 | 47.2872 | 48.4347 | 48.9148 | 48.4414 | 47.2919 | 47.2872 | 47.2872 | 47.2872 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 10 | 4066 | 13.3 | 13.3 | 14.0917 | 15.1215 | 15 | 89 | 89 | 2.7889 | 140.0462 | 48.1507 | 117.6749 | 0 | 1.1479 | 2.0985 | 1.8197 | 0.47502 | 0 | 0 | 0 | 1.9538 | 70.0951 | 70.0951 | 70.0951 | 70.0951 | 70.0951 | 70.0951 | 70.0951 | 70.0951 | 140.0462 | 70.0951 | 71.243 | 72.1935 | 71.9148 | 70.5701 | 70.0951 | 70.0951 | 70.0951 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 11 | 4067 | 14.3 | 14.3 | 14.0917 | 15.1215 | 15 | 85 | 85 | 18.1644 | 293.5968 | 55.5019 | 136.6214 | 0 | 3.6089 | 10.7324 | 11.569 | 5.6286 | 0 | 0 | 0 | 14.4032 | 137.8827 | 147.4192 | 166.2431 | 168.4538 | 152.7563 | 137.8827 | 137.8827 | 137.8827 | 293.5968 | 137.8827 | 151.0281 | 176.9755 | 180.0228 | 158.385 | 137.8827 | 137.8827 | 137.8827 | 308 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 12 | 4068 | 14.8 | 14.8 | 14.0917 | 15.1215 | 15 | 81 | 81 | 115.014 | 384.9367 | 60.2958 | 161.0839 | 0 | 0 | 44.7403 | 65.1155 | 47.3469 | 1.8432 | 0 | 0 | 98.0633 | 164.9389 | 164.9389 | 240.0762 | 274.2946 | 244.4539 | 168.0344 | 164.9389 | 164.9389 | 384.9367 | 164.9389 | 164.9389 | 284.8165 | 339.41 | 291.8008 | 169.8776 | 164.9389 | 164.9389 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 13 | 4069 | 16.1 | 16.1 | 14.0917 | 15.1215 | 15 | 68 | 68 | 128.1303 | 395.8296 | 61.0716 | 189.3594 | 0 | 0 | 20.5829 | 57.0249 | 60.0626 | 27.9163 | 0 | 0 | 112.1704 | 168.9136 | 168.9136 | 200.5487 | 256.5589 | 261.2276 | 211.82 | 168.9136 | 168.9136 | 395.8296 | 168.9136 | 168.9136 | 221.1316 | 313.5838 | 321.2901 | 239.7363 | 168.9136 | 168.9136 | 508 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 14 | 4070 | 15.6 | 15.6 | 14.0917 | 15.1215 | 15 | 75 | 75 | 36.2172 | 351.8617 | 57.5202 | 215.6012 | 0 | 0 | 0 | 10.2082 | 17.2856 | 14.2374 | 2.849 | 0 | 31.1383 | 152.5235 | 152.5235 | 152.5235 | 186.802 | 210.5675 | 200.3316 | 162.0903 | 152.5235 | 351.8617 | 152.5235 | 152.5235 | 152.5235 | 197.0102 | 227.8531 | 214.5689 | 164.9394 | 152.5235 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 15 | 4071 | 15.1 | 15.1 | 14.0917 | 15.1215 | 15 | 73 | 73 | 7.4773 | 249.9679 | 50.8796 | 236.3536 | 0 | 0 | 0 | 0.65573 | 3.2648 | 3.9614 | 2.3375 | 0 | 6.0321 | 124.0931 | 124.0931 | 124.0931 | 125.2072 | 129.64 | 130.8235 | 128.0644 | 124.0931 | 249.9679 | 124.0931 | 124.0931 | 124.0931 | 125.8629 | 132.9048 | 134.7849 | 130.4019 | 124.0931 | 256 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 16 | 4072 | 13.5 | 13.5 | 14.0917 | 15.1215 | 15 | 88 | 88 | 1.7016 | 112.7748 | 42.5757 | 252.4469 | 0 | 0 | 0 | 0 | 0.59486 | 1.0526 | 0.89377 | 0.21136 | 1.2252 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 112.7748 | 55.6933 | 55.6933 | 55.6933 | 55.6933 | 56.2882 | 56.7459 | 56.5871 | 55.9047 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 17 | 4073 | 14.2 | 14.2 | 14.0917 | 15.1215 | 15 | 88 | 88 | 3.5753 | 136.8345 | 33.5435 | 265.6781 | 0 | 0 | 0 | 0 | 0.79403 | 2.3365 | 2.5102 | 1.2135 | 2.1655 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 136.8345 | 68.3214 | 68.3214 | 68.3214 | 68.3214 | 69.1155 | 70.6579 | 70.8317 | 69.535 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 19 | 18 | 4074 | 14 | 14 | 14.0917 | 15.1215 | 15 | 87 | 87 | 3.0544 | 98.5601 | 24.349 | 277.4028 | 0 | 0 | 0 | 0 | 0.19185 | 1.9306 | 2.5385 | 1.6593 | 1.4399 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 98.5601 | 48.5826 | 48.5826 | 48.5826 | 48.5826 | 48.7744 | 50.5132 | 51.1211 | 50.2419 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 19 | 4075 | 13.8 | 13.8 | 14.0917 | 15.1215 | 15 | 89 | 89 | 1.9974 | 55.3479 | 15.3843 | 288.5176 | 0.23447 | 0 | 0 | 0 | 0 | 1.1103 | 1.8046 | 1.4418 | 0.65208 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 55.3479 | 26.9994 | 26.7649 | 26.7649 | 26.7649 | 26.7649 | 27.8752 | 28.5695 | 28.2068 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 20 | 4076 | 14 | 14 | 14.0917 | 15.1215 | 15 | 87 | 87 | 4.0292 | 43.2723 | 6.9835 | 299.6359 | 1.2338 | 0 | 0 | 0 | 0 | 1.7323 | 3.6837 | 3.4772 | 0.72768 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 43.2723 | 22.216 | 20.9822 | 20.9822 | 20.9822 | 20.9822 | 22.7145 | 24.6659 | 24.4594 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 21 | 4077 | 13.7 | 13.7 | 14.0917 | 15.1215 | 15 | 87 | 87 | 4.2867 | 10.8124 | -0.51792 | 311.196 | 2.104 | 0 | 0 | 0 | 0 | 1.1274 | 3.6983 | 4.1029 | 0.18764 | 6.1316 | 5.7598 | 5.7598 | 5.7598 | 5.7598 | 5.959 | 6.4134 | 6.4849 | 10.8124 | 8.2356 | 5.7598 | 5.7598 | 5.7598 | 5.7598 | 7.0864 | 10.1117 | 10.5877 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 22 | 4078 | 13.1 | 13.1 | 14.0917 | 15.1215 | 15 | 94 | 94 | 0 | 0 | -6.7578 | 323.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 23 | 4079 | 12.6 | 12.6 | 14.0917 | 15.1215 | 15 | 94 | 94 | 0 | 0 | -11.3566 | 336.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 19 | 24 | 4080 | 12.8 | 12.8 | 13.575 | 14.7723 | 15 | 89 | 89 | 0 | 0 | -13.9672 | 350.4717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 1 | 4081 | 12.8 | 12.8 | 13.575 | 14.7723 | 15 | 93 | 93 | 0 | 0 | -14.3589 | 4.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 2 | 4082 | 12.3 | 12.3 | 13.575 | 14.7723 | 15 | 95 | 95 | 0 | 0 | -12.4906 | 18.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 3 | 4083 | 11.9 | 11.9 | 13.575 | 14.7723 | 15 | 93 | 93 | 0 | 0 | -8.5483 | 32.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 4 | 4084 | 11.7 | 11.7 | 13.575 | 14.7723 | 15 | 91 | 91 | 0 | 0 | -2.8369 | 44.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 5 | 4085 | 11.1 | 11.1 | 13.575 | 14.7723 | 15 | 91 | 91 | 19.979 | 7.5963 | 4.2676 | 56.4046 | 14.2042 | 19.9541 | 14.0151 | 0 | 0 | 0 | 0 | 0.13373 | 0.40374 | 8.2434 | 10.3691 | 8.1735 | 2.9921 | 2.9921 | 2.9921 | 2.9921 | 3.0416 | 7.5963 | 22.4477 | 30.3232 | 22.1886 | 2.9921 | 2.9921 | 2.9921 | 2.9921 | 3.1753 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 6 | 4086 | 11.3 | 11.3 | 13.575 | 14.7723 | 15 | 90 | 90 | 67.6479 | 67.5635 | 12.3942 | 67.6331 | 37.3275 | 66.1284 | 56.1922 | 13.3394 | 0 | 0 | 0 | 0 | 10.4365 | 150.6908 | 245.2252 | 212.6111 | 71.9535 | 28.1692 | 28.1692 | 28.1692 | 28.1692 | 67.5635 | 188.0183 | 311.3536 | 268.8033 | 85.2929 | 28.1692 | 28.1692 | 28.1692 | 28.1692 | 78 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 7 | 4087 | 12.7 | 12.7 | 13.575 | 14.7723 | 15 | 85 | 85 | 321.1225 | 120.9284 | 21.1995 | 78.6888 | 119.3509 | 289.4846 | 290.0422 | 120.697 | 0 | 0 | 0 | 0 | 96.0716 | 107.811 | 167.0322 | 167.2262 | 108.2796 | 66.2666 | 66.2666 | 66.2666 | 66.2666 | 120.9284 | 227.1618 | 456.5167 | 457.2684 | 228.9765 | 66.2666 | 66.2666 | 66.2666 | 66.2666 | 217 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 20 | 8 | 4088 | 13.6 | 13.6 | 13.575 | 14.7723 | 15 | 84 | 84 | 232.1926 | 193.6617 | 30.3537 | 90.1165 | 42.4597 | 180.1244 | 212.2747 | 120.0773 | 0 | 0 | 0 | 0 | 103.3383 | 122.4484 | 210.3732 | 230.9072 | 172.0219 | 95.3299 | 95.3299 | 95.3299 | 95.3299 | 193.6617 | 164.9081 | 390.4976 | 443.1819 | 292.0992 | 95.3299 | 95.3299 | 95.3299 | 95.3299 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 9 | 4089 | 14.9 | 14.9 | 13.575 | 14.7723 | 15 | 78 | 78 | 161.4733 | 262.022 | 39.4946 | 102.6964 | 0 | 98.327 | 139.3386 | 98.7275 | 0.2832 | 0 | 0 | 0 | 93.978 | 121.7824 | 220.8843 | 262.2191 | 221.288 | 122.0679 | 121.7824 | 121.7824 | 121.7824 | 262.022 | 121.7824 | 319.2113 | 401.5577 | 320.0155 | 122.3511 | 121.7824 | 121.7824 | 121.7824 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 10 | 4090 | 16.9 | 16.9 | 13.575 | 14.7723 | 15 | 66 | 66 | 546.8079 | 210.848 | 48.1347 | 117.6052 | 0 | 225.4996 | 411.6457 | 356.6553 | 92.741 | 0 | 0 | 0 | 383.152 | 129.4832 | 194.1244 | 247.4846 | 231.7211 | 156.0681 | 129.4832 | 129.4832 | 129.4832 | 210.848 | 129.4832 | 419.624 | 659.1302 | 588.3764 | 248.8091 | 129.4832 | 129.4832 | 129.4832 | 594 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 11 | 4091 | 17.4 | 17.4 | 13.575 | 14.7723 | 15 | 60 | 60 | 871.9616 | 136.4731 | 55.4933 | 136.5359 | 0 | 173.971 | 515.6854 | 555.3183 | 269.6533 | 0 | 0 | 0 | 691.5269 | 130.7547 | 147.1852 | 179.4581 | 183.2012 | 156.2218 | 130.7547 | 130.7547 | 130.7547 | 136.4731 | 130.7547 | 321.1562 | 695.1435 | 738.5195 | 425.8751 | 130.7547 | 130.7547 | 130.7547 | 828 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 12 | 4092 | 17.6 | 17.6 | 13.575 | 14.7723 | 15 | 63 | 63 | 551.6678 | 254.5674 | 60.2999 | 160.985 | 0 | 0 | 214.9835 | 312.4092 | 226.8298 | 8.3766 | 0 | 0 | 470.4326 | 147.3691 | 147.3691 | 220.0527 | 252.9913 | 224.0579 | 150.2012 | 147.3691 | 147.3691 | 254.5674 | 147.3691 | 147.3691 | 435.0362 | 565.4006 | 450.8877 | 158.5778 | 147.3691 | 147.3691 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 13 | 4093 | 18.3 | 18.3 | 13.575 | 14.7723 | 15 | 61 | 61 | 613.4312 | 234.9023 | 61.0912 | 189.2662 | 0 | 0 | 99.0257 | 273.2063 | 287.3464 | 133.1629 | 0 | 0 | 537.0977 | 143.72 | 143.72 | 169.7131 | 215.4334 | 219.145 | 178.6737 | 143.72 | 143.72 | 234.9023 | 143.72 | 143.72 | 268.7387 | 488.6397 | 506.4914 | 311.8365 | 143.72 | 143.72 | 772 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 14 | 4094 | 17.6 | 17.6 | 13.575 | 14.7723 | 15 | 63 | 63 | 569.7509 | 249.0762 | 57.552 | 215.5313 | 0 | 0 | 0 | 160.855 | 271.8329 | 223.5748 | 44.3496 | 0 | 489.9238 | 142.7957 | 142.7957 | 142.7957 | 190.1714 | 222.8571 | 208.6439 | 155.8577 | 142.7957 | 249.0762 | 142.7957 | 142.7957 | 142.7957 | 351.0265 | 494.6901 | 432.2187 | 200.2073 | 142.7957 | 739 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 15 | 4095 | 17.6 | 17.6 | 13.575 | 14.7723 | 15 | 68 | 68 | 11.7243 | 276.5402 | 50.9179 | 236.3048 | 0 | 0 | 0 | 1.0348 | 5.1192 | 6.2048 | 3.6557 | 0 | 9.4598 | 135.193 | 135.193 | 135.193 | 137.1763 | 145.004 | 147.0845 | 142.1992 | 135.193 | 276.5402 | 135.193 | 135.193 | 135.193 | 138.2111 | 150.1232 | 153.2893 | 145.8549 | 135.193 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 16 | 4096 | 17.4 | 17.4 | 13.575 | 14.7723 | 15 | 67 | 67 | 12.3092 | 249.1352 | 42.6169 | 252.4105 | 0 | 0 | 0 | 0 | 4.3051 | 7.6096 | 6.4565 | 1.5212 | 8.8648 | 121.8314 | 121.8314 | 121.8314 | 121.8314 | 128.8253 | 134.1935 | 132.3201 | 124.3027 | 249.1352 | 121.8314 | 121.8314 | 121.8314 | 121.8314 | 133.1304 | 141.8031 | 138.7766 | 125.8239 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 17 | 4097 | 17.2 | 17.2 | 13.575 | 14.7723 | 15 | 69 | 69 | 125.6912 | 273.8541 | 33.5858 | 265.6479 | 0 | 0 | 0 | 0 | 27.9518 | 82.1114 | 88.1712 | 42.5816 | 76.1459 | 126.3507 | 126.3507 | 126.3507 | 126.3507 | 157.0219 | 216.4507 | 223.1002 | 173.0751 | 273.8541 | 126.3507 | 126.3507 | 126.3507 | 126.3507 | 184.9737 | 298.5621 | 311.2714 | 215.6567 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 20 | 18 | 4098 | 17.6 | 17.6 | 13.575 | 14.7723 | 15 | 69 | 69 | 114.7623 | 212.8784 | 24.3911 | 277.3749 | 0 | 0 | 0 | 0 | 7.255 | 72.5371 | 95.328 | 62.277 | 54.1216 | 101.2722 | 101.2722 | 101.2722 | 101.2722 | 108.4728 | 173.2654 | 195.8854 | 163.0823 | 212.8784 | 101.2722 | 101.2722 | 101.2722 | 101.2722 | 115.7278 | 245.8026 | 291.2134 | 225.3593 | 267 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 19 | 4099 | 16.9 | 16.9 | 13.575 | 14.7723 | 15 | 70 | 70 | 14.9948 | 117.1021 | 15.4254 | 288.4896 | 1.753 | 0 | 0 | 0 | 0 | 8.3372 | 13.5435 | 10.8162 | 4.8979 | 58.63 | 57.6925 | 57.6925 | 57.6925 | 57.6925 | 62.1513 | 64.9357 | 63.4772 | 117.1021 | 60.383 | 57.6925 | 57.6925 | 57.6925 | 57.6925 | 70.4885 | 78.4792 | 74.2934 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 20 | 4100 | 16.7 | 16.7 | 13.575 | 14.7723 | 15 | 76 | 76 | 20.5796 | 68.2792 | 7.0227 | 299.606 | 6.2914 | 0 | 0 | 0 | 0 | 8.855 | 18.8143 | 17.7524 | 3.7208 | 41.9664 | 34.0141 | 34.0141 | 34.0141 | 34.0141 | 45.2068 | 57.7953 | 56.453 | 68.2792 | 48.2578 | 34.0141 | 34.0141 | 34.0141 | 34.0141 | 54.0618 | 76.6095 | 74.2054 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 21 | 4101 | 16 | 16 | 13.575 | 14.7723 | 15 | 80 | 80 | 7.557 | 13.6676 | -0.4816 | 311.1628 | 3.7054 | 0 | 0 | 0 | 0 | 1.991 | 6.5211 | 7.2312 | 0.33241 | 8.1802 | 7.2356 | 7.2356 | 7.2356 | 7.2356 | 7.7431 | 8.8979 | 9.079 | 13.6676 | 11.8856 | 7.2356 | 7.2356 | 7.2356 | 7.2356 | 9.7341 | 15.4191 | 16.3102 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 22 | 4102 | 16 | 16 | 13.575 | 14.7723 | 15 | 82 | 82 | 0 | 0 | -6.7257 | 323.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 23 | 4103 | 15.7 | 15.7 | 13.575 | 14.7723 | 15 | 87 | 87 | 0 | 0 | -11.33 | 336.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 20 | 24 | 4104 | 15.4 | 15.4 | 15.275 | 14.8084 | 15 | 91 | 91 | 0 | 0 | -13.9474 | 350.4253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 1 | 4105 | 15.3 | 15.3 | 15.275 | 14.8084 | 15 | 93 | 93 | 0 | 0 | -14.3468 | 4.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 2 | 4106 | 14.9 | 14.9 | 15.275 | 14.8084 | 15 | 94 | 94 | 0 | 0 | -12.4931 | 18.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 3 | 4107 | 14.6 | 14.6 | 15.275 | 14.8084 | 15 | 96 | 96 | 0 | 0 | -8.5578 | 31.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 4 | 4108 | 14.8 | 14.8 | 15.275 | 14.8084 | 15 | 93 | 93 | 0 | 0 | -2.8522 | 44.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 5 | 4109 | 14.9 | 14.9 | 15.275 | 14.8084 | 15 | 94 | 94 | 6.0301 | 5.8775 | 4.2478 | 56.3612 | 4.2904 | 6.0224 | 4.2266 | 0 | 0 | 0 | 0 | 0.045108 | 0.12254 | 6.3991 | 8.1258 | 6.3355 | 2.1217 | 2.1217 | 2.1217 | 2.1217 | 2.1667 | 5.8775 | 10.6895 | 14.1483 | 10.5621 | 2.1217 | 2.1217 | 2.1217 | 2.1217 | 2.2118 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 6 | 4110 | 15.3 | 15.3 | 15.275 | 14.8084 | 15 | 94 | 94 | 1.7805 | 24.7251 | 12.3712 | 67.5904 | 0.9836 | 1.7408 | 1.4783 | 0.34978 | 0 | 0 | 0 | 0 | 0.27488 | 18.1305 | 22.9637 | 21.2879 | 14.0848 | 11.8522 | 11.8522 | 11.8522 | 11.8522 | 24.7251 | 19.1141 | 24.7045 | 22.7662 | 14.4346 | 11.8522 | 11.8522 | 11.8522 | 11.8522 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 7 | 4111 | 15.6 | 15.6 | 15.275 | 14.8084 | 15 | 95 | 95 | 1.8952 | 49.4328 | 21.1745 | 78.6454 | 0.70573 | 1.7092 | 1.7114 | 0.71113 | 0 | 0 | 0 | 0 | 0.56719 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 49.4328 | 25.0415 | 26.045 | 26.0472 | 25.0469 | 24.3358 | 24.3358 | 24.3358 | 24.3358 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 21 | 8 | 4112 | 16.4 | 16.4 | 15.275 | 14.8084 | 15 | 90 | 90 | 2.0847 | 77.072 | 30.328 | 90.07 | 0.38273 | 1.6183 | 1.9059 | 1.077 | 0 | 0 | 0 | 0 | 0.92799 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 77.072 | 38.3969 | 39.6325 | 39.9201 | 39.0912 | 38.0142 | 38.0142 | 38.0142 | 38.0142 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 9 | 4113 | 16.8 | 16.8 | 15.275 | 14.8084 | 15 | 86 | 86 | 1.7707 | 92.9693 | 39.4698 | 102.6438 | 0 | 1.0794 | 1.5284 | 1.082 | 0.0018679 | 0 | 0 | 0 | 1.0307 | 45.7668 | 45.7668 | 45.7668 | 45.7668 | 45.7668 | 45.7668 | 45.7668 | 45.7668 | 92.9693 | 45.7668 | 46.8462 | 47.2952 | 46.8489 | 45.7687 | 45.7668 | 45.7668 | 45.7668 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 10 | 4114 | 17 | 17 | 15.275 | 14.8084 | 15 | 74 | 74 | 25.8687 | 273.8717 | 48.113 | 117.5417 | 0 | 10.6874 | 19.4853 | 16.8691 | 4.3711 | 0 | 0 | 0 | 18.1283 | 125.6888 | 152.528 | 174.6223 | 168.0521 | 136.666 | 125.6888 | 125.6888 | 125.6888 | 273.8717 | 125.6888 | 163.2154 | 194.1076 | 184.9211 | 141.0371 | 125.6888 | 125.6888 | 125.6888 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 11 | 4115 | 17.3 | 17.3 | 15.275 | 14.8084 | 15 | 76 | 76 | 5.6108 | 223.5499 | 55.4785 | 136.4561 | 0 | 1.1239 | 3.3216 | 3.5736 | 1.7322 | 0 | 0 | 0 | 4.4501 | 110.0554 | 112.7691 | 118.0758 | 118.6842 | 114.238 | 110.0554 | 110.0554 | 110.0554 | 223.5499 | 110.0554 | 113.893 | 121.3974 | 122.2578 | 115.9702 | 110.0554 | 110.0554 | 110.0554 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 12 | 4116 | 18.6 | 18.6 | 15.275 | 14.8084 | 15 | 74 | 74 | 77.8462 | 377.6118 | 60.2972 | 160.8891 | 0 | 0 | 30.3924 | 44.1024 | 31.9778 | 1.121 | 0 | 0 | 66.3882 | 165.0558 | 165.0558 | 219.987 | 244.7664 | 222.8524 | 167.0819 | 165.0558 | 165.0558 | 377.6118 | 165.0558 | 165.0558 | 250.3794 | 288.8688 | 254.8302 | 168.203 | 165.0558 | 165.0558 | 444 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 13 | 4117 | 18.6 | 18.6 | 15.275 | 14.8084 | 15 | 69 | 69 | 5.9998 | 252.7464 | 61.104 | 189.1713 | 0 | 0 | 0.97332 | 2.6745 | 2.8091 | 1.2981 | 0 | 0 | 5.2536 | 125.9466 | 125.9466 | 127.7812 | 130.988 | 131.2415 | 128.3933 | 125.9466 | 125.9466 | 252.7464 | 125.9466 | 125.9466 | 128.7546 | 133.6625 | 134.0506 | 129.6914 | 125.9466 | 125.9466 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 14 | 4118 | 19.8 | 19.8 | 15.275 | 14.8084 | 15 | 57 | 57 | 110.7221 | 387.7838 | 57.5774 | 215.4562 | 0 | 0 | 0 | 31.3189 | 52.8194 | 43.3789 | 8.5277 | 0 | 95.2162 | 164.5252 | 164.5252 | 164.5252 | 218.7331 | 255.9468 | 239.607 | 179.2853 | 164.5252 | 387.7838 | 164.5252 | 164.5252 | 164.5252 | 250.052 | 308.7661 | 282.9859 | 187.813 | 164.5252 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 15 | 4119 | 20.6 | 20.6 | 15.275 | 14.8084 | 15 | 54 | 54 | 49.7407 | 342.8631 | 50.9505 | 236.2497 | 0 | 0 | 0 | 4.4217 | 21.7234 | 26.2998 | 15.4701 | 0 | 40.1369 | 150.4281 | 150.4281 | 150.4281 | 161.0142 | 202.4362 | 213.3926 | 187.4652 | 150.4281 | 342.8631 | 150.4281 | 150.4281 | 150.4281 | 165.4359 | 224.1596 | 239.6924 | 202.9354 | 150.4281 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 16 | 4120 | 20.4 | 20.4 | 15.275 | 14.8084 | 15 | 54 | 54 | 133.8544 | 325.592 | 42.6528 | 252.3681 | 0 | 0 | 0 | 0 | 46.85 | 82.7069 | 70.1152 | 16.451 | 96.408 | 145.9979 | 145.9979 | 145.9979 | 145.9979 | 202.0119 | 244.8827 | 229.828 | 165.6669 | 325.592 | 145.9979 | 145.9979 | 145.9979 | 145.9979 | 248.8619 | 327.5895 | 299.9433 | 182.1179 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 17 | 4121 | 19.6 | 19.6 | 15.275 | 14.8084 | 15 | 57 | 57 | 149.411 | 273.4722 | 33.6229 | 265.6121 | 0 | 0 | 0 | 0 | 33.285 | 97.5881 | 104.7254 | 50.5159 | 90.5278 | 127.6516 | 127.6516 | 127.6516 | 127.6516 | 158.3101 | 217.5389 | 224.1129 | 174.1813 | 273.4722 | 127.6516 | 127.6516 | 127.6516 | 127.6516 | 191.5951 | 315.127 | 328.8383 | 224.6972 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 21 | 18 | 4122 | 19.8 | 19.8 | 15.275 | 14.8084 | 15 | 63 | 63 | 84.6919 | 210.0521 | 24.4281 | 277.342 | 0 | 0 | 0 | 0 | 5.3956 | 53.5363 | 70.3162 | 45.9058 | 39.9479 | 99.2982 | 99.2982 | 99.2982 | 99.2982 | 104.3063 | 148.9896 | 164.5644 | 141.9071 | 210.0521 | 99.2982 | 99.2982 | 99.2982 | 99.2982 | 109.7019 | 202.5259 | 234.8806 | 187.8129 | 250 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 19 | 4123 | 19 | 19 | 15.275 | 14.8084 | 15 | 62 | 62 | 88.9518 | 145.9361 | 15.4612 | 288.4571 | 10.3498 | 0 | 0 | 0 | 0 | 49.4799 | 80.3249 | 64.1167 | 29.0639 | 81.604 | 71.4477 | 71.4477 | 71.4477 | 71.4477 | 120.003 | 150.2716 | 134.3662 | 145.9361 | 91.9538 | 71.4477 | 71.4477 | 71.4477 | 71.4477 | 169.4828 | 230.5965 | 198.4829 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 20 | 4124 | 18.8 | 18.8 | 15.275 | 14.8084 | 15 | 61 | 61 | 89.4121 | 80.8248 | 7.0563 | 299.5721 | 27.283 | 0 | 0 | 0 | 0 | 38.5094 | 81.7435 | 77.0934 | 16.1752 | 59.4607 | 41.4171 | 41.4171 | 41.4171 | 41.4171 | 66.8853 | 95.478 | 92.4026 | 80.8248 | 86.7436 | 41.4171 | 41.4171 | 41.4171 | 41.4171 | 105.3947 | 177.2215 | 169.496 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 21 | 4125 | 18 | 18 | 15.275 | 14.8084 | 15 | 68 | 68 | 30.1259 | 19.9075 | -0.45124 | 311.1261 | 14.7551 | 0 | 0 | 0 | 0 | 7.9536 | 26.0031 | 28.8204 | 5.0925 | 20.833 | 11.1141 | 11.1141 | 11.1141 | 11.1141 | 16.353 | 28.242 | 30.0977 | 19.9075 | 35.5881 | 11.1141 | 11.1141 | 11.1141 | 11.1141 | 24.3065 | 54.2451 | 58.9181 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 22 | 4126 | 17.1 | 17.1 | 15.275 | 14.8084 | 15 | 73 | 73 | 0 | 0 | -6.6998 | 323.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 23 | 4127 | 16.6 | 16.6 | 15.275 | 14.8084 | 15 | 76 | 76 | 0 | 0 | -11.31 | 336.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 21 | 24 | 4128 | 16 | 16 | 17.325 | 15.3728 | 15 | 77 | 77 | 0 | 0 | -13.9344 | 350.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 1 | 4129 | 15.5 | 15.5 | 17.325 | 15.3728 | 15 | 82 | 82 | 0 | 0 | -14.3416 | 4.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 2 | 4130 | 15.3 | 15.3 | 17.325 | 15.3728 | 15 | 82 | 82 | 0 | 0 | -12.5022 | 18.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 3 | 4131 | 15.7 | 15.7 | 17.325 | 15.3728 | 15 | 75 | 75 | 0 | 0 | -8.5736 | 31.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 4 | 4132 | 15.7 | 15.7 | 17.325 | 15.3728 | 15 | 72 | 72 | 0 | 0 | -2.8735 | 44.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 5 | 4133 | 15.6 | 15.6 | 17.325 | 15.3728 | 15 | 74 | 74 | 1.4781 | 2.9699 | 4.2224 | 56.3217 | 1.0524 | 1.4762 | 1.0353 | 0 | 0 | 0 | 0 | 0.012135 | 0.030056 | 2.2845 | 2.6717 | 2.2688 | 1.3229 | 1.3229 | 1.3229 | 1.3229 | 1.334 | 2.9699 | 3.3369 | 4.1479 | 3.304 | 1.3229 | 1.3229 | 1.3229 | 1.3229 | 1.3461 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 6 | 4134 | 15.2 | 15.2 | 17.325 | 15.3728 | 15 | 70 | 70 | 0.34469 | 10.9468 | 12.3428 | 67.5522 | 0.19062 | 0.33706 | 0.28606 | 0.067485 | 0 | 0 | 0 | 0 | 0.053218 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 10.9468 | 5.4028 | 5.5493 | 5.4983 | 5.2797 | 5.2122 | 5.2122 | 5.2122 | 5.2122 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 7 | 4135 | 15.4 | 15.4 | 17.325 | 15.3728 | 15 | 71 | 71 | 2.1296 | 52.3627 | 21.1443 | 78.6069 | 0.79436 | 1.9213 | 1.9227 | 0.79786 | 0 | 0 | 0 | 0 | 0.63734 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 52.3627 | 26.6755 | 27.8024 | 27.8038 | 26.679 | 25.8811 | 25.8811 | 25.8811 | 25.8811 | 53 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 22 | 8 | 4136 | 15.3 | 15.3 | 17.325 | 15.3728 | 15 | 71 | 71 | 1.9275 | 74.142 | 30.2973 | 90.029 | 0.35513 | 1.4973 | 1.7623 | 0.99505 | 0 | 0 | 0 | 0 | 0.85805 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 74.142 | 36.8416 | 37.9837 | 38.2488 | 37.4815 | 36.4864 | 36.4864 | 36.4864 | 36.4864 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 9 | 4137 | 16 | 16 | 17.325 | 15.3728 | 15 | 64 | 64 | 2.6045 | 112.4839 | 39.4398 | 102.5971 | 0 | 1.5893 | 2.2488 | 1.5909 | 0.0011396 | 0 | 0 | 0 | 1.5161 | 55.992 | 55.992 | 55.992 | 55.992 | 55.992 | 55.992 | 55.992 | 55.992 | 112.4839 | 55.992 | 57.5813 | 58.2407 | 57.5829 | 55.9931 | 55.992 | 55.992 | 55.992 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 10 | 4138 | 16.2 | 16.2 | 17.325 | 15.3728 | 15 | 63 | 63 | 2.788 | 140.0462 | 48.0859 | 117.4844 | 0 | 1.1538 | 2.1014 | 1.8179 | 0.4696 | 0 | 0 | 0 | 1.9538 | 70.0996 | 70.0996 | 70.0996 | 70.0996 | 70.0996 | 70.0996 | 70.0996 | 70.0996 | 140.0462 | 70.0996 | 71.2534 | 72.2009 | 71.9175 | 70.5692 | 70.0996 | 70.0996 | 70.0996 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 11 | 4139 | 16 | 16 | 17.325 | 15.3728 | 15 | 64 | 64 | 1.5286 | 117.7876 | 55.4576 | 136.382 | 0 | 0.30732 | 0.90586 | 0.97376 | 0.47125 | 0 | 0 | 0 | 1.2124 | 58.2602 | 58.2602 | 58.2602 | 58.2602 | 58.2602 | 58.2602 | 58.2602 | 58.2602 | 117.7876 | 58.2602 | 58.5675 | 59.1661 | 59.234 | 58.7315 | 58.2602 | 58.2602 | 58.2602 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 12 | 4140 | 16.2 | 16.2 | 17.325 | 15.3728 | 15 | 64 | 64 | 2.7621 | 169.6444 | 60.2877 | 160.7964 | 0 | 0 | 1.0804 | 1.5657 | 1.1338 | 0.037773 | 0 | 0 | 2.3556 | 85.4844 | 85.4844 | 85.4844 | 85.4844 | 85.4844 | 85.4844 | 85.4844 | 85.4844 | 169.6444 | 85.4844 | 85.4844 | 86.5648 | 87.0501 | 86.6182 | 85.5221 | 85.4844 | 85.4844 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 13 | 4141 | 16.5 | 16.5 | 17.325 | 15.3728 | 15 | 63 | 63 | 3.9429 | 207.5475 | 61.1098 | 189.075 | 0 | 0 | 0.64282 | 1.7595 | 1.8455 | 0.85046 | 0 | 0 | 3.4525 | 105.9045 | 105.9045 | 105.9045 | 105.9045 | 105.9045 | 105.9045 | 105.9045 | 105.9045 | 207.5475 | 105.9045 | 105.9045 | 106.5473 | 107.6641 | 107.7501 | 106.755 | 105.9045 | 105.9045 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 14 | 4142 | 16.5 | 16.5 | 17.325 | 15.3728 | 15 | 66 | 66 | 4.7732 | 223.8952 | 57.5964 | 215.3762 | 0 | 0 | 0 | 1.353 | 2.2772 | 1.8674 | 0.36373 | 0 | 4.1048 | 113.7198 | 113.7198 | 113.7198 | 114.4548 | 114.9569 | 114.7343 | 113.9174 | 113.7198 | 223.8952 | 113.7198 | 113.7198 | 113.7198 | 115.8079 | 117.2341 | 116.6017 | 114.2811 | 113.7198 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 15 | 4143 | 15.6 | 15.6 | 17.325 | 15.3728 | 15 | 68 | 68 | 19.8561 | 302.9775 | 50.9773 | 236.1886 | 0 | 0 | 0 | 1.7789 | 8.6759 | 10.4907 | 6.1602 | 0 | 16.0225 | 146.1034 | 146.1034 | 146.1034 | 149.1288 | 160.8593 | 163.946 | 156.5807 | 146.1034 | 302.9775 | 146.1034 | 146.1034 | 146.1034 | 150.9077 | 169.5352 | 174.4367 | 162.7409 | 146.1034 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 16 | 4144 | 15.6 | 15.6 | 17.325 | 15.3728 | 15 | 74 | 74 | 5.3941 | 199.1149 | 42.6834 | 252.3197 | 0 | 0 | 0 | 0 | 1.8899 | 3.3317 | 2.8219 | 0.65901 | 3.8851 | 100.5657 | 100.5657 | 100.5657 | 100.5657 | 101.4185 | 102.0692 | 101.8391 | 100.8631 | 199.1149 | 100.5657 | 100.5657 | 100.5657 | 100.5657 | 103.3084 | 105.4009 | 104.661 | 101.5221 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 17 | 4145 | 17.2 | 17.2 | 17.325 | 15.3728 | 15 | 59 | 59 | 97.5397 | 271.9001 | 33.6548 | 265.5708 | 0 | 0 | 0 | 0 | 21.7764 | 63.7048 | 68.3157 | 32.9082 | 59.0999 | 125.9561 | 125.9561 | 125.9561 | 125.9561 | 147.8325 | 189.9531 | 194.5852 | 159.0153 | 271.9001 | 125.9561 | 125.9561 | 125.9561 | 125.9561 | 169.6089 | 253.6579 | 262.9009 | 191.9236 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 22 | 18 | 4146 | 16.9 | 16.9 | 17.325 | 15.3728 | 15 | 64 | 64 | 148.5993 | 212.9065 | 24.4599 | 277.3041 | 0 | 0 | 0 | 0 | 9.5524 | 93.9573 | 123.3234 | 80.4483 | 70.0935 | 102.8844 | 102.8844 | 102.8844 | 102.8844 | 110.1982 | 174.8237 | 197.3081 | 164.4803 | 212.9065 | 102.8844 | 102.8844 | 102.8844 | 102.8844 | 119.7506 | 268.781 | 320.6315 | 244.9286 | 283 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 19 | 4147 | 16.4 | 16.4 | 17.325 | 15.3728 | 15 | 65 | 65 | 277.2201 | 137.4189 | 15.4916 | 288.4201 | 32.0816 | 0 | 0 | 0 | 0 | 154.2983 | 250.2923 | 199.6685 | 90.5811 | 87.5173 | 74.3846 | 74.3846 | 74.3846 | 74.3846 | 137.5474 | 176.8431 | 156.12 | 137.4189 | 119.5989 | 74.3846 | 74.3846 | 74.3846 | 74.3846 | 291.8457 | 427.1354 | 355.7885 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 20 | 4148 | 16.1 | 16.1 | 17.325 | 15.3728 | 15 | 68 | 68 | 59.306 | 78.2705 | 7.0843 | 299.5342 | 18.0588 | 0 | 0 | 0 | 0 | 25.5721 | 54.2232 | 51.1111 | 10.7295 | 56.9634 | 39.7643 | 39.7643 | 39.7643 | 39.7643 | 64.1192 | 91.4064 | 88.4424 | 78.2705 | 75.0222 | 39.7643 | 39.7643 | 39.7643 | 39.7643 | 89.6913 | 145.6297 | 139.5535 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 21 | 4149 | 16 | 16 | 17.325 | 15.3728 | 15 | 69 | 69 | 63.3851 | 19.2039 | -0.42686 | 311.0861 | 31.0067 | 0 | 0 | 0 | 0 | 16.7735 | 54.728 | 60.6236 | 2.7961 | 32.1345 | 10.7746 | 10.7746 | 10.7746 | 10.7746 | 22.3295 | 48.4756 | 52.5369 | 19.2039 | 63.1412 | 10.7746 | 10.7746 | 10.7746 | 10.7746 | 39.103 | 103.2035 | 113.1605 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 22 | 4150 | 15.6 | 15.6 | 17.325 | 15.3728 | 15 | 75 | 75 | 0 | 0 | -6.6804 | 323.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 23 | 4151 | 14.9 | 14.9 | 17.325 | 15.3728 | 15 | 81 | 81 | 0 | 0 | -11.2967 | 336.4917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 22 | 24 | 4152 | 15.1 | 15.1 | 15.8542 | 15.4212 | 15 | 80 | 80 | 0 | 0 | -13.9284 | 350.3302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 1 | 4153 | 14.6 | 14.6 | 15.8542 | 15.4212 | 15 | 74 | 74 | 0 | 0 | -14.3432 | 4.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 2 | 4154 | 14.3 | 14.3 | 15.8542 | 15.4212 | 15 | 76 | 76 | 0 | 0 | -12.5181 | 18.4832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 3 | 4155 | 14 | 14 | 15.8542 | 15.4212 | 15 | 78 | 78 | 0 | 0 | -8.5958 | 31.8995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 4 | 4156 | 14 | 14 | 15.8542 | 15.4212 | 15 | 80 | 80 | 0 | 0 | -2.9008 | 44.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 5 | 4157 | 14.1 | 14.1 | 15.8542 | 15.4212 | 15 | 83 | 83 | 6.0917 | 5.8767 | 4.1913 | 56.2861 | 4.34 | 6.0836 | 4.2635 | 0 | 0 | 0 | 0 | 0.054095 | 0.12331 | 6.404 | 8.1245 | 6.3285 | 2.1215 | 2.1215 | 2.1215 | 2.1215 | 2.1749 | 5.8767 | 10.7441 | 14.2082 | 10.5921 | 2.1215 | 2.1215 | 2.1215 | 2.1215 | 2.229 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 6 | 4158 | 14.3 | 14.3 | 15.8542 | 15.4212 | 15 | 84 | 84 | 2.236 | 27.655 | 12.3091 | 67.5184 | 1.2378 | 2.1869 | 1.855 | 0.43644 | 0 | 0 | 0 | 0 | 0.34504 | 25.6421 | 35.364 | 31.9641 | 17.4342 | 12.9638 | 12.9638 | 12.9638 | 12.9638 | 27.655 | 26.8799 | 37.5509 | 33.8191 | 17.8706 | 12.9638 | 12.9638 | 12.9638 | 12.9638 | 28 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 7 | 4159 | 15 | 15 | 15.8542 | 15.4212 | 15 | 82 | 82 | 23.2054 | 115.0568 | 21.1091 | 78.5733 | 8.6694 | 20.9434 | 20.949 | 8.6829 | 0 | 0 | 0 | 0 | 6.9432 | 95.2636 | 161.2313 | 161.2614 | 95.336 | 48.6686 | 48.6686 | 48.6686 | 48.6686 | 115.0568 | 103.933 | 182.1747 | 182.2103 | 104.019 | 48.6686 | 48.6686 | 48.6686 | 48.6686 | 122 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 23 | 8 | 4160 | 14.9 | 14.9 | 15.8542 | 15.4212 | 15 | 82 | 82 | 8.6816 | 143.136 | 30.2614 | 89.9935 | 1.6045 | 6.7479 | 7.9385 | 4.4788 | 0 | 0 | 0 | 0 | 3.864 | 74.6005 | 102.961 | 109.5257 | 90.4491 | 65.7532 | 65.7532 | 65.7532 | 65.7532 | 143.136 | 76.205 | 109.709 | 117.4642 | 94.9279 | 65.7532 | 65.7532 | 65.7532 | 65.7532 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 9 | 4161 | 16.3 | 16.3 | 15.8542 | 15.4212 | 15 | 73 | 73 | 17.7694 | 214.6577 | 39.4046 | 102.5564 | 0.0017316 | 10.8539 | 15.348 | 10.8515 | 0 | 0 | 0 | 0 | 10.3423 | 97.8879 | 135.7483 | 151.427 | 135.7397 | 97.8819 | 97.8819 | 97.8819 | 97.8819 | 214.6577 | 97.8897 | 146.6022 | 166.7751 | 146.5912 | 97.8819 | 97.8819 | 97.8819 | 97.8819 | 225 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 10 | 4162 | 16.7 | 16.7 | 15.8542 | 15.4212 | 15 | 74 | 74 | 111.3497 | 315.974 | 48.0532 | 117.4336 | 0 | 46.1567 | 83.9802 | 72.6092 | 18.7047 | 0 | 0 | 0 | 78.026 | 142.7334 | 198.822 | 244.7842 | 230.9665 | 165.463 | 142.7334 | 142.7334 | 142.7334 | 315.974 | 142.7334 | 244.9787 | 328.7644 | 303.5756 | 184.1677 | 142.7334 | 142.7334 | 142.7334 | 394 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 11 | 4163 | 17.6 | 17.6 | 15.8542 | 15.4212 | 15 | 64 | 64 | 174.6737 | 355.4678 | 55.4306 | 136.3139 | 0 | 35.2392 | 103.6289 | 111.3142 | 53.7932 | 0 | 0 | 0 | 138.5322 | 160.1173 | 197.0499 | 268.7261 | 276.7807 | 216.4955 | 160.1173 | 160.1173 | 160.1173 | 355.4678 | 160.1173 | 232.2891 | 372.355 | 388.095 | 270.2887 | 160.1173 | 160.1173 | 160.1173 | 494 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 12 | 4164 | 13.5 | 13.5 | 15.8542 | 15.4212 | 15 | 87 | 87 | 15.8289 | 308.5016 | 60.2714 | 160.7071 | 0 | 0 | 6.2035 | 8.979 | 6.4948 | 0.20594 | 0 | 0 | 13.4984 | 146.9667 | 146.9667 | 162.6501 | 169.667 | 163.3864 | 147.4873 | 146.9667 | 146.9667 | 308.5016 | 146.9667 | 146.9667 | 168.8536 | 178.6461 | 169.8812 | 147.6932 | 146.9667 | 146.9667 | 322 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 13 | 4165 | 16.8 | 16.8 | 15.8542 | 15.4212 | 15 | 75 | 75 | 94.4756 | 392.2787 | 61.1086 | 188.9774 | 0 | 0 | 15.479 | 42.2127 | 44.2187 | 20.322 | 0 | 0 | 82.7213 | 171.5928 | 171.5928 | 195.2417 | 236.0856 | 239.1504 | 202.6409 | 171.5928 | 171.5928 | 392.2787 | 171.5928 | 171.5928 | 210.7207 | 278.2982 | 283.3691 | 222.963 | 171.5928 | 171.5928 | 475 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 14 | 4166 | 17.9 | 17.9 | 15.8542 | 15.4212 | 15 | 61 | 61 | 682.4774 | 202.1298 | 57.6089 | 215.2914 | 0 | 0 | 0 | 193.921 | 325.7 | 266.6883 | 51.4543 | 0 | 586.8702 | 138.2498 | 138.2498 | 138.2498 | 179.5593 | 207.6311 | 195.0603 | 149.2107 | 138.2498 | 202.1298 | 138.2498 | 138.2498 | 138.2498 | 373.4803 | 533.3311 | 461.7487 | 200.6649 | 138.2498 | 789 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 15 | 4167 | 17.2 | 17.2 | 15.8542 | 15.4212 | 15 | 65 | 65 | 25.8084 | 315.1759 | 50.9982 | 236.1215 | 0 | 0 | 0 | 2.3315 | 11.2847 | 13.6275 | 7.9874 | 0 | 20.8241 | 138.5356 | 138.5356 | 138.5356 | 147.9909 | 184.3 | 193.801 | 170.9282 | 138.5356 | 315.1759 | 138.5356 | 138.5356 | 138.5356 | 150.3224 | 195.5847 | 207.4284 | 178.9157 | 138.5356 | 336 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 16 | 4168 | 17.1 | 17.1 | 15.8542 | 15.4212 | 15 | 64 | 64 | 29.5303 | 286.7324 | 42.7085 | 252.2654 | 0 | 0 | 0 | 0 | 10.3597 | 18.2357 | 15.4294 | 3.5848 | 21.2676 | 128.2113 | 128.2113 | 128.2113 | 128.2113 | 161.5993 | 186.9824 | 177.9382 | 139.7646 | 286.7324 | 128.2113 | 128.2113 | 128.2113 | 128.2113 | 171.959 | 205.2181 | 193.3676 | 143.3494 | 308 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 17 | 4169 | 18.1 | 18.1 | 15.8542 | 15.4212 | 15 | 56 | 56 | 593.819 | 168.2389 | 33.6815 | 265.5241 | 0 | 0 | 0 | 0 | 132.9144 | 387.8654 | 415.6101 | 199.896 | 359.7611 | 109.4448 | 109.4448 | 109.4448 | 109.4448 | 137.4634 | 191.2076 | 197.0563 | 151.5833 | 168.2389 | 109.4448 | 109.4448 | 109.4448 | 109.4448 | 270.3779 | 579.073 | 612.6664 | 351.4793 | 528 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 18 | 4170 | 17.3 | 17.3 | 15.8542 | 15.4212 | 15 | 56 | 56 | 477.8961 | 157.6122 | 24.4864 | 277.2613 | 0 | 0 | 0 | 0 | 31.0341 | 302.2842 | 396.4603 | 258.3953 | 225.3878 | 94.5066 | 94.5066 | 94.5066 | 94.5066 | 102.9038 | 176.2986 | 201.7807 | 164.4231 | 157.6122 | 94.5066 | 94.5066 | 94.5066 | 94.5066 | 133.9379 | 478.5828 | 598.241 | 422.8185 | 383 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 19 | 4171 | 16.9 | 16.9 | 15.8542 | 15.4212 | 15 | 56 | 56 | 277.5437 | 137.3343 | 15.5166 | 288.3786 | 31.9249 | 0 | 0 | 0 | 0 | 154.5954 | 250.5557 | 199.744 | 90.6657 | 87.3994 | 74.3552 | 74.3552 | 74.3552 | 74.3552 | 137.5216 | 176.7303 | 155.969 | 137.3343 | 119.3243 | 74.3552 | 74.3552 | 74.3552 | 74.3552 | 292.117 | 427.2861 | 355.713 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 20 | 4172 | 15.6 | 15.6 | 15.8542 | 15.4212 | 15 | 59 | 59 | 267.2937 | 76.6642 | 7.1066 | 299.4923 | 81.2046 | 0 | 0 | 0 | 0 | 115.4071 | 244.4148 | 230.2477 | 48.3358 | 71.3727 | 43.5304 | 43.5304 | 43.5304 | 43.5304 | 83.0996 | 127.3321 | 122.4747 | 76.6642 | 152.5773 | 43.5304 | 43.5304 | 43.5304 | 43.5304 | 198.5067 | 371.747 | 352.7224 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 21 | 4173 | 14.5 | 14.5 | 15.8542 | 15.4212 | 15 | 71 | 71 | 38.5377 | 18.3548 | -0.40851 | 311.0426 | 18.8266 | 0 | 0 | 0 | 0 | 10.2246 | 33.2864 | 36.8494 | 12.6452 | 31.7958 | 11.3151 | 11.3151 | 11.3151 | 11.3151 | 22.438 | 47.526 | 51.4021 | 18.3548 | 50.6224 | 11.3151 | 11.3151 | 11.3151 | 11.3151 | 32.6626 | 80.8123 | 88.2516 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 22 | 4174 | 13.9 | 13.9 | 15.8542 | 15.4212 | 15 | 77 | 77 | 0 | 0 | -6.6672 | 323.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 23 | 4175 | 13.4 | 13.4 | 15.8542 | 15.4212 | 15 | 80 | 80 | 0 | 0 | -11.2901 | 336.4441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 23 | 24 | 4176 | 13 | 13 | 15.4583 | 15.4414 | 15 | 84 | 84 | 0 | 0 | -13.9291 | 350.2816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 1 | 4177 | 12.5 | 12.5 | 15.4583 | 15.4414 | 15 | 88 | 88 | 0 | 0 | -14.3518 | 4.4634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 2 | 4178 | 12.8 | 12.8 | 15.4583 | 15.4414 | 15 | 84 | 84 | 0 | 0 | -12.5407 | 18.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 3 | 4179 | 12.8 | 12.8 | 15.4583 | 15.4414 | 15 | 85 | 85 | 0 | 0 | -8.6245 | 31.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 4 | 4180 | 12.7 | 12.7 | 15.4583 | 15.4414 | 15 | 86 | 86 | 0 | 0 | -2.9341 | 44.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 5 | 4181 | 12.5 | 12.5 | 15.4583 | 15.4414 | 15 | 85 | 85 | 6.2475 | 5.8747 | 4.1546 | 56.2546 | 4.4536 | 6.239 | 4.3697 | 0 | 0 | 0 | 0 | 0.059294 | 0.12526 | 6.4046 | 8.1218 | 6.3239 | 2.121 | 2.121 | 2.121 | 2.121 | 2.178 | 5.8747 | 10.8581 | 14.3608 | 10.6936 | 2.121 | 2.121 | 2.121 | 2.121 | 2.2373 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 6 | 4182 | 12.6 | 12.6 | 15.4583 | 15.4414 | 15 | 82 | 82 | 15.5733 | 55.5997 | 12.2701 | 67.4892 | 8.6283 | 15.2336 | 12.9154 | 3.0314 | 0 | 0 | 0 | 0 | 2.4003 | 147.0112 | 243.5089 | 209.6413 | 65.2475 | 20.9613 | 20.9613 | 20.9613 | 20.9613 | 55.5997 | 155.6394 | 258.7425 | 222.5566 | 68.2789 | 20.9613 | 20.9613 | 20.9613 | 20.9613 | 58 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 7 | 4183 | 14.4 | 14.4 | 15.4583 | 15.4414 | 15 | 71 | 71 | 333.1934 | 119.3626 | 21.0687 | 78.5448 | 124.6514 | 300.822 | 300.7752 | 124.5384 | 0 | 0 | 0 | 0 | 99.6374 | 107.5756 | 166.3945 | 166.3789 | 107.5378 | 65.9576 | 65.9576 | 65.9576 | 65.9576 | 119.3626 | 232.2269 | 467.2165 | 467.1541 | 232.0762 | 65.9576 | 65.9576 | 65.9576 | 65.9576 | 219 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 24 | 8 | 4184 | 14.9 | 14.9 | 15.4583 | 15.4414 | 15 | 68 | 68 | 417.3235 | 161.3205 | 30.2206 | 89.9636 | 77.3403 | 324.5681 | 381.6682 | 215.1923 | 0 | 0 | 0 | 0 | 185.6795 | 117.3969 | 193.5332 | 211.1178 | 159.8498 | 93.5791 | 93.5791 | 93.5791 | 93.5791 | 161.3205 | 194.7372 | 518.1013 | 592.786 | 375.0422 | 93.5791 | 93.5791 | 93.5791 | 93.5791 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 9 | 4185 | 13 | 13 | 15.4583 | 15.4414 | 15 | 79 | 79 | 130.6377 | 262.9833 | 39.3644 | 102.5218 | 0.071745 | 79.8712 | 112.8832 | 79.7697 | 0 | 0 | 0 | 0 | 76.0167 | 121.0175 | 201.5946 | 234.9283 | 201.4921 | 120.945 | 120.945 | 120.945 | 120.945 | 262.9833 | 121.0892 | 281.4658 | 347.8114 | 281.2618 | 120.945 | 120.945 | 120.945 | 120.945 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 10 | 4186 | 13.8 | 13.8 | 15.4583 | 15.4414 | 15 | 82 | 82 | 24.6117 | 271.757 | 48.0151 | 117.3891 | 0 | 10.2176 | 18.5754 | 16.052 | 4.1255 | 0 | 0 | 0 | 17.243 | 124.803 | 151.295 | 172.9649 | 166.4221 | 135.4994 | 124.803 | 124.803 | 124.803 | 271.757 | 124.803 | 161.5127 | 191.5403 | 182.4741 | 139.6249 | 124.803 | 124.803 | 124.803 | 289 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 11 | 4187 | 14.6 | 14.6 | 15.4583 | 15.4414 | 15 | 76 | 76 | 119.6667 | 358.1074 | 55.3975 | 136.2518 | 0 | 24.2189 | 71.0759 | 76.2976 | 36.8252 | 0 | 0 | 0 | 94.8926 | 156.5882 | 194.0111 | 266.4141 | 274.4826 | 213.4901 | 156.5882 | 156.5882 | 156.5882 | 358.1074 | 156.5882 | 218.23 | 337.49 | 350.7802 | 250.3153 | 156.5882 | 156.5882 | 156.5882 | 453 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 12 | 4188 | 15.1 | 15.1 | 15.4583 | 15.4414 | 15 | 72 | 72 | 24.0092 | 329.5284 | 60.2484 | 160.6214 | 0 | 0 | 9.428 | 13.6311 | 9.8492 | 0.29785 | 0 | 0 | 20.4716 | 155.2702 | 155.2702 | 175.3699 | 184.3304 | 176.2679 | 155.9052 | 155.2702 | 155.2702 | 329.5284 | 155.2702 | 155.2702 | 184.7979 | 197.9615 | 186.1171 | 156.2031 | 155.2702 | 155.2702 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 13 | 4189 | 16.5 | 16.5 | 15.4583 | 15.4414 | 15 | 56 | 56 | 21.9399 | 333.7922 | 61.1005 | 188.8788 | 0 | 0 | 3.6126 | 9.8169 | 10.2707 | 4.708 | 0 | 0 | 19.2078 | 159.0222 | 159.0222 | 166.3283 | 178.8762 | 179.7939 | 168.5438 | 159.0222 | 159.0222 | 333.7922 | 159.0222 | 159.0222 | 169.9409 | 188.6931 | 190.0645 | 173.2518 | 159.0222 | 159.0222 | 353 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 14 | 4190 | 16.8 | 16.8 | 15.4583 | 15.4414 | 15 | 53 | 53 | 361.794 | 332.9293 | 57.6149 | 215.2018 | 0 | 0 | 0 | 103.0706 | 172.7505 | 141.2355 | 26.9866 | 0 | 311.0707 | 152.9332 | 152.9332 | 152.9332 | 218.7029 | 263.1658 | 243.056 | 170.1535 | 152.9332 | 332.9293 | 152.9332 | 152.9332 | 152.9332 | 321.7735 | 435.9163 | 384.2914 | 197.1401 | 152.9332 | 644 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 15 | 4191 | 17.5 | 17.5 | 15.4583 | 15.4414 | 15 | 55 | 55 | 369.906 | 309.5752 | 51.0133 | 236.0485 | 0 | 0 | 0 | 33.7164 | 161.8927 | 195.2345 | 114.2105 | 0 | 298.4248 | 146.7757 | 146.7757 | 146.7757 | 166.4406 | 241.199 | 260.6455 | 213.3885 | 146.7757 | 309.5752 | 146.7757 | 146.7757 | 146.7757 | 200.157 | 403.0917 | 455.8799 | 327.5991 | 146.7757 | 608 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 16 | 4192 | 17.3 | 17.3 | 15.4583 | 15.4414 | 15 | 54 | 54 | 683.3663 | 168.9281 | 42.7282 | 252.2054 | 0 | 0 | 0 | 0 | 240.1135 | 421.9645 | 356.6343 | 82.3926 | 492.0719 | 120.9255 | 120.9255 | 120.9255 | 120.9255 | 165.0756 | 198.5129 | 186.5005 | 136.0752 | 168.9281 | 120.9255 | 120.9255 | 120.9255 | 120.9255 | 405.1892 | 620.4773 | 543.1348 | 218.4679 | 661 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 17 | 4193 | 16.7 | 16.7 | 15.4583 | 15.4414 | 15 | 53 | 53 | 236.6343 | 262.6688 | 33.7029 | 265.472 | 0 | 0 | 0 | 0 | 53.1226 | 154.5971 | 165.5107 | 79.4704 | 143.3312 | 125.2382 | 125.2382 | 125.2382 | 125.2382 | 163.9427 | 237.8757 | 245.8273 | 183.1393 | 262.6688 | 125.2382 | 125.2382 | 125.2382 | 125.2382 | 217.0653 | 392.4729 | 411.338 | 262.6097 | 406 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 18 | 4194 | 16.2 | 16.2 | 15.4583 | 15.4414 | 15 | 59 | 59 | 245.6723 | 203.1713 | 24.5076 | 277.2136 | 0 | 0 | 0 | 0 | 16.135 | 155.4774 | 203.7433 | 132.6591 | 115.8287 | 102.491 | 102.491 | 102.491 | 102.491 | 111.9272 | 193.4188 | 221.6461 | 180.074 | 203.1713 | 102.491 | 102.491 | 102.491 | 102.491 | 128.0622 | 348.8962 | 425.3893 | 312.7331 | 319 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 19 | 4195 | 14.7 | 14.7 | 15.4583 | 15.4414 | 15 | 59 | 59 | 2.8598 | 66.0663 | 15.5362 | 288.3327 | 0.32674 | 0 | 0 | 0 | 0 | 1.5944 | 2.5815 | 2.0565 | 0.93374 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 66.0663 | 32.5184 | 32.1916 | 32.1916 | 32.1916 | 32.1916 | 33.786 | 34.7731 | 34.2481 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 20 | 4196 | 14.2 | 14.2 | 15.4583 | 15.4414 | 15 | 65 | 65 | 4.5968 | 46.1696 | 7.1232 | 299.4466 | 1.393 | 0 | 0 | 0 | 0 | 1.9877 | 4.2041 | 3.9578 | 0.83045 | 22.453 | 22.453 | 22.453 | 22.453 | 22.453 | 22.453 | 22.453 | 22.453 | 46.1696 | 23.8461 | 22.453 | 22.453 | 22.453 | 22.453 | 24.4407 | 26.6571 | 26.4108 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 21 | 4197 | 12.1 | 12.1 | 15.4583 | 15.4414 | 15 | 82 | 82 | 31.6236 | 17.6139 | -0.39621 | 310.9959 | 15.4266 | 0 | 0 | 0 | 0 | 8.414 | 27.3258 | 30.2305 | 1.3861 | 17.7713 | 9.5853 | 9.5853 | 9.5853 | 9.5853 | 14.0502 | 24.0856 | 25.627 | 17.6139 | 33.1979 | 9.5853 | 9.5853 | 9.5853 | 9.5853 | 22.4642 | 51.4114 | 55.8574 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 22 | 4198 | 10.7 | 10.7 | 15.4583 | 15.4414 | 15 | 94 | 94 | 0 | 0 | -6.6605 | 323.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 23 | 4199 | 10.7 | 10.7 | 15.4583 | 15.4414 | 15 | 93 | 93 | 0 | 0 | -11.2902 | 336.3948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 24 | 24 | 4200 | 12.2 | 12.2 | 14.0542 | 15.157 | 15 | 84 | 84 | 0 | 0 | -13.9368 | 350.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 1 | 4201 | 13.2 | 13.2 | 14.0542 | 15.157 | 15 | 78 | 78 | 0 | 0 | -14.3672 | 4.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 2 | 4202 | 12.5 | 12.5 | 14.0542 | 15.157 | 15 | 91 | 91 | 0 | 0 | -12.5699 | 18.3974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 3 | 4203 | 12.5 | 12.5 | 14.0542 | 15.157 | 15 | 91 | 91 | 0 | 0 | -8.6594 | 31.8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 4 | 4204 | 12.5 | 12.5 | 14.0542 | 15.157 | 15 | 92 | 92 | 0 | 0 | -2.9733 | 44.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 5 | 4205 | 12.9 | 12.9 | 14.0542 | 15.157 | 15 | 87 | 87 | 1.5666 | 2.9691 | 4.1123 | 56.2272 | 1.1173 | 1.5644 | 1.0951 | 0 | 0 | 0 | 0 | 0.01573 | 0.030946 | 2.9323 | 3.6653 | 2.8958 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.126 | 2.9691 | 4.0496 | 5.2297 | 3.9908 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.1418 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 6 | 4206 | 12.6 | 12.6 | 14.0542 | 15.157 | 15 | 89 | 89 | 0.3472 | 10.9466 | 12.2259 | 67.4646 | 0.19251 | 0.33968 | 0.28787 | 0.067426 | 0 | 0 | 0 | 0 | 0.053417 | 5.216 | 5.216 | 5.216 | 5.216 | 5.216 | 5.216 | 5.216 | 5.216 | 10.9466 | 5.4085 | 5.5557 | 5.5039 | 5.2835 | 5.216 | 5.216 | 5.216 | 5.216 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 7 | 4207 | 12.6 | 12.6 | 14.0542 | 15.157 | 15 | 84 | 84 | 1.1572 | 38.6542 | 21.0234 | 78.5214 | 0.43345 | 1.0452 | 1.0446 | 0.43216 | 0 | 0 | 0 | 0 | 0.34576 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 38.6542 | 19.2018 | 19.8135 | 19.813 | 19.2005 | 18.7684 | 18.7684 | 18.7684 | 18.7684 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 25 | 8 | 4208 | 12.1 | 12.1 | 14.0542 | 15.157 | 15 | 92 | 92 | 1.0771 | 55.521 | 30.1749 | 89.9392 | 0.20007 | 0.83817 | 0.98528 | 0.55522 | 0 | 0 | 0 | 0 | 0.47898 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 55.521 | 27.1233 | 27.7614 | 27.9085 | 27.4784 | 26.9232 | 26.9232 | 26.9232 | 26.9232 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 9 | 4209 | 11.9 | 11.9 | 14.0542 | 15.157 | 15 | 93 | 93 | 1.3171 | 80.2339 | 39.3191 | 102.4934 | 0.0012076 | 0.80596 | 1.1386 | 0.80426 | 0 | 0 | 0 | 0 | 0.76611 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 80.2339 | 39.2164 | 40.0212 | 40.3538 | 40.0195 | 39.2152 | 39.2152 | 39.2152 | 39.2152 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 10 | 4210 | 11.9 | 11.9 | 14.0542 | 15.157 | 15 | 93 | 93 | 1.4688 | 101.9712 | 47.9716 | 117.3512 | 0 | 0.61066 | 1.1094 | 0.9583 | 0.24582 | 0 | 0 | 0 | 1.0288 | 50.1747 | 50.1747 | 50.1747 | 50.1747 | 50.1747 | 50.1747 | 50.1747 | 50.1747 | 101.9712 | 50.1747 | 50.7853 | 51.2841 | 51.133 | 50.4205 | 50.1747 | 50.1747 | 50.1747 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 11 | 4211 | 12.2 | 12.2 | 14.0542 | 15.157 | 15 | 94 | 94 | 1.1465 | 102.0911 | 55.3585 | 136.1958 | 0 | 0.23271 | 0.68174 | 0.73142 | 0.35265 | 0 | 0 | 0 | 0.9089 | 50.1898 | 50.1898 | 50.1898 | 50.1898 | 50.1898 | 50.1898 | 50.1898 | 50.1898 | 102.0911 | 50.1898 | 50.4225 | 50.8716 | 50.9213 | 50.5425 | 50.1898 | 50.1898 | 50.1898 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 12 | 4212 | 12.6 | 12.6 | 14.0542 | 15.157 | 15 | 93 | 93 | 1.6532 | 131.5906 | 60.2187 | 160.5395 | 0 | 0 | 0.6505 | 0.93956 | 0.67824 | 0.019612 | 0 | 0 | 1.4094 | 65.4413 | 65.4413 | 65.4413 | 65.4413 | 65.4413 | 65.4413 | 65.4413 | 65.4413 | 131.5906 | 65.4413 | 65.4413 | 66.0918 | 66.3809 | 66.1196 | 65.461 | 65.4413 | 65.4413 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 13 | 4213 | 13 | 13 | 14.0542 | 15.157 | 15 | 94 | 94 | 1.8383 | 142.391 | 61.0855 | 188.7794 | 0 | 0 | 0.30419 | 0.82383 | 0.86089 | 0.39365 | 0 | 0 | 1.609 | 71.1302 | 71.1302 | 71.1302 | 71.1302 | 71.1302 | 71.1302 | 71.1302 | 71.1302 | 142.391 | 71.1302 | 71.1302 | 71.4344 | 71.9541 | 71.9911 | 71.5239 | 71.1302 | 71.1302 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 14 | 4214 | 13.6 | 13.6 | 14.0542 | 15.157 | 15 | 93 | 93 | 1.5773 | 129.6441 | 57.6143 | 215.1078 | 0 | 0 | 0 | 0.45064 | 0.75371 | 0.61526 | 0.1164 | 0 | 1.3559 | 64.5081 | 64.5081 | 64.5081 | 64.5081 | 64.5081 | 64.5081 | 64.5081 | 64.5081 | 129.6441 | 64.5081 | 64.5081 | 64.5081 | 64.9587 | 65.2618 | 65.1234 | 64.6245 | 64.5081 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 15 | 4215 | 14.3 | 14.3 | 14.0542 | 15.157 | 15 | 96 | 96 | 2.0171 | 137.373 | 51.0224 | 235.9698 | 0 | 0 | 0 | 0.18561 | 0.88385 | 1.0643 | 0.62136 | 0 | 1.627 | 68.4864 | 68.4864 | 68.4864 | 68.4864 | 68.4864 | 68.4864 | 68.4864 | 68.4864 | 137.373 | 68.4864 | 68.4864 | 68.4864 | 68.672 | 69.3703 | 69.5508 | 69.1078 | 68.4864 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 16 | 4216 | 14.8 | 14.8 | 14.0542 | 15.157 | 15 | 97 | 97 | 1.1093 | 91.2014 | 42.7423 | 252.1396 | 0 | 0 | 0 | 0 | 0.3905 | 0.68503 | 0.57828 | 0.13278 | 0.79858 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 91.2014 | 44.6781 | 44.6781 | 44.6781 | 44.6781 | 45.0686 | 45.3632 | 45.2564 | 44.8109 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 17 | 4217 | 16 | 16 | 14.0542 | 15.157 | 15 | 97 | 97 | 1.2155 | 80.264 | 33.719 | 265.4147 | 0 | 0 | 0 | 0 | 0.27378 | 0.79437 | 0.84964 | 0.40719 | 0.73597 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 80.264 | 39.1128 | 39.1128 | 39.1128 | 39.1128 | 39.3866 | 39.9072 | 39.9625 | 39.52 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 25 | 18 | 4218 | 16.5 | 16.5 | 14.0542 | 15.157 | 15 | 95 | 95 | 0.95913 | 55.548 | 24.5234 | 277.161 | 0 | 0 | 0 | 0 | 0.063777 | 0.6074 | 0.79522 | 0.51721 | 0.45199 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 55.548 | 26.7589 | 26.7589 | 26.7589 | 26.7589 | 26.8227 | 27.3663 | 27.5541 | 27.2761 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 19 | 4219 | 16.5 | 16.5 | 14.0542 | 15.157 | 15 | 96 | 96 | 0.97052 | 38.6834 | 15.5502 | 288.2825 | 0.11007 | 0 | 0 | 0 | 0 | 0.54165 | 0.87608 | 0.69732 | 0.31664 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 38.6834 | 18.5902 | 18.4801 | 18.4801 | 18.4801 | 18.4801 | 19.0217 | 19.3562 | 19.1774 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 20 | 4220 | 16.3 | 16.3 | 14.0542 | 15.157 | 15 | 97 | 97 | 0.40912 | 13.9262 | 7.134 | 299.397 | 0.12364 | 0 | 0 | 0 | 0 | 0.1772 | 0.37425 | 0.35207 | 0.0738 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 13.9262 | 6.6528 | 6.5291 | 6.5291 | 6.5291 | 6.5291 | 6.7063 | 6.9034 | 6.8812 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 21 | 4221 | 16.5 | 16.5 | 14.0542 | 15.157 | 15 | 96 | 96 | 1.2898 | 5.9438 | -0.39 | 310.9459 | 0.62819 | 0 | 0 | 0 | 0 | 0.34422 | 1.115 | 1.2326 | 0.056158 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 5.9438 | 3.3962 | 2.768 | 2.768 | 2.768 | 2.768 | 3.1123 | 3.883 | 4.0007 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 22 | 4222 | 16.6 | 16.6 | 14.0542 | 15.157 | 15 | 94 | 94 | 0 | 0 | -6.6602 | 323.2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 23 | 4223 | 16.7 | 16.7 | 14.0542 | 15.157 | 15 | 93 | 93 | 0 | 0 | -11.2969 | 336.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 25 | 24 | 4224 | 16.5 | 16.5 | 14.0333 | 14.9227 | 15 | 94 | 94 | 0 | 0 | -13.9513 | 350.1828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 1 | 4225 | 16.3 | 16.3 | 14.0333 | 14.9227 | 15 | 96 | 96 | 0 | 0 | -14.3894 | 4.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 2 | 4226 | 16.4 | 16.4 | 14.0333 | 14.9227 | 15 | 94 | 94 | 0 | 0 | -12.6058 | 18.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 3 | 4227 | 16.3 | 16.3 | 14.0333 | 14.9227 | 15 | 95 | 95 | 0 | 0 | -8.7007 | 31.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 4 | 4228 | 16.3 | 16.3 | 14.0333 | 14.9227 | 15 | 96 | 96 | 0 | 0 | -3.0185 | 44.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 5 | 4229 | 16.5 | 16.5 | 14.0333 | 14.9227 | 15 | 94 | 94 | 1.6317 | 2.9684 | 4.0645 | 56.2039 | 1.1643 | 1.6294 | 1.14 | 0 | 0 | 0 | 0 | 0.017181 | 0.031584 | 2.9325 | 3.6645 | 2.8942 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.1271 | 2.9684 | 4.0968 | 5.2939 | 4.0343 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.1443 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 6 | 4230 | 16.7 | 16.7 | 14.0333 | 14.9227 | 15 | 94 | 94 | 1.8022 | 24.7234 | 12.1765 | 67.4447 | 0.99992 | 1.7634 | 1.4939 | 0.34928 | 0 | 0 | 0 | 0 | 0.2766 | 19.4881 | 25.3761 | 23.2976 | 14.4702 | 11.7765 | 11.7765 | 11.7765 | 11.7765 | 24.7234 | 20.488 | 27.1394 | 24.7915 | 14.8195 | 11.7765 | 11.7765 | 11.7765 | 11.7765 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 7 | 4231 | 17.1 | 17.1 | 14.0333 | 14.9227 | 15 | 92 | 92 | 3.9534 | 70.8201 | 20.973 | 78.5031 | 1.4823 | 3.5717 | 3.5689 | 1.4754 | 0 | 0 | 0 | 0 | 1.1799 | 41.9178 | 53.7341 | 53.7179 | 41.8788 | 33.5348 | 33.5348 | 33.5348 | 33.5348 | 70.8201 | 43.4001 | 57.3058 | 57.2868 | 43.3542 | 33.5348 | 33.5348 | 33.5348 | 33.5348 | 72 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 26 | 8 | 4232 | 17.9 | 17.9 | 14.0333 | 14.9227 | 15 | 89 | 89 | 4.7085 | 114.9076 | 30.1243 | 89.9205 | 0.87629 | 3.6661 | 4.3083 | 2.4268 | 0 | 0 | 0 | 0 | 2.0924 | 58.5468 | 69.6265 | 72.1771 | 64.7047 | 55.0666 | 55.0666 | 55.0666 | 55.0666 | 114.9076 | 59.4231 | 73.2925 | 76.4855 | 67.1315 | 55.0666 | 55.0666 | 55.0666 | 55.0666 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 9 | 4233 | 18.8 | 18.8 | 14.0333 | 14.9227 | 15 | 86 | 86 | 92.6112 | 260.1564 | 39.2688 | 102.4711 | 0.11111 | 56.7199 | 80.103 | 56.5628 | 0 | 0 | 0 | 0 | 53.8436 | 117.8784 | 197.2749 | 230.0707 | 197.0545 | 117.7226 | 117.7226 | 117.7226 | 117.7226 | 260.1564 | 117.9895 | 253.9948 | 310.1737 | 253.6173 | 117.7226 | 117.7226 | 117.7226 | 117.7226 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 10 | 4234 | 19.4 | 19.4 | 14.0333 | 14.9227 | 15 | 84 | 84 | 8.9525 | 226.7319 | 47.9228 | 117.3199 | 0 | 3.7269 | 6.7674 | 5.8436 | 1.4967 | 0 | 0 | 0 | 6.2681 | 107.6533 | 121.302 | 132.4367 | 129.0536 | 113.1345 | 107.6533 | 107.6533 | 107.6533 | 226.7319 | 107.6533 | 125.0289 | 139.204 | 134.8972 | 114.6312 | 107.6533 | 107.6533 | 107.6533 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 11 | 4235 | 20.4 | 20.4 | 14.0333 | 14.9227 | 15 | 79 | 79 | 184.4804 | 353.7898 | 55.3135 | 136.1461 | 0 | 37.5455 | 109.8367 | 117.787 | 56.7393 | 0 | 0 | 0 | 146.2102 | 160.3417 | 197.4159 | 268.7995 | 276.6501 | 216.3687 | 160.3417 | 160.3417 | 160.3417 | 353.7898 | 160.3417 | 234.9614 | 378.6362 | 394.437 | 273.108 | 160.3417 | 160.3417 | 160.3417 | 500 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 12 | 4236 | 20.5 | 20.5 | 14.0333 | 14.9227 | 15 | 78 | 78 | 34.1241 | 345.9176 | 60.1824 | 160.4615 | 0 | 0 | 13.4543 | 19.4157 | 14.0036 | 0.38844 | 0 | 0 | 29.0824 | 150.422 | 150.422 | 198.8222 | 220.2676 | 200.7984 | 151.8194 | 150.422 | 150.422 | 345.9176 | 150.422 | 150.422 | 212.2765 | 239.6833 | 214.802 | 152.2078 | 150.422 | 150.422 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 13 | 4237 | 22 | 22 | 14.0333 | 14.9227 | 15 | 72 | 72 | 634.9207 | 225.3936 | 61.0635 | 188.6794 | 0 | 0 | 105.5855 | 285.045 | 297.5291 | 135.7246 | 0 | 0 | 555.6064 | 142.7511 | 142.7511 | 168.7809 | 213.0228 | 216.1004 | 176.2111 | 142.7511 | 142.7511 | 225.3936 | 142.7511 | 142.7511 | 274.3664 | 498.0678 | 513.6295 | 311.9357 | 142.7511 | 142.7511 | 781 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 14 | 4238 | 22 | 22 | 14.0333 | 14.9227 | 15 | 76 | 76 | 476.0976 | 287.8407 | 57.6073 | 215.0095 | 0 | 0 | 0 | 136.44 | 227.717 | 185.6005 | 34.7617 | 0 | 409.1593 | 149.0207 | 149.0207 | 149.0207 | 208.8121 | 248.812 | 230.3555 | 164.2541 | 149.0207 | 287.8407 | 149.0207 | 149.0207 | 149.0207 | 345.2521 | 476.529 | 415.9559 | 199.0158 | 149.0207 | 697 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 15 | 4239 | 22.5 | 22.5 | 14.0333 | 14.9227 | 15 | 68 | 68 | 776.9864 | 156.4832 | 51.0256 | 235.8855 | 0 | 0 | 0 | 72.2126 | 340.93 | 409.9352 | 238.806 | 0 | 626.5168 | 128.3979 | 128.3979 | 128.3979 | 136.7836 | 167.9884 | 176.0016 | 156.1292 | 128.3979 | 156.4832 | 128.3979 | 128.3979 | 128.3979 | 208.9962 | 508.9184 | 585.9369 | 394.9352 | 128.3979 | 783 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 16 | 4240 | 23.4 | 23.4 | 14.0333 | 14.9227 | 15 | 64 | 64 | 596.3358 | 198.8625 | 42.7509 | 252.0681 | 0 | 0 | 0 | 0 | 210.363 | 368.3306 | 310.5351 | 70.8324 | 429.1375 | 124.8965 | 124.8965 | 124.8965 | 124.8965 | 174.4889 | 211.7293 | 198.1042 | 141.595 | 198.8625 | 124.8965 | 124.8965 | 124.8965 | 124.8965 | 384.8519 | 580.0599 | 508.6394 | 212.4275 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 17 | 4241 | 23.6 | 23.6 | 14.0333 | 14.9227 | 15 | 66 | 66 | 741.6946 | 126.1106 | 33.7296 | 265.3521 | 0 | 0 | 0 | 0 | 167.6853 | 484.9788 | 518.1783 | 247.8359 | 448.8894 | 103.8379 | 103.8379 | 103.8379 | 103.8379 | 121.707 | 155.5189 | 159.0568 | 130.2482 | 126.1106 | 103.8379 | 103.8379 | 103.8379 | 103.8379 | 289.3924 | 640.4978 | 677.2351 | 378.0841 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 26 | 18 | 4242 | 23.5 | 23.5 | 14.0333 | 14.9227 | 15 | 64 | 64 | 641.8422 | 119.7287 | 24.5339 | 277.1038 | 0 | 0 | 0 | 0 | 43.2552 | 406.7977 | 532.0436 | 345.6256 | 302.2713 | 86.5848 | 86.5848 | 86.5848 | 86.5848 | 93.4727 | 151.3632 | 171.3073 | 141.6222 | 119.7287 | 86.5848 | 86.5848 | 86.5848 | 86.5848 | 136.728 | 558.1609 | 703.351 | 487.2477 | 422 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 19 | 4243 | 23.2 | 23.2 | 14.0333 | 14.9227 | 15 | 66 | 66 | 539.6169 | 99.1255 | 15.5587 | 288.2281 | 60.7077 | 0 | 0 | 0 | 0 | 301.5261 | 487.13 | 387.3797 | 175.8745 | 76.7034 | 65.9342 | 65.9342 | 65.9342 | 65.9342 | 119.4231 | 152.348 | 134.653 | 99.1255 | 137.4111 | 65.9342 | 65.9342 | 65.9342 | 65.9342 | 420.9491 | 639.478 | 522.0327 | 275 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 20 | 4244 | 22.5 | 22.5 | 14.0333 | 14.9227 | 15 | 70 | 70 | 298.2713 | 74.3048 | 7.139 | 299.3437 | 89.8805 | 0 | 0 | 0 | 0 | 129.4302 | 272.9224 | 256.5404 | 53.6952 | 70.1398 | 42.9969 | 42.9969 | 42.9969 | 42.9969 | 82.0834 | 125.4164 | 120.4692 | 74.3048 | 160.0203 | 42.9969 | 42.9969 | 42.9969 | 42.9969 | 211.5136 | 398.3388 | 377.0096 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 21 | 4245 | 19.8 | 19.8 | 14.0333 | 14.9227 | 15 | 87 | 87 | 23.2807 | 19.0473 | -0.3899 | 310.8928 | 11.3202 | 0 | 0 | 0 | 0 | 6.234 | 20.1364 | 22.2432 | 8.9527 | 20.0748 | 11.0702 | 11.0702 | 11.0702 | 11.0702 | 16.029 | 27.0876 | 28.7634 | 19.0473 | 31.395 | 11.0702 | 11.0702 | 11.0702 | 11.0702 | 22.263 | 47.224 | 51.0066 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 22 | 4246 | 17.3 | 17.3 | 14.0333 | 14.9227 | 15 | 95 | 95 | 0 | 0 | -6.6664 | 323.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 23 | 4247 | 16.5 | 16.5 | 14.0333 | 14.9227 | 15 | 96 | 96 | 0 | 0 | -11.3104 | 336.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 26 | 24 | 4248 | 16.3 | 16.3 | 19.3833 | 16.1489 | 15 | 94 | 94 | 0 | 0 | -13.9726 | 350.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 1 | 4249 | 16.5 | 16.5 | 19.3833 | 16.1489 | 15 | 94 | 94 | 0 | 0 | -14.4185 | 4.3235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 2 | 4250 | 16 | 16 | 19.3833 | 16.1489 | 15 | 94 | 94 | 0 | 0 | -12.6483 | 18.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 3 | 4251 | 15.9 | 15.9 | 19.3833 | 16.1489 | 15 | 93 | 93 | 0 | 0 | -8.7482 | 31.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 4 | 4252 | 16.3 | 16.3 | 19.3833 | 16.1489 | 15 | 91 | 91 | 0 | 0 | -3.0695 | 44.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 5 | 4253 | 17 | 17 | 19.3833 | 16.1489 | 15 | 89 | 89 | 3.5174 | 8.5204 | 4.0113 | 56.1848 | 2.5107 | 3.5121 | 2.4562 | 0 | 0 | 0 | 0 | 0.038533 | 2.4796 | 6.7991 | 7.9054 | 6.7389 | 4.0254 | 4.0254 | 4.0254 | 4.0254 | 4.0679 | 8.5204 | 9.3097 | 11.4175 | 9.195 | 4.0254 | 4.0254 | 4.0254 | 4.0254 | 4.1065 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 6 | 4254 | 18.7 | 18.7 | 19.3833 | 16.1489 | 15 | 82 | 82 | 111.2384 | 68.9787 | 12.1219 | 67.4294 | 61.7543 | 108.8583 | 92.1945 | 21.5245 | 0 | 0 | 0 | 0 | 17.0213 | 153.7569 | 248.8726 | 215.2239 | 72.5219 | 29.0582 | 29.0582 | 29.0582 | 29.0582 | 68.9787 | 215.5113 | 357.7309 | 307.4185 | 94.0464 | 29.0582 | 29.0582 | 29.0582 | 29.0582 | 86 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 7 | 4255 | 19.9 | 19.9 | 19.3833 | 16.1489 | 15 | 80 | 80 | 309.7155 | 121.7006 | 20.9178 | 78.49 | 116.2251 | 279.9024 | 279.6167 | 115.5353 | 0 | 0 | 0 | 0 | 92.2994 | 107.7905 | 166.6123 | 166.5096 | 107.5426 | 66.0218 | 66.0218 | 66.0218 | 66.0218 | 121.7006 | 224.0155 | 446.5147 | 446.1263 | 223.0779 | 66.0218 | 66.0218 | 66.0218 | 66.0218 | 214 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 27 | 8 | 4256 | 22 | 22 | 19.3833 | 16.1489 | 15 | 76 | 76 | 514.9469 | 140.3669 | 30.0688 | 89.9075 | 95.98 | 401.1526 | 471.3355 | 265.4164 | 0 | 0 | 0 | 0 | 228.6331 | 111.0535 | 181.4949 | 197.6948 | 150.1636 | 88.8989 | 88.8989 | 88.8989 | 88.8989 | 140.3669 | 207.0335 | 582.6475 | 669.0303 | 415.58 | 88.8989 | 88.8989 | 88.8989 | 88.8989 | 369 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 9 | 4257 | 23.4 | 23.4 | 19.3833 | 16.1489 | 15 | 72 | 72 | 609.6562 | 156.7677 | 39.2136 | 102.455 | 0.85167 | 373.6792 | 527.6106 | 372.4748 | 0 | 0 | 0 | 0 | 354.2323 | 107.8554 | 186.841 | 219.4522 | 186.5858 | 107.6749 | 107.6749 | 107.6749 | 107.6749 | 156.7677 | 108.707 | 560.5203 | 747.0628 | 559.0606 | 107.6749 | 107.6749 | 107.6749 | 107.6749 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 10 | 4258 | 25 | 25 | 19.3833 | 16.1489 | 15 | 66 | 66 | 703.6719 | 157.5556 | 47.8686 | 117.2952 | 0 | 293.2971 | 532.3702 | 459.588 | 117.5854 | 0 | 0 | 0 | 492.4444 | 119.4399 | 169.5529 | 210.4012 | 197.9656 | 139.5306 | 119.4399 | 119.4399 | 119.4399 | 157.5556 | 119.4399 | 462.8501 | 742.7714 | 657.5536 | 257.116 | 119.4399 | 119.4399 | 119.4399 | 650 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 11 | 4259 | 26.7 | 26.7 | 19.3833 | 16.1489 | 15 | 58 | 58 | 759.7093 | 159.1224 | 55.2626 | 136.1028 | 0 | 154.987 | 452.8923 | 485.4994 | 233.7076 | 0 | 0 | 0 | 601.8776 | 129.2012 | 153.7577 | 200.9586 | 206.1249 | 166.2304 | 129.2012 | 129.2012 | 129.2012 | 159.1224 | 129.2012 | 308.7447 | 653.8509 | 691.6244 | 399.938 | 129.2012 | 129.2012 | 129.2012 | 761 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 12 | 4260 | 27.8 | 27.8 | 19.3833 | 16.1489 | 15 | 53 | 53 | 812.4601 | 154.8137 | 60.1394 | 160.3876 | 0 | 0 | 320.9963 | 462.8676 | 333.5973 | 8.9103 | 0 | 0 | 692.1863 | 135.2117 | 135.2117 | 170.5742 | 186.2034 | 171.9624 | 136.1933 | 135.2117 | 135.2117 | 154.8137 | 135.2117 | 135.2117 | 491.5705 | 649.071 | 505.5597 | 145.1035 | 135.2117 | 135.2117 | 847 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 13 | 4261 | 28.3 | 28.3 | 19.3833 | 16.1489 | 15 | 48 | 48 | 797.7194 | 163.1582 | 61.0346 | 188.5789 | 0 | 0 | 133.3147 | 358.8217 | 374.1358 | 170.2863 | 0 | 0 | 697.8418 | 136.8099 | 136.8099 | 152.3843 | 178.729 | 180.5181 | 156.7035 | 136.8099 | 136.8099 | 163.1582 | 136.8099 | 136.8099 | 285.699 | 537.5507 | 554.6539 | 326.9897 | 136.8099 | 136.8099 | 861 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 14 | 4262 | 28.8 | 28.8 | 19.3833 | 16.1489 | 15 | 46 | 46 | 855.5933 | 147.9475 | 57.5936 | 214.907 | 0 | 0 | 0 | 246.0047 | 409.7122 | 333.4159 | 61.8091 | 0 | 735.0525 | 135.1102 | 135.1102 | 135.1102 | 160.0114 | 176.5823 | 168.8594 | 141.3666 | 135.1102 | 147.9475 | 135.1102 | 135.1102 | 135.1102 | 406.0161 | 586.2945 | 502.2753 | 203.1757 | 135.1102 | 883 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 15 | 4263 | 29.3 | 29.3 | 19.3833 | 16.1489 | 15 | 46 | 46 | 824.0628 | 143.7714 | 51.0227 | 235.7956 | 0 | 0 | 0 | 77.3944 | 362.1749 | 434.7983 | 252.7227 | 0 | 664.2286 | 127.7936 | 127.7936 | 127.7936 | 135.745 | 165.0031 | 172.4644 | 153.7581 | 127.7936 | 143.7714 | 127.7936 | 127.7936 | 127.7936 | 213.1394 | 527.178 | 607.2627 | 406.4809 | 127.7936 | 808 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 16 | 4264 | 29.7 | 29.7 | 19.3833 | 16.1489 | 15 | 49 | 49 | 787.051 | 136.8728 | 42.7539 | 251.9912 | 0 | 0 | 0 | 0 | 278.299 | 486.3031 | 409.4374 | 92.7289 | 566.1272 | 117.5621 | 117.5621 | 117.5621 | 117.5621 | 146.5827 | 168.273 | 160.2576 | 127.2317 | 136.8728 | 117.5621 | 117.5621 | 117.5621 | 117.5621 | 424.8816 | 654.5761 | 569.695 | 219.9606 | 703 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 17 | 4265 | 30.1 | 30.1 | 19.3833 | 16.1489 | 15 | 47 | 47 | 719.282 | 131.9276 | 33.7349 | 265.2843 | 0 | 0 | 0 | 0 | 163.2851 | 470.6235 | 502.277 | 239.7035 | 435.0724 | 103.3559 | 103.3559 | 103.3559 | 103.3559 | 127.3927 | 172.6352 | 177.2948 | 138.642 | 131.9276 | 103.3559 | 103.3559 | 103.3559 | 103.3559 | 290.6778 | 643.2587 | 679.5718 | 378.3455 | 567 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 27 | 18 | 4266 | 30 | 30 | 19.3833 | 16.1489 | 15 | 47 | 47 | 630.9905 | 122.0821 | 24.5389 | 277.0418 | 0 | 0 | 0 | 0 | 43.1397 | 400.297 | 522.9658 | 339.2883 | 296.9179 | 86.9916 | 86.9916 | 86.9916 | 86.9916 | 94.0691 | 152.6637 | 172.7885 | 142.6547 | 122.0821 | 86.9916 | 86.9916 | 86.9916 | 86.9916 | 137.2087 | 552.9606 | 695.7543 | 481.943 | 419 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 19 | 4267 | 29.1 | 29.1 | 19.3833 | 16.1489 | 15 | 53 | 53 | 429.7005 | 116.131 | 15.5616 | 288.1694 | 47.9206 | 0 | 0 | 0 | 0 | 240.431 | 387.9414 | 308.2009 | 139.869 | 82.0906 | 69.9385 | 69.9385 | 69.9385 | 69.9385 | 130.9092 | 168.3162 | 148.0949 | 116.131 | 130.0112 | 69.9385 | 69.9385 | 69.9385 | 69.9385 | 371.3401 | 556.2576 | 456.2958 | 256 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 20 | 4268 | 27.9 | 27.9 | 19.3833 | 16.1489 | 15 | 57 | 57 | 189.4752 | 79.9773 | 7.1382 | 299.2867 | 56.9178 | 0 | 0 | 0 | 0 | 82.3855 | 173.4284 | 162.8793 | 34.0227 | 69.9058 | 43.5938 | 43.5938 | 43.5938 | 43.5938 | 81.6791 | 123.7666 | 118.8899 | 79.9773 | 126.8236 | 43.5938 | 43.5938 | 43.5938 | 43.5938 | 164.0645 | 297.195 | 281.7693 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 21 | 4269 | 24.5 | 24.5 | 19.3833 | 16.1489 | 15 | 74 | 74 | 36.3018 | 17.4515 | -0.39593 | 310.8365 | 17.6205 | 0 | 0 | 0 | 0 | 9.7552 | 31.4164 | 34.6743 | 1.5485 | 29.1545 | 9.7305 | 9.7305 | 9.7305 | 9.7305 | 20.4842 | 44.3625 | 47.9538 | 17.4515 | 46.7749 | 9.7305 | 9.7305 | 9.7305 | 9.7305 | 30.2394 | 75.7789 | 82.6281 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 22 | 4270 | 22.9 | 22.9 | 19.3833 | 16.1489 | 15 | 79 | 79 | 0 | 0 | -6.679 | 323.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 23 | 4271 | 21.1 | 21.1 | 19.3833 | 16.1489 | 15 | 89 | 89 | 0 | 0 | -11.3306 | 336.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 27 | 24 | 4272 | 20.4 | 20.4 | 23.6375 | 18.1568 | 15 | 91 | 91 | 0 | 0 | -14.0008 | 350.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 1 | 4273 | 21.1 | 21.1 | 23.6375 | 18.1568 | 15 | 85 | 85 | 0 | 0 | -14.4544 | 4.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 2 | 4274 | 22.3 | 22.3 | 23.6375 | 18.1568 | 15 | 77 | 77 | 0 | 0 | -12.6973 | 18.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 3 | 4275 | 21.5 | 21.5 | 23.6375 | 18.1568 | 15 | 80 | 80 | 0 | 0 | -8.802 | 31.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 4 | 4276 | 21.6 | 21.6 | 23.6375 | 18.1568 | 15 | 78 | 78 | 0 | 0 | -3.1264 | 44.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 5 | 4277 | 21.9 | 21.9 | 23.6375 | 18.1568 | 15 | 77 | 77 | 8.5269 | 5.8443 | 3.9526 | 56.1699 | 6.0883 | 8.5137 | 5.9519 | 0 | 0 | 0 | 0 | 0.096501 | 0.15565 | 6.3815 | 8.0819 | 6.2858 | 2.1132 | 2.1132 | 2.1132 | 2.1132 | 2.1808 | 5.8443 | 12.4698 | 16.5956 | 12.2377 | 2.1132 | 2.1132 | 2.1132 | 2.1132 | 2.2773 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 6 | 4278 | 22.1 | 22.1 | 23.6375 | 18.1568 | 15 | 78 | 78 | 21.1255 | 57.7793 | 12.0622 | 67.4188 | 11.7333 | 20.676 | 17.507 | 4.0827 | 0 | 0 | 0 | 0 | 3.2207 | 118.7984 | 190.8204 | 165.2985 | 57.183 | 24.3025 | 24.3025 | 24.3025 | 24.3025 | 57.7793 | 130.5317 | 211.4964 | 182.8055 | 61.2657 | 24.3025 | 24.3025 | 24.3025 | 24.3025 | 61 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 7 | 4279 | 23.1 | 23.1 | 23.6375 | 18.1568 | 15 | 76 | 76 | 54.8815 | 127.6729 | 20.8577 | 78.4821 | 20.6088 | 49.6134 | 49.5552 | 20.4682 | 0 | 0 | 0 | 0 | 16.3271 | 108.9754 | 182.2606 | 182.1135 | 108.6203 | 56.9039 | 56.9039 | 56.9039 | 56.9039 | 127.6729 | 129.5842 | 231.874 | 231.6687 | 129.0886 | 56.9039 | 56.9039 | 56.9039 | 56.9039 | 144 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 28 | 8 | 4280 | 24.9 | 24.9 | 23.6375 | 18.1568 | 15 | 71 | 71 | 481.7861 | 147.3176 | 30.0086 | 89.9002 | 89.896 | 375.5043 | 441.1472 | 248.3721 | 0 | 0 | 0 | 0 | 213.6824 | 112.5912 | 183.937 | 200.3348 | 152.179 | 90.135 | 90.135 | 90.135 | 90.135 | 147.3176 | 202.4872 | 559.4412 | 641.482 | 400.5511 | 90.135 | 90.135 | 90.135 | 90.135 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 9 | 4281 | 25.9 | 25.9 | 23.6375 | 18.1568 | 15 | 69 | 69 | 146.3086 | 262.0524 | 39.1535 | 102.4453 | 0.22062 | 89.7435 | 126.6958 | 89.4315 | 0 | 0 | 0 | 0 | 84.9476 | 120.9757 | 221.5575 | 263.0747 | 221.207 | 120.7278 | 120.7278 | 120.7278 | 120.7278 | 262.0524 | 121.1963 | 311.301 | 389.7705 | 310.6385 | 120.7278 | 120.7278 | 120.7278 | 120.7278 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 10 | 4282 | 27 | 27 | 23.6375 | 18.1568 | 15 | 60 | 60 | 30.0099 | 279.0103 | 47.8093 | 117.2773 | 0 | 12.5225 | 22.7246 | 19.615 | 5.0152 | 0 | 0 | 0 | 20.9897 | 127.417 | 156.9114 | 180.9406 | 173.6164 | 139.2293 | 127.417 | 127.417 | 127.417 | 279.0103 | 127.417 | 169.4338 | 203.6652 | 193.2314 | 144.2444 | 127.417 | 127.417 | 127.417 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 11 | 4283 | 26.3 | 26.3 | 23.6375 | 18.1568 | 15 | 63 | 63 | 98.1009 | 355.3158 | 55.2058 | 136.0659 | 0 | 20.056 | 58.5582 | 62.7578 | 30.1947 | 0 | 0 | 0 | 77.6842 | 157.9329 | 186.4895 | 241.3108 | 247.2904 | 200.9256 | 157.9329 | 157.9329 | 157.9329 | 355.3158 | 157.9329 | 206.5455 | 299.8689 | 310.0482 | 231.1203 | 157.9329 | 157.9329 | 157.9329 | 433 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 12 | 4284 | 26.2 | 26.2 | 23.6375 | 18.1568 | 15 | 61 | 61 | 3.9748 | 202.615 | 60.0898 | 160.318 | 0 | 0 | 1.5737 | 2.2678 | 1.6334 | 0.042195 | 0 | 0 | 3.385 | 103.0382 | 103.0382 | 103.2552 | 103.3509 | 103.2634 | 103.044 | 103.0382 | 103.0382 | 202.615 | 103.0382 | 103.0382 | 104.8289 | 105.6186 | 104.8968 | 103.0862 | 103.0382 | 103.0382 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 13 | 4285 | 27.1 | 27.1 | 23.6375 | 18.1568 | 15 | 64 | 64 | 4.3783 | 218.1714 | 60.9987 | 188.4783 | 0 | 0 | 0.73529 | 1.9735 | 2.0556 | 0.93362 | 0 | 0 | 3.8286 | 110.9675 | 110.9675 | 111.2558 | 111.7411 | 111.7733 | 111.3335 | 110.9675 | 110.9675 | 218.1714 | 110.9675 | 110.9675 | 111.991 | 113.7146 | 113.8289 | 112.2671 | 110.9675 | 110.9675 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 14 | 4286 | 29.9 | 29.9 | 23.6375 | 18.1568 | 15 | 57 | 57 | 441.9477 | 301.4697 | 57.5733 | 214.8006 | 0 | 0 | 0 | 127.5175 | 211.9277 | 172.1935 | 31.5907 | 0 | 379.5303 | 150.3409 | 150.3409 | 150.3409 | 212.5378 | 253.7091 | 234.3287 | 165.7493 | 150.3409 | 301.4697 | 150.3409 | 150.3409 | 150.3409 | 340.0553 | 465.6368 | 406.5222 | 197.3401 | 150.3409 | 681 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 15 | 4287 | 31.8 | 31.8 | 23.6375 | 18.1568 | 15 | 54 | 54 | 738.641 | 168.8925 | 51.0138 | 235.7004 | 0 | 0 | 0 | 70.1345 | 325.2334 | 389.815 | 226.0482 | 0 | 595.1075 | 129.3795 | 129.3795 | 129.3795 | 138.4333 | 171.3644 | 179.7013 | 158.5604 | 129.3795 | 168.8925 | 129.3795 | 129.3795 | 129.3795 | 208.5678 | 496.5978 | 569.5163 | 384.6087 | 129.3795 | 764 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 16 | 4288 | 32 | 32 | 23.6375 | 18.1568 | 15 | 47 | 47 | 722.0644 | 155.8982 | 42.7512 | 251.9088 | 0 | 0 | 0 | 0 | 255.9928 | 446.3757 | 375.2777 | 84.3472 | 519.1018 | 118.9264 | 118.9264 | 118.9264 | 118.9264 | 160.9219 | 192.1541 | 180.4906 | 132.7635 | 155.8982 | 118.9264 | 118.9264 | 118.9264 | 118.9264 | 416.9147 | 638.5298 | 555.7683 | 217.1107 | 675 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 17 | 4289 | 32 | 32 | 23.6375 | 18.1568 | 15 | 47 | 47 | 658.9876 | 148.6765 | 33.7346 | 265.2115 | 0 | 0 | 0 | 0 | 150.2655 | 431.5071 | 459.9776 | 218.9996 | 398.3235 | 106.1114 | 106.1114 | 106.1114 | 106.1114 | 132.404 | 181.6141 | 186.5957 | 144.4307 | 148.6765 | 106.1114 | 106.1114 | 106.1114 | 106.1114 | 282.6695 | 613.1211 | 646.5734 | 363.4303 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 28 | 18 | 4290 | 31.3 | 31.3 | 23.6375 | 18.1568 | 15 | 50 | 50 | 314.7257 | 191.049 | 24.5384 | 276.9753 | 0 | 0 | 0 | 0 | 21.8487 | 199.8757 | 260.8183 | 168.977 | 147.951 | 100.9393 | 100.9393 | 100.9393 | 100.9393 | 110.4668 | 188.0987 | 214.6738 | 174.6248 | 191.049 | 100.9393 | 100.9393 | 100.9393 | 100.9393 | 132.3155 | 387.9744 | 475.4921 | 343.6018 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 19 | 4291 | 29.7 | 29.7 | 23.6375 | 18.1568 | 15 | 63 | 63 | 9.9726 | 107.759 | 15.5589 | 288.1066 | 1.1017 | 0 | 0 | 0 | 0 | 5.5883 | 9.0047 | 7.1463 | 3.241 | 53.9212 | 53.6691 | 53.6691 | 53.6691 | 53.6691 | 54.9477 | 55.7293 | 55.3041 | 107.759 | 55.0228 | 53.6691 | 53.6691 | 53.6691 | 53.6691 | 60.536 | 64.7341 | 62.4505 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 20 | 4292 | 20.5 | 20.5 | 23.6375 | 18.1568 | 15 | 94 | 94 | 0 | 0 | 7.1315 | 299.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 21 | 4293 | 20.3 | 20.3 | 23.6375 | 18.1568 | 15 | 96 | 96 | 0 | 0 | -0.40812 | 310.7772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 22 | 4294 | 20.2 | 20.2 | 23.6375 | 18.1568 | 15 | 94 | 94 | 0 | 0 | -6.698 | 323.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 23 | 4295 | 19.7 | 19.7 | 23.6375 | 18.1568 | 15 | 94 | 94 | 0 | 0 | -11.3575 | 336.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 28 | 24 | 4296 | 20.2 | 20.2 | 24.9417 | 19.9811 | 15 | 96 | 96 | 0 | 0 | -14.0359 | 350.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 1 | 4297 | 19.6 | 19.6 | 24.9417 | 19.9811 | 15 | 90 | 90 | 0 | 0 | -14.4971 | 4.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 2 | 4298 | 19 | 19 | 24.9417 | 19.9811 | 15 | 95 | 95 | 0 | 0 | -12.753 | 18.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 3 | 4299 | 18.4 | 18.4 | 24.9417 | 19.9811 | 15 | 98 | 98 | 0 | 0 | -8.8619 | 31.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 4 | 4300 | 18.7 | 18.7 | 24.9417 | 19.9811 | 15 | 96 | 96 | 0 | 0 | -3.189 | 44.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 5 | 4301 | 18.7 | 18.7 | 24.9417 | 19.9811 | 15 | 98 | 98 | 1.9847 | 2.9652 | 3.8885 | 56.1593 | 1.4175 | 1.9815 | 1.3849 | 0 | 0 | 0 | 0 | 0.023052 | 0.034835 | 2.9313 | 3.6603 | 2.8891 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 1.129 | 2.9652 | 4.3487 | 5.6419 | 4.274 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 1.152 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 6 | 4302 | 17.7 | 17.7 | 24.9417 | 19.9811 | 15 | 96 | 96 | 0.026533 | 2.996 | 11.9976 | 67.413 | 0.014742 | 0.025971 | 0.021987 | 0.0051232 | 0 | 0 | 0 | 0 | 0.0040277 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 2.996 | 1.4015 | 1.4127 | 1.4087 | 1.3919 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 7 | 4303 | 17.2 | 17.2 | 24.9417 | 19.9811 | 15 | 96 | 96 | 0.093254 | 10.9723 | 20.7928 | 78.4794 | 0.035035 | 0.084326 | 0.08422 | 0.034779 | 0 | 0 | 0 | 0 | 0.027686 | 5.129 | 5.129 | 5.129 | 5.129 | 5.129 | 5.129 | 5.129 | 5.129 | 10.9723 | 5.1641 | 5.2133 | 5.2132 | 5.1638 | 5.129 | 5.129 | 5.129 | 5.129 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 29 | 8 | 4304 | 16.8 | 16.8 | 24.9417 | 19.9811 | 15 | 94 | 94 | 1.4181 | 63.3718 | 29.9437 | 89.8987 | 0.26477 | 1.1057 | 1.299 | 0.73131 | 0 | 0 | 0 | 0 | 0.62816 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 63.3718 | 31.202 | 32.043 | 32.2362 | 31.6685 | 30.9372 | 30.9372 | 30.9372 | 30.9372 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 9 | 4305 | 16.5 | 16.5 | 24.9417 | 19.9811 | 15 | 93 | 93 | 1.1355 | 74.3413 | 39.0887 | 102.4418 | 0.0017394 | 0.69699 | 0.98395 | 0.69453 | 0 | 0 | 0 | 0 | 0.65872 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 74.3413 | 36.2185 | 36.9138 | 37.2008 | 36.9113 | 36.2168 | 36.2168 | 36.2168 | 36.2168 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 10 | 4306 | 16.2 | 16.2 | 24.9417 | 19.9811 | 15 | 89 | 89 | 0.84598 | 77.4087 | 47.7448 | 117.2661 | 0 | 0.35337 | 0.64121 | 0.55343 | 0.14147 | 0 | 0 | 0 | 0.59131 | 37.6631 | 37.6631 | 37.6631 | 37.6631 | 37.6631 | 37.6631 | 37.6631 | 37.6631 | 77.4087 | 37.6631 | 38.0165 | 38.3043 | 38.2165 | 37.8046 | 37.6631 | 37.6631 | 37.6631 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 11 | 4307 | 16.2 | 16.2 | 24.9417 | 19.9811 | 15 | 88 | 88 | 0.61004 | 74.5172 | 55.1432 | 136.0356 | 0 | 0.12495 | 0.36463 | 0.39072 | 0.18793 | 0 | 0 | 0 | 0.48281 | 36.2385 | 36.2385 | 36.2385 | 36.2385 | 36.2385 | 36.2385 | 36.2385 | 36.2385 | 74.5172 | 36.2385 | 36.3634 | 36.6031 | 36.6292 | 36.4264 | 36.2385 | 36.2385 | 36.2385 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 12 | 4308 | 16.9 | 16.9 | 24.9417 | 19.9811 | 15 | 83 | 83 | 5.3556 | 234.4413 | 60.0336 | 160.2528 | 0 | 0 | 2.1249 | 3.0604 | 2.2031 | 0.055322 | 0 | 0 | 4.5587 | 116.7864 | 116.7864 | 120.6526 | 122.3547 | 120.795 | 116.887 | 116.7864 | 116.7864 | 234.4413 | 116.7864 | 116.7864 | 122.7775 | 125.4151 | 122.9981 | 116.9423 | 116.7864 | 116.7864 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 13 | 4309 | 18 | 18 | 24.9417 | 19.9811 | 15 | 72 | 72 | 21.2121 | 331.4595 | 60.9559 | 188.3777 | 0 | 0 | 3.5798 | 9.5827 | 9.9722 | 4.5201 | 0 | 0 | 18.5405 | 157.9978 | 157.9978 | 165.355 | 177.6921 | 178.4925 | 167.2874 | 157.9978 | 157.9978 | 331.4595 | 157.9978 | 157.9978 | 168.9349 | 187.2748 | 188.4647 | 171.8075 | 157.9978 | 157.9978 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 14 | 4310 | 18.4 | 18.4 | 24.9417 | 19.9811 | 15 | 68 | 68 | 630.3631 | 222.9204 | 57.5464 | 214.6904 | 0 | 0 | 0 | 182.5587 | 302.7649 | 245.6155 | 44.5879 | 0 | 541.0796 | 140.2256 | 140.2256 | 140.2256 | 185.3301 | 215.0292 | 200.9094 | 151.2419 | 140.2256 | 222.9204 | 140.2256 | 140.2256 | 140.2256 | 367.8888 | 517.7941 | 446.5249 | 195.8298 | 140.2256 | 764 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 15 | 4311 | 19.2 | 19.2 | 24.9417 | 19.9811 | 15 | 66 | 66 | 635.8171 | 207.0052 | 50.9988 | 235.6001 | 0 | 0 | 0 | 61.0615 | 280.5394 | 335.6811 | 194.1854 | 0 | 511.9948 | 133.6676 | 133.6676 | 133.6676 | 147.7365 | 198.3057 | 211.0107 | 178.4092 | 133.6676 | 207.0052 | 133.6676 | 133.6676 | 133.6676 | 208.798 | 478.8451 | 546.6919 | 372.5946 | 133.6676 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 16 | 4312 | 18.8 | 18.8 | 24.9417 | 19.9811 | 15 | 63 | 63 | 642.5302 | 182.3682 | 42.7428 | 251.8211 | 0 | 0 | 0 | 0 | 228.4543 | 397.4676 | 333.6498 | 74.3844 | 461.6318 | 122.5842 | 122.5842 | 122.5842 | 122.5842 | 169.7372 | 204.6215 | 191.4495 | 137.9372 | 182.3682 | 122.5842 | 122.5842 | 122.5842 | 122.5842 | 398.1915 | 602.0891 | 525.0993 | 212.3216 | 644 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 17 | 4313 | 18.8 | 18.8 | 24.9417 | 19.9811 | 15 | 65 | 65 | 703.873 | 135.8937 | 33.7289 | 265.1338 | 0 | 0 | 0 | 0 | 161.2739 | 461.3179 | 491.1281 | 233.2422 | 425.1063 | 103.9073 | 103.9073 | 103.9073 | 103.9073 | 128.6979 | 174.8199 | 179.4023 | 139.7607 | 135.8937 | 103.9073 | 103.9073 | 103.9073 | 103.9073 | 289.9718 | 636.1378 | 670.5304 | 373.0029 | 561 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 6 | 29 | 18 | 4314 | 17.9 | 17.9 | 24.9417 | 19.9811 | 15 | 63 | 63 | 344.7193 | 185.136 | 24.5324 | 276.9042 | 0 | 0 | 0 | 0 | 24.3202 | 219.1897 | 285.6609 | 184.7957 | 161.864 | 99.981 | 99.981 | 99.981 | 99.981 | 109.4359 | 185.1947 | 211.0365 | 171.8234 | 185.136 | 99.981 | 99.981 | 99.981 | 99.981 | 133.7561 | 404.3844 | 496.6973 | 356.6192 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 19 | 4315 | 17.6 | 17.6 | 24.9417 | 19.9811 | 15 | 62 | 62 | 197.4983 | 143.931 | 15.5506 | 288.0398 | 21.598 | 0 | 0 | 0 | 0 | 110.8521 | 178.3666 | 141.3963 | 64.069 | 87.2787 | 74.4606 | 74.4606 | 74.4606 | 74.4606 | 140.2495 | 180.3182 | 158.377 | 143.931 | 108.8766 | 74.4606 | 74.4606 | 74.4606 | 74.4606 | 251.1017 | 358.6848 | 299.7733 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 20 | 4316 | 16.8 | 16.8 | 24.9417 | 19.9811 | 15 | 70 | 70 | 336.9644 | 70.8971 | 7.119 | 299.1618 | 100.5304 | 0 | 0 | 0 | 0 | 147.1778 | 308.6713 | 289.3493 | 60.1029 | 68.2528 | 42.0776 | 42.0776 | 42.0776 | 42.0776 | 80.3984 | 122.4466 | 117.4157 | 70.8971 | 168.7832 | 42.0776 | 42.0776 | 42.0776 | 42.0776 | 227.5762 | 431.1179 | 406.765 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 21 | 4317 | 15.2 | 15.2 | 24.9417 | 19.9811 | 15 | 77 | 77 | 38.4493 | 17.8137 | -0.42649 | 310.715 | 18.5911 | 0 | 0 | 0 | 0 | 10.4127 | 33.3169 | 36.7045 | 10.1863 | 30.5172 | 10.7849 | 10.7849 | 10.7849 | 10.7849 | 21.8368 | 46.1471 | 49.7426 | 17.8137 | 49.1083 | 10.7849 | 10.7849 | 10.7849 | 10.7849 | 32.2496 | 79.4639 | 86.447 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 22 | 4318 | 14.3 | 14.3 | 24.9417 | 19.9811 | 15 | 83 | 83 | 0 | 0 | -6.7235 | 322.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 23 | 4319 | 13.5 | 13.5 | 24.9417 | 19.9811 | 15 | 88 | 88 | 0 | 0 | -11.3911 | 336.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 29 | 24 | 4320 | 12.7 | 12.7 | 17.2125 | 19.4635 | 15 | 92 | 92 | 0 | 0 | -14.0778 | 349.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 1 | 4321 | 11.4 | 11.4 | 17.2125 | 19.4635 | 15 | 96 | 96 | 0 | 0 | -14.5466 | 4.1907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 2 | 4322 | 11.3 | 11.3 | 17.2125 | 19.4635 | 15 | 96 | 96 | 0 | 0 | -12.8151 | 18.2161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 3 | 4323 | 9.9 | 9.9 | 17.2125 | 19.4635 | 15 | 100 | 100 | 0 | 0 | -8.9281 | 31.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 4 | 4324 | 8.9 | 8.9 | 17.2125 | 19.4635 | 15 | 99 | 99 | 0 | 0 | -3.2574 | 44.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 5 | 4325 | 9 | 9 | 17.2125 | 19.4635 | 15 | 100 | 100 | 2.18 | 2.9635 | 3.8191 | 56.153 | 1.5572 | 2.1763 | 1.5206 | 0 | 0 | 0 | 0 | 0.025827 | 0.036509 | 2.9301 | 3.6583 | 2.8871 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 1.1291 | 2.9635 | 4.4872 | 5.8346 | 4.4078 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 1.1549 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 6 | 4326 | 12.4 | 12.4 | 17.2125 | 19.4635 | 15 | 82 | 82 | 100.3603 | 67.8406 | 11.9279 | 67.4121 | 55.7743 | 98.2462 | 83.1669 | 19.3695 | 0 | 0 | 0 | 0 | 15.1594 | 152.6348 | 247.4066 | 213.7586 | 71.4013 | 28.1802 | 28.1802 | 28.1802 | 28.1802 | 67.8406 | 208.409 | 345.6528 | 296.9255 | 90.7708 | 28.1802 | 28.1802 | 28.1802 | 28.1802 | 83 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 7 | 4327 | 14.7 | 14.7 | 17.2125 | 19.4635 | 15 | 71 | 71 | 284.4667 | 123.7403 | 20.7232 | 78.4821 | 106.9048 | 257.3016 | 256.9747 | 106.1154 | 0 | 0 | 0 | 0 | 84.2597 | 107.5778 | 166.2707 | 166.1431 | 107.2697 | 65.8578 | 65.8578 | 65.8578 | 65.8578 | 123.7403 | 214.4826 | 423.5724 | 423.1178 | 213.3851 | 65.8578 | 65.8578 | 65.8578 | 65.8578 | 208 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 6 | 30 | 8 | 4328 | 15.9 | 15.9 | 17.2125 | 19.4635 | 15 | 66 | 66 | 512.3025 | 140.3894 | 29.8741 | 89.903 | 95.6754 | 399.6449 | 469.5078 | 264.3394 | 0 | 0 | 0 | 0 | 226.6106 | 110.8382 | 181.2163 | 197.3917 | 149.889 | 88.6864 | 88.6864 | 88.6864 | 88.6864 | 140.3894 | 206.5136 | 580.8612 | 666.8994 | 414.2283 | 88.6864 | 88.6864 | 88.6864 | 88.6864 | 367 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 9 | 4329 | 16.9 | 16.9 | 17.2125 | 19.4635 | 15 | 62 | 62 | 604.1233 | 157.895 | 39.019 | 102.4447 | 0.88692 | 371.0434 | 523.8477 | 369.7891 | 0 | 0 | 0 | 0 | 350.105 | 107.9326 | 187.3997 | 220.2045 | 187.1304 | 107.7422 | 107.7422 | 107.7422 | 107.7422 | 157.895 | 108.8195 | 558.4431 | 744.0522 | 556.9196 | 107.7422 | 107.7422 | 107.7422 | 107.7422 | 508 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 10 | 4330 | 17.4 | 17.4 | 17.2125 | 19.4635 | 15 | 58 | 58 | 415.7284 | 253.6402 | 47.6752 | 117.2617 | 0 | 173.8076 | 315.4058 | 272.2435 | 69.6047 | 0 | 0 | 0 | 290.3598 | 137.7622 | 207.9241 | 265.0838 | 247.6603 | 165.8599 | 137.7622 | 137.7622 | 137.7622 | 253.6402 | 137.7622 | 381.7318 | 580.4896 | 519.9038 | 235.4646 | 137.7622 | 137.7622 | 137.7622 | 544 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 11 | 4331 | 18.6 | 18.6 | 17.2125 | 19.4635 | 15 | 50 | 50 | 422.5848 | 284.7525 | 55.0749 | 136.0119 | 0 | 86.6908 | 252.9343 | 271.0123 | 130.335 | 0 | 0 | 0 | 334.2475 | 147.5083 | 187.3822 | 263.8466 | 272.1616 | 207.4565 | 147.5083 | 147.5083 | 147.5083 | 284.7525 | 147.5083 | 274.073 | 516.7809 | 543.1739 | 337.7914 | 147.5083 | 147.5083 | 147.5083 | 619 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 12 | 4332 | 18.1 | 18.1 | 17.2125 | 19.4635 | 15 | 52 | 52 | 321.5712 | 343.4271 | 59.9709 | 160.1921 | 0 | 0 | 127.86 | 184.0725 | 132.4578 | 3.2512 | 0 | 0 | 273.5729 | 160.346 | 160.346 | 246.4427 | 284.2943 | 249.5387 | 162.5352 | 160.346 | 160.346 | 343.4271 | 160.346 | 160.346 | 374.3027 | 468.3669 | 381.9966 | 165.7863 | 160.346 | 160.346 | 617 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 13 | 4333 | 19.3 | 19.3 | 17.2125 | 19.4635 | 15 | 52 | 52 | 326.187 | 351.0449 | 60.9062 | 188.2773 | 0 | 0 | 55.3158 | 147.7109 | 153.579 | 69.4826 | 0 | 0 | 284.9551 | 161.0311 | 161.0311 | 199.0451 | 262.5406 | 266.5732 | 208.7808 | 161.0311 | 161.0311 | 351.0449 | 161.0311 | 161.0311 | 254.3608 | 410.2515 | 420.1522 | 278.2633 | 161.0311 | 161.0311 | 636 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 14 | 4334 | 18.8 | 18.8 | 17.2125 | 19.4635 | 15 | 54 | 54 | 214.2307 | 377.2121 | 57.5129 | 214.5767 | 0 | 0 | 0 | 62.2864 | 103.0827 | 83.4945 | 14.9964 | 0 | 183.7879 | 170.0731 | 170.0731 | 170.0731 | 223.9314 | 259.2075 | 242.2698 | 183.0403 | 170.0731 | 377.2121 | 170.0731 | 170.0731 | 170.0731 | 286.2179 | 362.2902 | 325.7643 | 198.0367 | 170.0731 | 561 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 15 | 4335 | 18.6 | 18.6 | 17.2125 | 19.4635 | 15 | 50 | 50 | 576.2668 | 230.2383 | 50.9776 | 235.4946 | 0 | 0 | 0 | 55.9977 | 254.8473 | 304.4108 | 175.6546 | 0 | 463.7617 | 136.0932 | 136.0932 | 136.0932 | 151.3813 | 205.6698 | 219.2013 | 184.0492 | 136.0932 | 230.2383 | 136.0932 | 136.0932 | 136.0932 | 207.3791 | 460.5172 | 523.6121 | 359.7038 | 136.0932 | 694 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 16 | 4336 | 18.3 | 18.3 | 17.2125 | 19.4635 | 15 | 44 | 44 | 800.6997 | 133.1465 | 42.7287 | 251.7283 | 0 | 0 | 0 | 0 | 285.5868 | 495.7062 | 415.4476 | 91.8255 | 574.8535 | 117.0706 | 117.0706 | 117.0706 | 117.0706 | 145.75 | 166.8507 | 158.7909 | 126.292 | 133.1465 | 117.0706 | 117.0706 | 117.0706 | 117.0706 | 431.3368 | 662.5569 | 574.2385 | 218.1174 | 708 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 17 | 4337 | 18.6 | 18.6 | 17.2125 | 19.4635 | 15 | 50 | 50 | 793.0289 | 113.4967 | 33.7175 | 265.0511 | 0 | 0 | 0 | 0 | 182.6398 | 520.2943 | 553.1674 | 262.0026 | 478.5033 | 101.8426 | 101.8426 | 101.8426 | 101.8426 | 118.7187 | 149.9182 | 152.9557 | 126.0518 | 113.4967 | 101.8426 | 101.8426 | 101.8426 | 101.8426 | 301.3585 | 670.2125 | 706.1231 | 388.0544 | 592 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 18 | 4338 | 17.1 | 17.1 | 17.2125 | 19.4635 | 15 | 54 | 54 | 661.6258 | 114.742 | 24.5209 | 276.8287 | 0 | 0 | 0 | 0 | 47.4752 | 421.2613 | 548.2782 | 354.1212 | 310.258 | 85.3641 | 85.3641 | 85.3641 | 85.3641 | 92.4916 | 148.6086 | 167.6779 | 138.5288 | 114.742 | 85.3641 | 85.3641 | 85.3641 | 85.3641 | 139.9668 | 569.8699 | 715.9561 | 492.65 | 425 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 19 | 4339 | 16.3 | 16.3 | 17.2125 | 19.4635 | 15 | 57 | 57 | 635.5539 | 83.2563 | 15.5365 | 287.969 | 68.7525 | 0 | 0 | 0 | 0 | 357.3567 | 574.1312 | 454.5875 | 205.7437 | 71.5043 | 62.191 | 62.191 | 62.191 | 62.191 | 110.5989 | 139.9634 | 123.7699 | 83.2563 | 140.2568 | 62.191 | 62.191 | 62.191 | 62.191 | 467.9557 | 714.0947 | 578.3574 | 289 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 20 | 4340 | 14.9 | 14.9 | 17.2125 | 19.4635 | 15 | 65 | 65 | 260.9322 | 75.6513 | 7.1005 | 299.0941 | 77.5567 | 0 | 0 | 0 | 0 | 114.2534 | 239.1354 | 223.9351 | 46.3487 | 69.9115 | 42.8726 | 42.8726 | 42.8726 | 42.8726 | 82.7052 | 126.2433 | 120.944 | 75.6513 | 147.4682 | 42.8726 | 42.8726 | 42.8726 | 42.8726 | 196.9587 | 365.3788 | 344.8791 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 21 | 4341 | 13.4 | 13.4 | 17.2125 | 19.4635 | 15 | 72 | 72 | 26.6628 | 15.9182 | -0.45105 | 310.6498 | 12.8653 | 0 | 0 | 0 | 0 | 7.2511 | 23.1199 | 25.4453 | 1.0818 | 15.8286 | 8.6854 | 8.6854 | 8.6854 | 8.6854 | 12.7115 | 21.5223 | 22.8135 | 15.9182 | 28.6939 | 8.6854 | 8.6854 | 8.6854 | 8.6854 | 19.9626 | 44.6422 | 48.2588 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 22 | 4342 | 12.6 | 12.6 | 17.2125 | 19.4635 | 15 | 80 | 80 | 0 | 0 | -6.7556 | 322.9346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 23 | 4343 | 12.2 | 12.2 | 17.2125 | 19.4635 | 15 | 84 | 84 | 0 | 0 | -11.4314 | 336.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 6 | 30 | 24 | 4344 | 11.8 | 11.8 | 14.85 | 18.4679 | 15 | 86 | 86 | 0 | 0 | -14.1266 | 349.9288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 1 | 4345 | 11.9 | 11.9 | 14.85 | 18.4679 | 15 | 84 | 84 | 0 | 0 | -14.6029 | 4.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 2 | 4346 | 11.7 | 11.7 | 14.85 | 18.4679 | 15 | 92 | 92 | 0 | 0 | -12.8838 | 18.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 3 | 4347 | 11.2 | 11.2 | 14.85 | 18.4679 | 15 | 93 | 93 | 0 | 0 | -9.0003 | 31.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 4 | 4348 | 10.4 | 10.4 | 14.85 | 18.4679 | 15 | 95 | 95 | 0 | 0 | -3.3314 | 44.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 5 | 4349 | 10.5 | 10.5 | 14.85 | 18.4679 | 15 | 96 | 96 | 7.1236 | 6.9317 | 3.7445 | 56.1511 | 5.0888 | 7.1111 | 4.9678 | 0 | 0 | 0 | 0 | 0.085576 | 1.0683 | 7.6553 | 9.6669 | 7.5349 | 2.5933 | 2.5933 | 2.5933 | 2.5933 | 2.6784 | 6.9317 | 12.7441 | 16.778 | 12.5027 | 2.5933 | 2.5933 | 2.5933 | 2.5933 | 2.764 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 6 | 4350 | 13.2 | 13.2 | 14.85 | 18.4679 | 15 | 95 | 95 | 63.8574 | 65.4082 | 11.8533 | 67.4159 | 35.493 | 62.5181 | 52.9209 | 12.3234 | 0 | 0 | 0 | 0 | 9.5918 | 155.2865 | 253.3238 | 218.5088 | 71.2357 | 26.5308 | 26.5308 | 26.5308 | 26.5308 | 65.4082 | 190.7795 | 315.8418 | 271.4297 | 83.5591 | 26.5308 | 26.5308 | 26.5308 | 26.5308 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 7 | 4351 | 17.3 | 17.3 | 14.85 | 18.4679 | 15 | 73 | 73 | 246.4518 | 127.1921 | 20.6489 | 78.49 | 92.6288 | 222.9718 | 222.701 | 91.9749 | 0 | 0 | 0 | 0 | 72.8079 | 107.6236 | 166.2961 | 166.1742 | 107.3292 | 65.9277 | 65.9277 | 65.9277 | 65.9277 | 127.1921 | 200.2524 | 389.268 | 388.8751 | 199.3041 | 65.9277 | 65.9277 | 65.9277 | 65.9277 | 200 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 1 | 8 | 4352 | 20.1 | 20.1 | 14.85 | 18.4679 | 15 | 60 | 60 | 501.7157 | 142.4293 | 29.8 | 89.9131 | 93.6804 | 391.5419 | 460.0435 | 259.0579 | 0 | 0 | 0 | 0 | 221.5707 | 111.1989 | 181.8402 | 198.0862 | 150.4201 | 88.9816 | 88.9816 | 88.9816 | 88.9816 | 142.4293 | 204.8793 | 573.3822 | 658.1297 | 409.478 | 88.9816 | 88.9816 | 88.9816 | 88.9816 | 364 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 9 | 4353 | 21.2 | 21.2 | 14.85 | 18.4679 | 15 | 51 | 51 | 626.2447 | 151.4818 | 38.9447 | 102.454 | 0.82421 | 384.8479 | 543.433 | 383.6823 | 0 | 0 | 0 | 0 | 362.5182 | 104.9873 | 176.7276 | 206.3533 | 176.5099 | 104.8334 | 104.8334 | 104.8334 | 104.8334 | 151.4818 | 105.8115 | 561.5756 | 749.7862 | 560.1922 | 104.8334 | 104.8334 | 104.8334 | 104.8334 | 514 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 10 | 4354 | 22.2 | 22.2 | 14.85 | 18.4679 | 15 | 47 | 47 | 724.1398 | 150.6658 | 47.6006 | 117.2641 | 0 | 302.9892 | 549.9493 | 474.7566 | 121.4579 | 0 | 0 | 0 | 505.3342 | 118.2214 | 167.1498 | 207.0303 | 194.8877 | 137.8351 | 118.2214 | 118.2214 | 118.2214 | 150.6658 | 118.2214 | 470.139 | 756.9796 | 669.6443 | 259.293 | 118.2214 | 118.2214 | 118.2214 | 656 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 11 | 4355 | 22.9 | 22.9 | 14.85 | 18.4679 | 15 | 41 | 41 | 769.8346 | 155.5184 | 55.0009 | 135.9948 | 0 | 158.132 | 461.4262 | 494.4233 | 237.7939 | 0 | 0 | 0 | 608.4816 | 128.6038 | 152.9283 | 199.5821 | 204.6579 | 165.1822 | 128.6038 | 128.6038 | 128.6038 | 155.5184 | 128.6038 | 311.0602 | 661.0084 | 699.0812 | 402.976 | 128.6038 | 128.6038 | 128.6038 | 764 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 12 | 4356 | 24.1 | 24.1 | 14.85 | 18.4679 | 15 | 38 | 38 | 787.234 | 161.6853 | 59.9017 | 160.1361 | 0 | 0 | 313.6879 | 451.461 | 324.7744 | 7.8393 | 0 | 0 | 669.3147 | 135.3419 | 135.3419 | 172.1355 | 188.2954 | 173.4359 | 136.2614 | 135.3419 | 135.3419 | 161.6853 | 135.3419 | 135.3419 | 485.8234 | 639.7564 | 498.2103 | 144.1008 | 135.3419 | 135.3419 | 831 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 13 | 4357 | 24.6 | 24.6 | 14.85 | 18.4679 | 15 | 41 | 41 | 795.5028 | 163.4649 | 60.8495 | 188.1773 | 0 | 0 | 135.5523 | 361.1545 | 375.1973 | 169.4546 | 0 | 0 | 694.5351 | 136.6695 | 136.6695 | 152.5676 | 179.0271 | 180.6741 | 156.5438 | 136.6695 | 136.6695 | 163.4649 | 136.6695 | 136.6695 | 288.1199 | 540.1816 | 555.8714 | 325.9984 | 136.6695 | 136.6695 | 858 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 14 | 4358 | 25.9 | 25.9 | 14.85 | 18.4679 | 15 | 34 | 34 | 813.5661 | 155.4706 | 57.4727 | 214.4596 | 0 | 0 | 0 | 237.5139 | 392.2627 | 317.2293 | 56.3673 | 0 | 697.5294 | 133.9652 | 133.9652 | 133.9652 | 160.2227 | 177.3304 | 169.0354 | 140.1967 | 133.9652 | 155.4706 | 133.9652 | 133.9652 | 133.9652 | 397.7366 | 569.5931 | 486.2647 | 196.564 | 133.9652 | 853 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 15 | 4359 | 26.4 | 26.4 | 14.85 | 18.4679 | 15 | 30 | 30 | 827.1961 | 142.7511 | 50.9504 | 235.3843 | 0 | 0 | 0 | 81.3636 | 366.7358 | 437.2792 | 251.6704 | 0 | 665.2489 | 127.5764 | 127.5764 | 127.5764 | 135.8587 | 164.908 | 172.0889 | 153.195 | 127.5764 | 142.7511 | 127.5764 | 127.5764 | 127.5764 | 217.2223 | 531.6438 | 609.3681 | 404.8653 | 127.5764 | 808 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 16 | 4360 | 27 | 27 | 14.85 | 18.4679 | 15 | 30 | 30 | 801.9181 | 132.742 | 42.7088 | 251.6303 | 0 | 0 | 0 | 0 | 286.9906 | 496.9284 | 415.7723 | 91.0624 | 575.258 | 116.9683 | 116.9683 | 116.9683 | 116.9683 | 145.6807 | 166.6843 | 158.5649 | 126.0788 | 132.742 | 116.9683 | 116.9683 | 116.9683 | 116.9683 | 432.6714 | 663.6127 | 574.3372 | 217.1411 | 708 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 17 | 4361 | 27.2 | 27.2 | 14.85 | 18.4679 | 15 | 32 | 32 | 765.4109 | 119.6493 | 33.7006 | 264.9637 | 0 | 0 | 0 | 0 | 177.2485 | 502.7672 | 533.7717 | 252.1 | 461.3507 | 102.5766 | 102.5766 | 102.5766 | 102.5766 | 120.2116 | 152.5986 | 155.6833 | 127.6588 | 119.6493 | 102.5766 | 102.5766 | 102.5766 | 102.5766 | 297.4601 | 655.3658 | 689.455 | 379.7589 | 581 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 18 | 4362 | 27 | 27 | 14.85 | 18.4679 | 15 | 34 | 34 | 696.2943 | 106.9713 | 24.5038 | 276.7488 | 0 | 0 | 0 | 0 | 50.8532 | 443.9905 | 577.0442 | 372.0732 | 326.0287 | 83.7394 | 83.7394 | 83.7394 | 83.7394 | 90.6498 | 144.0727 | 162.1532 | 134.3 | 106.9713 | 83.7394 | 83.7394 | 83.7394 | 83.7394 | 141.503 | 588.0632 | 739.1973 | 506.3732 | 433 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 19 | 4363 | 26.7 | 26.7 | 14.85 | 18.4679 | 15 | 35 | 35 | 591.4173 | 89.9966 | 15.5168 | 287.8943 | 63.2417 | 0 | 0 | 0 | 0 | 333.1745 | 534.4217 | 422.6118 | 191.0034 | 73.2955 | 63.622 | 63.622 | 63.622 | 63.622 | 114.5844 | 145.3671 | 128.2647 | 89.9966 | 136.5372 | 63.622 | 63.622 | 63.622 | 63.622 | 447.7589 | 679.7888 | 550.8766 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 20 | 4364 | 24.4 | 24.4 | 14.85 | 18.4679 | 15 | 43 | 43 | 367.791 | 67.9759 | 7.0761 | 299.023 | 108.889 | 0 | 0 | 0 | 0 | 161.4703 | 337.2425 | 315.4626 | 65.0241 | 66.5732 | 41.2196 | 41.2196 | 41.2196 | 41.2196 | 78.8162 | 119.7429 | 114.6717 | 67.9759 | 175.4622 | 41.2196 | 41.2196 | 41.2196 | 41.2196 | 240.2866 | 456.9854 | 430.1343 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 21 | 4365 | 20.7 | 20.7 | 14.85 | 18.4679 | 15 | 57 | 57 | 39.9278 | 17.7168 | -0.48182 | 310.5817 | 19.2239 | 0 | 0 | 0 | 0 | 10.9064 | 34.6479 | 38.0931 | 7.2832 | 30.0828 | 10.4432 | 10.4432 | 10.4432 | 10.4432 | 21.5855 | 45.8405 | 49.3602 | 17.7168 | 49.3067 | 10.4432 | 10.4432 | 10.4432 | 10.4432 | 32.492 | 80.4884 | 87.4533 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 22 | 4366 | 18.7 | 18.7 | 14.85 | 18.4679 | 15 | 64 | 64 | 0 | 0 | -6.7941 | 322.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 23 | 4367 | 19 | 19 | 14.85 | 18.4679 | 15 | 63 | 63 | 0 | 0 | -11.4785 | 336.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 1 | 24 | 4368 | 18.3 | 18.3 | 20.1083 | 19.1746 | 15 | 66 | 66 | 0 | 0 | -14.1821 | 349.8774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 1 | 4369 | 17.5 | 17.5 | 20.1083 | 19.1746 | 15 | 71 | 71 | 0 | 0 | -14.6659 | 4.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 2 | 4370 | 17 | 17 | 20.1083 | 19.1746 | 15 | 73 | 73 | 0 | 0 | -12.9589 | 18.1581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 3 | 4371 | 16.5 | 16.5 | 20.1083 | 19.1746 | 15 | 75 | 75 | 0 | 0 | -9.0786 | 31.6479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 4 | 4372 | 14.1 | 14.1 | 20.1083 | 19.1746 | 15 | 85 | 85 | 0 | 0 | -3.4111 | 44.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 5 | 4373 | 15.3 | 15.3 | 20.1083 | 19.1746 | 15 | 86 | 86 | 3.1564 | 6.6354 | 3.6647 | 56.1535 | 2.2549 | 3.1506 | 2.2008 | 0 | 0 | 0 | 0 | 0.03823 | 1.3646 | 5.2403 | 6.0982 | 5.1885 | 3.0806 | 3.0806 | 3.0806 | 3.0806 | 3.1172 | 6.6354 | 7.4951 | 9.2488 | 7.3893 | 3.0806 | 3.0806 | 3.0806 | 3.0806 | 3.1555 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 6 | 4374 | 18.8 | 18.8 | 20.1083 | 19.1746 | 15 | 72 | 72 | 105.9778 | 67.1809 | 11.7739 | 67.4247 | 58.9057 | 103.7635 | 87.8381 | 20.4583 | 0 | 0 | 0 | 0 | 15.8191 | 152.7959 | 248.0295 | 214.2197 | 71.1716 | 27.7385 | 27.7385 | 27.7385 | 27.7385 | 67.1809 | 211.7016 | 351.7931 | 302.0578 | 91.6299 | 27.7385 | 27.7385 | 27.7385 | 27.7385 | 83 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 7 | 4375 | 20.7 | 20.7 | 20.1083 | 19.1746 | 15 | 67 | 67 | 323.6657 | 118.6612 | 20.57 | 78.5033 | 121.6402 | 292.8958 | 292.577 | 120.8706 | 0 | 0 | 0 | 0 | 95.3388 | 106.3607 | 164.6218 | 164.5133 | 106.0989 | 64.9788 | 64.9788 | 64.9788 | 64.9788 | 118.6612 | 228.0009 | 457.5176 | 457.0903 | 226.9695 | 64.9788 | 64.9788 | 64.9788 | 64.9788 | 214 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 2 | 8 | 4376 | 23.2 | 23.2 | 20.1083 | 19.1746 | 15 | 61 | 61 | 491.4098 | 144.3694 | 29.7213 | 89.9291 | 91.6989 | 383.6388 | 450.8483 | 253.9569 | 0 | 0 | 0 | 0 | 216.6306 | 111.4986 | 182.359 | 198.6723 | 150.8823 | 89.2412 | 89.2412 | 89.2412 | 89.2412 | 144.3694 | 203.1976 | 565.9978 | 649.5206 | 404.8392 | 89.2412 | 89.2412 | 89.2412 | 89.2412 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 9 | 4377 | 26 | 26 | 20.1083 | 19.1746 | 15 | 52 | 52 | 570.9275 | 166.9159 | 38.8658 | 102.4697 | 0.6139 | 351.0317 | 495.8199 | 350.1635 | 0 | 0 | 0 | 0 | 330.0841 | 109.4972 | 191.6294 | 225.5654 | 191.4259 | 109.3533 | 109.3533 | 109.3533 | 109.3533 | 166.9159 | 110.1111 | 542.6611 | 721.3853 | 541.5895 | 109.3533 | 109.3533 | 109.3533 | 109.3533 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 10 | 4378 | 27.6 | 27.6 | 20.1083 | 19.1746 | 15 | 50 | 50 | 564.4065 | 203.5083 | 47.521 | 117.2734 | 0 | 236.3161 | 429.0904 | 370.5094 | 94.889 | 0 | 0 | 0 | 393.4917 | 127.9477 | 192.026 | 244.2978 | 228.4132 | 153.6774 | 127.9477 | 127.9477 | 127.9477 | 203.5083 | 127.9477 | 428.3421 | 673.3882 | 598.9226 | 248.5664 | 127.9477 | 127.9477 | 127.9477 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 11 | 4379 | 29.5 | 29.5 | 20.1083 | 19.1746 | 15 | 46 | 46 | 676.5244 | 187.6885 | 54.9212 | 135.9845 | 0 | 139.1059 | 406.0805 | 435.1786 | 209.355 | 0 | 0 | 0 | 534.3115 | 132.6189 | 160.308 | 213.4495 | 219.2415 | 174.2912 | 132.6189 | 132.6189 | 132.6189 | 187.6885 | 132.6189 | 299.4139 | 619.53 | 654.4201 | 383.6462 | 132.6189 | 132.6189 | 132.6189 | 722 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 12 | 4380 | 30.7 | 30.7 | 20.1083 | 19.1746 | 15 | 44 | 44 | 726.9089 | 182.4012 | 59.8261 | 160.0849 | 0 | 0 | 290.2794 | 417.6945 | 300.4299 | 7.1775 | 0 | 0 | 617.5988 | 136.9918 | 136.9918 | 190.2026 | 213.5589 | 192.0633 | 138.3075 | 136.9918 | 136.9918 | 182.4012 | 136.9918 | 136.9918 | 480.4819 | 631.2534 | 492.4932 | 145.485 | 136.9918 | 136.9918 | 800 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 13 | 4381 | 25.4 | 25.4 | 20.1083 | 19.1746 | 15 | 62 | 62 | 54.6883 | 374.2844 | 60.786 | 188.078 | 0 | 0 | 9.3631 | 24.8952 | 25.844 | 11.6537 | 0 | 0 | 47.7156 | 162.0121 | 162.0121 | 185.0521 | 223.2722 | 225.6069 | 190.6887 | 162.0121 | 162.0121 | 374.2844 | 162.0121 | 162.0121 | 194.4152 | 248.1674 | 251.4509 | 202.3424 | 162.0121 | 162.0121 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 14 | 4382 | 26.2 | 26.2 | 20.1083 | 19.1746 | 15 | 62 | 62 | 14.3642 | 304.6929 | 57.4259 | 214.3394 | 0 | 0 | 0 | 4.2116 | 6.9412 | 5.6048 | 0.98515 | 0 | 12.3071 | 147.6181 | 147.6181 | 147.6181 | 156.4833 | 162.2291 | 159.416 | 149.6918 | 147.6181 | 304.6929 | 147.6181 | 147.6181 | 147.6181 | 160.6948 | 169.1703 | 165.0207 | 150.677 | 147.6181 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 15 | 4383 | 27.1 | 27.1 | 20.1083 | 19.1746 | 15 | 58 | 58 | 81.2465 | 356.7093 | 50.9169 | 235.2692 | 0 | 0 | 0 | 8.0919 | 36.1185 | 42.9874 | 24.6748 | 0 | 65.2907 | 157.787 | 157.787 | 157.787 | 170.4136 | 214.1462 | 224.8643 | 196.2895 | 157.787 | 356.7093 | 157.787 | 157.787 | 157.787 | 178.5055 | 250.2647 | 267.8517 | 220.9643 | 157.787 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 16 | 4384 | 24.6 | 24.6 | 20.1083 | 19.1746 | 15 | 71 | 71 | 3.9127 | 169.1958 | 42.6831 | 251.5274 | 0 | 0 | 0 | 0 | 1.4054 | 2.4272 | 2.0273 | 0.43976 | 2.8042 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 169.1958 | 85.3268 | 85.3268 | 85.3268 | 85.3268 | 86.7322 | 87.754 | 87.3541 | 85.7666 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 17 | 4385 | 24 | 24 | 20.1083 | 19.1746 | 15 | 75 | 75 | 5.0412 | 160.965 | 33.6781 | 264.8716 | 0 | 0 | 0 | 0 | 1.1742 | 3.3157 | 3.5149 | 1.6551 | 3.035 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 160.965 | 81.1968 | 81.1968 | 81.1968 | 81.1968 | 82.371 | 84.5125 | 84.7117 | 82.852 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 2 | 18 | 4386 | 21.8 | 21.8 | 20.1083 | 19.1746 | 15 | 87 | 87 | 4.8577 | 122.7292 | 24.4811 | 276.6647 | 0 | 0 | 0 | 0 | 0.36134 | 3.1025 | 4.0262 | 2.5915 | 2.2708 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 122.7292 | 61.2672 | 61.2672 | 61.2672 | 61.2672 | 61.6285 | 64.3697 | 65.2934 | 63.8587 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 19 | 4387 | 20.5 | 20.5 | 20.1083 | 19.1746 | 15 | 95 | 95 | 0.40923 | 24.8682 | 15.4913 | 287.8157 | 0.043225 | 0 | 0 | 0 | 0 | 0.23101 | 0.36993 | 0.29214 | 0.13182 | 11.761 | 11.761 | 11.761 | 11.761 | 11.761 | 11.761 | 11.761 | 11.761 | 24.8682 | 11.8042 | 11.761 | 11.761 | 11.761 | 11.761 | 11.992 | 12.1309 | 12.0531 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 20 | 4388 | 20.5 | 20.5 | 20.1083 | 19.1746 | 15 | 93 | 93 | 0.43048 | 13.9243 | 7.0457 | 298.9486 | 0.12692 | 0 | 0 | 0 | 0 | 0.18952 | 0.39495 | 0.36902 | 0.07571 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 13.9243 | 6.6554 | 6.5285 | 6.5285 | 6.5285 | 6.5285 | 6.718 | 6.9235 | 6.8975 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 21 | 4389 | 20 | 20 | 20.1083 | 19.1746 | 15 | 95 | 95 | 2.905 | 7.8876 | -0.51882 | 310.5109 | 1.3955 | 0 | 0 | 0 | 0 | 0.79717 | 2.5229 | 2.7707 | 0.11239 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 7.8876 | 5.6259 | 4.2304 | 4.2304 | 4.2304 | 4.2304 | 5.0276 | 6.7533 | 7.0011 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 22 | 4390 | 19.4 | 19.4 | 20.1083 | 19.1746 | 15 | 94 | 94 | 0 | 0 | -6.8391 | 322.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 23 | 4391 | 18.9 | 18.9 | 20.1083 | 19.1746 | 15 | 95 | 95 | 0 | 0 | -11.5322 | 335.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 2 | 24 | 4392 | 18.4 | 18.4 | 21.8208 | 20.0969 | 15 | 99 | 99 | 0 | 0 | -14.2445 | 349.8259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 1 | 4393 | 18.1 | 18.1 | 21.8208 | 20.0969 | 15 | 98 | 98 | 0 | 0 | -14.7357 | 4.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 2 | 4394 | 18.1 | 18.1 | 21.8208 | 20.0969 | 15 | 97 | 97 | 0 | 0 | -13.0404 | 18.1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 3 | 4395 | 18.6 | 18.6 | 21.8208 | 20.0969 | 15 | 97 | 97 | 0 | 0 | -9.1629 | 31.6351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 4 | 4396 | 18.3 | 18.3 | 21.8208 | 20.0969 | 15 | 97 | 97 | 0 | 0 | -3.4964 | 44.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 5 | 4397 | 18.4 | 18.4 | 21.8208 | 20.0969 | 15 | 98 | 98 | 0 | 0 | 3.5797 | 56.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 6 | 4398 | 19.3 | 19.3 | 21.8208 | 20.0969 | 15 | 96 | 96 | 4.7023 | 38.303 | 11.6897 | 67.4383 | 2.6134 | 4.6043 | 3.8981 | 0.90838 | 0 | 0 | 0 | 0 | 0.69705 | 72.0758 | 114.8262 | 99.6609 | 35.4634 | 15.9579 | 15.9579 | 15.9579 | 15.9579 | 38.303 | 74.6893 | 119.4306 | 103.559 | 36.3718 | 15.9579 | 15.9579 | 15.9579 | 15.9579 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 7 | 4399 | 19.6 | 19.6 | 21.8208 | 20.0969 | 15 | 95 | 95 | 2.9323 | 60.139 | 20.4866 | 78.522 | 1.1017 | 2.6541 | 2.6517 | 1.096 | 0 | 0 | 0 | 0 | 0.86096 | 32.9792 | 38.458 | 38.4497 | 32.9591 | 29.0909 | 29.0909 | 29.0909 | 29.0909 | 60.139 | 34.081 | 41.1121 | 41.1014 | 34.0551 | 29.0909 | 29.0909 | 29.0909 | 29.0909 | 61 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 3 | 8 | 4400 | 19.2 | 19.2 | 21.8208 | 20.0969 | 15 | 91 | 91 | 3.5096 | 98.4559 | 29.6382 | 89.9509 | 0.65421 | 2.7408 | 3.2219 | 1.8156 | 0 | 0 | 0 | 0 | 1.5441 | 49.5628 | 53.8812 | 54.8768 | 51.9664 | 48.2089 | 48.2089 | 48.2089 | 48.2089 | 98.4559 | 50.217 | 56.622 | 58.0986 | 53.782 | 48.2089 | 48.2089 | 48.2089 | 48.2089 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 9 | 4401 | 18.6 | 18.6 | 21.8208 | 20.0969 | 15 | 88 | 88 | 6.8127 | 174.0666 | 38.7823 | 102.4918 | 0.0050755 | 4.1906 | 5.9213 | 4.1834 | 0 | 0 | 0 | 0 | 3.9334 | 82.4258 | 100.8405 | 108.4551 | 100.809 | 82.4035 | 82.4035 | 82.4035 | 82.4035 | 174.0666 | 82.4309 | 105.0312 | 114.3764 | 104.9924 | 82.4035 | 82.4035 | 82.4035 | 82.4035 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 10 | 4402 | 18.7 | 18.7 | 21.8208 | 20.0969 | 15 | 84 | 84 | 4.4376 | 174.9094 | 47.4364 | 117.2896 | 0 | 1.8591 | 3.3774 | 2.9173 | 0.74824 | 0 | 0 | 0 | 3.0906 | 86.6187 | 89.7711 | 92.3457 | 91.5654 | 87.8875 | 86.6187 | 86.6187 | 86.6187 | 174.9094 | 86.6187 | 91.6302 | 95.7231 | 94.4827 | 88.6357 | 86.6187 | 86.6187 | 86.6187 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 11 | 4403 | 18.5 | 18.5 | 21.8208 | 20.0969 | 15 | 83 | 83 | 3.0426 | 164.599 | 54.836 | 135.9809 | 0 | 0.62607 | 1.829 | 1.9605 | 0.94359 | 0 | 0 | 0 | 2.401 | 82.9084 | 82.9084 | 82.9084 | 82.9084 | 82.9084 | 82.9084 | 82.9084 | 82.9084 | 164.599 | 82.9084 | 83.5345 | 84.7374 | 84.869 | 83.852 | 82.9084 | 82.9084 | 82.9084 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 12 | 4404 | 19 | 19 | 21.8208 | 20.0969 | 15 | 76 | 76 | 4.6452 | 218.0563 | 59.7441 | 160.0386 | 0 | 0 | 1.859 | 2.6749 | 1.9238 | 0.045797 | 0 | 0 | 3.9437 | 109.7058 | 109.7058 | 111.6869 | 112.5564 | 111.756 | 109.7546 | 109.7058 | 109.7058 | 218.0563 | 109.7058 | 109.7058 | 113.546 | 115.2312 | 113.6798 | 109.8004 | 109.7058 | 109.7058 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 13 | 4405 | 19.1 | 19.1 | 21.8208 | 20.0969 | 15 | 76 | 76 | 6.8287 | 263.0463 | 60.7157 | 187.9794 | 0 | 0 | 1.1746 | 3.1174 | 3.234 | 1.4562 | 0 | 0 | 5.9537 | 130.1019 | 130.1019 | 132.7223 | 137.0563 | 137.3165 | 133.3505 | 130.1019 | 130.1019 | 263.0463 | 130.1019 | 130.1019 | 133.8969 | 140.1737 | 140.5505 | 134.8067 | 130.1019 | 130.1019 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 14 | 4406 | 18 | 18 | 21.8208 | 20.0969 | 15 | 82 | 82 | 2.1696 | 151.1425 | 57.3723 | 214.2163 | 0 | 0 | 0 | 0.63898 | 1.051 | 0.84732 | 0.14732 | 0 | 1.8575 | 75.7321 | 75.7321 | 75.7321 | 75.7321 | 75.7321 | 75.7321 | 75.7321 | 75.7321 | 151.1425 | 75.7321 | 75.7321 | 75.7321 | 76.3711 | 76.7831 | 76.5795 | 75.8795 | 75.7321 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 15 | 4407 | 17.8 | 17.8 | 21.8208 | 20.0969 | 15 | 84 | 84 | 2.3709 | 148.0963 | 50.8772 | 235.1495 | 0 | 0 | 0 | 0.23918 | 1.0571 | 1.2557 | 0.71882 | 0 | 1.9037 | 74.1012 | 74.1012 | 74.1012 | 74.1012 | 74.1012 | 74.1012 | 74.1012 | 74.1012 | 148.0963 | 74.1012 | 74.1012 | 74.1012 | 74.3404 | 75.1583 | 75.357 | 74.82 | 74.1012 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 16 | 4408 | 18 | 18 | 21.8208 | 20.0969 | 15 | 81 | 81 | 2.5605 | 137.1668 | 42.6516 | 251.4197 | 0 | 0 | 0 | 0 | 0.92322 | 1.5903 | 1.3258 | 0.2847 | 1.8332 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 137.1668 | 68.3614 | 68.3614 | 68.3614 | 68.3614 | 69.2846 | 69.9517 | 69.6873 | 68.6461 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 17 | 4409 | 18.6 | 18.6 | 21.8208 | 20.0969 | 15 | 78 | 78 | 8.9401 | 194.6247 | 33.6499 | 264.7749 | 0 | 0 | 0 | 0 | 2.0951 | 5.8886 | 6.2326 | 2.9256 | 5.3753 | 96.3566 | 96.3566 | 96.3566 | 96.3566 | 98.6427 | 102.7819 | 103.1573 | 99.5489 | 194.6247 | 96.3566 | 96.3566 | 96.3566 | 96.3566 | 100.7378 | 108.6705 | 109.3899 | 102.4746 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 3 | 18 | 4410 | 18.9 | 18.9 | 21.8208 | 20.0969 | 15 | 75 | 75 | 9.6182 | 153.5121 | 24.4527 | 276.5763 | 0 | 0 | 0 | 0 | 0.72915 | 6.1536 | 7.9733 | 5.1224 | 4.4879 | 76.0781 | 76.0781 | 76.0781 | 76.0781 | 76.5925 | 80.4193 | 81.7031 | 79.6918 | 153.5121 | 76.0781 | 76.0781 | 76.0781 | 76.0781 | 77.3217 | 86.5728 | 89.6764 | 84.8142 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 19 | 4411 | 18.5 | 18.5 | 21.8208 | 20.0969 | 15 | 79 | 79 | 2.6976 | 63.1336 | 15.46 | 287.7334 | 0.28123 | 0 | 0 | 0 | 0 | 1.5261 | 2.4394 | 1.9238 | 0.86638 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 63.1336 | 30.9828 | 30.7015 | 30.7015 | 30.7015 | 30.7015 | 32.2276 | 33.141 | 32.6253 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 20 | 4412 | 18.1 | 18.1 | 21.8208 | 20.0969 | 15 | 86 | 86 | 2.8796 | 35.4965 | 7.0094 | 298.8709 | 0.84536 | 0 | 0 | 0 | 0 | 1.2715 | 2.6435 | 2.467 | 0.50352 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 35.4965 | 17.9062 | 17.0608 | 17.0608 | 17.0608 | 17.0608 | 18.3323 | 19.7044 | 19.5278 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 21 | 4413 | 17.2 | 17.2 | 21.8208 | 20.0969 | 15 | 83 | 83 | 3.0762 | 7.8844 | -0.56204 | 310.4375 | 1.4742 | 0 | 0 | 0 | 0 | 0.84819 | 2.6737 | 2.933 | 0.11565 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 7.8844 | 5.703 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 5.077 | 6.9026 | 7.1619 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 22 | 4414 | 16.5 | 16.5 | 21.8208 | 20.0969 | 15 | 89 | 89 | 0 | 0 | -6.8906 | 322.7353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 23 | 4415 | 16.1 | 16.1 | 21.8208 | 20.0969 | 15 | 90 | 90 | 0 | 0 | -11.5927 | 335.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 3 | 24 | 4416 | 16.1 | 16.1 | 18.2208 | 19.5428 | 15 | 86 | 86 | 0 | 0 | -14.3136 | 349.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 1 | 4417 | 15.6 | 15.6 | 18.2208 | 19.5428 | 15 | 85 | 85 | 0 | 0 | -14.8121 | 4.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 2 | 4418 | 15 | 15 | 18.2208 | 19.5428 | 15 | 88 | 88 | 0 | 0 | -13.1283 | 18.1092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 3 | 4419 | 14 | 14 | 18.2208 | 19.5428 | 15 | 88 | 88 | 0 | 0 | -9.2532 | 31.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 4 | 4420 | 12.8 | 12.8 | 18.2208 | 19.5428 | 15 | 92 | 92 | 0 | 0 | -3.5871 | 44.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 5 | 4421 | 12.3 | 12.3 | 18.2208 | 19.5428 | 15 | 94 | 94 | 3.8973 | 2.9512 | 3.4896 | 56.1719 | 2.7835 | 3.8893 | 2.7168 | 0 | 0 | 0 | 0 | 0.047176 | 0.048814 | 3.225 | 4.0828 | 3.1732 | 1.0657 | 1.0657 | 1.0657 | 1.0657 | 1.1023 | 2.9512 | 6.0085 | 7.9721 | 5.89 | 1.0657 | 1.0657 | 1.0657 | 1.0657 | 1.1495 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 6 | 4422 | 13.7 | 13.7 | 18.2208 | 19.5428 | 15 | 94 | 94 | 9.7687 | 48.5629 | 11.6008 | 67.457 | 5.4282 | 9.5658 | 8.0999 | 1.8892 | 0 | 0 | 0 | 0 | 1.4371 | 128.77 | 213.0321 | 183.1794 | 56.6991 | 18.2259 | 18.2259 | 18.2259 | 18.2259 | 48.5629 | 134.1981 | 222.5979 | 191.2793 | 58.5883 | 18.2259 | 18.2259 | 18.2259 | 18.2259 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 7 | 4423 | 16.6 | 16.6 | 18.2208 | 19.5428 | 15 | 86 | 86 | 256.1026 | 125.0718 | 20.3986 | 78.546 | 96.1783 | 231.8467 | 231.7025 | 95.8301 | 0 | 0 | 0 | 0 | 74.9282 | 106.5019 | 164.772 | 164.7101 | 106.3524 | 65.193 | 65.193 | 65.193 | 65.193 | 125.0718 | 202.6802 | 396.6187 | 396.4125 | 202.1825 | 65.193 | 65.193 | 65.193 | 65.193 | 200 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 4 | 8 | 4424 | 18 | 18 | 18.2208 | 19.5428 | 15 | 75 | 75 | 96.1384 | 196.7938 | 29.5507 | 89.9786 | 17.894 | 75.1011 | 88.315 | 49.7952 | 0 | 0 | 0 | 0 | 42.2062 | 114.3065 | 194.0913 | 212.5202 | 158.798 | 89.3504 | 89.3504 | 89.3504 | 89.3504 | 196.7938 | 132.2005 | 269.1924 | 300.8352 | 208.5932 | 89.3504 | 89.3504 | 89.3504 | 89.3504 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 9 | 4425 | 19.6 | 19.6 | 18.2208 | 19.5428 | 15 | 69 | 69 | 575.7584 | 165.0801 | 38.6943 | 102.5203 | 0.18702 | 354.2963 | 500.8636 | 354.0318 | 0 | 0 | 0 | 0 | 331.9199 | 108.8757 | 190.6555 | 224.5045 | 190.5944 | 108.8325 | 108.8325 | 108.8325 | 108.8325 | 165.0801 | 109.0627 | 544.9518 | 725.3681 | 544.6262 | 108.8325 | 108.8325 | 108.8325 | 108.8325 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 10 | 4426 | 20.1 | 20.1 | 18.2208 | 19.5428 | 15 | 64 | 64 | 392.5529 | 259.92 | 47.347 | 117.3126 | 0 | 164.5287 | 299.0987 | 258.4607 | 66.4199 | 0 | 0 | 0 | 273.08 | 138.394 | 209.9668 | 268.507 | 250.8288 | 167.2878 | 138.394 | 138.394 | 138.394 | 259.92 | 138.394 | 374.4955 | 567.6057 | 509.2895 | 233.7077 | 138.394 | 138.394 | 138.394 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 11 | 4427 | 21 | 21 | 18.2208 | 19.5428 | 15 | 56 | 56 | 408.61 | 288.8651 | 54.7452 | 135.9841 | 0 | 84.1153 | 245.9914 | 263.769 | 127.0344 | 0 | 0 | 0 | 322.1349 | 147.7877 | 188.0643 | 265.5748 | 274.0872 | 208.6151 | 147.7877 | 147.7877 | 147.7877 | 288.8651 | 147.7877 | 272.1796 | 511.5662 | 537.8563 | 335.6494 | 147.7877 | 147.7877 | 147.7877 | 611 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 12 | 4428 | 20.6 | 20.6 | 18.2208 | 19.5428 | 15 | 53 | 53 | 542.6846 | 256.6573 | 59.6557 | 159.9973 | 0 | 0 | 217.6607 | 313.1985 | 225.2689 | 5.3799 | 0 | 0 | 460.3427 | 147.4268 | 147.4268 | 222.4591 | 255.393 | 225.0818 | 149.2814 | 147.4268 | 147.4268 | 256.6573 | 147.4268 | 147.4268 | 440.1198 | 568.5915 | 450.3508 | 154.6612 | 147.4268 | 147.4268 | 717 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 13 | 4429 | 21.2 | 21.2 | 18.2208 | 19.5428 | 15 | 49 | 49 | 748.4179 | 178.999 | 60.6384 | 187.882 | 0 | 0 | 129.3338 | 342.6798 | 355.2887 | 159.7742 | 0 | 0 | 652.001 | 137.4758 | 137.4758 | 154.6828 | 183.0671 | 184.7446 | 158.7327 | 137.4758 | 137.4758 | 178.999 | 137.4758 | 137.4758 | 284.0166 | 525.7469 | 540.0333 | 318.5069 | 137.4758 | 137.4758 | 831 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 14 | 4430 | 21.3 | 21.3 | 18.2208 | 19.5428 | 15 | 48 | 48 | 834.1892 | 150.3983 | 57.3121 | 214.0904 | 0 | 0 | 0 | 246.8261 | 405.1547 | 326.1492 | 56.0899 | 0 | 713.6017 | 133.9436 | 133.9436 | 133.9436 | 159.8886 | 176.5312 | 168.2266 | 139.8394 | 133.9436 | 150.3983 | 133.9436 | 133.9436 | 133.9436 | 406.7147 | 581.6859 | 494.3758 | 195.9293 | 133.9436 | 864 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 15 | 4431 | 21.3 | 21.3 | 18.2208 | 19.5428 | 15 | 49 | 49 | 775.0935 | 156.2145 | 50.8313 | 235.0255 | 0 | 0 | 0 | 79.2242 | 346.6647 | 411.0337 | 234.6247 | 0 | 621.7855 | 127.9374 | 127.9374 | 127.9374 | 137.1471 | 168.2367 | 175.7195 | 155.2122 | 127.9374 | 156.2145 | 127.9374 | 127.9374 | 127.9374 | 216.3713 | 514.9014 | 586.7532 | 389.8369 | 127.9374 | 778 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 16 | 4432 | 21.5 | 21.5 | 18.2208 | 19.5428 | 15 | 47 | 47 | 650.3935 | 178.8406 | 42.6142 | 251.3073 | 0 | 0 | 0 | 0 | 235.471 | 404.5197 | 336.6062 | 71.5134 | 465.1594 | 121.7651 | 121.7651 | 121.7651 | 121.7651 | 169.1247 | 203.1249 | 189.4657 | 136.1484 | 178.8406 | 121.7651 | 121.7651 | 121.7651 | 121.7651 | 404.5957 | 607.6446 | 526.0719 | 207.6618 | 644 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 17 | 4433 | 20.5 | 20.5 | 18.2208 | 19.5428 | 15 | 47 | 47 | 625.8354 | 157.245 | 33.616 | 264.6738 | 0 | 0 | 0 | 0 | 147.6095 | 412.8695 | 436.2762 | 204.1182 | 375.755 | 107.0689 | 107.0689 | 107.0689 | 107.0689 | 135.3221 | 186.0942 | 190.5743 | 146.1381 | 157.245 | 107.0689 | 107.0689 | 107.0689 | 107.0689 | 282.9316 | 598.9637 | 626.8505 | 350.2563 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 4 | 18 | 4434 | 20.4 | 20.4 | 18.2208 | 19.5428 | 15 | 48 | 48 | 615.854 | 124.216 | 24.4186 | 276.4839 | 0 | 0 | 0 | 0 | 47.607 | 394.746 | 510.6482 | 327.4196 | 286.784 | 86.8388 | 86.8388 | 86.8388 | 86.8388 | 94.9351 | 153.9712 | 173.682 | 142.5213 | 124.216 | 86.8388 | 86.8388 | 86.8388 | 86.8388 | 142.5421 | 548.7172 | 684.3303 | 469.941 | 411 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 19 | 4435 | 19.4 | 19.4 | 18.2208 | 19.5428 | 15 | 52 | 52 | 606.3001 | 86.891 | 15.4229 | 287.6474 | 62.3417 | 0 | 0 | 0 | 0 | 343.7905 | 548.5349 | 431.955 | 194.109 | 71.7119 | 62.6038 | 62.6038 | 62.6038 | 62.6038 | 112.8317 | 142.7449 | 125.7126 | 86.891 | 134.0536 | 62.6038 | 62.6038 | 62.6038 | 62.6038 | 456.6222 | 691.2798 | 557.6676 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 20 | 4436 | 18.2 | 18.2 | 18.2208 | 19.5428 | 15 | 57 | 57 | 370.7294 | 66.5863 | 6.9671 | 298.79 | 108.3426 | 0 | 0 | 0 | 0 | 164.2031 | 340.5608 | 317.4226 | 64.4137 | 65.2669 | 40.5115 | 40.5115 | 40.5115 | 40.5115 | 78.0306 | 118.3269 | 113.04 | 66.5863 | 173.6095 | 40.5115 | 40.5115 | 40.5115 | 40.5115 | 242.2337 | 458.8877 | 430.4626 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 21 | 4437 | 16.2 | 16.2 | 18.2208 | 19.5428 | 15 | 71 | 71 | 36.1977 | 13.5152 | -0.6115 | 310.3613 | 17.3041 | 0 | 0 | 0 | 0 | 10.0303 | 31.4891 | 34.502 | 14.4848 | 24.4775 | 8.9306 | 8.9306 | 8.9306 | 8.9306 | 17.9423 | 37.222 | 39.929 | 13.5152 | 41.7816 | 8.9306 | 8.9306 | 8.9306 | 8.9306 | 27.9727 | 68.7111 | 74.431 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 22 | 4438 | 13 | 13 | 18.2208 | 19.5428 | 15 | 91 | 91 | 0 | 0 | -6.9486 | 322.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 23 | 4439 | 11.2 | 11.2 | 18.2208 | 19.5428 | 15 | 92 | 92 | 0 | 0 | -11.6599 | 335.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 4 | 24 | 4440 | 10.3 | 10.3 | 17.2417 | 18.6992 | 15 | 95 | 95 | 0 | 0 | -14.3895 | 349.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 1 | 4441 | 9.8 | 9.8 | 17.2417 | 18.6992 | 15 | 97 | 97 | 0 | 0 | -14.8951 | 3.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 2 | 4442 | 9.8 | 9.8 | 17.2417 | 18.6992 | 15 | 98 | 98 | 0 | 0 | -13.2225 | 18.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 3 | 4443 | 9.2 | 9.2 | 17.2417 | 18.6992 | 15 | 97 | 97 | 0 | 0 | -9.3494 | 31.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 4 | 4444 | 9.1 | 9.1 | 17.2417 | 18.6992 | 15 | 98 | 98 | 0 | 0 | -3.6833 | 44.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 5 | 4445 | 9.5 | 9.5 | 17.2417 | 18.6992 | 15 | 99 | 99 | 5.8047 | 5.0076 | 3.3945 | 56.1878 | 4.145 | 5.7923 | 4.0465 | 0 | 0 | 0 | 0 | 0.069642 | 0.99237 | 5.5565 | 7.0107 | 5.4696 | 1.8973 | 1.8973 | 1.8973 | 1.8973 | 1.9588 | 5.0076 | 9.7015 | 12.803 | 9.5161 | 1.8973 | 1.8973 | 1.8973 | 1.8973 | 2.0284 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 6 | 4446 | 12.3 | 12.3 | 17.2417 | 18.6992 | 15 | 89 | 89 | 60.3222 | 63.1993 | 11.5072 | 67.4805 | 33.5088 | 59.0721 | 50.0317 | 11.6835 | 0 | 0 | 0 | 0 | 8.8007 | 154.7494 | 253.581 | 218.6297 | 70.3695 | 25.1992 | 25.1992 | 25.1992 | 25.1992 | 63.1993 | 188.2582 | 312.6531 | 268.6614 | 82.0529 | 25.1992 | 25.1992 | 25.1992 | 25.1992 | 72 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 7 | 4447 | 15.1 | 15.1 | 17.2417 | 18.6992 | 15 | 79 | 79 | 244.8779 | 125.6309 | 20.3063 | 78.5755 | 91.9024 | 221.7214 | 221.659 | 91.7518 | 0 | 0 | 0 | 0 | 71.3691 | 106.1182 | 164.2393 | 164.2114 | 106.0508 | 64.9727 | 64.9727 | 64.9727 | 64.9727 | 125.6309 | 198.0206 | 385.9607 | 385.8704 | 197.8026 | 64.9727 | 64.9727 | 64.9727 | 64.9727 | 197 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 5 | 8 | 4448 | 17.6 | 17.6 | 17.2417 | 18.6992 | 15 | 68 | 68 | 381.9484 | 165.712 | 29.4588 | 90.0122 | 70.953 | 298.4459 | 351.1133 | 198.1032 | 0 | 0 | 0 | 0 | 167.288 | 117.5623 | 195.2609 | 213.249 | 160.9896 | 93.3288 | 93.3288 | 93.3288 | 93.3288 | 165.712 | 188.5153 | 493.7068 | 564.3623 | 359.0928 | 93.3288 | 93.3288 | 93.3288 | 93.3288 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 9 | 4449 | 19.8 | 19.8 | 17.2417 | 18.6992 | 15 | 64 | 64 | 551.2161 | 171.7469 | 38.6018 | 102.5553 | 0 | 339.3027 | 479.9489 | 339.4475 | 0.1024 | 0 | 0 | 0 | 317.2531 | 110.0003 | 193.5814 | 228.227 | 193.6171 | 110.0255 | 110.0003 | 110.0003 | 110.0003 | 171.7469 | 110.0003 | 532.8841 | 708.1759 | 533.0646 | 110.1279 | 110.0003 | 110.0003 | 110.0003 | 489 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 10 | 4450 | 21.9 | 21.9 | 17.2417 | 18.6992 | 15 | 55 | 55 | 656.9153 | 171.5835 | 47.2528 | 117.3426 | 0 | 275.4207 | 501.103 | 433.246 | 111.5994 | 0 | 0 | 0 | 456.4165 | 120.9545 | 173.9386 | 217.3543 | 204.3003 | 142.4235 | 120.9545 | 120.9545 | 120.9545 | 171.5835 | 120.9545 | 449.3592 | 718.4573 | 637.5463 | 254.0228 | 120.9545 | 120.9545 | 120.9545 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 11 | 4451 | 22.6 | 22.6 | 17.2417 | 18.6992 | 15 | 48 | 48 | 739.0384 | 164.9608 | 54.649 | 135.9941 | 0 | 152.1577 | 445.5891 | 478.0004 | 230.4056 | 0 | 0 | 0 | 582.0392 | 129.4882 | 154.9132 | 203.9446 | 209.3604 | 167.9882 | 129.4882 | 129.4882 | 129.4882 | 164.9608 | 129.4882 | 307.0709 | 649.5337 | 687.3608 | 398.3938 | 129.4882 | 129.4882 | 129.4882 | 747 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 12 | 4452 | 23.5 | 23.5 | 17.2417 | 18.6992 | 15 | 43 | 43 | 731.0379 | 180.4436 | 59.5611 | 159.9611 | 0 | 0 | 293.8486 | 422.903 | 304.2266 | 7.3384 | 0 | 0 | 619.5564 | 136.6054 | 136.6054 | 189.7317 | 213.0642 | 191.6081 | 137.9321 | 136.6054 | 136.6054 | 180.4436 | 136.6054 | 136.6054 | 483.5803 | 635.9672 | 495.8347 | 145.2705 | 136.6054 | 136.6054 | 800 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 13 | 4453 | 23.7 | 23.7 | 17.2417 | 18.6992 | 15 | 42 | 42 | 500.7069 | 281.1749 | 60.5544 | 187.7857 | 0 | 0 | 86.9215 | 229.9741 | 238.3109 | 107.0484 | 0 | 0 | 435.8251 | 150.4487 | 150.4487 | 185.8132 | 244.0149 | 247.4068 | 194.0019 | 150.4487 | 150.4487 | 281.1749 | 150.4487 | 150.4487 | 272.7347 | 473.989 | 485.7177 | 301.0504 | 150.4487 | 150.4487 | 717 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 14 | 4454 | 23.9 | 23.9 | 17.2417 | 18.6992 | 15 | 42 | 42 | 28.9522 | 339.2551 | 57.2452 | 213.962 | 0 | 0 | 0 | 8.608 | 14.1016 | 11.3347 | 1.9281 | 0 | 24.7449 | 147.4357 | 147.4357 | 147.4357 | 181.7348 | 203.6246 | 192.5997 | 155.1184 | 147.4357 | 339.2551 | 147.4357 | 147.4357 | 147.4357 | 190.3428 | 217.7262 | 203.9344 | 157.0465 | 147.4357 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 15 | 4455 | 23.7 | 23.7 | 17.2417 | 18.6992 | 15 | 42 | 42 | 85.0723 | 356.8221 | 50.7791 | 234.8972 | 0 | 0 | 0 | 8.8125 | 38.1759 | 45.1764 | 25.7132 | 0 | 68.1779 | 158.1199 | 158.1199 | 158.1199 | 171.2749 | 215.1075 | 225.5576 | 196.5036 | 158.1199 | 356.8221 | 158.1199 | 158.1199 | 158.1199 | 180.0874 | 253.2835 | 270.734 | 222.2167 | 158.1199 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 16 | 4456 | 22.6 | 22.6 | 17.2417 | 18.6992 | 15 | 48 | 48 | 1.8851 | 117.6534 | 42.5708 | 251.1903 | 0 | 0 | 0 | 0 | 0.68545 | 1.1743 | 0.9752 | 0.20488 | 1.3466 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 117.6534 | 58.2111 | 58.2111 | 58.2111 | 58.2111 | 58.8966 | 59.3854 | 59.1863 | 58.416 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 17 | 4457 | 19.9 | 19.9 | 17.2417 | 18.6992 | 15 | 75 | 75 | 1.2402 | 80.2565 | 33.5764 | 264.5683 | 0 | 0 | 0 | 0 | 0.29448 | 0.81956 | 0.86455 | 0.4031 | 0.74347 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 80.2565 | 39.1096 | 39.1096 | 39.1096 | 39.1096 | 39.4041 | 39.9292 | 39.9742 | 39.5127 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 5 | 18 | 4458 | 18.6 | 18.6 | 17.2417 | 18.6992 | 15 | 85 | 85 | 1.2887 | 63.4012 | 24.3789 | 276.3875 | 0 | 0 | 0 | 0 | 0.10164 | 0.82768 | 1.0689 | 0.68395 | 0.59882 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 63.4012 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.7744 | 31.5005 | 31.7417 | 31.3567 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 19 | 4459 | 18.6 | 18.6 | 17.2417 | 18.6992 | 15 | 86 | 86 | 2.7335 | 63.1279 | 15.3801 | 287.5579 | 0.27699 | 0 | 0 | 0 | 0 | 1.5537 | 2.4743 | 1.9454 | 0.87211 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 63.1279 | 30.9783 | 30.7013 | 30.7013 | 30.7013 | 30.7013 | 32.255 | 33.1756 | 32.6467 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 20 | 4460 | 18.6 | 18.6 | 17.2417 | 18.6992 | 15 | 83 | 83 | 247.9685 | 74.2132 | 6.9187 | 298.706 | 72.1254 | 0 | 0 | 0 | 0 | 110.1844 | 227.9497 | 212.1852 | 42.7868 | 68.0934 | 41.8571 | 41.8571 | 41.8571 | 41.8571 | 81.9376 | 124.7757 | 119.0413 | 74.2132 | 140.2188 | 41.8571 | 41.8571 | 41.8571 | 41.8571 | 192.1221 | 352.7255 | 331.2265 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 21 | 4461 | 16.6 | 16.6 | 17.2417 | 18.6992 | 15 | 92 | 92 | 20.7466 | 13.2715 | -0.66722 | 310.2827 | 9.8924 | 0 | 0 | 0 | 0 | 5.7784 | 18.0643 | 19.7683 | 0.72854 | 13.0407 | 7.2742 | 7.2742 | 7.2742 | 7.2742 | 10.6426 | 17.8043 | 18.7976 | 13.2715 | 22.933 | 7.2742 | 7.2742 | 7.2742 | 7.2742 | 16.421 | 35.8686 | 38.566 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 22 | 4462 | 16.2 | 16.2 | 17.2417 | 18.6992 | 15 | 94 | 94 | 0 | 0 | -7.0131 | 322.5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 23 | 4463 | 16.4 | 16.4 | 17.2417 | 18.6992 | 15 | 94 | 94 | 0 | 0 | -11.7337 | 335.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 5 | 24 | 4464 | 15 | 15 | 17.25 | 18.1124 | 15 | 97 | 97 | 0 | 0 | -14.4722 | 349.6718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 1 | 4465 | 15.1 | 15.1 | 17.25 | 18.1124 | 15 | 97 | 97 | 0 | 0 | -14.9848 | 3.9531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 2 | 4466 | 15.3 | 15.3 | 17.25 | 18.1124 | 15 | 97 | 97 | 0 | 0 | -13.323 | 18.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 3 | 4467 | 15.2 | 15.2 | 17.25 | 18.1124 | 15 | 97 | 97 | 0 | 0 | -9.4514 | 31.6163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 4 | 4468 | 14.6 | 14.6 | 17.25 | 18.1124 | 15 | 98 | 98 | 0 | 0 | -3.7849 | 44.3213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 5 | 4469 | 14.6 | 14.6 | 17.25 | 18.1124 | 15 | 99 | 99 | 1.6252 | 3.2528 | 3.2945 | 56.2083 | 1.1602 | 1.6215 | 1.133 | 0 | 0 | 0 | 0 | 0.01921 | 4.7472 | 2.9762 | 3.3962 | 2.9515 | 1.9202 | 1.9202 | 1.9202 | 1.9202 | 1.9376 | 3.2528 | 4.1364 | 5.0177 | 4.0845 | 1.9202 | 1.9202 | 1.9202 | 1.9202 | 1.9568 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 6 | 4470 | 16.3 | 16.3 | 17.25 | 18.1124 | 15 | 95 | 95 | 44.2434 | 60.6031 | 11.409 | 67.5091 | 24.5665 | 43.3278 | 36.7084 | 8.5856 | 0 | 0 | 0 | 0 | 6.3969 | 145.4926 | 238.1526 | 205.4599 | 66.5655 | 24.1622 | 24.1622 | 24.1622 | 24.1622 | 60.6031 | 170.0591 | 281.4805 | 242.1683 | 75.1511 | 24.1622 | 24.1622 | 24.1622 | 24.1622 | 67 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 7 | 4471 | 17.3 | 17.3 | 17.25 | 18.1124 | 15 | 93 | 93 | 4.5359 | 73.6835 | 20.2096 | 78.6104 | 1.7009 | 4.1075 | 4.1081 | 1.7022 | 0 | 0 | 0 | 0 | 1.3165 | 47.5116 | 66.3899 | 66.3941 | 47.5219 | 34.1699 | 34.1699 | 34.1699 | 34.1699 | 73.6835 | 49.2125 | 70.4974 | 70.5022 | 49.2241 | 34.1699 | 34.1699 | 34.1699 | 34.1699 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 6 | 8 | 4472 | 17.6 | 17.6 | 17.25 | 18.1124 | 15 | 90 | 90 | 8.6197 | 140.2342 | 29.3627 | 90.0518 | 1.5974 | 6.7367 | 7.9298 | 4.4776 | 0 | 0 | 0 | 0 | 3.7658 | 73.6317 | 104.4199 | 111.567 | 90.8863 | 64.062 | 64.062 | 64.062 | 64.062 | 140.2342 | 75.2291 | 111.1566 | 119.4967 | 95.3639 | 64.062 | 64.062 | 64.062 | 64.062 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 9 | 4473 | 19.3 | 19.3 | 17.25 | 18.1124 | 15 | 79 | 79 | 158.9495 | 258.6774 | 38.505 | 102.5967 | 0 | 97.8668 | 138.5297 | 98.0437 | 0.12513 | 0 | 0 | 0 | 91.3226 | 119.9812 | 221.2263 | 263.2929 | 221.4094 | 120.1106 | 119.9812 | 119.9812 | 119.9812 | 258.6774 | 119.9812 | 319.0931 | 401.8226 | 319.4532 | 120.2357 | 119.9812 | 119.9812 | 119.9812 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 10 | 4474 | 19.9 | 19.9 | 17.25 | 18.1124 | 15 | 66 | 66 | 403.9236 | 255.735 | 47.1538 | 117.3795 | 0 | 169.3859 | 308.4834 | 266.8755 | 68.9356 | 0 | 0 | 0 | 280.265 | 137.6472 | 208.4335 | 266.5624 | 249.1745 | 166.4554 | 137.6472 | 137.6472 | 137.6472 | 255.735 | 137.6472 | 377.8194 | 575.0457 | 516.05 | 235.391 | 137.6472 | 137.6472 | 137.6472 | 536 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 11 | 4475 | 21 | 21 | 17.25 | 18.1124 | 15 | 55 | 55 | 478.5115 | 262.5573 | 54.5474 | 136.011 | 0 | 98.5031 | 288.9518 | 310.1364 | 149.6473 | 0 | 0 | 0 | 376.4427 | 144.5212 | 182.5092 | 255.9562 | 264.1261 | 202.2331 | 144.5212 | 144.5212 | 144.5212 | 262.5573 | 144.5212 | 281.0123 | 544.908 | 574.2626 | 351.8804 | 144.5212 | 144.5212 | 144.5212 | 639 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 12 | 4476 | 20.1 | 20.1 | 17.25 | 18.1124 | 15 | 49 | 49 | 199.1679 | 375.3695 | 59.4602 | 159.9301 | 0 | 0 | 80.2332 | 115.5053 | 83.1159 | 2.0384 | 0 | 0 | 168.6305 | 169.086 | 169.086 | 244.7963 | 278.0799 | 247.5164 | 171.0094 | 169.086 | 169.086 | 375.3695 | 169.086 | 169.086 | 325.0295 | 393.5852 | 330.6323 | 173.0478 | 169.086 | 169.086 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 13 | 4477 | 21.8 | 21.8 | 17.25 | 18.1124 | 15 | 46 | 46 | 228.8593 | 378.9821 | 60.4636 | 187.6909 | 0 | 0 | 39.9075 | 105.4561 | 109.23 | 49.0184 | 0 | 0 | 199.0179 | 161.355 | 161.355 | 202.7562 | 270.7584 | 274.6735 | 212.2081 | 161.355 | 161.355 | 378.9821 | 161.355 | 161.355 | 242.6638 | 376.2145 | 383.9035 | 261.2265 | 161.355 | 161.355 | 578 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 14 | 4478 | 21.5 | 21.5 | 17.25 | 18.1124 | 15 | 47 | 47 | 413.3592 | 311.0496 | 57.1716 | 213.8313 | 0 | 0 | 0 | 123.5118 | 201.943 | 162.0788 | 27.271 | 0 | 352.9504 | 150.9549 | 150.9549 | 150.9549 | 216.6011 | 258.2872 | 237.0994 | 165.4493 | 150.9549 | 311.0496 | 150.9549 | 150.9549 | 150.9549 | 340.1129 | 460.2302 | 399.1782 | 192.7203 | 150.9549 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 15 | 4479 | 22.4 | 22.4 | 17.25 | 18.1124 | 15 | 45 | 45 | 492.3282 | 261.865 | 50.7207 | 234.7649 | 0 | 0 | 0 | 51.6986 | 221.7113 | 261.8484 | 148.5983 | 0 | 394.135 | 141.308 | 141.308 | 141.308 | 161.4229 | 227.5715 | 243.1881 | 199.1247 | 141.308 | 261.865 | 141.308 | 141.308 | 141.308 | 213.1216 | 449.2828 | 505.0366 | 347.7231 | 141.308 | 656 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 16 | 4480 | 23.1 | 23.1 | 17.25 | 18.1124 | 15 | 47 | 47 | 18.5042 | 264.7985 | 42.5216 | 251.0689 | 0 | 0 | 0 | 0 | 6.7588 | 11.5453 | 9.5688 | 1.987 | 13.2015 | 128.3123 | 128.3123 | 128.3123 | 128.3123 | 138.2736 | 145.3282 | 142.4151 | 131.2408 | 264.7985 | 128.3123 | 128.3123 | 128.3123 | 128.3123 | 145.0324 | 156.8735 | 151.9838 | 133.2277 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 17 | 4481 | 19.9 | 19.9 | 17.25 | 18.1124 | 15 | 54 | 54 | 5.1007 | 160.9473 | 33.531 | 264.4585 | 0 | 0 | 0 | 0 | 1.2196 | 3.3769 | 3.556 | 1.6521 | 3.0527 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 160.9473 | 81.1959 | 81.1959 | 81.1959 | 81.1959 | 82.4155 | 84.5728 | 84.7519 | 82.8479 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 6 | 18 | 4482 | 17.9 | 17.9 | 17.25 | 18.1124 | 15 | 77 | 77 | 5.9409 | 133.246 | 24.3334 | 276.2872 | 0 | 0 | 0 | 0 | 0.47822 | 3.8236 | 4.9291 | 3.1472 | 2.754 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 133.246 | 66.8988 | 66.8988 | 66.8988 | 66.8988 | 67.377 | 70.7223 | 71.8279 | 70.046 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 19 | 4483 | 17 | 17 | 17.25 | 18.1124 | 15 | 85 | 85 | 2.1084 | 55.3298 | 15.3314 | 287.4648 | 0.21038 | 0 | 0 | 0 | 0 | 1.2015 | 1.9096 | 1.499 | 0.67018 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 55.3298 | 26.9691 | 26.7587 | 26.7587 | 26.7587 | 26.7587 | 27.9602 | 28.6683 | 28.2577 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 20 | 4484 | 17.9 | 17.9 | 17.25 | 18.1124 | 15 | 74 | 74 | 27.1142 | 67.3565 | 6.8644 | 298.6189 | 7.8479 | 0 | 0 | 0 | 0 | 12.0886 | 24.9438 | 23.1873 | 4.6435 | 41.077 | 33.6797 | 33.6797 | 33.6797 | 33.6797 | 45.0743 | 57.1915 | 55.5358 | 67.3565 | 48.9249 | 33.6797 | 33.6797 | 33.6797 | 33.6797 | 57.1629 | 82.1353 | 78.723 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 21 | 4485 | 17.9 | 17.9 | 17.25 | 18.1124 | 15 | 66 | 66 | 66.7756 | 14.7476 | -0.72917 | 310.2015 | 31.755 | 0 | 0 | 0 | 0 | 18.6974 | 58.1971 | 63.6057 | 2.2524 | 28.683 | 8.4634 | 8.4634 | 8.4634 | 8.4634 | 20.3687 | 45.5197 | 48.9636 | 14.7476 | 60.438 | 8.4634 | 8.4634 | 8.4634 | 8.4634 | 39.0661 | 103.7168 | 112.5693 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 22 | 4486 | 15.8 | 15.8 | 17.25 | 18.1124 | 15 | 81 | 81 | 0 | 0 | -7.084 | 322.5188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 23 | 4487 | 14.4 | 14.4 | 17.25 | 18.1124 | 15 | 91 | 91 | 0 | 0 | -11.8142 | 335.6971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 6 | 24 | 4488 | 14.6 | 14.6 | 17.9375 | 18.1378 | 15 | 91 | 91 | 0 | 0 | -14.5615 | 349.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 1 | 4489 | 14.8 | 14.8 | 17.9375 | 18.1378 | 15 | 89 | 89 | 0 | 0 | -15.0811 | 3.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 2 | 4490 | 14 | 14 | 17.9375 | 18.1378 | 15 | 90 | 90 | 0 | 0 | -13.4298 | 18.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 3 | 4491 | 13.9 | 13.9 | 17.9375 | 18.1378 | 15 | 89 | 89 | 0 | 0 | -9.5593 | 31.6168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 4 | 4492 | 13.9 | 13.9 | 17.9375 | 18.1378 | 15 | 88 | 88 | 0 | 0 | -3.8918 | 44.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 5 | 4493 | 13.9 | 13.9 | 17.9375 | 18.1378 | 15 | 88 | 88 | 1.4927 | 3.3785 | 3.1896 | 56.2333 | 1.0652 | 1.4892 | 1.0408 | 0 | 0 | 0 | 0 | 0.017273 | 2.6215 | 2.8599 | 3.2963 | 2.8347 | 1.7633 | 1.7633 | 1.7633 | 1.7633 | 1.7811 | 3.3785 | 3.9251 | 4.7854 | 3.8755 | 1.7633 | 1.7633 | 1.7633 | 1.7633 | 1.7984 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 6 | 4494 | 14.9 | 14.9 | 17.9375 | 18.1378 | 15 | 86 | 86 | 14.3873 | 50.94 | 11.3063 | 67.5427 | 7.9842 | 14.0898 | 11.9417 | 2.7984 | 0 | 0 | 0 | 0 | 2.06 | 155.8309 | 261.2178 | 224.1405 | 66.3184 | 18.0161 | 18.0161 | 18.0161 | 18.0161 | 50.94 | 163.8151 | 275.3076 | 236.0822 | 69.1167 | 18.0161 | 18.0161 | 18.0161 | 18.0161 | 53 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 7 | 4495 | 15.2 | 15.2 | 17.9375 | 18.1378 | 15 | 82 | 82 | 5.3379 | 79.4576 | 20.1086 | 78.6508 | 1.9995 | 4.8344 | 4.8374 | 2.0067 | 0 | 0 | 0 | 0 | 1.5424 | 54.6478 | 80.8594 | 80.8871 | 54.7145 | 36.1606 | 36.1606 | 36.1606 | 36.1606 | 79.4576 | 56.6473 | 85.6938 | 85.7244 | 56.7212 | 36.1606 | 36.1606 | 36.1606 | 36.1606 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 7 | 8 | 4496 | 15.5 | 15.5 | 17.9375 | 18.1378 | 15 | 80 | 80 | 4.1737 | 106.1816 | 29.2624 | 90.0972 | 0.77126 | 3.2625 | 3.8426 | 2.1718 | 0 | 0 | 0 | 0 | 1.8184 | 53.9499 | 62.82 | 64.8855 | 58.9364 | 51.2038 | 51.2038 | 51.2038 | 51.2038 | 106.1816 | 54.7212 | 66.0825 | 68.7281 | 61.1082 | 51.2038 | 51.2038 | 51.2038 | 51.2038 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 9 | 4497 | 16.8 | 16.8 | 17.9375 | 18.1378 | 15 | 77 | 77 | 13.9814 | 202.9823 | 38.4039 | 102.6446 | 0 | 8.6101 | 12.1972 | 8.6394 | 0.020692 | 0 | 0 | 0 | 8.0177 | 92.9162 | 127.8778 | 142.4434 | 127.9966 | 93.0002 | 92.9162 | 92.9162 | 92.9162 | 202.9823 | 92.9162 | 136.4879 | 154.6406 | 136.636 | 93.0209 | 92.9162 | 92.9162 | 92.9162 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 10 | 4498 | 18.3 | 18.3 | 17.9375 | 18.1378 | 15 | 69 | 69 | 193.2962 | 308.0731 | 47.0501 | 117.4233 | 0 | 81.0659 | 147.803 | 127.9592 | 33.1586 | 0 | 0 | 0 | 133.9269 | 143.3124 | 214.9466 | 273.9192 | 256.3842 | 172.6131 | 143.3124 | 143.3124 | 143.3124 | 308.0731 | 143.3124 | 296.0125 | 421.7223 | 384.3434 | 205.7718 | 143.3124 | 143.3124 | 143.3124 | 442 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 11 | 4499 | 18.2 | 18.2 | 17.9375 | 18.1378 | 15 | 57 | 57 | 138.7458 | 354.9785 | 54.4404 | 136.0348 | 0 | 28.548 | 83.9124 | 90.1221 | 43.5394 | 0 | 0 | 0 | 109.0215 | 156.9778 | 194.9276 | 268.5252 | 276.7799 | 214.8561 | 156.9778 | 156.9778 | 156.9778 | 354.9785 | 156.9778 | 223.4757 | 352.4377 | 366.9019 | 258.3955 | 156.9778 | 156.9778 | 156.9778 | 464 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 12 | 4500 | 18.5 | 18.5 | 17.9375 | 18.1378 | 15 | 60 | 60 | 70.3909 | 371.4642 | 59.3531 | 159.9043 | 0 | 0 | 28.4185 | 40.9291 | 29.464 | 0.73926 | 0 | 0 | 59.5358 | 162.2437 | 162.2437 | 218.126 | 242.7268 | 220.1818 | 163.6974 | 162.2437 | 162.2437 | 371.4642 | 162.2437 | 162.2437 | 246.5445 | 283.656 | 249.6458 | 164.4366 | 162.2437 | 162.2437 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 13 | 4501 | 15.9 | 15.9 | 17.9375 | 18.1378 | 15 | 82 | 82 | 8.5779 | 278.5481 | 60.3661 | 187.5976 | 0 | 0 | 1.5024 | 3.9659 | 4.1063 | 1.8413 | 0 | 0 | 7.4519 | 136.3923 | 136.3923 | 140.1173 | 146.2256 | 146.5737 | 140.9577 | 136.3923 | 136.3923 | 278.5481 | 136.3923 | 136.3923 | 141.6197 | 150.1916 | 150.6801 | 142.799 | 136.3923 | 136.3923 | 286 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 14 | 4502 | 17.3 | 17.3 | 17.9375 | 18.1378 | 15 | 68 | 68 | 50.5159 | 362.9111 | 57.0913 | 213.6986 | 0 | 0 | 0 | 15.1718 | 24.7586 | 19.8422 | 3.3025 | 0 | 43.0889 | 157.6095 | 157.6095 | 157.6095 | 196.0387 | 220.3215 | 207.8684 | 165.9744 | 157.6095 | 362.9111 | 157.6095 | 157.6095 | 157.6095 | 211.2105 | 245.0801 | 227.7106 | 169.2769 | 157.6095 | 406 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 15 | 4503 | 16.8 | 16.8 | 17.9375 | 18.1378 | 15 | 82 | 82 | 7.9472 | 251.6451 | 50.6559 | 234.6288 | 0 | 0 | 0 | 0.84615 | 3.5922 | 4.234 | 2.3956 | 0 | 6.3549 | 124.6756 | 124.6756 | 124.6756 | 126.1366 | 130.8784 | 131.9866 | 128.8121 | 124.6756 | 251.6451 | 124.6756 | 124.6756 | 124.6756 | 126.9828 | 134.4706 | 136.2206 | 131.2077 | 124.6756 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 16 | 4504 | 17.9 | 17.9 | 17.9375 | 18.1378 | 15 | 74 | 74 | 210.602 | 313.9575 | 42.4664 | 250.9433 | 0 | 0 | 0 | 0 | 77.289 | 131.6357 | 108.8721 | 22.3326 | 150.0425 | 140.5897 | 140.5897 | 140.5897 | 140.5897 | 213.858 | 265.3776 | 243.7981 | 161.7605 | 313.9575 | 140.5897 | 140.5897 | 140.5897 | 140.5897 | 291.147 | 397.0133 | 352.6702 | 184.0931 | 464 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 17 | 4505 | 15.8 | 15.8 | 17.9375 | 18.1378 | 15 | 87 | 87 | 5.3077 | 163.8291 | 33.4799 | 264.3447 | 0 | 0 | 0 | 0 | 1.2784 | 3.5208 | 3.7008 | 1.7129 | 3.1709 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 163.8291 | 82.7533 | 82.7533 | 82.7533 | 82.7533 | 84.0317 | 86.2741 | 86.4541 | 84.4662 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 18 | 4506 | 16.5 | 16.5 | 17.9375 | 18.1378 | 15 | 78 | 78 | 190.6146 | 205.8592 | 24.2821 | 276.183 | 0 | 0 | 0 | 0 | 15.6673 | 122.9526 | 158.214 | 100.7957 | 88.1408 | 102.0038 | 102.0038 | 102.0038 | 102.0038 | 110.9829 | 172.4695 | 192.6782 | 159.7711 | 205.8592 | 102.0038 | 102.0038 | 102.0038 | 102.0038 | 126.6502 | 295.4221 | 350.8922 | 260.5668 | 294 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 19 | 4507 | 15.1 | 15.1 | 17.9375 | 18.1378 | 15 | 91 | 91 | 3.0423 | 66.0369 | 15.2769 | 287.3683 | 0.29868 | 0 | 0 | 0 | 0 | 1.7383 | 2.757 | 2.1607 | 0.96313 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 66.0369 | 32.4859 | 32.1872 | 32.1872 | 32.1872 | 32.1872 | 33.9255 | 34.9442 | 34.3479 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 20 | 4508 | 15.2 | 15.2 | 17.9375 | 18.1378 | 15 | 88 | 88 | 7.073 | 51.7985 | 6.804 | 298.5289 | 2.0368 | 0 | 0 | 0 | 0 | 3.1644 | 6.512 | 6.0449 | 1.2015 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 51.7985 | 27.4184 | 25.3816 | 25.3816 | 25.3816 | 25.3816 | 28.5461 | 31.8936 | 31.4265 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 21 | 4509 | 15.6 | 15.6 | 17.9375 | 18.1378 | 15 | 83 | 83 | 31.8904 | 12.9716 | -0.79738 | 310.118 | 15.1236 | 0 | 0 | 0 | 0 | 8.9783 | 27.8208 | 30.3663 | 1.0284 | 22.4248 | 7.2935 | 7.2935 | 7.2935 | 7.2935 | 16.2763 | 35.1284 | 37.6752 | 12.9716 | 37.5484 | 7.2935 | 7.2935 | 7.2935 | 7.2935 | 25.2546 | 62.9492 | 68.0415 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 22 | 4510 | 15.6 | 15.6 | 17.9375 | 18.1378 | 15 | 82 | 82 | 0 | 0 | -7.1615 | 322.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 23 | 4511 | 15.8 | 15.8 | 17.9375 | 18.1378 | 15 | 79 | 79 | 0 | 0 | -11.9013 | 335.6322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 7 | 24 | 4512 | 15.5 | 15.5 | 15.8708 | 17.6442 | 15 | 82 | 82 | 0 | 0 | -14.6575 | 349.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 1 | 4513 | 14.1 | 14.1 | 15.8708 | 17.6442 | 15 | 94 | 94 | 0 | 0 | -15.1839 | 3.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 2 | 4514 | 14.2 | 14.2 | 15.8708 | 17.6442 | 15 | 94 | 94 | 0 | 0 | -13.5427 | 18.0405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 3 | 4515 | 14.2 | 14.2 | 15.8708 | 17.6442 | 15 | 95 | 95 | 0 | 0 | -9.6729 | 31.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 4 | 4516 | 14 | 14 | 15.8708 | 17.6442 | 15 | 96 | 96 | 0 | 0 | -4.004 | 44.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 5 | 4517 | 13.9 | 13.9 | 15.8708 | 17.6442 | 15 | 96 | 96 | 0 | 0 | 3.0799 | 56.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 6 | 4518 | 14.2 | 14.2 | 15.8708 | 17.6442 | 15 | 96 | 96 | 2.1145 | 24.7004 | 11.1992 | 67.5813 | 1.1726 | 2.0708 | 1.7558 | 0.41239 | 0 | 0 | 0 | 0 | 0.2996 | 28.2375 | 41.2288 | 36.6736 | 17.2402 | 11.275 | 11.275 | 11.275 | 11.275 | 24.7004 | 29.4101 | 43.2996 | 38.4295 | 17.6526 | 11.275 | 11.275 | 11.275 | 11.275 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 7 | 4519 | 14.7 | 14.7 | 15.8708 | 17.6442 | 15 | 95 | 95 | 8.3442 | 91.6005 | 20.0034 | 78.6966 | 3.1216 | 7.5577 | 7.5666 | 3.1431 | 0 | 0 | 0 | 0 | 2.3995 | 70.9937 | 114.8709 | 114.9589 | 71.2061 | 40.118 | 40.118 | 40.118 | 40.118 | 91.6005 | 74.1153 | 122.4287 | 122.5256 | 74.3492 | 40.118 | 40.118 | 40.118 | 40.118 | 94 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 8 | 8 | 4520 | 15.6 | 15.6 | 15.8708 | 17.6442 | 15 | 88 | 88 | 4.0437 | 104.2433 | 29.1579 | 90.1486 | 0.74477 | 3.1614 | 3.7261 | 2.1081 | 0 | 0 | 0 | 0 | 1.7567 | 52.8912 | 61.0373 | 62.9408 | 57.4868 | 50.3807 | 50.3807 | 50.3807 | 50.3807 | 104.2433 | 53.636 | 64.1986 | 66.6669 | 59.5949 | 50.3807 | 50.3807 | 50.3807 | 50.3807 | 106 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 9 | 4521 | 16.6 | 16.6 | 15.8708 | 17.6442 | 15 | 82 | 82 | 18.0858 | 211.6496 | 38.2985 | 102.6989 | 0 | 11.139 | 15.7939 | 11.197 | 0.040951 | 0 | 0 | 0 | 10.3504 | 95.9736 | 136.7235 | 153.7525 | 136.9354 | 96.1235 | 95.9736 | 95.9736 | 95.9736 | 211.6496 | 95.9736 | 147.8625 | 169.5464 | 148.1323 | 96.1644 | 95.9736 | 95.9736 | 95.9736 | 222 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 10 | 4522 | 16.8 | 16.8 | 15.8708 | 17.6442 | 15 | 80 | 80 | 5.5079 | 193.1897 | 46.9418 | 117.474 | 0 | 2.3098 | 4.2168 | 3.6536 | 0.95021 | 0 | 0 | 0 | 3.8103 | 93.9762 | 100.9547 | 106.7161 | 105.0147 | 96.847 | 93.9762 | 93.9762 | 93.9762 | 193.1897 | 93.9762 | 103.2646 | 110.9329 | 108.6683 | 97.7972 | 93.9762 | 93.9762 | 93.9762 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 11 | 4523 | 14.8 | 14.8 | 15.8708 | 17.6442 | 15 | 91 | 91 | 3.8154 | 183.0058 | 54.3281 | 136.0654 | 0 | 0.78445 | 2.3112 | 2.484 | 1.2018 | 0 | 0 | 0 | 2.9942 | 92.4559 | 92.6787 | 93.1123 | 93.1614 | 92.7972 | 92.4559 | 92.4559 | 92.4559 | 183.0058 | 92.4559 | 93.4631 | 95.4235 | 95.6454 | 93.999 | 92.4559 | 92.4559 | 92.4559 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 12 | 4524 | 16.6 | 16.6 | 15.8708 | 17.6442 | 15 | 83 | 83 | 54.237 | 362.1784 | 59.2399 | 159.8839 | 0 | 0 | 21.9446 | 31.6224 | 22.7763 | 0.58807 | 0 | 0 | 45.8216 | 157.7104 | 157.7104 | 211.5635 | 235.3133 | 213.6044 | 159.1535 | 157.7104 | 157.7104 | 362.1784 | 157.7104 | 157.7104 | 233.5081 | 266.9357 | 236.3806 | 159.7416 | 157.7104 | 157.7104 | 408 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 13 | 4525 | 15.9 | 15.9 | 15.8708 | 17.6442 | 15 | 85 | 85 | 17.918 | 320.4506 | 60.2618 | 187.5061 | 0 | 0 | 3.1517 | 8.3133 | 8.605 | 3.8561 | 0 | 0 | 15.5494 | 153.297 | 153.297 | 160.2412 | 171.6136 | 172.2564 | 161.793 | 153.297 | 153.297 | 320.4506 | 153.297 | 153.297 | 163.3929 | 179.9269 | 180.8614 | 165.6491 | 153.297 | 153.297 | 336 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 14 | 4526 | 17.6 | 17.6 | 15.8708 | 17.6442 | 15 | 74 | 74 | 357.3967 | 331.4858 | 57.0044 | 213.564 | 0 | 0 | 0 | 107.9074 | 175.7628 | 140.6588 | 23.1587 | 0 | 304.5142 | 156.6341 | 156.6341 | 156.6341 | 221.365 | 262.0698 | 241.0118 | 170.5264 | 156.6341 | 331.4858 | 156.6341 | 156.6341 | 156.6341 | 329.2724 | 437.8326 | 381.6705 | 193.6851 | 156.6341 | 636 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 15 | 4527 | 17.2 | 17.2 | 15.8708 | 17.6442 | 15 | 63 | 63 | 67.1318 | 349.3851 | 50.5848 | 234.489 | 0 | 0 | 0 | 7.2485 | 30.4629 | 35.8325 | 20.2119 | 0 | 53.6149 | 154.0778 | 154.0778 | 154.0778 | 167.3695 | 209.9376 | 219.7838 | 191.1404 | 154.0778 | 349.3851 | 154.0778 | 154.0778 | 154.0778 | 174.618 | 240.4005 | 255.6164 | 211.3523 | 154.0778 | 403 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 16 | 4528 | 13 | 13 | 15.8708 | 17.6442 | 15 | 81 | 81 | 3.4788 | 158.5252 | 42.4052 | 250.8135 | 0 | 0 | 0 | 0 | 1.283 | 2.1786 | 1.798 | 0.36414 | 2.4748 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 158.5252 | 79.6367 | 79.6367 | 79.6367 | 79.6367 | 80.9197 | 81.8153 | 81.4347 | 80.0008 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 17 | 4529 | 14.5 | 14.5 | 15.8708 | 17.6442 | 15 | 82 | 82 | 2.9849 | 123.2202 | 33.4229 | 264.2268 | 0 | 0 | 0 | 0 | 0.72433 | 1.9841 | 2.0816 | 0.95972 | 1.7798 | 61.175 | 61.175 | 61.175 | 61.175 | 61.175 | 61.175 | 61.175 | 61.175 | 123.2202 | 61.175 | 61.175 | 61.175 | 61.175 | 61.8993 | 63.1591 | 63.2566 | 62.1347 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 18 | 4530 | 16.4 | 16.4 | 15.8708 | 17.6442 | 15 | 70 | 70 | 127.1028 | 208.3853 | 24.2251 | 276.0752 | 0 | 0 | 0 | 0 | 10.6711 | 82.1775 | 105.5455 | 67.0863 | 58.6147 | 100.0036 | 100.0036 | 100.0036 | 100.0036 | 109.3332 | 171.8499 | 192.2801 | 158.656 | 208.3853 | 100.0036 | 100.0036 | 100.0036 | 100.0036 | 120.0042 | 254.0275 | 297.8256 | 225.7423 | 267 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 19 | 4531 | 15.9 | 15.9 | 15.8708 | 17.6442 | 15 | 73 | 73 | 34.4842 | 128.1296 | 15.2165 | 287.2685 | 3.3282 | 0 | 0 | 0 | 0 | 19.7585 | 31.271 | 24.4653 | 10.8704 | 66.4353 | 61.8759 | 61.8759 | 61.8759 | 61.8759 | 88.9435 | 104.7147 | 95.3915 | 128.1296 | 69.7635 | 61.8759 | 61.8759 | 61.8759 | 61.8759 | 108.7021 | 135.9857 | 119.8568 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 20 | 4532 | 15 | 15 | 15.8708 | 17.6442 | 15 | 73 | 73 | 4.2246 | 41.2885 | 6.7376 | 298.436 | 1.2101 | 0 | 0 | 0 | 0 | 1.8969 | 3.8928 | 3.6083 | 0.71145 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 41.2885 | 21.1979 | 19.9878 | 19.9878 | 19.9878 | 19.9878 | 21.8847 | 23.8805 | 23.5961 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 21 | 4533 | 12.3 | 12.3 | 15.8708 | 17.6442 | 15 | 91 | 91 | 4.6218 | 7.8583 | -0.87184 | 310.0321 | 2.1856 | 0 | 0 | 0 | 0 | 1.3085 | 4.0361 | 4.3994 | 0.14174 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 7.8583 | 6.4019 | 4.2163 | 4.2163 | 4.2163 | 4.2163 | 5.5248 | 8.2524 | 8.6157 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 22 | 4534 | 12.3 | 12.3 | 15.8708 | 17.6442 | 15 | 94 | 94 | 0 | 0 | -7.2454 | 322.3659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 23 | 4535 | 13.6 | 13.6 | 15.8708 | 17.6442 | 15 | 93 | 93 | 0 | 0 | -11.9951 | 335.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 8 | 24 | 4536 | 11.7 | 11.7 | 14.7958 | 16.7387 | 15 | 92 | 92 | 0 | 0 | -14.7602 | 349.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 1 | 4537 | 11.8 | 11.8 | 14.7958 | 16.7387 | 15 | 91 | 91 | 0 | 0 | -15.2932 | 3.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 2 | 4538 | 10.7 | 10.7 | 14.7958 | 16.7387 | 15 | 96 | 96 | 0 | 0 | -13.6618 | 18.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 3 | 4539 | 12.2 | 12.2 | 14.7958 | 16.7387 | 15 | 97 | 97 | 0 | 0 | -9.7922 | 31.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 4 | 4540 | 12.6 | 12.6 | 14.7958 | 16.7387 | 15 | 97 | 97 | 0 | 0 | -4.1214 | 44.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 5 | 4541 | 12.8 | 12.8 | 14.7958 | 16.7387 | 15 | 97 | 97 | 2.0276 | 0.99 | 2.9654 | 56.2973 | 1.4455 | 2.0222 | 1.4144 | 0 | 0 | 0 | 0 | 0.022019 | 5.01 | 1.5775 | 1.8527 | 1.5627 | 0.88778 | 0.88778 | 0.88778 | 0.88778 | 0.89828 | 0.99 | 3.023 | 3.875 | 2.977 | 0.88778 | 0.88778 | 0.88778 | 0.88778 | 0.9203 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 6 | 4542 | 14.3 | 14.3 | 14.7958 | 16.7387 | 15 | 96 | 96 | 140.6592 | 63.2928 | 11.0876 | 67.625 | 77.945 | 137.7491 | 116.8617 | 27.5182 | 0 | 0 | 0 | 0 | 19.7072 | 150.6874 | 246.7028 | 213.1681 | 69.7274 | 25.5469 | 25.5469 | 25.5469 | 25.5469 | 63.2928 | 228.6324 | 384.4519 | 330.0297 | 97.2456 | 25.5469 | 25.5469 | 25.5469 | 25.5469 | 83 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 7 | 4543 | 15.5 | 15.5 | 14.7958 | 16.7387 | 15 | 90 | 90 | 161.6681 | 128.7466 | 19.894 | 78.7478 | 60.3929 | 146.4411 | 146.7061 | 61.0326 | 0 | 0 | 0 | 0 | 46.2534 | 125.4066 | 218.8143 | 219.1019 | 126.101 | 59.8484 | 59.8484 | 59.8484 | 59.8484 | 128.7466 | 185.7995 | 365.2554 | 365.808 | 187.1336 | 59.8484 | 59.8484 | 59.8484 | 59.8484 | 175 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 9 | 8 | 4544 | 16.5 | 16.5 | 14.7958 | 16.7387 | 15 | 80 | 80 | 483.7481 | 143.4967 | 29.0494 | 90.2058 | 88.7595 | 378.2282 | 446.136 | 252.7034 | 0 | 0 | 0 | 0 | 209.5033 | 109.7342 | 180.2969 | 196.8506 | 149.6982 | 88.0976 | 88.0976 | 88.0976 | 88.0976 | 143.4967 | 198.4936 | 558.5252 | 642.9866 | 402.4016 | 88.0976 | 88.0976 | 88.0976 | 88.0976 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 9 | 4545 | 16.8 | 16.8 | 14.7958 | 16.7387 | 15 | 71 | 71 | 320.8488 | 230.7745 | 38.1889 | 102.7596 | 0 | 197.62 | 280.4846 | 199.0451 | 1.0077 | 0 | 0 | 0 | 183.2255 | 120.1568 | 216.9644 | 257.5571 | 217.6625 | 120.6504 | 120.1568 | 120.1568 | 120.1568 | 230.7745 | 120.1568 | 414.5845 | 538.0417 | 416.7076 | 121.6581 | 120.1568 | 120.1568 | 120.1568 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 10 | 4546 | 17.5 | 17.5 | 14.7958 | 16.7387 | 15 | 69 | 69 | 102.0867 | 310.4927 | 46.829 | 117.5316 | 0 | 42.8047 | 78.2564 | 67.8665 | 17.7213 | 0 | 0 | 0 | 70.5073 | 139.7344 | 196.5382 | 243.5841 | 229.7963 | 163.2514 | 139.7344 | 139.7344 | 139.7344 | 310.4927 | 139.7344 | 239.3429 | 321.8405 | 297.6628 | 180.9728 | 139.7344 | 139.7344 | 139.7344 | 381 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 11 | 4547 | 18.1 | 18.1 | 14.7958 | 16.7387 | 15 | 65 | 65 | 140.2885 | 354.054 | 54.2107 | 136.1029 | 0 | 28.812 | 85.1129 | 91.5558 | 44.3666 | 0 | 0 | 0 | 109.946 | 156.7725 | 194.6017 | 268.5231 | 276.9825 | 215.0245 | 156.7725 | 156.7725 | 156.7725 | 354.054 | 156.7725 | 223.4137 | 353.636 | 368.5384 | 259.3911 | 156.7725 | 156.7725 | 156.7725 | 464 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 12 | 4548 | 18.2 | 18.2 | 14.7958 | 16.7387 | 15 | 62 | 62 | 150.9123 | 380.6556 | 59.1207 | 159.869 | 0 | 0 | 61.1927 | 88.2382 | 63.595 | 1.6987 | 0 | 0 | 127.3444 | 166.6617 | 166.6617 | 244.3687 | 278.713 | 247.4192 | 168.8188 | 166.6617 | 166.6617 | 380.6556 | 166.6617 | 166.6617 | 305.5614 | 366.9512 | 311.0142 | 170.5174 | 166.6617 | 166.6617 | 508 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 13 | 4549 | 18.6 | 18.6 | 14.7958 | 16.7387 | 15 | 62 | 62 | 118.3847 | 391.3823 | 60.1509 | 187.4166 | 0 | 0 | 20.9112 | 55.1247 | 57.0469 | 25.5518 | 0 | 0 | 102.6177 | 166.8001 | 166.8001 | 201.1986 | 257.4789 | 260.6408 | 208.8321 | 166.8001 | 166.8001 | 391.3823 | 166.8001 | 166.8001 | 222.1098 | 312.6036 | 317.6877 | 234.3839 | 166.8001 | 166.8001 | 494 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 14 | 4550 | 18.6 | 18.6 | 14.7958 | 16.7387 | 15 | 57 | 57 | 38.2007 | 350.49 | 56.9108 | 213.4278 | 0 | 0 | 0 | 11.5964 | 18.8541 | 15.0673 | 2.4543 | 0 | 32.51 | 152.2272 | 152.2272 | 152.2272 | 189.0899 | 212.1606 | 200.1231 | 160.0288 | 152.2272 | 350.49 | 152.2272 | 152.2272 | 152.2272 | 200.6863 | 231.0147 | 215.1904 | 162.4831 | 152.2272 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 15 | 4551 | 17.7 | 17.7 | 14.7958 | 16.7387 | 15 | 69 | 69 | 23.1329 | 306.549 | 50.5074 | 234.3457 | 0 | 0 | 0 | 2.5335 | 10.5402 | 12.3726 | 6.9573 | 0 | 18.451 | 147.397 | 147.397 | 147.397 | 151.3977 | 164.0412 | 166.9348 | 158.3834 | 147.397 | 306.549 | 147.397 | 147.397 | 147.397 | 153.9312 | 174.5814 | 179.3073 | 165.3407 | 147.397 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 16 | 4552 | 16.2 | 16.2 | 14.7958 | 16.7387 | 15 | 80 | 80 | 2.2056 | 126.4334 | 42.3379 | 250.6798 | 0 | 0 | 0 | 0 | 0.81764 | 1.3841 | 1.1398 | 0.22779 | 1.5666 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 126.4334 | 62.7607 | 62.7607 | 62.7607 | 62.7607 | 63.5783 | 64.1448 | 63.9005 | 62.9885 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 17 | 4553 | 15.6 | 15.6 | 14.7958 | 16.7387 | 15 | 86 | 86 | 4.788 | 155.1508 | 33.3601 | 264.105 | 0 | 0 | 0 | 0 | 1.1709 | 3.1896 | 3.3399 | 1.5337 | 2.8492 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 155.1508 | 78.0882 | 78.0882 | 78.0882 | 78.0882 | 79.2591 | 81.2778 | 81.4281 | 79.6219 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 9 | 18 | 4554 | 15.1 | 15.1 | 14.7958 | 16.7387 | 15 | 92 | 92 | 2.3755 | 84.9076 | 24.1623 | 275.9637 | 0 | 0 | 0 | 0 | 0.20378 | 1.5396 | 1.9736 | 1.2515 | 1.0924 | 41.558 | 41.558 | 41.558 | 41.558 | 41.558 | 41.558 | 41.558 | 41.558 | 84.9076 | 41.558 | 41.558 | 41.558 | 41.558 | 41.7618 | 43.0977 | 43.5316 | 42.8095 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 19 | 4555 | 14.8 | 14.8 | 14.7958 | 16.7387 | 15 | 93 | 93 | 2.5666 | 60.1946 | 15.1502 | 287.1655 | 0.2433 | 0 | 0 | 0 | 0 | 1.4749 | 2.3291 | 1.8189 | 0.80537 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 60.1946 | 29.4628 | 29.2195 | 29.2195 | 29.2195 | 29.2195 | 30.6944 | 31.5486 | 31.0385 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 20 | 4556 | 14.7 | 14.7 | 14.7958 | 16.7387 | 15 | 96 | 96 | 1.9128 | 27.6809 | 6.6652 | 298.3402 | 0.5449 | 0 | 0 | 0 | 0 | 0.86207 | 1.7641 | 1.6327 | 0.31914 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 27.6809 | 13.7372 | 13.1923 | 13.1923 | 13.1923 | 13.1923 | 14.0544 | 14.9564 | 14.825 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 21 | 4557 | 14.7 | 14.7 | 14.7958 | 16.7387 | 15 | 95 | 95 | 2.9087 | 5.9157 | -0.95255 | 309.9439 | 1.3714 | 0 | 0 | 0 | 0 | 0.82824 | 2.5427 | 2.7677 | 0.08433 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 5.9157 | 4.5416 | 3.1701 | 3.1701 | 3.1701 | 3.1701 | 3.9984 | 5.7129 | 5.9379 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 22 | 4558 | 14.8 | 14.8 | 14.7958 | 16.7387 | 15 | 97 | 97 | 0 | 0 | -7.3357 | 322.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 23 | 4559 | 15.4 | 15.4 | 14.7958 | 16.7387 | 15 | 97 | 97 | 0 | 0 | -12.0954 | 335.5001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 9 | 24 | 4560 | 16 | 16 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | -14.8695 | 349.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 1 | 4561 | 16 | 16 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | -15.409 | 3.8211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 2 | 4562 | 16.2 | 16.2 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | -13.7869 | 18.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 3 | 4563 | 16.3 | 16.3 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | -9.9171 | 31.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 4 | 4564 | 16.2 | 16.2 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | -4.2439 | 44.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 5 | 4565 | 16.1 | 16.1 | 15.3833 | 16.1652 | 15 | 97 | 97 | 0 | 0 | 2.8462 | 56.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 6 | 4566 | 16.5 | 16.5 | 15.3833 | 16.1652 | 15 | 96 | 96 | 2.2149 | 24.6934 | 10.9717 | 67.6738 | 1.2262 | 2.169 | 1.8412 | 0.43483 | 0 | 0 | 0 | 0 | 0.30661 | 30.8042 | 45.933 | 40.6726 | 18.1044 | 11.1264 | 11.1264 | 11.1264 | 11.1264 | 24.6934 | 32.0304 | 48.102 | 42.5137 | 18.5392 | 11.1264 | 11.1264 | 11.1264 | 11.1264 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 7 | 4567 | 17.2 | 17.2 | 15.3833 | 16.1652 | 15 | 93 | 93 | 5.5028 | 79.4342 | 19.7806 | 78.8046 | 2.0522 | 4.9847 | 4.9972 | 2.0825 | 0 | 0 | 0 | 0 | 1.5658 | 56.2932 | 85.4364 | 85.5611 | 56.594 | 35.8985 | 35.8985 | 35.8985 | 35.8985 | 79.4342 | 58.3453 | 90.4211 | 90.5583 | 58.6765 | 35.8985 | 35.8985 | 35.8985 | 35.8985 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 10 | 8 | 4568 | 17 | 17 | 15.3833 | 16.1652 | 15 | 96 | 96 | 1.3562 | 60.4146 | 28.9369 | 90.269 | 0.24777 | 1.0604 | 1.2519 | 0.70999 | 0 | 0 | 0 | 0 | 0.5854 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 60.4146 | 29.7184 | 30.531 | 30.7225 | 30.1806 | 29.4706 | 29.4706 | 29.4706 | 29.4706 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 9 | 4569 | 17.1 | 17.1 | 15.3833 | 16.1652 | 15 | 95 | 95 | 1.5472 | 85.1185 | 38.0752 | 102.8267 | 0 | 0.95294 | 1.354 | 0.96193 | 0.0063578 | 0 | 0 | 0 | 0.88154 | 41.7619 | 41.7619 | 41.7619 | 41.7619 | 41.7619 | 41.7619 | 41.7619 | 41.7619 | 85.1185 | 41.7619 | 42.7148 | 43.1159 | 42.7238 | 41.7682 | 41.7619 | 41.7619 | 41.7619 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 10 | 4570 | 17 | 17 | 15.3833 | 16.1652 | 15 | 96 | 96 | 1.0566 | 85.2715 | 46.7117 | 117.596 | 0 | 0.4429 | 0.81101 | 0.70404 | 0.18465 | 0 | 0 | 0 | 0.72849 | 41.6466 | 41.6466 | 41.6466 | 41.6466 | 41.6466 | 41.6466 | 41.6466 | 41.6466 | 85.2715 | 41.6466 | 42.0895 | 42.4576 | 42.3506 | 41.8312 | 41.6466 | 41.6466 | 41.6466 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 11 | 4571 | 17.3 | 17.3 | 15.3833 | 16.1652 | 15 | 96 | 96 | 1.0433 | 96.1835 | 54.088 | 136.1472 | 0 | 0.21397 | 0.63398 | 0.68261 | 0.33138 | 0 | 0 | 0 | 0.81648 | 47.1718 | 47.1718 | 47.1718 | 47.1718 | 47.1718 | 47.1718 | 47.1718 | 47.1718 | 96.1835 | 47.1718 | 47.3857 | 47.8057 | 47.8544 | 47.5032 | 47.1718 | 47.1718 | 47.1718 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 12 | 4572 | 17.7 | 17.7 | 15.3833 | 16.1652 | 15 | 94 | 94 | 1.354 | 117.8589 | 58.9954 | 159.8594 | 0 | 0 | 0.55022 | 0.79402 | 0.5727 | 0.0159 | 0 | 0 | 1.1411 | 58.3193 | 58.3193 | 58.3193 | 58.3193 | 58.3193 | 58.3193 | 58.3193 | 58.3193 | 117.8589 | 58.3193 | 58.3193 | 58.8695 | 59.1133 | 58.892 | 58.3352 | 58.3193 | 58.3193 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 13 | 4573 | 18.1 | 18.1 | 15.3833 | 16.1652 | 15 | 93 | 93 | 1.9578 | 145.305 | 60.0334 | 187.3291 | 0 | 0 | 0.34725 | 0.91504 | 0.94682 | 0.42396 | 0 | 0 | 1.695 | 72.6396 | 72.6396 | 72.6396 | 72.6396 | 72.6396 | 72.6396 | 72.6396 | 72.6396 | 145.305 | 72.6396 | 72.6396 | 72.9869 | 73.5547 | 73.5864 | 73.0636 | 72.6396 | 72.6396 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 14 | 4574 | 17.9 | 17.9 | 15.3833 | 16.1652 | 15 | 96 | 96 | 1.2868 | 115.9063 | 56.8105 | 213.2901 | 0 | 0 | 0 | 0.39279 | 0.63749 | 0.50875 | 0.081994 | 0 | 1.0937 | 57.3944 | 57.3944 | 57.3944 | 57.3944 | 57.3944 | 57.3944 | 57.3944 | 57.3944 | 115.9063 | 57.3944 | 57.3944 | 57.3944 | 57.7872 | 58.0319 | 57.9032 | 57.4764 | 57.3944 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 15 | 4575 | 18.2 | 18.2 | 15.3833 | 16.1652 | 15 | 94 | 94 | 1.0072 | 96.1978 | 50.4237 | 234.1991 | 0 | 0 | 0 | 0.1119 | 0.46087 | 0.53987 | 0.30262 | 0 | 0.80223 | 47.2755 | 47.2755 | 47.2755 | 47.2755 | 47.2755 | 47.2755 | 47.2755 | 47.2755 | 96.1978 | 47.2755 | 47.2755 | 47.2755 | 47.3874 | 47.7364 | 47.8154 | 47.5781 | 47.2755 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 16 | 4576 | 19.5 | 19.5 | 15.3833 | 16.1652 | 15 | 92 | 92 | 4.1362 | 172.067 | 42.2647 | 250.5422 | 0 | 0 | 0 | 0 | 1.5415 | 2.6013 | 2.1373 | 0.42128 | 2.933 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 172.067 | 86.8759 | 86.8759 | 86.8759 | 86.8759 | 88.4174 | 89.4772 | 89.0132 | 87.2972 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 17 | 4577 | 18.7 | 18.7 | 15.3833 | 16.1652 | 15 | 90 | 90 | 7.5646 | 184.5082 | 33.2915 | 263.9794 | 0 | 0 | 0 | 0 | 1.8648 | 5.051 | 5.2784 | 2.4138 | 4.4918 | 91.9237 | 91.9237 | 91.9237 | 91.9237 | 93.4976 | 96.1868 | 96.3787 | 93.9609 | 184.5082 | 91.9237 | 91.9237 | 91.9237 | 91.9237 | 95.3624 | 101.2378 | 101.6571 | 96.3747 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 10 | 18 | 4578 | 18.3 | 18.3 | 15.3833 | 16.1652 | 15 | 92 | 92 | 6.4774 | 136.0305 | 24.0936 | 275.8488 | 0 | 0 | 0 | 0 | 0.56789 | 4.209 | 5.3846 | 3.4059 | 2.9695 | 68.3884 | 68.3884 | 68.3884 | 68.3884 | 68.3992 | 68.4689 | 68.4914 | 68.4535 | 136.0305 | 68.3884 | 68.3884 | 68.3884 | 68.3884 | 68.9671 | 72.6779 | 73.8759 | 71.8594 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 19 | 4579 | 17.8 | 17.8 | 15.3833 | 16.1652 | 15 | 92 | 92 | 8.6374 | 100.3028 | 15.078 | 287.0593 | 0.8035 | 0 | 0 | 0 | 0 | 4.9783 | 7.8439 | 6.1146 | 2.6972 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 100.3028 | 50.9648 | 50.1613 | 50.1613 | 50.1613 | 50.1613 | 55.1396 | 58.0052 | 56.2759 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 20 | 4580 | 17.1 | 17.1 | 15.3833 | 16.1652 | 15 | 94 | 94 | 3.2252 | 35.4672 | 6.5867 | 298.2418 | 0.91357 | 0 | 0 | 0 | 0 | 1.4592 | 2.9771 | 2.7511 | 0.53278 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 35.4672 | 17.9735 | 17.0599 | 17.0599 | 17.0599 | 17.0599 | 18.519 | 20.037 | 19.811 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 21 | 4581 | 16.1 | 16.1 | 15.3833 | 16.1652 | 15 | 96 | 96 | 22.1708 | 10.3965 | -1.0395 | 309.8536 | 10.4218 | 0 | 0 | 0 | 0 | 6.3504 | 19.4026 | 21.0891 | 0.60355 | 18.4383 | 5.8594 | 5.8594 | 5.8594 | 5.8594 | 13.5242 | 29.2779 | 31.3134 | 10.3965 | 28.8601 | 5.8594 | 5.8594 | 5.8594 | 5.8594 | 19.8745 | 48.6805 | 52.4025 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 22 | 4582 | 15.7 | 15.7 | 15.3833 | 16.1652 | 15 | 95 | 95 | 0 | 0 | -7.4325 | 322.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 23 | 4583 | 15.1 | 15.1 | 15.3833 | 16.1652 | 15 | 95 | 95 | 0 | 0 | -12.2024 | 335.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 10 | 24 | 4584 | 14.8 | 14.8 | 16.9958 | 16.2931 | 15 | 96 | 96 | 0 | 0 | -14.9854 | 349.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 1 | 4585 | 14.3 | 14.3 | 16.9958 | 16.2931 | 15 | 96 | 96 | 0 | 0 | -15.5312 | 3.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 2 | 4586 | 13.9 | 13.9 | 16.9958 | 16.2931 | 15 | 97 | 97 | 0 | 0 | -13.918 | 18.0162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 3 | 4587 | 13.9 | 13.9 | 16.9958 | 16.2931 | 15 | 96 | 96 | 0 | 0 | -10.0476 | 31.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 4 | 4588 | 13.6 | 13.6 | 16.9958 | 16.2931 | 15 | 96 | 96 | 0 | 0 | -4.3715 | 44.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 5 | 4589 | 13.9 | 13.9 | 16.9958 | 16.2931 | 15 | 96 | 96 | 0.62016 | 0.495 | 2.7224 | 56.38 | 0.44155 | 0.61833 | 0.4329 | 0 | 0 | 0 | 0 | 0.0061125 | 2.505 | 0.79016 | 0.93489 | 0.78308 | 0.42865 | 0.42865 | 0.42865 | 0.42865 | 0.43366 | 0.495 | 1.2317 | 1.5532 | 1.216 | 0.42865 | 0.42865 | 0.42865 | 0.42865 | 0.43977 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 6 | 4590 | 14.6 | 14.6 | 16.9958 | 16.2931 | 15 | 95 | 95 | 7.8782 | 42.9233 | 10.8516 | 67.7276 | 4.3571 | 7.7146 | 6.553 | 1.5527 | 0 | 0 | 0 | 0 | 1.0767 | 121.1114 | 202.3795 | 174.2628 | 53.2317 | 15.648 | 15.648 | 15.648 | 15.648 | 42.9233 | 125.4686 | 210.0942 | 180.8158 | 54.7844 | 15.648 | 15.648 | 15.648 | 15.648 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 7 | 4591 | 15.2 | 15.2 | 16.9958 | 16.2931 | 15 | 93 | 93 | 5.566 | 79.4253 | 19.6631 | 78.8668 | 2.0718 | 5.042 | 5.0586 | 2.112 | 0 | 0 | 0 | 0 | 1.5747 | 56.9188 | 87.1931 | 87.3625 | 57.3279 | 35.8009 | 35.8009 | 35.8009 | 35.8009 | 79.4253 | 58.9907 | 92.2351 | 92.4211 | 59.4398 | 35.8009 | 35.8009 | 35.8009 | 35.8009 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 11 | 8 | 4592 | 16.9 | 16.9 | 16.9958 | 16.2931 | 15 | 87 | 87 | 66.9796 | 188.1878 | 28.8204 | 90.3381 | 12.179 | 52.3725 | 61.8869 | 35.1488 | 0 | 0 | 0 | 0 | 28.8122 | 108.2947 | 186.4579 | 204.9603 | 152.9634 | 84.6106 | 84.6106 | 84.6106 | 84.6106 | 188.1878 | 120.4737 | 238.8304 | 266.8472 | 188.1122 | 84.6106 | 84.6106 | 84.6106 | 84.6106 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 9 | 4593 | 17.4 | 17.4 | 16.9958 | 16.2931 | 15 | 83 | 83 | 42.2208 | 237.0022 | 37.9574 | 102.9002 | 0 | 26.0018 | 36.9904 | 26.3105 | 0.2183 | 0 | 0 | 0 | 23.9978 | 106.1745 | 177.6082 | 207.7967 | 178.4563 | 106.7743 | 106.1745 | 106.1745 | 106.1745 | 237.0022 | 106.1745 | 203.61 | 244.7871 | 204.7669 | 106.9925 | 106.1745 | 106.1745 | 106.1745 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 10 | 4594 | 17.8 | 17.8 | 16.9958 | 16.2931 | 15 | 78 | 78 | 23.3599 | 264.9239 | 46.5899 | 117.6673 | 0 | 9.7875 | 17.9536 | 15.6028 | 4.112 | 0 | 0 | 0 | 16.0761 | 121.3338 | 148.4978 | 171.1618 | 164.6373 | 132.7461 | 121.3338 | 121.3338 | 121.3338 | 264.9239 | 121.3338 | 158.2853 | 189.1155 | 180.24 | 136.8581 | 121.3338 | 121.3338 | 121.3338 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 11 | 4595 | 19.2 | 19.2 | 16.9958 | 16.2931 | 15 | 70 | 70 | 16.3397 | 284.232 | 53.9603 | 136.1983 | 0 | 3.3453 | 9.945 | 10.719 | 5.214 | 0 | 0 | 0 | 12.768 | 133.4586 | 143.0191 | 161.8801 | 164.0922 | 148.3595 | 133.4586 | 133.4586 | 133.4586 | 284.232 | 133.4586 | 146.3644 | 171.8251 | 174.8112 | 153.5735 | 133.4586 | 133.4586 | 133.4586 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 12 | 4596 | 20.4 | 20.4 | 16.9958 | 16.2931 | 15 | 66 | 66 | 362.898 | 325.574 | 58.8642 | 159.8554 | 0 | 0 | 147.7838 | 213.4631 | 154.0985 | 4.4651 | 0 | 0 | 305.426 | 158.3526 | 158.3526 | 242.6943 | 280.1781 | 246.2982 | 160.9009 | 158.3526 | 158.3526 | 325.574 | 158.3526 | 158.3526 | 390.4782 | 493.6412 | 400.3967 | 165.366 | 158.3526 | 158.3526 | 631 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 13 | 4597 | 19.2 | 19.2 | 16.9958 | 16.2931 | 15 | 65 | 65 | 100.0878 | 388.4586 | 59.9093 | 187.244 | 0 | 0 | 17.823 | 46.9585 | 48.5864 | 21.753 | 0 | 0 | 86.5414 | 170.7366 | 170.7366 | 196.2671 | 238.002 | 240.3338 | 201.8965 | 170.7366 | 170.7366 | 388.4586 | 170.7366 | 170.7366 | 214.0901 | 284.9606 | 288.9202 | 223.6495 | 170.7366 | 170.7366 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 14 | 4598 | 17.6 | 17.6 | 16.9958 | 16.2931 | 15 | 79 | 79 | 2.2061 | 151.1274 | 56.7036 | 213.1513 | 0 | 0 | 0 | 0.67725 | 1.0972 | 0.87449 | 0.13947 | 0 | 1.8726 | 75.7123 | 75.7123 | 75.7123 | 75.7123 | 75.7123 | 75.7123 | 75.7123 | 75.7123 | 151.1274 | 75.7123 | 75.7123 | 75.7123 | 76.3896 | 76.8096 | 76.5868 | 75.8518 | 75.7123 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 15 | 4599 | 18.1 | 18.1 | 16.9958 | 16.2931 | 15 | 83 | 83 | 5.4347 | 220.6777 | 50.3336 | 234.0495 | 0 | 0 | 0 | 0.61259 | 2.4979 | 2.9199 | 1.6315 | 0 | 4.3223 | 111.3429 | 111.3429 | 111.3429 | 111.8324 | 113.3387 | 113.6759 | 112.6465 | 111.3429 | 220.6777 | 111.3429 | 111.3429 | 111.3429 | 112.4449 | 115.8365 | 116.5958 | 114.278 | 111.3429 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 16 | 4600 | 16.6 | 16.6 | 16.9958 | 16.2931 | 15 | 90 | 90 | 35.5053 | 288.8676 | 42.1854 | 250.401 | 0 | 0 | 0 | 0 | 13.3055 | 22.3815 | 18.3467 | 3.5647 | 25.1324 | 129.3844 | 129.3844 | 129.3844 | 129.3844 | 165.7094 | 190.4876 | 179.4724 | 139.1163 | 288.8676 | 129.3844 | 129.3844 | 129.3844 | 129.3844 | 179.0149 | 212.8691 | 197.8192 | 142.681 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 17 | 4601 | 17.7 | 17.7 | 16.9958 | 16.2931 | 15 | 89 | 89 | 54.087 | 253.9569 | 33.217 | 263.8502 | 0 | 0 | 0 | 0 | 13.4433 | 36.2028 | 37.7552 | 17.1911 | 32.0431 | 116.4935 | 116.4935 | 116.4935 | 116.4935 | 138.4688 | 175.6729 | 178.2106 | 144.5952 | 253.9569 | 116.4935 | 116.4935 | 116.4935 | 116.4935 | 151.9121 | 211.8757 | 215.9657 | 161.7863 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 11 | 18 | 4602 | 20 | 20 | 16.9958 | 16.2931 | 15 | 75 | 75 | 379.8799 | 173.4072 | 24.0192 | 275.7304 | 0 | 0 | 0 | 0 | 34.046 | 247.5054 | 315.9794 | 199.357 | 173.5928 | 95.7127 | 95.7127 | 95.7127 | 95.7127 | 108.0317 | 185.2686 | 210.0448 | 167.8469 | 173.4072 | 95.7127 | 95.7127 | 95.7127 | 95.7127 | 142.0778 | 432.774 | 526.0242 | 367.2038 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 19 | 4603 | 19.3 | 19.3 | 16.9958 | 16.2931 | 15 | 76 | 76 | 706.0186 | 69.6691 | 15 | 286.95 | 64.3905 | 0 | 0 | 0 | 0 | 408.1921 | 641.6613 | 499.254 | 219.3309 | 64.7348 | 59.1354 | 59.1354 | 59.1354 | 59.1354 | 94.6318 | 114.9343 | 102.5505 | 69.6691 | 129.1253 | 59.1354 | 59.1354 | 59.1354 | 59.1354 | 502.8239 | 756.5956 | 601.8045 | 289 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 20 | 4604 | 17.8 | 17.8 | 16.9958 | 16.2931 | 15 | 86 | 86 | 371.8483 | 41.1157 | 6.5022 | 298.1407 | 104.7138 | 0 | 0 | 0 | 0 | 168.9004 | 343.575 | 316.988 | 105.8843 | 50.7495 | 32.7313 | 32.7313 | 32.7313 | 32.7313 | 61.7941 | 91.8505 | 87.2756 | 41.1157 | 155.4632 | 32.7313 | 32.7313 | 32.7313 | 32.7313 | 230.6945 | 435.4255 | 404.2637 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 21 | 4605 | 16.6 | 16.6 | 16.9958 | 16.2931 | 15 | 80 | 80 | 9.6875 | 9.8181 | -1.1327 | 309.7611 | 4.5396 | 0 | 0 | 0 | 0 | 2.7915 | 8.4874 | 9.2115 | 9.1819 | 10.4541 | 6.2954 | 6.2954 | 6.2954 | 6.2954 | 8.8527 | 14.0706 | 14.7339 | 9.8181 | 14.9937 | 6.2954 | 6.2954 | 6.2954 | 6.2954 | 11.6442 | 22.558 | 23.9454 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 22 | 4606 | 14.7 | 14.7 | 16.9958 | 16.2931 | 15 | 90 | 90 | 0 | 0 | -7.5358 | 322.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 23 | 4607 | 14.4 | 14.4 | 16.9958 | 16.2931 | 15 | 88 | 88 | 0 | 0 | -12.3159 | 335.3657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 11 | 24 | 4608 | 14.8 | 14.8 | 16.5792 | 16.3114 | 15 | 89 | 89 | 0 | 0 | -15.1078 | 349.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 1 | 4609 | 14.5 | 14.5 | 16.5792 | 16.3114 | 15 | 93 | 93 | 0 | 0 | -15.6598 | 3.7646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 2 | 4610 | 13.2 | 13.2 | 16.5792 | 16.3114 | 15 | 94 | 94 | 0 | 0 | -14.0551 | 18.0136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 3 | 4611 | 12.7 | 12.7 | 16.5792 | 16.3114 | 15 | 93 | 93 | 0 | 0 | -10.1835 | 31.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 4 | 4612 | 13.7 | 13.7 | 16.5792 | 16.3114 | 15 | 94 | 94 | 0 | 0 | -4.5041 | 44.4687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 5 | 4613 | 14 | 14 | 16.5792 | 16.3114 | 15 | 93 | 93 | 0 | 3 | 2.5941 | 56.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 6 | 4614 | 14.6 | 14.6 | 16.5792 | 16.3114 | 15 | 91 | 91 | 10.8866 | 45.5323 | 10.7273 | 67.7866 | 6.0139 | 10.6598 | 9.0614 | 2.1549 | 0 | 0 | 0 | 0 | 1.4677 | 143.74 | 242.5956 | 208.5838 | 61.6282 | 15.7768 | 15.7768 | 15.7768 | 15.7768 | 45.5323 | 149.7539 | 253.2555 | 217.6452 | 63.7831 | 15.7768 | 15.7768 | 15.7768 | 15.7768 | 47 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 7 | 4615 | 13.9 | 13.9 | 16.5792 | 16.3114 | 15 | 94 | 94 | 1.306 | 38.6328 | 19.5417 | 78.9344 | 0.48511 | 1.183 | 1.1879 | 0.49697 | 0 | 0 | 0 | 0 | 0.36725 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 38.6328 | 19.3504 | 20.0483 | 20.0532 | 19.3622 | 18.8653 | 18.8653 | 18.8653 | 18.8653 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 12 | 8 | 4616 | 13.9 | 13.9 | 16.5792 | 16.3114 | 15 | 92 | 92 | 12.1158 | 147.8073 | 28.7001 | 90.4131 | 2.1915 | 9.4732 | 11.2056 | 6.374 | 0 | 0 | 0 | 0 | 5.1927 | 78.6632 | 120.1193 | 129.9824 | 102.475 | 66.1868 | 66.1868 | 66.1868 | 66.1868 | 147.8073 | 80.8546 | 129.5924 | 141.1881 | 108.8489 | 66.1868 | 66.1868 | 66.1868 | 66.1868 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 9 | 4617 | 14.8 | 14.8 | 16.5792 | 16.3114 | 15 | 90 | 90 | 20.2383 | 213.5261 | 37.8356 | 102.9801 | 0 | 12.4617 | 17.7515 | 12.6427 | 0.12799 | 0 | 0 | 0 | 11.4739 | 96.3158 | 140.247 | 158.8951 | 140.8851 | 96.767 | 96.3158 | 96.3158 | 96.3158 | 213.5261 | 96.3158 | 152.7087 | 176.6466 | 153.5278 | 96.895 | 96.3158 | 96.3158 | 96.3158 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 10 | 4618 | 15.7 | 15.7 | 16.5792 | 16.3114 | 15 | 83 | 83 | 44.6583 | 288.326 | 46.4637 | 117.7454 | 0 | 18.7006 | 34.3687 | 29.9041 | 7.9221 | 0 | 0 | 0 | 30.674 | 128.0529 | 178.4428 | 220.6616 | 208.6314 | 149.3994 | 128.0529 | 128.0529 | 128.0529 | 288.326 | 128.0529 | 197.1435 | 255.0303 | 238.5355 | 157.3215 | 128.0529 | 128.0529 | 128.0529 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 11 | 4619 | 16.6 | 16.6 | 16.5792 | 16.3114 | 15 | 66 | 66 | 240.2084 | 337.5985 | 53.8275 | 136.2563 | 0 | 49.0782 | 146.4353 | 158.0125 | 77.0282 | 0 | 0 | 0 | 187.4015 | 159.2284 | 194.7164 | 265.1144 | 273.4858 | 214.9268 | 159.2284 | 159.2284 | 159.2284 | 337.5985 | 159.2284 | 243.7946 | 411.5497 | 431.4983 | 291.9549 | 159.2284 | 159.2284 | 159.2284 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 12 | 4620 | 17.9 | 17.9 | 16.5792 | 16.3114 | 15 | 59 | 59 | 168.2694 | 377.5799 | 58.7271 | 159.8568 | 0 | 0 | 68.6703 | 99.2919 | 71.7496 | 2.1774 | 0 | 0 | 141.4201 | 167.1535 | 167.1535 | 244.7046 | 279.2863 | 248.1822 | 169.6125 | 167.1535 | 167.1535 | 377.5799 | 167.1535 | 167.1535 | 313.3749 | 378.5782 | 319.9318 | 171.79 | 167.1535 | 167.1535 | 519 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 13 | 4621 | 16.9 | 16.9 | 16.5792 | 16.3114 | 15 | 61 | 61 | 368.1163 | 332.1376 | 59.7786 | 187.1612 | 0 | 0 | 65.8068 | 173.392 | 179.4066 | 80.3272 | 0 | 0 | 317.8624 | 159.0929 | 159.0929 | 197.274 | 259.6949 | 263.1846 | 205.6987 | 159.0929 | 159.0929 | 332.1376 | 159.0929 | 159.0929 | 263.0807 | 433.0869 | 442.5912 | 286.0259 | 159.0929 | 159.0929 | 650 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 14 | 4622 | 18.6 | 18.6 | 16.5792 | 16.3114 | 15 | 56 | 56 | 561.8009 | 248.7845 | 56.59 | 213.0115 | 0 | 0 | 0 | 173.468 | 280.5726 | 223.3215 | 35.2517 | 0 | 476.2155 | 141.9056 | 141.9056 | 141.9056 | 193.3971 | 225.1896 | 208.1954 | 152.3696 | 141.9056 | 248.7845 | 141.9056 | 141.9056 | 141.9056 | 366.8652 | 505.7622 | 431.5169 | 187.6213 | 141.9056 | 725 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 15 | 4623 | 17.6 | 17.6 | 16.5792 | 16.3114 | 15 | 55 | 55 | 379.7903 | 301.4117 | 50.2371 | 233.897 | 0 | 0 | 0 | 43.4379 | 175.3621 | 204.5615 | 113.9316 | 0 | 301.5883 | 145.1431 | 145.1431 | 145.1431 | 169.2575 | 242.4948 | 258.7047 | 208.3918 | 145.1431 | 301.4117 | 145.1431 | 145.1431 | 145.1431 | 212.6954 | 417.8568 | 463.2662 | 322.3234 | 145.1431 | 603 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 16 | 4624 | 17.6 | 17.6 | 16.5792 | 16.3114 | 15 | 56 | 56 | 255.7435 | 302.3087 | 42.1001 | 250.2562 | 0 | 0 | 0 | 0 | 96.3857 | 161.6084 | 132.1631 | 25.2984 | 180.6913 | 139.9244 | 139.9244 | 139.9244 | 139.9244 | 212.9567 | 262.3765 | 240.0655 | 159.0933 | 302.3087 | 139.9244 | 139.9244 | 139.9244 | 139.9244 | 309.3424 | 423.9849 | 372.2286 | 184.3917 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 17 | 4625 | 17.4 | 17.4 | 16.5792 | 16.3114 | 15 | 54 | 54 | 392.5606 | 220.9915 | 33.1366 | 263.7175 | 0 | 0 | 0 | 0 | 98.3953 | 263.4273 | 274.1472 | 124.2753 | 232.0085 | 117.301 | 117.301 | 117.301 | 117.301 | 158.0455 | 226.3836 | 230.8226 | 168.7622 | 220.9915 | 117.301 | 117.301 | 117.301 | 117.301 | 256.4409 | 489.8109 | 504.9698 | 293.0375 | 453 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 12 | 18 | 4626 | 16.2 | 16.2 | 16.5792 | 16.3114 | 15 | 63 | 63 | 21.541 | 173.1899 | 23.9389 | 275.6088 | 0 | 0 | 0 | 0 | 1.9739 | 14.0738 | 17.9294 | 11.2823 | 9.8101 | 84.4086 | 84.4086 | 84.4086 | 84.4086 | 86.0575 | 96.1652 | 99.386 | 93.8333 | 173.1899 | 84.4086 | 84.4086 | 84.4086 | 84.4086 | 88.0314 | 110.2389 | 117.3154 | 105.1156 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 19 | 4627 | 15.9 | 15.9 | 16.5792 | 16.3114 | 15 | 62 | 62 | 7.2135 | 94.7713 | 14.916 | 286.8378 | 0.64436 | 0 | 0 | 0 | 0 | 4.184 | 6.5614 | 5.0952 | 2.2287 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 94.7713 | 47.846 | 47.2017 | 47.2017 | 47.2017 | 47.2017 | 51.3856 | 53.7631 | 52.2969 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 20 | 4628 | 15.3 | 15.3 | 16.5792 | 16.3114 | 15 | 67 | 67 | 15.7803 | 58.4495 | 6.4117 | 298.0371 | 4.4169 | 0 | 0 | 0 | 0 | 7.1968 | 14.5948 | 13.4433 | 2.5505 | 34.9973 | 29.3923 | 29.3923 | 29.3923 | 29.3923 | 38.5249 | 47.9127 | 46.4515 | 58.4495 | 39.4142 | 29.3923 | 29.3923 | 29.3923 | 29.3923 | 45.7217 | 62.5075 | 59.8949 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 21 | 4629 | 14.5 | 14.5 | 16.5792 | 16.3114 | 15 | 72 | 72 | 9.9998 | 7.766 | -1.2321 | 309.6666 | 4.6709 | 0 | 0 | 0 | 0 | 2.8992 | 8.771 | 9.5049 | 0.23399 | 7.4854 | 4.3026 | 4.3026 | 4.3026 | 4.3026 | 6.2781 | 10.2792 | 10.7793 | 7.766 | 12.1563 | 4.3026 | 4.3026 | 4.3026 | 4.3026 | 9.1773 | 19.0502 | 20.2842 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 22 | 4630 | 12.6 | 12.6 | 16.5792 | 16.3114 | 15 | 83 | 83 | 0 | 0 | -7.6454 | 322.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 23 | 4631 | 12 | 12 | 16.5792 | 16.3114 | 15 | 88 | 88 | 0 | 0 | -12.4358 | 335.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 12 | 24 | 4632 | 12.7 | 12.7 | 15.1167 | 15.9306 | 15 | 84 | 84 | 0 | 0 | -15.2367 | 349.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 1 | 4633 | 12.8 | 12.8 | 15.1167 | 15.9306 | 15 | 82 | 82 | 0 | 0 | -15.7946 | 3.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 2 | 4634 | 12.1 | 12.1 | 15.1167 | 15.9306 | 15 | 85 | 85 | 0 | 0 | -14.1981 | 18.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 3 | 4635 | 11.4 | 11.4 | 15.1167 | 15.9306 | 15 | 90 | 90 | 0 | 0 | -10.3249 | 31.6935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 4 | 4636 | 12 | 12 | 15.1167 | 15.9306 | 15 | 89 | 89 | 0 | 0 | -4.6416 | 44.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 5 | 4637 | 11.6 | 11.6 | 15.1167 | 15.9306 | 15 | 94 | 94 | 0 | 3 | 2.4613 | 56.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 6 | 4638 | 12 | 12 | 15.1167 | 15.9306 | 15 | 93 | 93 | 11.6142 | 45.4568 | 10.5989 | 67.8506 | 6.4075 | 11.3713 | 9.6739 | 2.3097 | 0 | 0 | 0 | 0 | 1.5432 | 149.0433 | 252.5433 | 217.151 | 63.599 | 15.4396 | 15.4396 | 15.4396 | 15.4396 | 45.4568 | 155.4509 | 263.9146 | 226.825 | 65.9087 | 15.4396 | 15.4396 | 15.4396 | 15.4396 | 47 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 7 | 4639 | 13.9 | 13.9 | 15.1167 | 15.9306 | 15 | 89 | 89 | 62.573 | 121.5167 | 19.4165 | 79.0076 | 23.189 | 56.6786 | 56.9666 | 23.8844 | 0 | 0 | 0 | 0 | 17.4833 | 112.3383 | 197.295 | 198.0257 | 114.1024 | 53.5122 | 53.5122 | 53.5122 | 53.5122 | 121.5167 | 135.5273 | 253.9735 | 254.9923 | 137.9868 | 53.5122 | 53.5122 | 53.5122 | 53.5122 | 139 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 13 | 8 | 4640 | 16 | 16 | 15.1167 | 15.9306 | 15 | 77 | 77 | 235.8021 | 185.3285 | 28.576 | 90.494 | 42.4054 | 184.3544 | 218.3111 | 124.3841 | 0 | 0 | 0 | 0 | 100.6715 | 118.5897 | 210.5903 | 232.5985 | 171.7221 | 91.1057 | 91.1057 | 91.1057 | 91.1057 | 185.3285 | 160.9951 | 394.9447 | 450.9095 | 296.1062 | 91.1057 | 91.1057 | 91.1057 | 91.1057 | 286 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 9 | 4641 | 16.2 | 16.2 | 15.1167 | 15.9306 | 15 | 62 | 62 | 552.6413 | 168.524 | 37.7099 | 103.0663 | 0 | 340.2021 | 485.3026 | 346.1193 | 4.1841 | 0 | 0 | 0 | 312.476 | 108.36 | 190.9363 | 226.1561 | 192.3726 | 109.3756 | 108.36 | 108.36 | 108.36 | 168.524 | 108.36 | 531.1385 | 711.4587 | 538.4919 | 113.5596 | 108.36 | 108.36 | 108.36 | 481 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 10 | 4642 | 16.2 | 16.2 | 15.1167 | 15.9306 | 15 | 59 | 59 | 15.5664 | 247.3299 | 46.3332 | 117.8302 | 0 | 6.5138 | 11.996 | 10.4511 | 2.7841 | 0 | 0 | 0 | 10.6701 | 114.6106 | 136.4168 | 154.7697 | 149.5979 | 123.931 | 114.6106 | 114.6106 | 114.6106 | 247.3299 | 114.6106 | 142.9306 | 166.7657 | 160.0491 | 126.7151 | 114.6106 | 114.6106 | 114.6106 | 258 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 11 | 4643 | 18.2 | 18.2 | 15.1167 | 15.9306 | 15 | 54 | 54 | 639.0347 | 199.2873 | 53.6897 | 136.321 | 0 | 130.2531 | 390.1949 | 421.5659 | 205.9893 | 0 | 0 | 0 | 497.7127 | 133.1554 | 161.5928 | 218.3445 | 225.1936 | 178.1279 | 133.1554 | 133.1554 | 133.1554 | 199.2873 | 133.1554 | 291.8459 | 608.5395 | 646.7595 | 384.1172 | 133.1554 | 133.1554 | 133.1554 | 697 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 12 | 4644 | 18.8 | 18.8 | 15.1167 | 15.9306 | 15 | 48 | 48 | 444.7395 | 293.7811 | 58.5841 | 159.8639 | 0 | 0 | 181.8785 | 263.2863 | 190.4645 | 6.0712 | 0 | 0 | 373.2189 | 151.4685 | 151.4685 | 235.0375 | 272.4425 | 238.9826 | 154.258 | 151.4685 | 151.4685 | 293.7811 | 151.4685 | 151.4685 | 416.916 | 535.7288 | 429.4471 | 160.3293 | 151.4685 | 151.4685 | 667 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 13 | 4645 | 19.6 | 19.6 | 15.1167 | 15.9306 | 15 | 53 | 53 | 646.5523 | 217.5088 | 59.6414 | 187.0811 | 0 | 0 | 116.0174 | 305.775 | 316.4138 | 141.7017 | 0 | 0 | 557.4912 | 141.1558 | 141.1558 | 168.437 | 213.058 | 215.5597 | 174.4766 | 141.1558 | 141.1558 | 217.5088 | 141.1558 | 141.1558 | 284.4544 | 518.833 | 531.9735 | 316.1782 | 141.1558 | 141.1558 | 775 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 14 | 4646 | 18.4 | 18.4 | 15.1167 | 15.9306 | 15 | 62 | 62 | 359.4293 | 328.7745 | 56.4698 | 212.871 | 0 | 0 | 0 | 111.6379 | 180.2735 | 143.3074 | 22.3937 | 0 | 304.2255 | 156.1148 | 156.1148 | 156.1148 | 222.126 | 262.7101 | 240.8521 | 169.3562 | 156.1148 | 328.7745 | 156.1148 | 156.1148 | 156.1148 | 333.7639 | 442.9837 | 384.1595 | 191.7499 | 156.1148 | 633 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 15 | 4647 | 18 | 18 | 15.1167 | 15.9306 | 15 | 64 | 64 | 83.5341 | 352.7746 | 50.1343 | 233.7417 | 0 | 0 | 0 | 9.6951 | 38.7546 | 45.1122 | 25.0436 | 0 | 66.2254 | 156.5431 | 156.5431 | 156.5431 | 171.0985 | 214.726 | 224.2707 | 194.1415 | 156.5431 | 352.7746 | 156.5431 | 156.5431 | 156.5431 | 180.7937 | 253.4806 | 269.3829 | 219.1851 | 156.5431 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 16 | 4648 | 17 | 17 | 15.1167 | 15.9306 | 15 | 70 | 70 | 16.6225 | 257.2786 | 42.0087 | 250.1081 | 0 | 0 | 0 | 0 | 6.3016 | 10.5311 | 8.5917 | 1.6193 | 11.7214 | 125.014 | 125.014 | 125.014 | 125.014 | 134.3998 | 140.6994 | 137.8107 | 127.4259 | 257.2786 | 125.014 | 125.014 | 125.014 | 125.014 | 140.7014 | 151.2305 | 146.4024 | 129.0453 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 17 | 4649 | 17.6 | 17.6 | 15.1167 | 15.9306 | 15 | 65 | 65 | 23.9783 | 227.8643 | 33.0503 | 263.5814 | 0 | 0 | 0 | 0 | 6.0622 | 16.1334 | 16.7539 | 7.5602 | 14.1357 | 104.6539 | 104.6539 | 104.6539 | 104.6539 | 123.4583 | 154.6986 | 156.6235 | 128.1052 | 227.8643 | 104.6539 | 104.6539 | 104.6539 | 104.6539 | 129.5204 | 170.832 | 173.3774 | 135.6654 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 13 | 18 | 4650 | 17.9 | 17.9 | 15.1167 | 15.9306 | 15 | 66 | 66 | 162.5404 | 204.2407 | 23.8527 | 275.4839 | 0 | 0 | 0 | 0 | 15.2305 | 106.502 | 135.3861 | 84.9629 | 73.7593 | 99.9137 | 99.9137 | 99.9137 | 99.9137 | 110.1287 | 171.3441 | 190.7165 | 156.8979 | 204.2407 | 99.9137 | 99.9137 | 99.9137 | 99.9137 | 125.3591 | 277.8461 | 326.1026 | 241.8608 | 278 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 19 | 4651 | 17.7 | 17.7 | 15.1167 | 15.9306 | 15 | 64 | 64 | 154.5091 | 138.5348 | 14.8262 | 286.7227 | 13.5047 | 0 | 0 | 0 | 0 | 89.9162 | 140.6654 | 109.0147 | 47.4652 | 77.4601 | 70.2054 | 70.2054 | 70.2054 | 70.2054 | 118.5084 | 145.7708 | 128.7681 | 138.5348 | 90.9648 | 70.2054 | 70.2054 | 70.2054 | 70.2054 | 208.4245 | 286.4362 | 237.7829 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 20 | 4652 | 16.6 | 16.6 | 15.1167 | 15.9306 | 15 | 68 | 68 | 272.7829 | 67.4336 | 6.3151 | 297.931 | 75.8773 | 0 | 0 | 0 | 0 | 124.9255 | 252.5487 | 232.2323 | 43.5664 | 62.7848 | 38.8082 | 38.8082 | 38.8082 | 38.8082 | 78.2836 | 118.6114 | 112.1916 | 67.4336 | 138.6621 | 38.8082 | 38.8082 | 38.8082 | 38.8082 | 203.2091 | 371.1601 | 344.4239 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 21 | 4653 | 15.1 | 15.1 | 15.1167 | 15.9306 | 15 | 70 | 70 | 11.5335 | 4.125 | -1.3377 | 309.5702 | 5.3696 | 0 | 0 | 0 | 0 | 3.3648 | 10.1281 | 10.9586 | 20.875 | 9.8032 | 4.4247 | 4.4247 | 4.4247 | 4.4247 | 7.7951 | 14.5696 | 15.4014 | 4.125 | 15.1728 | 4.4247 | 4.4247 | 4.4247 | 4.4247 | 11.1599 | 24.6978 | 26.36 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 22 | 4654 | 13.6 | 13.6 | 15.1167 | 15.9306 | 15 | 81 | 81 | 0 | 0 | -7.7614 | 321.9575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 23 | 4655 | 11.5 | 11.5 | 15.1167 | 15.9306 | 15 | 93 | 93 | 0 | 0 | -12.5623 | 335.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 13 | 24 | 4656 | 10.9 | 10.9 | 15.2125 | 15.6625 | 15 | 96 | 96 | 0 | 0 | -15.3721 | 349.2749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 1 | 4657 | 10.5 | 10.5 | 15.2125 | 15.6625 | 15 | 98 | 98 | 0 | 0 | -15.9358 | 3.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 2 | 4658 | 9.2 | 9.2 | 15.2125 | 15.6625 | 15 | 98 | 98 | 0 | 0 | -14.3469 | 18.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 3 | 4659 | 8.8 | 8.8 | 15.2125 | 15.6625 | 15 | 98 | 98 | 0 | 0 | -10.4716 | 31.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 4 | 4660 | 8.3 | 8.3 | 15.2125 | 15.6625 | 15 | 98 | 98 | 0 | 0 | -4.7839 | 44.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 5 | 4661 | 9.1 | 9.1 | 15.2125 | 15.6625 | 15 | 99 | 99 | 0 | 3 | 2.3242 | 56.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 6 | 4662 | 11.6 | 11.6 | 15.2125 | 15.6625 | 15 | 99 | 99 | 3.1088 | 27.5932 | 10.4665 | 67.9197 | 1.7127 | 3.0434 | 2.5914 | 0.62137 | 0 | 0 | 0 | 0 | 0.40675 | 49.2197 | 78.4471 | 68.5194 | 25.2521 | 11.6052 | 11.6052 | 11.6052 | 11.6052 | 27.5932 | 50.9323 | 81.4905 | 71.1108 | 25.8735 | 11.6052 | 11.6052 | 11.6052 | 11.6052 | 28 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 7 | 4663 | 13.8 | 13.8 | 15.2125 | 15.6625 | 15 | 97 | 97 | 21.0236 | 105.1654 | 19.2874 | 79.0862 | 7.7714 | 19.0416 | 19.1575 | 8.0512 | 0 | 0 | 0 | 0 | 5.8346 | 98.9483 | 179.5543 | 180.3833 | 100.9498 | 43.3666 | 43.3666 | 43.3666 | 43.3666 | 105.1654 | 106.7197 | 198.5959 | 199.5409 | 109.001 | 43.3666 | 43.3666 | 43.3666 | 43.3666 | 111 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 14 | 8 | 4664 | 17.2 | 17.2 | 15.2125 | 15.6625 | 15 | 78 | 78 | 414.1503 | 154.9027 | 28.4481 | 90.5807 | 74.011 | 323.7462 | 383.8352 | 219.0788 | 0 | 0 | 0 | 0 | 176.0973 | 112.3777 | 188.4901 | 206.8036 | 156.5904 | 89.8212 | 89.8212 | 89.8212 | 89.8212 | 154.9027 | 186.3888 | 512.2363 | 590.6388 | 375.6692 | 89.8212 | 89.8212 | 89.8212 | 89.8212 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 9 | 4665 | 18.5 | 18.5 | 15.2125 | 15.6625 | 15 | 68 | 68 | 697.4497 | 128.7552 | 37.5804 | 103.1589 | 0 | 429.2036 | 613.2004 | 437.9928 | 6.2149 | 0 | 0 | 0 | 393.2448 | 99.5003 | 166.2682 | 194.8912 | 167.6355 | 100.4671 | 99.5003 | 99.5003 | 99.5003 | 128.7552 | 99.5003 | 595.4718 | 808.0916 | 605.6283 | 106.6821 | 99.5003 | 99.5003 | 99.5003 | 522 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 10 | 4666 | 19.9 | 19.9 | 15.2125 | 15.6625 | 15 | 70 | 70 | 720.8161 | 148.9696 | 46.1985 | 117.9217 | 0 | 301.3697 | 556.2463 | 485.2814 | 130.0452 | 0 | 0 | 0 | 493.0304 | 116.5585 | 165.2001 | 206.3375 | 194.8837 | 137.548 | 116.5585 | 116.5585 | 116.5585 | 148.9696 | 116.5585 | 466.5697 | 762.5838 | 680.165 | 267.5932 | 116.5585 | 116.5585 | 116.5585 | 642 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 11 | 4667 | 21.2 | 21.2 | 15.2125 | 15.6625 | 15 | 57 | 57 | 735.1334 | 164.4515 | 53.547 | 136.3924 | 0 | 149.4324 | 449.5972 | 486.3941 | 238.268 | 0 | 0 | 0 | 571.5485 | 128.5166 | 153.5756 | 203.9115 | 210.0822 | 168.4728 | 128.5166 | 128.5166 | 128.5166 | 164.4515 | 128.5166 | 303.0079 | 653.5088 | 696.4763 | 406.7407 | 128.5166 | 128.5166 | 128.5166 | 736 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 12 | 4668 | 21.6 | 21.6 | 15.2125 | 15.6625 | 15 | 60 | 60 | 226.8834 | 365.9011 | 58.4354 | 159.8764 | 0 | 0 | 92.9777 | 134.766 | 97.6103 | 3.2758 | 0 | 0 | 190.0989 | 168.3582 | 168.3582 | 243.2797 | 276.9529 | 247.0127 | 170.9978 | 168.3582 | 168.3582 | 365.9011 | 168.3582 | 168.3582 | 336.2574 | 411.7189 | 344.623 | 174.2735 | 168.3582 | 168.3582 | 556 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 13 | 4669 | 20.4 | 20.4 | 15.2125 | 15.6625 | 15 | 57 | 57 | 22.8167 | 330.3557 | 59.4979 | 187.0036 | 0 | 0 | 4.1091 | 10.8354 | 11.2145 | 5.0242 | 0 | 0 | 19.6443 | 157.0071 | 157.0071 | 165.226 | 178.6794 | 179.4375 | 167.0562 | 157.0071 | 157.0071 | 330.3557 | 157.0071 | 157.0071 | 169.3351 | 189.5149 | 190.652 | 172.0805 | 157.0071 | 157.0071 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 14 | 4670 | 22.4 | 22.4 | 15.2125 | 15.6625 | 15 | 50 | 50 | 132.369 | 382.1343 | 56.3431 | 212.7298 | 0 | 0 | 0 | 41.3609 | 66.6853 | 52.9464 | 8.1921 | 0 | 111.8657 | 164.7702 | 164.7702 | 164.7702 | 223.7557 | 259.8712 | 240.2778 | 176.4532 | 164.7702 | 382.1343 | 164.7702 | 164.7702 | 164.7702 | 265.1166 | 326.5565 | 293.2242 | 184.6453 | 164.7702 | 494 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 15 | 4671 | 22.9 | 22.9 | 15.2125 | 15.6625 | 15 | 48 | 48 | 522.1815 | 247.728 | 50.0252 | 233.584 | 0 | 0 | 0 | 61.5043 | 243.4539 | 282.7915 | 156.4737 | 0 | 413.272 | 138.921 | 138.921 | 138.921 | 160.52 | 224.4168 | 238.2313 | 193.8712 | 138.921 | 247.728 | 138.921 | 138.921 | 138.921 | 222.0243 | 467.8706 | 521.0228 | 350.3449 | 138.921 | 661 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 16 | 4672 | 23 | 23 | 15.2125 | 15.6625 | 15 | 47 | 47 | 806.6221 | 129.3774 | 41.9112 | 249.9569 | 0 | 0 | 0 | 0 | 307.635 | 512.41 | 417.0221 | 77.3484 | 567.6226 | 115.209 | 115.209 | 115.209 | 115.209 | 145.2855 | 165.3057 | 155.9799 | 122.7711 | 129.3774 | 115.209 | 115.209 | 115.209 | 115.209 | 452.9205 | 677.7156 | 573.002 | 200.1195 | 697 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 17 | 4673 | 21.9 | 21.9 | 15.2125 | 15.6625 | 15 | 51 | 51 | 644.9219 | 148.8156 | 32.9581 | 263.442 | 0 | 0 | 0 | 0 | 164.4883 | 435.1249 | 450.8712 | 202.5033 | 379.1844 | 104.419 | 104.419 | 104.419 | 104.419 | 133.8899 | 182.379 | 185.2002 | 140.7009 | 148.8156 | 104.419 | 104.419 | 104.419 | 104.419 | 298.3782 | 617.5039 | 636.0714 | 343.2042 | 528 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 18 | 4674 | 21.4 | 21.4 | 15.2125 | 15.6625 | 15 | 49 | 49 | 523.9926 | 141.1095 | 23.7608 | 275.356 | 0 | 0 | 0 | 0 | 50.2134 | 344.3626 | 436.7889 | 273.3502 | 236.8905 | 88.4422 | 88.4422 | 88.4422 | 88.4422 | 99.3022 | 162.9201 | 182.9099 | 147.5617 | 141.1095 | 88.4422 | 88.4422 | 88.4422 | 88.4422 | 149.5156 | 507.2827 | 619.6988 | 420.9119 | 378 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 19 | 4675 | 20.6 | 20.6 | 15.2125 | 15.6625 | 15 | 50 | 50 | 599.0255 | 84.0888 | 14.7305 | 286.6048 | 51.1758 | 0 | 0 | 0 | 0 | 349.7916 | 545.8559 | 422.1652 | 182.9112 | 67.7467 | 60.282 | 60.282 | 60.282 | 60.282 | 111.3045 | 139.9035 | 121.8613 | 84.0888 | 118.9226 | 60.282 | 60.282 | 60.282 | 60.282 | 461.0961 | 685.7594 | 544.0265 | 267 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 20 | 4676 | 19.3 | 19.3 | 15.2125 | 15.6625 | 15 | 57 | 57 | 405.2136 | 58.0943 | 6.2125 | 297.8225 | 111.9916 | 0 | 0 | 0 | 0 | 186.3659 | 375.5527 | 344.7459 | 63.9057 | 58.5427 | 36.4459 | 36.4459 | 36.4459 | 36.4459 | 73.2174 | 110.5456 | 104.4671 | 58.0943 | 170.5343 | 36.4459 | 36.4459 | 36.4459 | 36.4459 | 259.5833 | 486.0983 | 449.213 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 21 | 4677 | 17.7 | 17.7 | 15.2125 | 15.6625 | 15 | 64 | 64 | 14.1739 | 3.5408 | -1.4494 | 309.4719 | 6.5766 | 0 | 0 | 0 | 0 | 4.1614 | 12.4618 | 13.4622 | 15.4592 | 8.2424 | 3.5556 | 3.5556 | 3.5556 | 3.5556 | 6.5212 | 12.4364 | 13.1493 | 3.5408 | 14.819 | 3.5556 | 3.5556 | 3.5556 | 3.5556 | 10.6827 | 24.8982 | 26.6115 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 22 | 4678 | 16.2 | 16.2 | 15.2125 | 15.6625 | 15 | 72 | 72 | 0 | 0 | -7.8837 | 321.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 23 | 4679 | 14.5 | 14.5 | 15.2125 | 15.6625 | 15 | 84 | 84 | 0 | 0 | -12.6952 | 335.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 14 | 24 | 4680 | 16.1 | 16.1 | 16.9208 | 16.006 | 15 | 68 | 68 | 0 | 0 | -15.5139 | 349.2279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 1 | 4681 | 16.6 | 16.6 | 16.9208 | 16.006 | 15 | 71 | 71 | 0 | 0 | -16.0831 | 3.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 2 | 4682 | 16.7 | 16.7 | 16.9208 | 16.006 | 15 | 74 | 74 | 0 | 0 | -14.5015 | 18.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 3 | 4683 | 16.5 | 16.5 | 16.9208 | 16.006 | 15 | 78 | 78 | 0 | 0 | -10.6236 | 31.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 4 | 4684 | 15.9 | 15.9 | 16.9208 | 16.006 | 15 | 80 | 80 | 0 | 0 | -4.9311 | 44.5999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 5 | 4685 | 14.7 | 14.7 | 16.9208 | 16.006 | 15 | 84 | 84 | 0 | 3 | 2.1827 | 56.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 6 | 4686 | 15 | 15 | 16.9208 | 16.006 | 15 | 87 | 87 | 18.1566 | 47.6629 | 10.3301 | 67.994 | 9.9871 | 17.7727 | 15.1473 | 3.6489 | 0 | 0 | 0 | 0 | 2.3371 | 115.2786 | 190.6903 | 165.2609 | 53.8867 | 18.5439 | 18.5439 | 18.5439 | 18.5439 | 47.6629 | 125.2657 | 208.463 | 180.4083 | 57.5355 | 18.5439 | 18.5439 | 18.5439 | 18.5439 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 7 | 4687 | 15.7 | 15.7 | 16.9208 | 16.006 | 15 | 90 | 90 | 9.0489 | 89.5065 | 19.1546 | 79.1702 | 3.3357 | 8.1949 | 8.2536 | 3.4775 | 0 | 0 | 0 | 0 | 2.4935 | 74.5525 | 126.9577 | 127.5913 | 76.0819 | 38.5779 | 38.5779 | 38.5779 | 38.5779 | 89.5065 | 77.8881 | 135.1526 | 135.8449 | 79.5594 | 38.5779 | 38.5779 | 38.5779 | 38.5779 | 92 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 15 | 8 | 4688 | 16.1 | 16.1 | 16.9208 | 16.006 | 15 | 91 | 91 | 4.2542 | 104.1988 | 28.3166 | 90.6732 | 0.75508 | 3.325 | 3.9471 | 2.2571 | 0 | 0 | 0 | 0 | 1.8012 | 53.0736 | 63.5795 | 66.123 | 59.214 | 49.9867 | 49.9867 | 49.9867 | 49.9867 | 104.1988 | 53.8286 | 66.9045 | 70.0701 | 61.4712 | 49.9867 | 49.9867 | 49.9867 | 49.9867 | 106 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 9 | 4689 | 17 | 17 | 16.9208 | 16.006 | 15 | 89 | 89 | 2.6461 | 109.5124 | 37.447 | 103.2577 | 0 | 1.6277 | 2.3293 | 1.6664 | 0.027371 | 0 | 0 | 0 | 1.4876 | 54.5566 | 54.5566 | 54.5566 | 54.5566 | 54.5566 | 54.5566 | 54.5566 | 54.5566 | 109.5124 | 54.5566 | 56.1843 | 56.8859 | 56.223 | 54.5839 | 54.5566 | 54.5566 | 54.5566 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 10 | 4690 | 18.8 | 18.8 | 16.9208 | 16.006 | 15 | 83 | 83 | 6.8602 | 206.3183 | 46.0596 | 118.02 | 0 | 2.8653 | 5.3012 | 4.6317 | 1.249 | 0 | 0 | 0 | 4.6817 | 98.8349 | 109.5557 | 118.6696 | 116.1646 | 103.5082 | 98.8349 | 98.8349 | 98.8349 | 206.3183 | 98.8349 | 112.421 | 123.9708 | 120.7964 | 104.7572 | 98.8349 | 98.8349 | 98.8349 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 11 | 4691 | 17.7 | 17.7 | 16.9208 | 16.006 | 15 | 86 | 86 | 5.5544 | 217.6896 | 53.3994 | 136.4705 | 0 | 1.1256 | 3.4025 | 3.6862 | 1.8107 | 0 | 0 | 0 | 4.3104 | 106.9302 | 109.7764 | 115.5336 | 116.2512 | 111.5086 | 106.9302 | 106.9302 | 106.9302 | 217.6896 | 106.9302 | 110.9019 | 118.9361 | 119.9374 | 113.3192 | 106.9302 | 106.9302 | 106.9302 | 222 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 12 | 4692 | 18.3 | 18.3 | 16.9208 | 16.006 | 15 | 84 | 84 | 1.7941 | 134.4992 | 58.281 | 159.8946 | 0 | 0 | 0.73674 | 1.0694 | 0.77556 | 0.027452 | 0 | 0 | 1.5008 | 66.9428 | 66.9428 | 66.9428 | 66.9428 | 66.9428 | 66.9428 | 66.9428 | 66.9428 | 134.4992 | 66.9428 | 66.9428 | 67.6795 | 68.0122 | 67.7184 | 66.9703 | 66.9428 | 66.9428 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 13 | 4693 | 18.1 | 18.1 | 16.9208 | 16.006 | 15 | 86 | 86 | 2.0667 | 148.2234 | 59.3479 | 186.9289 | 0 | 0 | 0.37351 | 0.98562 | 1.0204 | 0.4574 | 0 | 0 | 1.7766 | 74.1613 | 74.1613 | 74.1613 | 74.1613 | 74.1613 | 74.1613 | 74.1613 | 74.1613 | 148.2234 | 74.1613 | 74.1613 | 74.5348 | 75.1469 | 75.1817 | 74.6187 | 74.1613 | 74.1613 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 14 | 4694 | 18.5 | 18.5 | 16.9208 | 16.006 | 15 | 84 | 84 | 1.6865 | 131.577 | 56.2098 | 212.5884 | 0 | 0 | 0 | 0.5302 | 0.85354 | 0.67689 | 0.10373 | 0 | 1.423 | 65.4832 | 65.4832 | 65.4832 | 65.4832 | 65.4832 | 65.4832 | 65.4832 | 65.4832 | 131.577 | 65.4832 | 65.4832 | 65.4832 | 66.0134 | 66.3368 | 66.1601 | 65.587 | 65.4832 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 15 | 4695 | 18.9 | 18.9 | 16.9208 | 16.006 | 15 | 82 | 82 | 1.6186 | 120.7213 | 49.9097 | 233.424 | 0 | 0 | 0 | 0.19349 | 0.75849 | 0.87918 | 0.48486 | 0 | 1.2787 | 59.8261 | 59.8261 | 59.8261 | 59.8261 | 59.8261 | 59.8261 | 59.8261 | 59.8261 | 120.7213 | 59.8261 | 59.8261 | 59.8261 | 60.0196 | 60.5846 | 60.7052 | 60.3109 | 59.8261 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 16 | 4696 | 20.3 | 20.3 | 16.9208 | 16.006 | 15 | 78 | 78 | 4.3614 | 174.9374 | 41.8076 | 249.8026 | 0 | 0 | 0 | 0 | 1.6737 | 2.7784 | 2.2556 | 0.41147 | 3.0626 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 174.9374 | 88.4293 | 88.4293 | 88.4293 | 88.4293 | 90.103 | 91.2077 | 90.6849 | 88.8407 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 17 | 4697 | 19.6 | 19.6 | 16.9208 | 16.006 | 15 | 80 | 80 | 7.0702 | 178.8546 | 32.86 | 263.2996 | 0 | 0 | 0 | 0 | 1.8195 | 4.7839 | 4.946 | 2.2107 | 4.1454 | 89.366 | 89.366 | 89.366 | 89.366 | 90.6197 | 92.6621 | 92.7738 | 90.8892 | 178.8546 | 89.366 | 89.366 | 89.366 | 89.366 | 92.4392 | 97.4461 | 97.7198 | 93.1 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 18 | 4698 | 19.4 | 19.4 | 16.9208 | 16.006 | 15 | 81 | 81 | 1.5025 | 66.3234 | 23.6629 | 275.2251 | 0 | 0 | 0 | 0 | 0.14726 | 0.9905 | 1.2535 | 0.78223 | 0.67661 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 66.3234 | 32.1431 | 32.1431 | 32.1431 | 32.1431 | 32.2904 | 33.1336 | 33.3966 | 32.9253 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 19 | 4699 | 19.6 | 19.6 | 16.9208 | 16.006 | 15 | 82 | 82 | 4.1471 | 73.7417 | 14.6288 | 286.4843 | 0.34592 | 0 | 0 | 0 | 0 | 2.4301 | 3.7826 | 2.9193 | 1.2583 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 73.7417 | 36.5211 | 36.1751 | 36.1751 | 36.1751 | 36.1751 | 38.6053 | 39.9578 | 39.0945 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 20 | 4700 | 19.1 | 19.1 | 16.9208 | 16.006 | 15 | 84 | 84 | 4.9439 | 41.2306 | 6.1039 | 297.7117 | 1.3574 | 0 | 0 | 0 | 0 | 2.2837 | 4.587 | 4.2033 | 0.76936 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 41.2306 | 21.3466 | 19.9892 | 19.9892 | 19.9892 | 19.9892 | 22.2729 | 24.5762 | 24.1925 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 21 | 4701 | 17.9 | 17.9 | 16.9208 | 16.006 | 15 | 89 | 89 | 3.5718 | 5.4766 | -1.5674 | 309.3718 | 1.6516 | 0 | 0 | 0 | 0 | 1.0555 | 3.1442 | 3.3911 | 8.5234 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 5.4766 | 5.4289 | 3.7773 | 3.7773 | 3.7773 | 3.7773 | 4.8328 | 6.9215 | 7.1685 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 22 | 4702 | 17.1 | 17.1 | 16.9208 | 16.006 | 15 | 92 | 92 | 0 | 0 | -8.0124 | 321.7852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 23 | 4703 | 17.5 | 17.5 | 16.9208 | 16.006 | 15 | 91 | 91 | 0 | 0 | -12.8346 | 335.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 15 | 24 | 4704 | 17.7 | 17.7 | 17.6125 | 16.4848 | 15 | 91 | 91 | 0 | 0 | -15.662 | 349.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 1 | 4705 | 17.5 | 17.5 | 17.6125 | 16.4848 | 15 | 93 | 93 | 0 | 0 | -16.2366 | 3.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 2 | 4706 | 17.6 | 17.6 | 17.6125 | 16.4848 | 15 | 93 | 93 | 0 | 0 | -14.6618 | 18.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 3 | 4707 | 16.6 | 16.6 | 17.6125 | 16.4848 | 15 | 90 | 90 | 0 | 0 | -10.7808 | 31.7815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 4 | 4708 | 16.1 | 16.1 | 17.6125 | 16.4848 | 15 | 92 | 92 | 0 | 0 | -5.0829 | 44.6523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 5 | 4709 | 15.6 | 15.6 | 17.6125 | 16.4848 | 15 | 92 | 92 | 0 | 0 | 2.037 | 56.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 6 | 4710 | 15.3 | 15.3 | 17.6125 | 16.4848 | 15 | 94 | 94 | 0.27134 | 7.9657 | 10.1899 | 68.0734 | 0.149 | 0.26557 | 0.22657 | 0.054849 | 0 | 0 | 0 | 0 | 0.03433 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 7.9657 | 3.9647 | 4.0812 | 4.0422 | 3.8705 | 3.8157 | 3.8157 | 3.8157 | 3.8157 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 7 | 4711 | 15.2 | 15.2 | 17.6125 | 16.4848 | 15 | 93 | 93 | 0.32747 | 18.9104 | 19.0182 | 79.2597 | 0.12036 | 0.29652 | 0.29899 | 0.12632 | 0 | 0 | 0 | 0 | 0.089569 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 18.9104 | 9.088 | 9.2642 | 9.2666 | 9.094 | 8.9676 | 8.9676 | 8.9676 | 8.9676 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 16 | 8 | 4712 | 15.4 | 15.4 | 17.6125 | 16.4848 | 15 | 90 | 90 | 1.2849 | 57.4584 | 28.1814 | 90.7716 | 0.22638 | 1.004 | 1.1935 | 0.68386 | 0 | 0 | 0 | 0 | 0.54161 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 57.4584 | 28.2203 | 28.9979 | 29.1874 | 28.6778 | 27.9939 | 27.9939 | 27.9939 | 27.9939 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 9 | 4713 | 16.6 | 16.6 | 17.6125 | 16.4848 | 15 | 83 | 83 | 5.3938 | 154.9771 | 37.3099 | 103.3627 | 0 | 3.3163 | 4.754 | 3.4069 | 0.064027 | 0 | 0 | 0 | 3.0229 | 74.2813 | 87.4321 | 93.1332 | 87.7912 | 74.5352 | 74.2813 | 74.2813 | 74.2813 | 154.9771 | 74.2813 | 90.7484 | 97.8872 | 91.198 | 74.5993 | 74.2813 | 74.2813 | 74.2813 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 10 | 4714 | 19 | 19 | 17.6125 | 16.4848 | 15 | 59 | 59 | 438.3931 | 240.5202 | 45.9165 | 118.1248 | 0 | 182.8987 | 339.2441 | 296.8649 | 80.5863 | 0 | 0 | 0 | 298.4798 | 132.3318 | 202.1446 | 261.822 | 245.6458 | 163.0918 | 132.3318 | 132.3318 | 132.3318 | 240.5202 | 132.3318 | 385.0433 | 601.0661 | 542.5106 | 243.678 | 132.3318 | 132.3318 | 132.3318 | 539 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 11 | 4715 | 19.4 | 19.4 | 17.6125 | 16.4848 | 15 | 59 | 59 | 289.9025 | 322.4606 | 53.2471 | 136.5553 | 0 | 58.5472 | 177.8722 | 193.002 | 95.0739 | 0 | 0 | 0 | 224.5394 | 152.9404 | 193.6058 | 276.4858 | 286.9946 | 218.9762 | 152.9404 | 152.9404 | 152.9404 | 322.4606 | 152.9404 | 252.153 | 454.3579 | 479.9965 | 314.0501 | 152.9404 | 152.9404 | 152.9404 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 12 | 4716 | 17.9 | 17.9 | 17.6125 | 16.4848 | 15 | 61 | 61 | 126.1759 | 377.6362 | 58.121 | 159.9183 | 0 | 0 | 51.9174 | 75.4715 | 54.8153 | 2.0491 | 0 | 0 | 105.3638 | 163.6366 | 163.6366 | 242.0834 | 277.6734 | 246.4622 | 166.7329 | 163.6366 | 163.6366 | 377.6362 | 163.6366 | 163.6366 | 294.0008 | 353.1448 | 301.2775 | 168.782 | 163.6366 | 163.6366 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 13 | 4717 | 18.8 | 18.8 | 17.6125 | 16.4848 | 15 | 54 | 54 | 604.6171 | 234.122 | 59.1916 | 186.8572 | 0 | 0 | 109.64 | 289.5899 | 299.902 | 134.5355 | 0 | 0 | 518.878 | 142.5589 | 142.5589 | 171.4704 | 218.9223 | 221.6415 | 178.0352 | 142.5589 | 142.5589 | 234.122 | 142.5589 | 142.5589 | 281.1104 | 508.5122 | 521.5435 | 312.5708 | 142.5589 | 142.5589 | 753 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 14 | 4718 | 19.4 | 19.4 | 17.6125 | 16.4848 | 15 | 52 | 52 | 527.7049 | 261.5115 | 56.07 | 212.4468 | 0 | 0 | 0 | 166.9275 | 268.3408 | 212.5636 | 32.2696 | 0 | 444.4885 | 145.1662 | 145.1662 | 145.1662 | 206.1999 | 243.2797 | 222.8858 | 156.9649 | 145.1662 | 261.5115 | 145.1662 | 145.1662 | 145.1662 | 373.1275 | 511.6204 | 435.4494 | 189.2344 | 145.1662 | 706 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 15 | 4719 | 19.4 | 19.4 | 17.6125 | 16.4848 | 15 | 54 | 54 | 671.0016 | 189.9004 | 49.7879 | 233.2619 | 0 | 0 | 0 | 81.4048 | 316.07 | 365.5857 | 200.9463 | 0 | 529.0996 | 130.3122 | 130.3122 | 130.3122 | 146.988 | 195.0592 | 205.2025 | 171.4761 | 130.3122 | 189.9004 | 130.3122 | 130.3122 | 130.3122 | 228.3927 | 511.1292 | 570.7882 | 372.4224 | 130.3122 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 16 | 4720 | 18.7 | 18.7 | 17.6125 | 16.4848 | 15 | 54 | 54 | 541.0164 | 212.9601 | 41.6979 | 249.6454 | 0 | 0 | 0 | 0 | 208.9313 | 345.6656 | 279.9137 | 50.1921 | 379.0399 | 124.8466 | 124.8466 | 124.8466 | 124.8466 | 181.3932 | 218.3999 | 200.6044 | 138.431 | 212.9601 | 124.8466 | 124.8466 | 124.8466 | 124.8466 | 390.3245 | 564.0655 | 480.5181 | 188.6231 | 592 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 17 | 4721 | 18.4 | 18.4 | 17.6125 | 16.4848 | 15 | 56 | 56 | 407.3067 | 214.8837 | 32.756 | 263.1541 | 0 | 0 | 0 | 0 | 105.782 | 276.4169 | 285.1305 | 126.8185 | 238.1163 | 115.8105 | 115.8105 | 115.8105 | 115.8105 | 157.2368 | 224.0609 | 227.4733 | 165.4752 | 214.8837 | 115.8105 | 115.8105 | 115.8105 | 115.8105 | 263.0189 | 500.4778 | 512.6038 | 292.2937 | 453 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 16 | 18 | 4722 | 17.6 | 17.6 | 17.6125 | 16.4848 | 15 | 57 | 57 | 178.7349 | 200.8454 | 23.5592 | 275.0914 | 0 | 0 | 0 | 0 | 17.9173 | 118.1989 | 149.2412 | 92.86 | 80.1546 | 99.2339 | 99.2339 | 99.2339 | 99.2339 | 109.9863 | 170.1666 | 188.7955 | 154.9604 | 200.8454 | 99.2339 | 99.2339 | 99.2339 | 99.2339 | 127.9036 | 288.3655 | 338.0367 | 247.8204 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 19 | 4723 | 17.2 | 17.2 | 17.6125 | 16.4848 | 15 | 63 | 63 | 109.6844 | 135.941 | 14.5213 | 286.3611 | 8.9225 | 0 | 0 | 0 | 0 | 64.5042 | 100.1452 | 77.1226 | 33.059 | 74.3152 | 67.6656 | 67.6656 | 67.6656 | 67.6656 | 115.7379 | 142.2997 | 125.1418 | 135.941 | 83.2377 | 67.6656 | 67.6656 | 67.6656 | 67.6656 | 180.2421 | 242.4449 | 202.2644 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 20 | 4724 | 16.4 | 16.4 | 17.6125 | 16.4848 | 15 | 63 | 63 | 317.5647 | 62.2711 | 5.9893 | 297.5987 | 86.5972 | 0 | 0 | 0 | 0 | 147.3427 | 294.9711 | 269.8095 | 48.7289 | 59.465 | 36.9138 | 36.9138 | 36.9138 | 36.9138 | 75.2841 | 113.7289 | 107.1764 | 62.2711 | 146.0622 | 36.9138 | 36.9138 | 36.9138 | 36.9138 | 222.6268 | 408.7001 | 376.986 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 21 | 4725 | 15.1 | 15.1 | 17.6125 | 16.4848 | 15 | 72 | 72 | 2.7518 | 2.805 | -1.6915 | 309.2699 | 1.2679 | 0 | 0 | 0 | 0 | 0.81846 | 2.4253 | 2.6115 | 14.195 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 2.805 | 4.1843 | 2.9164 | 2.9164 | 2.9164 | 2.9164 | 3.7349 | 5.3418 | 5.5279 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 22 | 4726 | 15.1 | 15.1 | 17.6125 | 16.4848 | 15 | 73 | 73 | 0 | 0 | -8.1474 | 321.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 23 | 4727 | 15.2 | 15.2 | 17.6125 | 16.4848 | 15 | 74 | 74 | 0 | 0 | -12.9803 | 335.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 16 | 24 | 4728 | 14.7 | 14.7 | 17.0083 | 16.6518 | 15 | 78 | 78 | 0 | 0 | -15.8165 | 349.1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 1 | 4729 | 14.9 | 14.9 | 17.0083 | 16.6518 | 15 | 78 | 78 | 0 | 0 | -16.3962 | 3.6547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 2 | 4730 | 14.9 | 14.9 | 17.0083 | 16.6518 | 15 | 79 | 79 | 0 | 0 | -14.8277 | 18.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 3 | 4731 | 14.4 | 14.4 | 17.0083 | 16.6518 | 15 | 83 | 83 | 0 | 0 | -10.9431 | 31.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 4 | 4732 | 14.2 | 14.2 | 17.0083 | 16.6518 | 15 | 83 | 83 | 0 | 0 | -5.2393 | 44.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 5 | 4733 | 14.8 | 14.8 | 17.0083 | 16.6518 | 15 | 83 | 83 | 0 | 0 | 1.8871 | 56.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 6 | 4734 | 14.8 | 14.8 | 17.0083 | 16.6518 | 15 | 84 | 84 | 0.53202 | 10.9339 | 10.0458 | 68.1578 | 0.29161 | 0.52061 | 0.44464 | 0.10821 | 0 | 0 | 0 | 0 | 0.066091 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 10.9339 | 5.6328 | 5.8618 | 5.7859 | 5.4494 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 7 | 4735 | 15.8 | 15.8 | 17.0083 | 16.6518 | 15 | 79 | 79 | 5.1821 | 73.5936 | 18.8781 | 79.3546 | 1.8984 | 4.6915 | 4.7363 | 2.0067 | 0 | 0 | 0 | 0 | 1.4064 | 53.7552 | 84.023 | 84.5089 | 54.9283 | 33.1821 | 33.1821 | 33.1821 | 33.1821 | 73.5936 | 55.6536 | 88.7145 | 89.2452 | 56.935 | 33.1821 | 33.1821 | 33.1821 | 33.1821 | 75 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 17 | 8 | 4736 | 16.4 | 16.4 | 17.0083 | 16.6518 | 15 | 82 | 82 | 7.0746 | 128.0319 | 28.0428 | 90.8758 | 1.2366 | 5.5263 | 6.5788 | 3.7775 | 0 | 0 | 0 | 0 | 2.9681 | 66.9453 | 95.2846 | 102.2377 | 83.7315 | 58.776 | 58.776 | 58.776 | 58.776 | 128.0319 | 68.1819 | 100.811 | 108.8166 | 87.5091 | 58.776 | 58.776 | 58.776 | 58.776 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 9 | 4737 | 16.6 | 16.6 | 17.0083 | 16.6518 | 15 | 79 | 79 | 2.3067 | 101.7114 | 37.1691 | 103.474 | 0 | 1.4174 | 2.0357 | 1.4614 | 0.031118 | 0 | 0 | 0 | 1.2886 | 50.4506 | 50.4506 | 50.4506 | 50.4506 | 50.4506 | 50.4506 | 50.4506 | 50.4506 | 101.7114 | 50.4506 | 51.868 | 52.4862 | 51.912 | 50.4817 | 50.4506 | 50.4506 | 50.4506 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 10 | 4738 | 16.9 | 16.9 | 17.0083 | 16.6518 | 15 | 80 | 80 | 4.5048 | 171.9404 | 45.7694 | 118.2362 | 0 | 1.877 | 3.4909 | 3.0599 | 0.83642 | 0 | 0 | 0 | 3.0596 | 84.8401 | 88.4965 | 91.6404 | 90.8007 | 86.4695 | 84.8401 | 84.8401 | 84.8401 | 171.9404 | 84.8401 | 90.3735 | 95.1313 | 93.8606 | 87.3059 | 84.8401 | 84.8401 | 84.8401 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 11 | 4739 | 16.6 | 16.6 | 17.0083 | 16.6518 | 15 | 77 | 77 | 11.3227 | 263.2479 | 53.09 | 136.6466 | 0 | 2.278 | 6.9583 | 7.5625 | 3.7367 | 0 | 0 | 0 | 8.7521 | 124.9748 | 132.33 | 147.4414 | 149.3921 | 137.0396 | 124.9748 | 124.9748 | 124.9748 | 263.2479 | 124.9748 | 134.608 | 154.3996 | 156.9546 | 140.7762 | 124.9748 | 124.9748 | 124.9748 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 12 | 4740 | 16.8 | 16.8 | 17.0083 | 16.6518 | 15 | 74 | 74 | 3.1993 | 178.3332 | 57.9553 | 159.9476 | 0 | 0 | 1.319 | 1.9206 | 1.3971 | 0.05521 | 0 | 0 | 2.6668 | 90.1509 | 90.1509 | 90.1509 | 90.1509 | 90.1509 | 90.1509 | 90.1509 | 90.1509 | 178.3332 | 90.1509 | 90.1509 | 91.47 | 92.0716 | 91.5481 | 90.2062 | 90.1509 | 90.1509 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 13 | 4741 | 16.2 | 16.2 | 17.0083 | 16.6518 | 15 | 80 | 80 | 4.3533 | 213.2705 | 59.029 | 186.7886 | 0 | 0 | 0.79197 | 2.0942 | 2.1697 | 0.97423 | 0 | 0 | 3.7295 | 108.3691 | 108.3691 | 108.6564 | 109.1287 | 109.1561 | 108.7225 | 108.3691 | 108.3691 | 213.2705 | 108.3691 | 108.3691 | 109.4483 | 111.223 | 111.3259 | 109.6967 | 108.3691 | 108.3691 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 14 | 4742 | 14.5 | 14.5 | 17.0083 | 16.6518 | 15 | 92 | 92 | 0.95978 | 99.193 | 55.9237 | 212.3052 | 0 | 0 | 0 | 0.30551 | 0.49045 | 0.38808 | 0.058383 | 0 | 0.807 | 48.8271 | 48.8271 | 48.8271 | 48.8271 | 48.8271 | 48.8271 | 48.8271 | 48.8271 | 99.193 | 48.8271 | 48.8271 | 48.8271 | 49.1326 | 49.3175 | 49.2152 | 48.8855 | 48.8271 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 15 | 4743 | 15.6 | 15.6 | 17.0083 | 16.6518 | 15 | 90 | 90 | 2.2718 | 142.2121 | 49.6597 | 233.0978 | 0 | 0 | 0 | 0.27973 | 1.0759 | 1.2418 | 0.68028 | 0 | 1.7879 | 71.0003 | 71.0003 | 71.0003 | 71.0003 | 71.0003 | 71.0003 | 71.0003 | 71.0003 | 142.2121 | 71.0003 | 71.0003 | 71.0003 | 71.28 | 72.0762 | 72.2421 | 71.6806 | 71.0003 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 16 | 4744 | 14.8 | 14.8 | 17.0083 | 16.6518 | 15 | 89 | 89 | 0.56889 | 63.6024 | 41.5822 | 249.4855 | 0 | 0 | 0 | 0 | 0.22112 | 0.36459 | 0.29448 | 0.051874 | 0.39763 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 63.6024 | 30.8198 | 30.8198 | 30.8198 | 30.8198 | 31.0409 | 31.1843 | 31.1142 | 30.8716 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 17 | 4745 | 15 | 15 | 17.0083 | 16.6518 | 15 | 87 | 87 | 13.7868 | 205.9646 | 32.6461 | 263.0057 | 0 | 0 | 0 | 0 | 3.614 | 9.3851 | 9.6586 | 4.2742 | 8.0354 | 100.8681 | 100.8681 | 100.8681 | 100.8681 | 105.1306 | 111.9374 | 112.2599 | 105.9093 | 205.9646 | 100.8681 | 100.8681 | 100.8681 | 100.8681 | 108.7446 | 121.3225 | 121.9185 | 110.1835 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 17 | 18 | 4746 | 14.5 | 14.5 | 17.0083 | 16.6518 | 15 | 91 | 91 | 6.5521 | 133.0743 | 23.4497 | 274.9549 | 0 | 0 | 0 | 0 | 0.67181 | 4.3471 | 5.476 | 3.397 | 2.9257 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 133.0743 | 66.8843 | 66.8843 | 66.8843 | 66.8843 | 67.5561 | 71.2315 | 72.3603 | 70.2814 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 19 | 4747 | 13.8 | 13.8 | 17.0083 | 16.6518 | 15 | 92 | 92 | 0.36659 | 21.8903 | 14.4079 | 286.2354 | 0.029048 | 0 | 0 | 0 | 0 | 0.21638 | 0.33506 | 0.25746 | 0.10972 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 21.8903 | 10.3585 | 10.3294 | 10.3294 | 10.3294 | 10.3294 | 10.5458 | 10.6645 | 10.5869 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 20 | 4748 | 13.8 | 13.8 | 17.0083 | 16.6518 | 15 | 94 | 94 | 0.3592 | 10.9457 | 5.8687 | 297.4835 | 0.097268 | 0 | 0 | 0 | 0 | 0.16741 | 0.33403 | 0.30497 | 0.054306 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 10.9457 | 5.2126 | 5.1153 | 5.1153 | 5.1153 | 5.1153 | 5.2828 | 5.4494 | 5.4203 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 21 | 4749 | 13.6 | 13.6 | 17.0083 | 16.6518 | 15 | 95 | 95 | 4.0847 | 2.9501 | -1.8218 | 309.1664 | 1.8752 | 0 | 0 | 0 | 0 | 1.223 | 3.6047 | 3.8748 | 0.049944 | 2.7961 | 1.6552 | 1.6552 | 1.6552 | 1.6552 | 2.3993 | 3.8484 | 4.0128 | 2.9501 | 4.6713 | 1.6552 | 1.6552 | 1.6552 | 1.6552 | 3.6222 | 7.4531 | 7.8876 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 22 | 4750 | 13.7 | 13.7 | 17.0083 | 16.6518 | 15 | 96 | 96 | 0 | 0 | -8.2886 | 321.6086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 23 | 4751 | 13.7 | 13.7 | 17.0083 | 16.6518 | 15 | 97 | 97 | 0 | 0 | -13.1323 | 334.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 17 | 24 | 4752 | 13.9 | 13.9 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | -15.9773 | 349.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 1 | 4753 | 13.8 | 13.8 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | -16.5618 | 3.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 2 | 4754 | 13.9 | 13.9 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | -14.9992 | 18.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 3 | 4755 | 14 | 14 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | -11.1105 | 31.8593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 4 | 4756 | 14.1 | 14.1 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | -5.4002 | 44.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 5 | 4757 | 14.3 | 14.3 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0 | 0 | 1.7332 | 56.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 6 | 4758 | 14.5 | 14.5 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0.29243 | 7.9644 | 9.898 | 68.2474 | 0.15997 | 0.2861 | 0.24464 | 0.059868 | 0 | 0 | 0 | 0 | 0.035633 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 7.9644 | 3.9896 | 4.1157 | 4.0743 | 3.8895 | 3.8296 | 3.8296 | 3.8296 | 3.8296 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 7 | 4759 | 14.7 | 14.7 | 15.0083 | 16.2049 | 15 | 97 | 97 | 0.58517 | 24.8425 | 18.7346 | 79.455 | 0.21363 | 0.52965 | 0.53541 | 0.22753 | 0 | 0 | 0 | 0 | 0.15752 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 24.8425 | 12.1194 | 12.4355 | 12.4412 | 12.1333 | 11.9058 | 11.9058 | 11.9058 | 11.9058 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 18 | 8 | 4760 | 15.1 | 15.1 | 15.0083 | 16.2049 | 15 | 96 | 96 | 2.3678 | 77.0114 | 27.9006 | 90.9857 | 0.41037 | 1.849 | 2.2045 | 1.2686 | 0 | 0 | 0 | 0 | 0.9886 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 77.0114 | 38.6078 | 40.0464 | 40.4019 | 39.4661 | 38.1975 | 38.1975 | 38.1975 | 38.1975 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 9 | 4761 | 16.9 | 16.9 | 15.0083 | 16.2049 | 15 | 89 | 89 | 35.3923 | 227.2951 | 37.0247 | 103.5914 | 0 | 21.7334 | 31.2737 | 22.4943 | 0.53806 | 0 | 0 | 0 | 19.7049 | 101.9485 | 170.7078 | 200.8912 | 173.1152 | 103.6508 | 101.9485 | 101.9485 | 101.9485 | 227.2951 | 101.9485 | 192.4412 | 232.1648 | 195.6095 | 104.1889 | 101.9485 | 101.9485 | 101.9485 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 10 | 4762 | 17.1 | 17.1 | 15.0083 | 16.2049 | 15 | 81 | 81 | 11.4484 | 231.2444 | 45.6183 | 118.3541 | 0 | 4.7633 | 8.8842 | 7.8008 | 2.1479 | 0 | 0 | 0 | 7.7556 | 108.1916 | 126.0796 | 141.5554 | 137.487 | 116.2578 | 108.1916 | 108.1916 | 108.1916 | 231.2444 | 108.1916 | 130.8429 | 150.4395 | 145.2879 | 118.4057 | 108.1916 | 108.1916 | 108.1916 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 11 | 4763 | 16.9 | 16.9 | 15.0083 | 16.2049 | 15 | 83 | 83 | 3.8187 | 180.0545 | 52.9283 | 136.7444 | 0 | 0.76511 | 2.3505 | 2.559 | 1.2685 | 0 | 0 | 0 | 2.9455 | 90.8414 | 91.1005 | 91.6376 | 91.7082 | 91.2711 | 90.8414 | 90.8414 | 90.8414 | 180.0545 | 90.8414 | 91.8657 | 93.9881 | 94.2672 | 92.5395 | 90.8414 | 90.8414 | 90.8414 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 12 | 4764 | 16.9 | 16.9 | 15.0083 | 16.2049 | 15 | 87 | 87 | 5.3208 | 228.5731 | 57.7842 | 159.9824 | 0 | 0 | 2.1979 | 3.206 | 2.336 | 0.097636 | 0 | 0 | 4.4269 | 113.6968 | 113.6968 | 117.7415 | 119.5966 | 117.9956 | 113.8765 | 113.6968 | 113.6968 | 228.5731 | 113.6968 | 113.6968 | 119.9395 | 122.8026 | 120.3316 | 113.9741 | 113.6968 | 113.6968 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 13 | 4765 | 17.5 | 17.5 | 15.0083 | 16.2049 | 15 | 85 | 85 | 2.8409 | 172.5705 | 58.8602 | 186.7231 | 0 | 0 | 0.51844 | 1.3728 | 1.423 | 0.63965 | 0 | 0 | 2.4295 | 87.0448 | 87.0448 | 87.0448 | 87.0448 | 87.0448 | 87.0448 | 87.0448 | 87.0448 | 172.5705 | 87.0448 | 87.0448 | 87.5632 | 88.4176 | 88.4678 | 87.6844 | 87.0448 | 87.0448 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 14 | 4766 | 19.3 | 19.3 | 15.0083 | 16.2049 | 15 | 69 | 69 | 44.0739 | 352.0107 | 55.771 | 212.1639 | 0 | 0 | 0 | 14.1187 | 22.6351 | 17.8922 | 2.6683 | 0 | 36.9893 | 153.3067 | 153.3067 | 153.3067 | 192.7093 | 216.477 | 203.2404 | 160.7533 | 153.3067 | 352.0107 | 153.3067 | 153.3067 | 153.3067 | 206.8279 | 239.1121 | 221.1326 | 163.4216 | 153.3067 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 15 | 4767 | 19.6 | 19.6 | 15.0083 | 16.2049 | 15 | 71 | 71 | 203.974 | 347.8078 | 49.5252 | 232.9321 | 0 | 0 | 0 | 25.49 | 97.1271 | 111.8686 | 61.0789 | 0 | 160.1922 | 159.2187 | 159.2187 | 159.2187 | 180.4278 | 240.0341 | 252.2998 | 210.0399 | 159.2187 | 347.8078 | 159.2187 | 159.2187 | 159.2187 | 205.9178 | 337.1613 | 364.1684 | 271.1188 | 159.2187 | 508 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 16 | 4768 | 19.1 | 19.1 | 15.0083 | 16.2049 | 15 | 66 | 66 | 27.3814 | 274.9085 | 41.4604 | 249.3231 | 0 | 0 | 0 | 0 | 10.7132 | 17.6036 | 14.1819 | 2.4527 | 19.0915 | 123.557 | 123.557 | 123.557 | 123.557 | 158.935 | 181.6887 | 170.3896 | 131.6567 | 274.9085 | 123.557 | 123.557 | 123.557 | 123.557 | 169.6482 | 199.2922 | 184.5715 | 134.1094 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 17 | 4769 | 18.5 | 18.5 | 15.0083 | 16.2049 | 15 | 75 | 75 | 6.347 | 171.3125 | 32.5302 | 262.8546 | 0 | 0 | 0 | 0 | 1.6795 | 4.3343 | 4.4501 | 1.9591 | 3.6875 | 86.005 | 86.005 | 86.005 | 86.005 | 86.7042 | 87.8095 | 87.8577 | 86.8206 | 171.3125 | 86.005 | 86.005 | 86.005 | 86.005 | 88.3837 | 92.1438 | 92.3078 | 88.7798 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 18 | 18 | 4770 | 18.1 | 18.1 | 15.0083 | 16.2049 | 15 | 75 | 75 | 4.0046 | 106.2199 | 23.3343 | 274.8158 | 0 | 0 | 0 | 0 | 0.41997 | 2.6658 | 3.3501 | 2.0719 | 1.7801 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 106.2199 | 52.6194 | 52.6194 | 52.6194 | 52.6194 | 53.0393 | 55.2852 | 55.9695 | 54.6913 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 19 | 4771 | 17.3 | 17.3 | 15.0083 | 16.2049 | 15 | 77 | 77 | 2.5849 | 57.2319 | 14.2886 | 286.1074 | 0.19926 | 0 | 0 | 0 | 0 | 1.5315 | 2.3651 | 1.8133 | 0.76808 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 57.2319 | 27.9437 | 27.7444 | 27.7444 | 27.7444 | 27.7444 | 29.2759 | 30.1096 | 29.5577 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 20 | 4772 | 16.3 | 16.3 | 15.0083 | 16.2049 | 15 | 87 | 87 | 0.11024 | 5.9836 | 5.7421 | 297.3663 | 0.02964 | 0 | 0 | 0 | 0 | 0.051618 | 0.10264 | 0.093535 | 0.016409 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 5.9836 | 2.8086 | 2.7789 | 2.7789 | 2.7789 | 2.7789 | 2.8305 | 2.8816 | 2.8725 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 21 | 4773 | 16.2 | 16.2 | 15.0083 | 16.2049 | 15 | 86 | 86 | 1.7883 | 1.815 | -1.9581 | 309.0613 | 0.81792 | 0 | 0 | 0 | 0 | 0.53902 | 1.5802 | 1.6957 | 9.185 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 1.815 | 2.7045 | 1.8866 | 1.8866 | 1.8866 | 1.8866 | 2.4256 | 3.4668 | 3.5823 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 22 | 4774 | 15.8 | 15.8 | 15.0083 | 16.2049 | 15 | 90 | 90 | 0 | 0 | -8.4361 | 321.5189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 23 | 4775 | 15.3 | 15.3 | 15.0083 | 16.2049 | 15 | 93 | 93 | 0 | 0 | -13.2907 | 334.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 18 | 24 | 4776 | 15.5 | 15.5 | 16.2792 | 16.2243 | 15 | 91 | 91 | 0 | 0 | -16.1442 | 349.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 1 | 4777 | 15.2 | 15.2 | 16.2792 | 16.2243 | 15 | 91 | 91 | 0 | 0 | -16.7334 | 3.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 2 | 4778 | 15.8 | 15.8 | 16.2792 | 16.2243 | 15 | 90 | 90 | 0 | 0 | -15.1762 | 18.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 3 | 4779 | 16.1 | 16.1 | 16.2792 | 16.2243 | 15 | 88 | 88 | 0 | 0 | -11.2829 | 31.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 4 | 4780 | 16 | 16 | 16.2792 | 16.2243 | 15 | 91 | 91 | 0 | 0 | -5.5656 | 44.8361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 5 | 4781 | 15.9 | 15.9 | 16.2792 | 16.2243 | 15 | 94 | 94 | 0 | 0 | 1.5753 | 56.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 6 | 4782 | 16.2 | 16.2 | 16.2792 | 16.2243 | 15 | 94 | 94 | 0.57581 | 10.9313 | 9.7466 | 68.3421 | 0.31433 | 0.56322 | 0.48219 | 0.11869 | 0 | 0 | 0 | 0 | 0.068746 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 10.9313 | 5.6848 | 5.9337 | 5.8527 | 5.4892 | 5.3705 | 5.3705 | 5.3705 | 5.3705 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 7 | 4783 | 16 | 16 | 16.2792 | 16.2243 | 15 | 96 | 96 | 0.34375 | 18.9083 | 18.5876 | 79.5607 | 0.12503 | 0.31106 | 0.31487 | 0.13423 | 0 | 0 | 0 | 0 | 0.091746 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 18.9083 | 9.1005 | 9.2865 | 9.2903 | 9.1097 | 8.9754 | 8.9754 | 8.9754 | 8.9754 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 19 | 8 | 4784 | 16.3 | 16.3 | 16.2792 | 16.2243 | 15 | 96 | 96 | 0.59788 | 38.7516 | 27.7551 | 91.1013 | 0.10268 | 0.46669 | 0.55732 | 0.32147 | 0 | 0 | 0 | 0 | 0.24836 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 38.7516 | 18.6785 | 19.0425 | 19.1331 | 18.8973 | 18.5758 | 18.5758 | 18.5758 | 18.5758 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 9 | 4785 | 16.6 | 16.6 | 16.2792 | 16.2243 | 15 | 93 | 93 | 1.3407 | 77.2562 | 36.8767 | 103.7149 | 0 | 0.82266 | 1.1862 | 0.85491 | 0.022804 | 0 | 0 | 0 | 0.74383 | 37.761 | 37.761 | 37.761 | 37.761 | 37.761 | 37.761 | 37.761 | 37.761 | 77.2562 | 37.761 | 38.5837 | 38.9473 | 38.6159 | 37.7838 | 37.761 | 37.761 | 37.761 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 10 | 4786 | 16.1 | 16.1 | 16.2792 | 16.2243 | 15 | 95 | 95 | 0.46599 | 55.6852 | 45.4632 | 118.4784 | 0 | 0.19357 | 0.36213 | 0.31856 | 0.088378 | 0 | 0 | 0 | 0.31484 | 26.8138 | 26.8138 | 26.8138 | 26.8138 | 26.8138 | 26.8138 | 26.8138 | 26.8138 | 55.6852 | 26.8138 | 27.0074 | 27.176 | 27.1324 | 26.9022 | 26.8138 | 26.8138 | 26.8138 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 11 | 4787 | 16.8 | 16.8 | 16.2792 | 16.2243 | 15 | 94 | 94 | 1.9652 | 129.4875 | 52.7619 | 136.8486 | 0 | 0.39195 | 1.2115 | 1.3214 | 0.65721 | 0 | 0 | 0 | 1.5125 | 64.3597 | 64.3597 | 64.3597 | 64.3597 | 64.3597 | 64.3597 | 64.3597 | 64.3597 | 129.4875 | 64.3597 | 64.7517 | 65.5712 | 65.6811 | 65.0169 | 64.3597 | 64.3597 | 64.3597 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 12 | 4788 | 18.6 | 18.6 | 16.2792 | 16.2243 | 15 | 84 | 84 | 27.3105 | 327.3223 | 57.6077 | 160.0227 | 0 | 0 | 11.3029 | 16.5178 | 12.0568 | 0.53312 | 0 | 0 | 22.6777 | 153.3076 | 153.3076 | 176.4426 | 187.1165 | 177.9857 | 154.3988 | 153.3076 | 153.3076 | 327.3223 | 153.3076 | 153.3076 | 187.7454 | 203.6343 | 190.0425 | 154.932 | 153.3076 | 153.3076 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 13 | 4789 | 16.9 | 16.9 | 16.2792 | 16.2243 | 15 | 87 | 87 | 58.4385 | 369.1181 | 58.6853 | 186.6609 | 0 | 0 | 10.6957 | 28.3679 | 29.4225 | 13.2418 | 0 | 0 | 49.8819 | 160.5683 | 160.5683 | 184.9888 | 225.3379 | 227.7458 | 190.8021 | 160.5683 | 160.5683 | 369.1181 | 160.5683 | 160.5683 | 195.6846 | 253.7058 | 257.1684 | 204.044 | 160.5683 | 160.5683 | 419 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 14 | 4790 | 16 | 16 | 16.2792 | 16.2243 | 15 | 95 | 95 | 1.7881 | 134.5022 | 55.6118 | 212.0231 | 0 | 0 | 0 | 0.57648 | 0.92307 | 0.72893 | 0.1078 | 0 | 1.4978 | 66.994 | 66.994 | 66.994 | 66.994 | 66.994 | 66.994 | 66.994 | 66.994 | 134.5022 | 66.994 | 66.994 | 66.994 | 67.5704 | 67.917 | 67.7229 | 67.1018 | 66.994 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 15 | 4791 | 17.4 | 17.4 | 16.2792 | 16.2243 | 15 | 91 | 91 | 51.574 | 334.5827 | 49.3845 | 232.7649 | 0 | 0 | 0 | 6.5411 | 24.6964 | 28.3849 | 15.4459 | 0 | 40.4173 | 147.5869 | 147.5869 | 147.5869 | 162.3221 | 203.2205 | 211.5295 | 182.3818 | 147.5869 | 334.5827 | 147.5869 | 147.5869 | 147.5869 | 168.8632 | 227.9169 | 239.9144 | 197.8277 | 147.5869 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 16 | 4792 | 16.3 | 16.3 | 16.2792 | 16.2243 | 15 | 83 | 83 | 22.0585 | 265.6591 | 41.3325 | 249.1584 | 0 | 0 | 0 | 0 | 8.6889 | 14.228 | 11.4326 | 1.9401 | 15.3409 | 128.3058 | 128.3058 | 128.3058 | 128.3058 | 140.1064 | 147.6292 | 143.8327 | 130.9407 | 265.6591 | 128.3058 | 128.3058 | 128.3058 | 128.3058 | 148.7952 | 161.8572 | 155.2652 | 132.8808 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 17 | 4793 | 17.9 | 17.9 | 16.2792 | 16.2243 | 15 | 77 | 77 | 273.5302 | 244.6068 | 32.4085 | 262.7009 | 0 | 0 | 0 | 0 | 73.0753 | 187.4025 | 191.9518 | 84.0584 | 158.3932 | 120.6194 | 120.6194 | 120.6194 | 120.6194 | 164.2737 | 232.5714 | 235.2892 | 170.8349 | 244.6068 | 120.6194 | 120.6194 | 120.6194 | 120.6194 | 237.349 | 419.9739 | 427.241 | 254.8933 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 19 | 18 | 4794 | 18.1 | 18.1 | 16.2792 | 16.2243 | 15 | 68 | 68 | 324.4126 | 178.4653 | 23.213 | 274.6741 | 0 | 0 | 0 | 0 | 34.7966 | 216.7014 | 271.6655 | 167.4916 | 143.5347 | 95.7268 | 95.7268 | 95.7268 | 95.7268 | 109.7843 | 183.2717 | 205.4765 | 163.3915 | 178.4653 | 95.7268 | 95.7268 | 95.7268 | 95.7268 | 144.5808 | 399.9731 | 477.142 | 330.8831 | 322 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 19 | 4795 | 18.4 | 18.4 | 16.2792 | 16.2243 | 15 | 68 | 68 | 493.1414 | 96.5809 | 14.1634 | 285.977 | 36.9319 | 0 | 0 | 0 | 0 | 293.294 | 451.7123 | 345.5236 | 145.4191 | 68.9347 | 61.8041 | 61.8041 | 61.8041 | 61.8041 | 118.4316 | 149.0181 | 128.5158 | 96.5809 | 105.8666 | 61.8041 | 61.8041 | 61.8041 | 61.8041 | 411.7256 | 600.7304 | 474.0395 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 20 | 4796 | 14.5 | 14.5 | 16.2792 | 16.2243 | 15 | 85 | 85 | 16.7799 | 53.5432 | 5.6095 | 297.2471 | 4.4783 | 0 | 0 | 0 | 0 | 7.8935 | 15.6414 | 14.2268 | 2.4568 | 31.8719 | 27.0571 | 27.0571 | 27.0571 | 27.0571 | 35.5437 | 43.8737 | 42.3528 | 53.5432 | 36.3502 | 27.0571 | 27.0571 | 27.0571 | 27.0571 | 43.4372 | 59.5151 | 56.5796 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 21 | 4797 | 13.4 | 13.4 | 16.2792 | 16.2243 | 15 | 96 | 96 | 1.4315 | 1.32 | -2.1005 | 308.9547 | 0.65223 | 0 | 0 | 0 | 0 | 0.43439 | 1.2665 | 1.3568 | 6.68 | 1.9119 | 1.4106 | 1.4106 | 1.4106 | 1.4106 | 1.7445 | 2.384 | 2.4534 | 1.32 | 2.5641 | 1.4106 | 1.4106 | 1.4106 | 1.4106 | 2.1788 | 3.6506 | 3.8102 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 22 | 4798 | 13.6 | 13.6 | 16.2792 | 16.2243 | 15 | 94 | 94 | 0 | 0 | -8.5897 | 321.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 23 | 4799 | 13.8 | 13.8 | 16.2792 | 16.2243 | 15 | 96 | 96 | 0 | 0 | -13.4553 | 334.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 19 | 24 | 4800 | 13.4 | 13.4 | 16.0542 | 16.2501 | 15 | 96 | 96 | 0 | 0 | -16.3174 | 349.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 1 | 4801 | 14 | 14 | 16.0542 | 16.2501 | 15 | 91 | 91 | 0 | 0 | -16.9109 | 3.6127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 2 | 4802 | 13.6 | 13.6 | 16.0542 | 16.2501 | 15 | 92 | 92 | 0 | 0 | -15.3586 | 18.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 3 | 4803 | 13.9 | 13.9 | 16.0542 | 16.2501 | 15 | 91 | 91 | 0 | 0 | -11.4601 | 31.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 4 | 4804 | 13 | 13 | 16.0542 | 16.2501 | 15 | 94 | 94 | 0 | 0 | -5.7354 | 44.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 5 | 4805 | 13 | 13 | 16.0542 | 16.2501 | 15 | 92 | 92 | 0 | 3 | 1.4134 | 56.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 6 | 4806 | 13.2 | 13.2 | 16.0542 | 16.2501 | 15 | 89 | 89 | 3.8944 | 27.545 | 9.5916 | 68.4419 | 2.1211 | 3.8083 | 3.2646 | 0.80859 | 0 | 0 | 0 | 0 | 0.45504 | 68.3511 | 114.3873 | 99.553 | 32.5379 | 10.4748 | 10.4748 | 10.4748 | 10.4748 | 27.545 | 70.4722 | 118.1956 | 102.8176 | 33.3465 | 10.4748 | 10.4748 | 10.4748 | 10.4748 | 28 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 7 | 4807 | 14.1 | 14.1 | 16.0542 | 16.2501 | 15 | 84 | 84 | 9.3141 | 86.5361 | 18.4372 | 79.6718 | 3.3746 | 8.4259 | 8.5414 | 3.6535 | 0 | 0 | 0 | 0 | 2.4639 | 76.3688 | 135.4998 | 136.8524 | 79.6344 | 36.866 | 36.866 | 36.866 | 36.866 | 86.5361 | 79.7433 | 143.9256 | 145.3938 | 83.2879 | 36.866 | 36.866 | 36.866 | 36.866 | 89 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 20 | 8 | 4808 | 15.1 | 15.1 | 16.0542 | 16.2501 | 15 | 76 | 76 | 25.6125 | 161.4165 | 27.6062 | 91.2226 | 4.3563 | 19.9831 | 23.9041 | 13.8224 | 0 | 0 | 0 | 0 | 10.5835 | 88.0704 | 153.7496 | 170.2294 | 127.8562 | 69.7611 | 69.7611 | 69.7611 | 69.7611 | 161.4165 | 92.4267 | 173.7327 | 194.1335 | 141.6786 | 69.7611 | 69.7611 | 69.7611 | 69.7611 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 9 | 4809 | 16.3 | 16.3 | 16.0542 | 16.2501 | 15 | 66 | 66 | 263.213 | 235.4978 | 36.7252 | 103.8444 | 0 | 161.3738 | 233.1939 | 168.4122 | 4.9769 | 0 | 0 | 0 | 145.5022 | 116.9877 | 210.1364 | 251.5926 | 214.1991 | 119.8605 | 116.9877 | 116.9877 | 116.9877 | 235.4978 | 116.9877 | 371.5103 | 484.7866 | 382.6113 | 124.8374 | 116.9877 | 116.9877 | 116.9877 | 381 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 10 | 4810 | 13.7 | 13.7 | 16.0542 | 16.2501 | 15 | 84 | 84 | 85.3276 | 300.5094 | 45.3042 | 118.6092 | 0 | 35.3831 | 66.4043 | 58.5268 | 16.3651 | 0 | 0 | 0 | 57.4906 | 134.5903 | 189.8099 | 238.2223 | 225.9285 | 160.13 | 134.5903 | 134.5903 | 134.5903 | 300.5094 | 134.5903 | 225.193 | 304.6266 | 284.4553 | 176.4951 | 134.5903 | 134.5903 | 134.5903 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 11 | 4811 | 14.9 | 14.9 | 16.0542 | 16.2501 | 15 | 87 | 87 | 10.2031 | 256.1652 | 52.591 | 136.9592 | 0 | 2.0251 | 6.3001 | 6.8846 | 3.4362 | 0 | 0 | 0 | 7.8348 | 122.0153 | 128.7073 | 142.8344 | 144.766 | 133.3706 | 122.0153 | 122.0153 | 122.0153 | 256.1652 | 122.0153 | 130.7323 | 149.1345 | 151.6507 | 136.8068 | 122.0153 | 122.0153 | 122.0153 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 12 | 4812 | 16 | 16 | 16.0542 | 16.2501 | 15 | 83 | 83 | 120.8945 | 374.8176 | 57.4257 | 160.0685 | 0 | 0 | 50.1266 | 73.4005 | 53.6775 | 2.5109 | 0 | 0 | 100.1824 | 162.309 | 162.309 | 240.89 | 277.3755 | 246.4566 | 166.2452 | 162.309 | 162.309 | 374.8176 | 162.309 | 162.309 | 291.0166 | 350.776 | 300.134 | 168.756 | 162.309 | 162.309 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 13 | 4813 | 14.2 | 14.2 | 16.0542 | 16.2501 | 15 | 86 | 86 | 6.6602 | 255.3261 | 58.5043 | 186.6021 | 0 | 0 | 1.2224 | 3.248 | 3.371 | 1.5193 | 0 | 0 | 5.6739 | 126.2525 | 126.2525 | 128.9263 | 133.3573 | 133.6263 | 129.5758 | 126.2525 | 126.2525 | 255.3261 | 126.2525 | 126.2525 | 130.1487 | 136.6053 | 136.9973 | 131.0951 | 126.2525 | 126.2525 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 14 | 4814 | 11.8 | 11.8 | 16.0542 | 16.2501 | 15 | 84 | 84 | 8.8854 | 270.5721 | 55.4463 | 211.8829 | 0 | 0 | 0 | 2.8833 | 4.6113 | 3.6381 | 0.53372 | 0 | 7.4279 | 132.9559 | 132.9559 | 132.9559 | 139.1247 | 142.8217 | 140.7395 | 134.0978 | 132.9559 | 270.5721 | 132.9559 | 132.9559 | 132.9559 | 142.0079 | 147.433 | 144.3776 | 134.6315 | 132.9559 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 15 | 4815 | 14.4 | 14.4 | 16.0542 | 16.2501 | 15 | 78 | 78 | 50.0836 | 332.8379 | 49.2374 | 232.5963 | 0 | 0 | 0 | 6.4466 | 24.1207 | 27.6652 | 15.0038 | 0 | 39.1621 | 146.8462 | 146.8462 | 146.8462 | 161.6969 | 202.4117 | 210.5769 | 181.4096 | 146.8462 | 332.8379 | 146.8462 | 146.8462 | 146.8462 | 168.1435 | 226.5323 | 238.2421 | 196.4134 | 146.8462 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 16 | 4816 | 14.1 | 14.1 | 16.0542 | 16.2501 | 15 | 84 | 84 | 7.6877 | 216.6677 | 41.1985 | 248.9914 | 0 | 0 | 0 | 0 | 3.049 | 4.9755 | 3.9874 | 0.66354 | 5.3323 | 107.6976 | 107.6976 | 107.6976 | 107.6976 | 111.4805 | 113.8707 | 112.6448 | 108.5209 | 216.6677 | 107.6976 | 107.6976 | 107.6976 | 107.6976 | 114.5295 | 118.8461 | 116.6321 | 109.1844 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 17 | 4817 | 16.5 | 16.5 | 16.0542 | 16.2501 | 15 | 60 | 60 | 477.6312 | 193.3672 | 32.2808 | 262.5448 | 0 | 0 | 0 | 0 | 128.8425 | 328.3366 | 335.4955 | 146.1258 | 275.6328 | 111.672 | 111.672 | 111.672 | 111.672 | 151.7406 | 213.7809 | 216.0073 | 157.1155 | 193.3672 | 111.672 | 111.672 | 111.672 | 111.672 | 280.5831 | 542.1175 | 551.5028 | 303.2412 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 20 | 18 | 4818 | 15.6 | 15.6 | 16.0542 | 16.2501 | 15 | 61 | 61 | 663.9494 | 107.6677 | 23.0859 | 274.53 | 0 | 0 | 0 | 0 | 72.833 | 445.0656 | 556.5848 | 342.0641 | 292.3323 | 80.8171 | 80.8171 | 80.8171 | 80.8171 | 91.3403 | 145.122 | 161.2347 | 130.2399 | 107.6677 | 80.8171 | 80.8171 | 80.8171 | 80.8171 | 164.1734 | 590.1876 | 717.8195 | 472.304 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 19 | 4819 | 15.2 | 15.2 | 16.0542 | 16.2501 | 15 | 59 | 59 | 485.7765 | 96.8847 | 14.0324 | 285.8444 | 35.2948 | 0 | 0 | 0 | 0 | 290.0437 | 445.4785 | 339.958 | 142.1153 | 68.5288 | 61.5936 | 61.5936 | 61.5936 | 61.5936 | 118.5858 | 149.128 | 128.3937 | 96.8847 | 103.8236 | 61.5936 | 61.5936 | 61.5936 | 61.5936 | 408.6295 | 594.6065 | 468.3518 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 20 | 4820 | 14.2 | 14.2 | 16.0542 | 16.2501 | 15 | 64 | 64 | 400.2144 | 53.4073 | 5.4711 | 297.126 | 106.0084 | 0 | 0 | 0 | 0 | 189.1591 | 373.5198 | 339.0776 | 57.5927 | 54.173 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 70.2837 | 106.0041 | 99.3309 | 53.4073 | 160.1814 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 259.4428 | 479.5239 | 438.4085 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 21 | 4821 | 13.4 | 13.4 | 16.0542 | 16.2501 | 15 | 69 | 69 | 1.4958 | 1.32 | -2.249 | 308.8466 | 0.67889 | 0 | 0 | 0 | 0 | 0.457 | 1.3252 | 1.4171 | 6.68 | 1.9193 | 1.4108 | 1.4108 | 1.4108 | 1.4108 | 1.7531 | 2.4034 | 2.4722 | 1.32 | 2.5982 | 1.4108 | 1.4108 | 1.4108 | 1.4108 | 2.2101 | 3.7285 | 3.8893 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 22 | 4822 | 12.7 | 12.7 | 16.0542 | 16.2501 | 15 | 74 | 74 | 0 | 0 | -8.7496 | 321.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 23 | 4823 | 11.9 | 11.9 | 16.0542 | 16.2501 | 15 | 81 | 81 | 0 | 0 | -13.626 | 334.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 20 | 24 | 4824 | 11.7 | 11.7 | 14.0208 | 15.6861 | 15 | 84 | 84 | 0 | 0 | -16.4966 | 348.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 1 | 4825 | 12.1 | 12.1 | 14.0208 | 15.6861 | 15 | 84 | 84 | 0 | 0 | -17.0942 | 3.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 2 | 4826 | 12.2 | 12.2 | 14.0208 | 15.6861 | 15 | 85 | 85 | 0 | 0 | -15.5463 | 18.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 3 | 4827 | 13.2 | 13.2 | 14.0208 | 15.6861 | 15 | 77 | 77 | 0 | 0 | -11.6422 | 32.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 4 | 4828 | 13.5 | 13.5 | 14.0208 | 15.6861 | 15 | 72 | 72 | 0 | 0 | -5.9094 | 44.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 5 | 4829 | 12.7 | 12.7 | 14.0208 | 15.6861 | 15 | 80 | 80 | 0 | 0 | 1.2477 | 57.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 6 | 4830 | 12.9 | 12.9 | 14.0208 | 15.6861 | 15 | 81 | 81 | 3.2484 | 24.629 | 9.4331 | 68.5468 | 1.765 | 3.1757 | 2.7261 | 0.67959 | 0 | 0 | 0 | 0 | 0.37103 | 56.2303 | 93.4751 | 81.6045 | 27.5721 | 9.6298 | 9.6298 | 9.6298 | 9.6298 | 24.629 | 57.9953 | 96.6509 | 84.3307 | 28.2517 | 9.6298 | 9.6298 | 9.6298 | 9.6298 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 7 | 4831 | 12.9 | 12.9 | 14.0208 | 15.6861 | 15 | 81 | 81 | 1.5014 | 38.6065 | 18.2836 | 79.7882 | 0.5417 | 1.3578 | 1.3785 | 0.5917 | 0 | 0 | 0 | 0 | 0.3935 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 38.6065 | 19.516 | 20.332 | 20.3527 | 19.566 | 18.9743 | 18.9743 | 18.9743 | 18.9743 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 21 | 8 | 4832 | 12.7 | 12.7 | 14.0208 | 15.6861 | 15 | 86 | 86 | 1.2591 | 55.4826 | 27.4541 | 91.3496 | 0.21195 | 0.98183 | 1.1766 | 0.68209 | 0 | 0 | 0 | 0 | 0.51743 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 55.4826 | 27.2313 | 28.0012 | 28.1959 | 27.7014 | 27.0194 | 27.0194 | 27.0194 | 27.0194 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 9 | 4833 | 13.1 | 13.1 | 14.0208 | 15.6861 | 15 | 81 | 81 | 1.0645 | 68.4138 | 36.5703 | 103.98 | 0 | 0.652 | 0.94432 | 0.68347 | 0.022247 | 0 | 0 | 0 | 0.5862 | 33.2623 | 33.2623 | 33.2623 | 33.2623 | 33.2623 | 33.2623 | 33.2623 | 33.2623 | 68.4138 | 33.2623 | 33.9143 | 34.2066 | 33.9458 | 33.2846 | 33.2623 | 33.2623 | 33.2623 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 10 | 4834 | 12.1 | 12.1 | 14.0208 | 15.6861 | 15 | 91 | 91 | 1.5938 | 101.9293 | 45.1414 | 118.7461 | 0 | 0.65964 | 1.2421 | 1.097 | 0.30923 | 0 | 0 | 0 | 1.0707 | 50.2012 | 50.2012 | 50.2012 | 50.2012 | 50.2012 | 50.2012 | 50.2012 | 50.2012 | 101.9293 | 50.2012 | 50.8608 | 51.4433 | 51.2981 | 50.5104 | 50.2012 | 50.2012 | 50.2012 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 11 | 4835 | 12.8 | 12.8 | 14.0208 | 15.6861 | 15 | 90 | 90 | 4.7615 | 199.3524 | 52.4156 | 137.076 | 0 | 0.94004 | 2.9446 | 3.2243 | 1.6152 | 0 | 0 | 0 | 3.6476 | 99.0049 | 100.6089 | 104.0295 | 104.5067 | 101.7611 | 99.0049 | 99.0049 | 99.0049 | 199.3524 | 99.0049 | 101.549 | 106.9741 | 107.731 | 103.3763 | 99.0049 | 99.0049 | 99.0049 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 12 | 4836 | 12.8 | 12.8 | 14.0208 | 15.6861 | 15 | 91 | 91 | 2.1427 | 145.2281 | 57.2385 | 160.1197 | 0 | 0 | 0.89005 | 1.3061 | 0.95701 | 0.047344 | 0 | 0 | 1.7719 | 72.5569 | 72.5569 | 72.5569 | 72.5569 | 72.5569 | 72.5569 | 72.5569 | 72.5569 | 145.2281 | 72.5569 | 72.5569 | 73.4469 | 73.8629 | 73.5139 | 72.6042 | 72.5569 | 72.5569 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 13 | 4837 | 12.9 | 12.9 | 14.0208 | 15.6861 | 15 | 92 | 92 | 3.3509 | 186.1511 | 58.3173 | 186.5467 | 0 | 0 | 0.61662 | 1.6418 | 1.7052 | 0.76976 | 0 | 0 | 2.8489 | 94.3201 | 94.3201 | 94.3201 | 94.3201 | 94.3201 | 94.3201 | 94.3201 | 94.3201 | 186.1511 | 94.3201 | 94.3201 | 94.9368 | 95.9619 | 96.0254 | 95.0899 | 94.3201 | 94.3201 | 189 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 14 | 4838 | 13 | 13 | 14.0208 | 15.6861 | 15 | 96 | 96 | 2.2808 | 151.0973 | 55.2744 | 211.7435 | 0 | 0 | 0 | 0.74496 | 1.1901 | 0.93811 | 0.13658 | 0 | 1.9027 | 75.6745 | 75.6745 | 75.6745 | 75.6745 | 75.6745 | 75.6745 | 75.6745 | 75.6745 | 151.0973 | 75.6745 | 75.6745 | 75.6745 | 76.4194 | 76.8646 | 76.6126 | 75.811 | 75.6745 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 15 | 4839 | 13.8 | 13.8 | 14.0208 | 15.6861 | 15 | 95 | 95 | 2.5068 | 148.0444 | 49.0841 | 232.4266 | 0 | 0 | 0 | 0.32746 | 1.2144 | 1.3899 | 0.75129 | 0 | 1.9556 | 74.0565 | 74.0565 | 74.0565 | 74.0565 | 74.0565 | 74.0565 | 74.0565 | 74.0565 | 148.0444 | 74.0565 | 74.0565 | 74.0565 | 74.384 | 75.2709 | 75.4465 | 74.8078 | 74.0565 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 16 | 4840 | 14.6 | 14.6 | 14.0208 | 15.6861 | 15 | 94 | 94 | 2.9387 | 141.9673 | 41.0585 | 248.8224 | 0 | 0 | 0 | 0 | 1.1736 | 1.9086 | 1.5255 | 0.24878 | 2.0327 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 141.9673 | 70.8892 | 70.8892 | 70.8892 | 70.8892 | 72.0629 | 72.7978 | 72.4147 | 71.138 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 17 | 4841 | 15.4 | 15.4 | 14.0208 | 15.6861 | 15 | 93 | 93 | 21.3954 | 218.6971 | 32.1472 | 262.3863 | 0 | 0 | 0 | 0 | 5.8282 | 14.7585 | 15.0435 | 6.5162 | 12.3029 | 106.1135 | 106.1135 | 106.1135 | 106.1135 | 112.5192 | 122.3344 | 122.6476 | 113.2754 | 218.6971 | 106.1135 | 106.1135 | 106.1135 | 106.1135 | 118.3475 | 137.0929 | 137.691 | 119.7915 | 231 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 18 | 4842 | 15.7 | 15.7 | 14.0208 | 15.6861 | 15 | 87 | 87 | 171.4735 | 196.8831 | 22.953 | 274.3836 | 0 | 0 | 0 | 0 | 19.2358 | 115.3571 | 143.9038 | 88.1536 | 75.1169 | 97.16 | 97.16 | 97.16 | 97.16 | 109.026 | 168.3203 | 185.9299 | 151.5393 | 196.8831 | 97.16 | 97.16 | 97.16 | 97.16 | 128.2618 | 283.6775 | 329.8338 | 239.6929 | 272 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 19 | 4843 | 15.5 | 15.5 | 14.0208 | 15.6861 | 15 | 84 | 84 | 57.5121 | 125.3132 | 13.8955 | 285.7097 | 4.0479 | 0 | 0 | 0 | 0 | 34.4755 | 52.8036 | 40.2001 | 16.6868 | 64.482 | 61.0768 | 61.0768 | 61.0768 | 61.0768 | 90.0782 | 105.4961 | 94.8938 | 125.3132 | 68.5298 | 61.0768 | 61.0768 | 61.0768 | 61.0768 | 124.5537 | 158.2997 | 135.0938 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 20 | 4844 | 14.7 | 14.7 | 14.0208 | 15.6861 | 15 | 87 | 87 | 49.2122 | 60.0457 | 5.3267 | 297.0031 | 12.9349 | 0 | 0 | 0 | 0 | 23.3717 | 45.9875 | 41.6645 | 6.9543 | 42.5311 | 31.0242 | 31.0242 | 31.0242 | 31.0242 | 51.8157 | 71.9348 | 68.089 | 60.0457 | 55.4661 | 31.0242 | 31.0242 | 31.0242 | 31.0242 | 75.1874 | 117.9223 | 109.7535 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 21 | 4845 | 13.6 | 13.6 | 14.0208 | 15.6861 | 15 | 94 | 94 | 0.94527 | 0.495 | -2.4035 | 308.7372 | 0.42734 | 0 | 0 | 0 | 0 | 0.2908 | 0.83858 | 0.89514 | 2.505 | 0.71879 | 0.52992 | 0.52992 | 0.52992 | 0.52992 | 0.65844 | 0.90055 | 0.92554 | 0.495 | 1.1461 | 0.52992 | 0.52992 | 0.52992 | 0.52992 | 0.94924 | 1.7391 | 1.8207 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 22 | 4846 | 13.4 | 13.4 | 14.0208 | 15.6861 | 15 | 96 | 96 | 0 | 0 | -8.9155 | 321.2448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 23 | 4847 | 13.3 | 13.3 | 14.0208 | 15.6861 | 15 | 96 | 96 | 0 | 0 | -13.803 | 334.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 21 | 24 | 4848 | 13.3 | 13.3 | 13.425 | 15.0111 | 15 | 96 | 96 | 0 | 0 | -16.6819 | 348.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 1 | 4849 | 13.3 | 13.3 | 13.425 | 15.0111 | 15 | 96 | 96 | 0 | 0 | -17.2834 | 3.5956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 2 | 4850 | 13.2 | 13.2 | 13.425 | 15.0111 | 15 | 94 | 94 | 0 | 0 | -15.7393 | 18.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 3 | 4851 | 13 | 13 | 13.425 | 15.0111 | 15 | 94 | 94 | 0 | 0 | -11.829 | 32.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 4 | 4852 | 12.6 | 12.6 | 13.425 | 15.0111 | 15 | 94 | 94 | 0 | 0 | -6.0877 | 45.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 5 | 4853 | 12.6 | 12.6 | 13.425 | 15.0111 | 15 | 95 | 95 | 0 | 0 | 1.0783 | 57.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 6 | 4854 | 12.9 | 12.9 | 13.425 | 15.0111 | 15 | 94 | 94 | 2.6387 | 21.7058 | 9.2712 | 68.6568 | 1.4301 | 2.5789 | 2.217 | 0.55641 | 0 | 0 | 0 | 0 | 0.29425 | 44.7698 | 73.7057 | 64.5898 | 22.7622 | 8.7473 | 8.7473 | 8.7473 | 8.7473 | 21.7058 | 46.1999 | 76.2846 | 66.8069 | 23.3186 | 8.7473 | 8.7473 | 8.7473 | 8.7473 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 7 | 4855 | 13.2 | 13.2 | 13.425 | 15.0111 | 15 | 87 | 87 | 3.1554 | 55.181 | 18.1267 | 79.9099 | 1.1334 | 2.8525 | 2.9006 | 1.2496 | 0 | 0 | 0 | 0 | 0.81904 | 34.436 | 47.1731 | 47.5296 | 35.2967 | 26.0382 | 26.0382 | 26.0382 | 26.0382 | 55.181 | 35.5694 | 50.0256 | 50.4302 | 36.5463 | 26.0382 | 26.0382 | 26.0382 | 26.0382 | 56 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 22 | 8 | 4856 | 14.1 | 14.1 | 13.425 | 15.0111 | 15 | 80 | 80 | 66.3516 | 178.8871 | 27.2988 | 91.4822 | 11.0476 | 51.7114 | 62.0833 | 36.0877 | 0 | 0 | 0 | 0 | 27.1129 | 102.558 | 184.8697 | 205.8646 | 153.2442 | 80.1954 | 80.1954 | 80.1954 | 80.1954 | 178.8871 | 113.6057 | 236.5811 | 267.9479 | 189.3319 | 80.1954 | 80.1954 | 80.1954 | 80.1954 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 9 | 4857 | 16 | 16 | 13.425 | 15.0111 | 15 | 75 | 75 | 481.3849 | 182.9382 | 36.4121 | 104.1214 | 0 | 294.5552 | 427.6285 | 310.2029 | 11.0646 | 0 | 0 | 0 | 264.0618 | 109.1768 | 193.7926 | 232.0201 | 198.2876 | 112.3552 | 109.1768 | 109.1768 | 109.1768 | 182.9382 | 109.1768 | 488.3477 | 659.6486 | 508.4905 | 123.4199 | 109.1768 | 109.1768 | 109.1768 | 447 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 10 | 4858 | 16.6 | 16.6 | 13.425 | 15.0111 | 15 | 69 | 69 | 461.913 | 229.6027 | 44.9748 | 118.8893 | 0 | 190.7809 | 360.4997 | 319.0426 | 90.6947 | 0 | 0 | 0 | 309.3973 | 129.7641 | 196.9618 | 256.7408 | 242.1386 | 161.709 | 129.7641 | 129.7641 | 129.7641 | 229.6027 | 129.7641 | 387.7427 | 617.2405 | 561.1813 | 252.4037 | 129.7641 | 129.7641 | 129.7641 | 539 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 11 | 4859 | 17.3 | 17.3 | 13.425 | 15.0111 | 15 | 66 | 66 | 410.7288 | 280.1353 | 52.2358 | 137.1991 | 0 | 80.6276 | 254.3983 | 279.1459 | 140.3737 | 0 | 0 | 0 | 313.8647 | 145.0894 | 182.3617 | 262.6919 | 274.1322 | 209.981 | 145.0894 | 145.0894 | 145.0894 | 280.1353 | 145.0894 | 262.9893 | 517.0902 | 553.2781 | 350.3546 | 145.0894 | 145.0894 | 145.0894 | 594 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 12 | 4860 | 18.5 | 18.5 | 13.425 | 15.0111 | 15 | 65 | 65 | 339.195 | 328.1267 | 57.0461 | 160.1764 | 0 | 0 | 141.141 | 207.5744 | 152.4135 | 7.9708 | 0 | 0 | 279.8733 | 157.5505 | 157.5505 | 243.8599 | 284.4846 | 250.7531 | 162.4247 | 157.5505 | 157.5505 | 328.1267 | 157.5505 | 157.5505 | 385.0009 | 492.059 | 403.1666 | 170.3956 | 157.5505 | 157.5505 | 608 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 13 | 4861 | 19.2 | 19.2 | 13.425 | 15.0111 | 15 | 67 | 67 | 361.1697 | 329.5803 | 58.1243 | 186.4948 | 0 | 0 | 66.6258 | 177.8 | 184.8213 | 83.5768 | 0 | 0 | 306.4197 | 158.1201 | 158.1201 | 197.0722 | 262.0689 | 266.1738 | 206.9824 | 158.1201 | 158.1201 | 329.5803 | 158.1201 | 158.1201 | 263.698 | 439.8689 | 450.9952 | 290.5592 | 158.1201 | 158.1201 | 636 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 14 | 4862 | 19.6 | 19.6 | 13.425 | 15.0111 | 15 | 67 | 67 | 222.0472 | 365.1651 | 55.0963 | 211.605 | 0 | 0 | 0 | 73.0032 | 116.5056 | 91.7606 | 13.2635 | 0 | 184.8349 | 156.5965 | 156.5965 | 156.5965 | 232.0864 | 277.0707 | 251.4828 | 170.3118 | 156.5965 | 365.1651 | 156.5965 | 156.5965 | 156.5965 | 305.0896 | 393.5763 | 343.2434 | 183.5752 | 156.5965 | 550 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 15 | 4863 | 20.2 | 20.2 | 13.425 | 15.0111 | 15 | 62 | 62 | 473.536 | 262.4684 | 48.9246 | 232.2559 | 0 | 0 | 0 | 62.7707 | 230.769 | 263.586 | 141.9979 | 0 | 368.5316 | 140.0493 | 140.0493 | 140.0493 | 165.2953 | 232.8633 | 246.0621 | 197.1601 | 140.0493 | 262.4684 | 140.0493 | 140.0493 | 140.0493 | 228.066 | 463.6323 | 509.6481 | 339.1579 | 140.0493 | 631 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 16 | 4864 | 19.7 | 19.7 | 13.425 | 15.0111 | 15 | 67 | 67 | 486.8546 | 228.2071 | 40.9124 | 248.6515 | 0 | 0 | 0 | 0 | 195.8152 | 317.3271 | 252.9531 | 40.4026 | 335.7929 | 127.7772 | 127.7772 | 127.7772 | 127.7772 | 195.78 | 237.9787 | 215.6229 | 141.8082 | 228.2071 | 127.7772 | 127.7772 | 127.7772 | 127.7772 | 391.5952 | 555.3058 | 468.576 | 182.2108 | 564 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 17 | 4865 | 18.9 | 18.9 | 13.425 | 15.0111 | 15 | 68 | 68 | 115.2177 | 258.9919 | 32.0078 | 262.2257 | 0 | 0 | 0 | 0 | 31.6975 | 79.7577 | 81.0969 | 34.9306 | 66.0081 | 120.0058 | 120.0058 | 120.0058 | 120.0058 | 156.0272 | 210.6434 | 212.1653 | 159.7014 | 258.9919 | 120.0058 | 120.0058 | 120.0058 | 120.0058 | 187.7247 | 290.401 | 293.2621 | 194.632 | 325 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 18 | 4866 | 18.1 | 18.1 | 13.425 | 15.0111 | 15 | 71 | 71 | 25.2982 | 169.9758 | 22.8143 | 274.2351 | 0 | 0 | 0 | 0 | 2.9019 | 17.0816 | 21.2551 | 12.9777 | 11.0242 | 80.2884 | 80.2884 | 80.2884 | 80.2884 | 86.8726 | 119.0458 | 128.5154 | 109.7343 | 169.9758 | 80.2884 | 80.2884 | 80.2884 | 80.2884 | 89.7745 | 136.1274 | 149.7705 | 122.7119 | 181 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 19 | 4867 | 18 | 18 | 13.425 | 15.0111 | 15 | 72 | 72 | 64.1337 | 125.5514 | 13.7528 | 285.573 | 4.3657 | 0 | 0 | 0 | 0 | 38.6004 | 58.9548 | 44.7744 | 18.4486 | 64.6574 | 61.328 | 61.328 | 61.328 | 61.328 | 90.7657 | 106.2886 | 95.4742 | 125.5514 | 69.023 | 61.328 | 61.328 | 61.328 | 61.328 | 129.3661 | 165.2435 | 140.2485 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 20 | 4868 | 17 | 17 | 13.425 | 15.0111 | 15 | 76 | 76 | 146.3997 | 62.7033 | 5.1764 | 296.8785 | 38.1766 | 0 | 0 | 0 | 0 | 69.866 | 136.9821 | 123.8559 | 20.2967 | 54.2609 | 34.1693 | 34.1693 | 34.1693 | 34.1693 | 70.9384 | 106.2603 | 99.3522 | 62.7033 | 92.4374 | 34.1693 | 34.1693 | 34.1693 | 34.1693 | 140.8044 | 243.2423 | 223.2081 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 21 | 4869 | 16.5 | 16.5 | 13.425 | 15.0111 | 15 | 79 | 79 | 0 | 11 | -2.564 | 308.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 11 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 5.2051 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 22 | 4870 | 16.1 | 16.1 | 13.425 | 15.0111 | 15 | 82 | 82 | 0 | 0 | -9.0875 | 321.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 23 | 4871 | 16.2 | 16.2 | 13.425 | 15.0111 | 15 | 84 | 84 | 0 | 0 | -13.986 | 334.6074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 22 | 24 | 4872 | 15.2 | 15.2 | 16.1667 | 15.2005 | 15 | 91 | 91 | 0 | 0 | -16.8732 | 348.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 1 | 4873 | 14.4 | 14.4 | 16.1667 | 15.2005 | 15 | 96 | 96 | 0 | 0 | -17.4782 | 3.5904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 2 | 4874 | 14.9 | 14.9 | 16.1667 | 15.2005 | 15 | 96 | 96 | 0 | 0 | -15.9375 | 18.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 3 | 4875 | 15.2 | 15.2 | 16.1667 | 15.2005 | 15 | 96 | 96 | 0 | 0 | -12.0205 | 32.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 4 | 4876 | 15.3 | 15.3 | 16.1667 | 15.2005 | 15 | 96 | 96 | 0 | 0 | -6.2701 | 45.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 5 | 4877 | 15.3 | 15.3 | 16.1667 | 15.2005 | 15 | 95 | 95 | 0 | 0 | 0.90522 | 57.2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 6 | 4878 | 15.7 | 15.7 | 16.1667 | 15.2005 | 15 | 95 | 95 | 1.6572 | 16.8198 | 9.106 | 68.7718 | 0.89573 | 1.6191 | 1.394 | 0.35231 | 0 | 0 | 0 | 0 | 0.18017 | 26.1083 | 41.3324 | 36.5949 | 14.6708 | 7.2556 | 7.2556 | 7.2556 | 7.2556 | 16.8198 | 27.004 | 42.9515 | 37.9889 | 15.0231 | 7.2556 | 7.2556 | 7.2556 | 7.2556 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 7 | 4879 | 16.7 | 16.7 | 16.1667 | 15.2005 | 15 | 90 | 90 | 1.9872 | 43.4894 | 17.9667 | 80.037 | 0.71046 | 1.7957 | 1.829 | 0.79093 | 0 | 0 | 0 | 0 | 0.51064 | 22.6757 | 24.7888 | 24.8537 | 22.8324 | 21.2924 | 21.2924 | 21.2924 | 21.2924 | 43.4894 | 23.3862 | 26.5844 | 26.6827 | 23.6233 | 21.2924 | 21.2924 | 21.2924 | 21.2924 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 23 | 8 | 4880 | 17.9 | 17.9 | 16.1667 | 15.2005 | 15 | 83 | 83 | 14.1063 | 144.2698 | 27.1403 | 91.6203 | 2.3216 | 10.9868 | 13.2161 | 7.7036 | 0 | 0 | 0 | 0 | 5.7302 | 77.1816 | 127.704 | 140.702 | 108.5614 | 63.6457 | 63.6457 | 63.6457 | 63.6457 | 144.2698 | 79.5031 | 138.6908 | 153.918 | 116.265 | 63.6457 | 63.6457 | 63.6457 | 63.6457 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 9 | 4881 | 19.5 | 19.5 | 16.1667 | 15.2005 | 15 | 73 | 73 | 131.0459 | 247.4073 | 36.2505 | 104.2688 | 0 | 80.0959 | 116.5701 | 84.7591 | 3.2974 | 0 | 0 | 0 | 71.5927 | 113.6581 | 196.5306 | 234.2692 | 201.3555 | 117.0698 | 113.6581 | 113.6581 | 113.6581 | 247.4073 | 113.6581 | 276.6264 | 350.8393 | 286.1146 | 120.3673 | 113.6581 | 113.6581 | 113.6581 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 10 | 4882 | 20.2 | 20.2 | 16.1667 | 15.2005 | 15 | 71 | 71 | 95.9317 | 299.9423 | 44.8045 | 119.0387 | 0 | 39.5334 | 74.9765 | 66.4993 | 19.0678 | 0 | 0 | 0 | 64.0577 | 134.8965 | 190.3324 | 240.0327 | 228.1455 | 161.6344 | 134.8965 | 134.8965 | 134.8965 | 299.9423 | 134.8965 | 229.8659 | 315.0091 | 294.6449 | 180.7021 | 134.8965 | 134.8965 | 134.8965 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 11 | 4883 | 21.1 | 21.1 | 16.1667 | 15.2005 | 15 | 66 | 66 | 319.9943 | 309.0969 | 52.0517 | 137.3282 | 0 | 62.4336 | 198.5 | 218.2878 | 110.2056 | 0 | 0 | 0 | 243.9031 | 150.8372 | 188.8685 | 271.7531 | 283.8068 | 217.9687 | 150.8372 | 150.8372 | 150.8372 | 309.0969 | 150.8372 | 251.3021 | 470.2531 | 502.0946 | 328.1743 | 150.8372 | 150.8372 | 150.8372 | 553 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 12 | 4884 | 21.1 | 21.1 | 16.1667 | 15.2005 | 15 | 66 | 66 | 17.2952 | 302.762 | 56.8484 | 160.2384 | 0 | 0 | 7.2089 | 10.6269 | 7.8199 | 0.43206 | 0 | 0 | 14.238 | 143.3427 | 143.3427 | 161.4925 | 170.0982 | 163.0309 | 144.4305 | 143.3427 | 143.3427 | 302.762 | 143.3427 | 143.3427 | 168.7014 | 180.7251 | 170.8508 | 144.8625 | 143.3427 | 143.3427 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 13 | 4885 | 21.1 | 21.1 | 16.1667 | 15.2005 | 15 | 67 | 67 | 64.9779 | 369.9923 | 57.9255 | 186.4465 | 0 | 0 | 12.0141 | 32.1415 | 33.4408 | 15.151 | 0 | 0 | 55.0077 | 161.408 | 161.408 | 186.2953 | 227.9891 | 230.6806 | 192.7932 | 161.408 | 161.408 | 369.9923 | 161.408 | 161.408 | 198.3094 | 260.1306 | 264.1214 | 207.9441 | 161.408 | 161.408 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 14 | 4886 | 21.2 | 21.2 | 16.1667 | 15.2005 | 15 | 69 | 69 | 60.6014 | 360.6679 | 54.9119 | 211.4677 | 0 | 0 | 0 | 20.0564 | 31.9772 | 25.1661 | 3.6131 | 0 | 50.3321 | 157.7177 | 157.7177 | 157.7177 | 200.2034 | 225.4553 | 211.0274 | 165.3713 | 157.7177 | 360.6679 | 157.7177 | 157.7177 | 157.7177 | 220.2599 | 257.4325 | 236.1935 | 168.9844 | 157.7177 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 15 | 4887 | 22.4 | 22.4 | 16.1667 | 15.2005 | 15 | 65 | 65 | 352.1294 | 304.6354 | 48.7588 | 232.0845 | 0 | 0 | 0 | 47.3641 | 172.648 | 196.7971 | 105.6651 | 0 | 273.3646 | 147.7412 | 147.7412 | 147.7412 | 174.2583 | 244.399 | 257.919 | 206.8983 | 147.7412 | 304.6354 | 147.7412 | 147.7412 | 147.7412 | 221.6224 | 417.0471 | 454.7161 | 312.5634 | 147.7412 | 578 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 16 | 4888 | 23 | 23 | 16.1667 | 15.2005 | 15 | 61 | 61 | 751.4838 | 141.2263 | 40.7603 | 248.4788 | 0 | 0 | 0 | 0 | 304.4228 | 491.6184 | 390.8306 | 61.0996 | 516.7737 | 114.8767 | 114.8767 | 114.8767 | 114.8767 | 149.0399 | 170.0475 | 158.7368 | 121.7335 | 141.2263 | 114.8767 | 114.8767 | 114.8767 | 114.8767 | 453.4626 | 661.6658 | 549.5674 | 182.8331 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 17 | 4889 | 22.9 | 22.9 | 16.1667 | 15.2005 | 15 | 59 | 59 | 67.744 | 250.3384 | 31.8624 | 262.0629 | 0 | 0 | 0 | 0 | 18.8237 | 47.0642 | 47.7351 | 20.4434 | 38.6616 | 115.6614 | 115.6614 | 115.6614 | 115.6614 | 140.2805 | 177.2157 | 178.0931 | 142.3989 | 250.3384 | 115.6614 | 115.6614 | 115.6614 | 115.6614 | 159.1043 | 224.2799 | 225.8282 | 162.8424 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 23 | 18 | 4890 | 21.4 | 21.4 | 16.1667 | 15.2005 | 15 | 71 | 71 | 101.1881 | 195.1455 | 22.6697 | 274.0844 | 0 | 0 | 0 | 0 | 11.8672 | 68.5786 | 85.1176 | 51.7959 | 43.8545 | 93.3407 | 93.3407 | 93.3407 | 93.3407 | 105.6745 | 164.6159 | 181.8052 | 147.1732 | 195.1455 | 93.3407 | 93.3407 | 93.3407 | 93.3407 | 117.5416 | 233.1944 | 266.9228 | 198.9691 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 19 | 4891 | 20.5 | 20.5 | 16.1667 | 15.2005 | 15 | 74 | 74 | 163.037 | 128.5186 | 13.6043 | 285.4344 | 10.7153 | 0 | 0 | 0 | 0 | 98.5308 | 150.059 | 113.6846 | 46.4814 | 70.9784 | 65.8359 | 65.8359 | 65.8359 | 65.8359 | 113.1227 | 137.8521 | 120.3953 | 128.5186 | 81.6937 | 65.8359 | 65.8359 | 65.8359 | 65.8359 | 211.6536 | 287.911 | 234.0799 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 20 | 4892 | 19.1 | 19.1 | 16.1667 | 15.2005 | 15 | 80 | 80 | 214.1018 | 59.9067 | 5.0203 | 296.7522 | 55.3812 | 0 | 0 | 0 | 0 | 102.6781 | 200.59 | 180.999 | 29.0933 | 55.1083 | 33.8172 | 33.8172 | 33.8172 | 33.8172 | 73.2914 | 110.9333 | 103.4016 | 59.9067 | 110.4895 | 33.8172 | 33.8172 | 33.8172 | 33.8172 | 175.9696 | 311.5233 | 284.4006 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 21 | 4893 | 16.6 | 16.6 | 16.1667 | 15.2005 | 15 | 90 | 90 | 0 | 8 | -2.7304 | 308.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 8 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 3.754 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 22 | 4894 | 15.3 | 15.3 | 16.1667 | 15.2005 | 15 | 96 | 96 | 0 | 0 | -9.2655 | 321.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 23 | 4895 | 14.5 | 14.5 | 16.1667 | 15.2005 | 15 | 97 | 97 | 0 | 0 | -14.1751 | 334.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 23 | 24 | 4896 | 13.6 | 13.6 | 18.2875 | 15.9456 | 15 | 97 | 97 | 0 | 0 | -17.0704 | 348.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 1 | 4897 | 14 | 14 | 18.2875 | 15.9456 | 15 | 97 | 97 | 0 | 0 | -17.6787 | 3.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 2 | 4898 | 14.6 | 14.6 | 18.2875 | 15.9456 | 15 | 94 | 94 | 0 | 0 | -16.1408 | 18.2188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 3 | 4899 | 13.9 | 13.9 | 18.2875 | 15.9456 | 15 | 96 | 96 | 0 | 0 | -12.2165 | 32.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 4 | 4900 | 14.1 | 14.1 | 18.2875 | 15.9456 | 15 | 95 | 95 | 0 | 0 | -6.4565 | 45.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 5 | 4901 | 13.4 | 13.4 | 18.2875 | 15.9456 | 15 | 96 | 96 | 0 | 0 | 0.72854 | 57.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 6 | 4902 | 14.3 | 14.3 | 18.2875 | 15.9456 | 15 | 94 | 94 | 48.1944 | 44.8986 | 8.9375 | 68.8919 | 25.9762 | 47.0696 | 40.5902 | 10.3336 | 0 | 0 | 0 | 0 | 5.1014 | 147.1274 | 254.8284 | 221.7452 | 67.2574 | 14.4946 | 14.4946 | 14.4946 | 14.4946 | 44.8986 | 173.1036 | 301.898 | 262.3354 | 77.5911 | 14.4946 | 14.4946 | 14.4946 | 14.4946 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 7 | 4903 | 16.7 | 16.7 | 18.2875 | 15.9456 | 15 | 87 | 87 | 261.0243 | 108.6232 | 17.8036 | 80.1693 | 92.8611 | 235.7598 | 240.5536 | 104.4343 | 0 | 0 | 0 | 0 | 66.3768 | 91.1675 | 144.8444 | 146.6451 | 95.5148 | 56.2862 | 56.2862 | 56.2862 | 56.2862 | 108.6232 | 184.0287 | 380.6042 | 387.1987 | 199.9491 | 56.2862 | 56.2862 | 56.2862 | 56.2862 | 175 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 24 | 8 | 4904 | 18.4 | 18.4 | 18.2875 | 15.9456 | 15 | 83 | 83 | 490.4794 | 132.9762 | 26.9788 | 91.7639 | 79.733 | 381.7431 | 460.1333 | 268.9836 | 0 | 0 | 0 | 0 | 198.0238 | 100.7114 | 169.7738 | 187.6997 | 143.9884 | 82.4784 | 82.4784 | 82.4784 | 82.4784 | 132.9762 | 180.4444 | 551.5169 | 647.833 | 412.9721 | 82.4784 | 82.4784 | 82.4784 | 82.4784 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 9 | 4905 | 20.7 | 20.7 | 18.2875 | 15.9456 | 15 | 75 | 75 | 633.9929 | 141.0957 | 36.0857 | 104.4219 | 0 | 387.027 | 564.7305 | 411.6224 | 17.3916 | 0 | 0 | 0 | 344.9043 | 99.1838 | 168.0447 | 199.6622 | 172.4208 | 102.2781 | 99.1838 | 99.1838 | 99.1838 | 141.0957 | 99.1838 | 555.0718 | 764.3927 | 584.0433 | 119.6697 | 99.1838 | 99.1838 | 99.1838 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 10 | 4906 | 22.1 | 22.1 | 18.2875 | 15.9456 | 15 | 65 | 65 | 727.9137 | 143.4989 | 44.6306 | 119.1941 | 0 | 299.2518 | 569.7169 | 506.4496 | 146.511 | 0 | 0 | 0 | 484.5011 | 113.8507 | 160.7228 | 203.086 | 193.1764 | 136.7989 | 113.8507 | 113.8507 | 113.8507 | 143.4989 | 113.8507 | 459.9746 | 772.8029 | 699.626 | 283.3098 | 113.8507 | 113.8507 | 113.8507 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 11 | 4907 | 23.3 | 23.3 | 18.2875 | 15.9456 | 15 | 56 | 56 | 793.5532 | 143.7474 | 51.8632 | 137.4633 | 0 | 153.8221 | 492.9967 | 543.3806 | 275.4595 | 0 | 0 | 0 | 603.2526 | 125.4835 | 142.1626 | 178.9396 | 184.4028 | 155.3519 | 125.4835 | 125.4835 | 125.4835 | 143.7474 | 125.4835 | 295.9847 | 671.9364 | 727.7834 | 430.8113 | 125.4835 | 125.4835 | 125.4835 | 747 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 12 | 4908 | 24 | 24 | 18.2875 | 15.9456 | 15 | 47 | 47 | 811.8075 | 150.2696 | 56.6457 | 160.3057 | 0 | 0 | 338.9265 | 500.8613 | 369.3983 | 21.5468 | 0 | 0 | 666.7304 | 132.2153 | 132.2153 | 168.8746 | 186.3899 | 172.1705 | 134.5458 | 132.2153 | 132.2153 | 150.2696 | 132.2153 | 132.2153 | 507.8011 | 687.2512 | 541.5688 | 156.0926 | 132.2153 | 132.2153 | 817 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 13 | 4909 | 24.5 | 24.5 | 18.2875 | 15.9456 | 15 | 47 | 47 | 814.8326 | 153.7529 | 57.7208 | 186.4018 | 0 | 0 | 150.9791 | 405.0158 | 421.7998 | 191.4992 | 0 | 0 | 688.2471 | 134.0115 | 134.0115 | 150.5217 | 178.3018 | 180.1372 | 154.9528 | 134.0115 | 134.0115 | 153.7529 | 134.0115 | 134.0115 | 301.5008 | 583.3176 | 601.937 | 346.4519 | 134.0115 | 134.0115 | 842 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 14 | 4910 | 25.4 | 25.4 | 18.2875 | 15.9456 | 15 | 47 | 47 | 826.6547 | 148.0239 | 54.7213 | 211.3317 | 0 | 0 | 0 | 275.4135 | 438.7179 | 345.0272 | 49.2243 | 0 | 684.9761 | 131.3365 | 131.3365 | 131.3365 | 160.1922 | 177.302 | 167.4858 | 136.4939 | 131.3365 | 148.0239 | 131.3365 | 131.3365 | 131.3365 | 435.6058 | 616.0199 | 512.513 | 185.7182 | 131.3365 | 833 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 15 | 4911 | 25.1 | 25.1 | 18.2875 | 15.9456 | 15 | 47 | 47 | 805.579 | 143.2258 | 48.5869 | 231.9125 | 0 | 0 | 0 | 109.9424 | 397.4161 | 452.0888 | 241.9341 | 0 | 623.7742 | 124.5293 | 124.5293 | 124.5293 | 136.0725 | 166.2554 | 171.9957 | 149.9308 | 124.5293 | 143.2258 | 124.5293 | 124.5293 | 124.5293 | 246.0149 | 563.6715 | 624.0846 | 391.8649 | 124.5293 | 767 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 16 | 4912 | 25.8 | 25.8 | 18.2875 | 15.9456 | 15 | 45 | 45 | 756.3338 | 139.4903 | 40.6022 | 248.3046 | 0 | 0 | 0 | 0 | 308.618 | 496.6653 | 393.7727 | 60.2135 | 518.5097 | 114.465 | 114.465 | 114.465 | 114.465 | 148.587 | 169.3782 | 158.002 | 121.1224 | 139.4903 | 114.465 | 114.465 | 114.465 | 114.465 | 457.205 | 666.0435 | 551.7748 | 181.3359 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 17 | 4913 | 24.8 | 24.8 | 18.2875 | 15.9456 | 15 | 47 | 47 | 569.3293 | 165.3726 | 31.7112 | 261.8983 | 0 | 0 | 0 | 0 | 159.7947 | 396.9951 | 401.6411 | 171.0113 | 323.6274 | 105.2095 | 105.2095 | 105.2095 | 105.2095 | 139.9942 | 191.629 | 192.6404 | 142.4359 | 165.3726 | 105.2095 | 105.2095 | 105.2095 | 105.2095 | 299.7889 | 588.6241 | 594.2815 | 313.4472 | 489 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 24 | 18 | 4914 | 25.2 | 25.2 | 18.2875 | 15.9456 | 15 | 47 | 47 | 561.4588 | 127.0383 | 22.5194 | 273.9318 | 0 | 0 | 0 | 0 | 67.3139 | 381.968 | 472.8704 | 286.7717 | 241.9617 | 83.643 | 83.643 | 83.643 | 83.643 | 96.4731 | 156.4467 | 173.7728 | 138.3021 | 127.0383 | 83.643 | 83.643 | 83.643 | 83.643 | 163.787 | 538.4146 | 646.6431 | 425.0738 | 369 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 19 | 4915 | 24.4 | 24.4 | 18.2875 | 15.9456 | 15 | 46 | 46 | 466.2171 | 96.3126 | 13.4501 | 285.2939 | 29.5303 | 0 | 0 | 0 | 0 | 282.9304 | 429.6543 | 324.6926 | 131.6874 | 66.8196 | 60.6049 | 60.6049 | 60.6049 | 60.6049 | 120.1472 | 151.0251 | 128.936 | 96.3126 | 96.3499 | 60.6049 | 60.6049 | 60.6049 | 60.6049 | 403.0776 | 580.6794 | 453.6286 | 228 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 20 | 4916 | 23 | 23 | 18.2875 | 15.9456 | 15 | 49 | 49 | 325.6404 | 53.6729 | 4.8584 | 296.6243 | 83.5384 | 0 | 0 | 0 | 0 | 156.9456 | 305.4929 | 275.0867 | 43.3271 | 52.1001 | 32.2832 | 32.2832 | 32.2832 | 32.2832 | 69.5137 | 104.752 | 97.539 | 53.6729 | 135.6384 | 32.2832 | 32.2832 | 32.2832 | 32.2832 | 226.4593 | 410.2449 | 372.6257 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 21 | 4917 | 20.1 | 20.1 | 18.2875 | 15.9456 | 15 | 60 | 60 | 0 | 11 | -2.9027 | 308.4016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 11 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 5.2132 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 22 | 4918 | 20.1 | 20.1 | 18.2875 | 15.9456 | 15 | 57 | 57 | 0 | 0 | -9.4495 | 320.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 23 | 4919 | 20.1 | 20.1 | 18.2875 | 15.9456 | 15 | 58 | 58 | 0 | 0 | -14.3701 | 334.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 24 | 24 | 4920 | 19.4 | 19.4 | 20.3083 | 17.1135 | 15 | 61 | 61 | 0 | 0 | -17.2735 | 348.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 1 | 4921 | 18.7 | 18.7 | 20.3083 | 17.1135 | 15 | 64 | 64 | 0 | 0 | -17.8847 | 3.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 2 | 4922 | 17.5 | 17.5 | 20.3083 | 17.1135 | 15 | 69 | 69 | 0 | 0 | -16.3491 | 18.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 3 | 4923 | 16.6 | 16.6 | 20.3083 | 17.1135 | 15 | 73 | 73 | 0 | 0 | -12.417 | 32.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 4 | 4924 | 15.8 | 15.8 | 20.3083 | 17.1135 | 15 | 76 | 76 | 0 | 0 | -6.6469 | 45.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 5 | 4925 | 16 | 16 | 20.3083 | 17.1135 | 15 | 75 | 75 | 0 | 0 | 0.54837 | 57.4931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 6 | 4926 | 16.8 | 16.8 | 20.3083 | 17.1135 | 15 | 73 | 73 | 15.9704 | 37.3566 | 8.7658 | 69.017 | 8.5821 | 15.5915 | 13.4676 | 3.4546 | 0 | 0 | 0 | 0 | 1.6434 | 108.4989 | 186.6021 | 162.9364 | 51.3648 | 12.8716 | 12.8716 | 12.8716 | 12.8716 | 37.3566 | 117.081 | 202.1937 | 176.4041 | 54.8194 | 12.8716 | 12.8716 | 12.8716 | 12.8716 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 7 | 4927 | 18.6 | 18.6 | 20.3083 | 17.1135 | 15 | 67 | 67 | 156.5148 | 113.63 | 17.6375 | 80.3068 | 55.392 | 141.2946 | 144.4288 | 62.9586 | 0 | 0 | 0 | 0 | 39.37 | 122.2262 | 231.7493 | 235.7453 | 131.8734 | 51.6033 | 51.6033 | 51.6033 | 51.6033 | 113.63 | 177.6182 | 373.0439 | 380.1741 | 194.8319 | 51.6033 | 51.6033 | 51.6033 | 51.6033 | 153 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 25 | 8 | 4928 | 20.2 | 20.2 | 20.3083 | 17.1135 | 15 | 65 | 65 | 331.7901 | 160.8919 | 26.8143 | 91.913 | 53.2383 | 258.0357 | 311.6793 | 182.7454 | 0 | 0 | 0 | 0 | 133.1081 | 107.9506 | 186.9742 | 207.6733 | 157.9225 | 87.4079 | 87.4079 | 87.4079 | 87.4079 | 160.8919 | 161.1889 | 445.0099 | 519.3526 | 340.6679 | 87.4079 | 87.4079 | 87.4079 | 87.4079 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 9 | 4929 | 19.4 | 19.4 | 20.3083 | 17.1135 | 15 | 67 | 67 | 126.705 | 245.3701 | 35.9177 | 104.5808 | 0 | 77.2464 | 113.0178 | 82.585 | 3.775 | 0 | 0 | 0 | 68.6299 | 112.5003 | 195.2315 | 233.5429 | 200.9492 | 116.5433 | 112.5003 | 112.5003 | 112.5003 | 245.3701 | 112.5003 | 272.4779 | 346.5608 | 283.5342 | 120.3182 | 112.5003 | 112.5003 | 112.5003 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 10 | 4930 | 21.9 | 21.9 | 20.3083 | 17.1135 | 15 | 62 | 62 | 70.6391 | 292.1384 | 44.453 | 119.3554 | 0 | 28.9656 | 55.3654 | 49.3329 | 14.4018 | 0 | 0 | 0 | 46.8616 | 130.4212 | 183.6067 | 232.0809 | 221.0043 | 156.8652 | 130.4212 | 130.4212 | 130.4212 | 292.1384 | 130.4212 | 212.5723 | 287.4463 | 270.3371 | 171.267 | 130.4212 | 130.4212 | 130.4212 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 11 | 4931 | 23.9 | 23.9 | 20.3083 | 17.1135 | 15 | 58 | 58 | 214.6322 | 334.2857 | 51.6705 | 137.6043 | 0 | 41.316 | 133.5371 | 147.5339 | 75.1074 | 0 | 0 | 0 | 162.7143 | 155.6506 | 189.3334 | 264.5165 | 275.9274 | 216.8818 | 155.6506 | 155.6506 | 155.6506 | 334.2857 | 155.6506 | 230.6495 | 398.0536 | 423.4613 | 291.9891 | 155.6506 | 155.6506 | 155.6506 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 12 | 4932 | 26 | 26 | 20.3083 | 17.1135 | 15 | 53 | 53 | 657.4587 | 203.3531 | 56.438 | 160.3782 | 0 | 0 | 274.9205 | 407.3235 | 301.122 | 18.5273 | 0 | 0 | 538.6469 | 137.1744 | 137.1744 | 196.954 | 225.7441 | 202.6513 | 141.2031 | 137.1744 | 137.1744 | 203.3531 | 137.1744 | 137.1744 | 471.8744 | 633.0676 | 503.7733 | 159.7304 | 137.1744 | 137.1744 | 742 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 13 | 4933 | 25.5 | 25.5 | 20.3083 | 17.1135 | 15 | 55 | 55 | 324.7645 | 340.3296 | 57.5104 | 186.3608 | 0 | 0 | 60.2922 | 162.2163 | 169.1163 | 76.9503 | 0 | 0 | 273.6704 | 158.6659 | 158.6659 | 198.7914 | 266.6237 | 271.2158 | 209.8777 | 158.6659 | 158.6659 | 340.3296 | 158.6659 | 158.6659 | 259.0835 | 428.84 | 440.3321 | 286.828 | 158.6659 | 158.6659 | 614 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 14 | 4934 | 28 | 28 | 20.3083 | 17.1135 | 15 | 50 | 50 | 304.3425 | 340.4254 | 54.5247 | 211.1972 | 0 | 0 | 0 | 102.0769 | 162.4699 | 127.6903 | 18.1115 | 0 | 251.5746 | 155.873 | 155.873 | 155.873 | 228.646 | 271.7017 | 246.9065 | 168.7851 | 155.873 | 340.4254 | 155.873 | 155.873 | 155.873 | 330.7229 | 434.1716 | 374.5968 | 186.8965 | 155.873 | 592 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 15 | 4935 | 27.7 | 27.7 | 20.3083 | 17.1135 | 15 | 49 | 49 | 768.7283 | 153.3475 | 48.4089 | 231.7402 | 0 | 0 | 0 | 106.4393 | 381.6181 | 433.2502 | 231.0902 | 0 | 593.6525 | 125.1351 | 125.1351 | 125.1351 | 137.4537 | 169.3012 | 175.2768 | 151.88 | 125.1351 | 153.3475 | 125.1351 | 125.1351 | 125.1351 | 243.893 | 550.9193 | 608.5269 | 382.9702 | 125.1351 | 747 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 16 | 4936 | 27.4 | 27.4 | 20.3083 | 17.1135 | 15 | 48 | 48 | 794.4835 | 129.0692 | 40.4381 | 248.129 | 0 | 0 | 0 | 0 | 326.5728 | 523.7413 | 414.1092 | 61.8976 | 542.9308 | 113.0724 | 113.0724 | 113.0724 | 113.0724 | 145.5697 | 165.1899 | 154.2804 | 119.2319 | 129.0692 | 113.0724 | 113.0724 | 113.0724 | 113.0724 | 472.1425 | 688.9312 | 568.3896 | 181.1294 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 17 | 4937 | 27.5 | 27.5 | 20.3083 | 17.1135 | 15 | 52 | 52 | 432.8002 | 201.9912 | 31.5542 | 261.7318 | 0 | 0 | 0 | 0 | 122.71 | 302.9305 | 305.6984 | 129.3923 | 245.0088 | 112.1121 | 112.1121 | 112.1121 | 112.1121 | 155.4593 | 219.1221 | 220.0999 | 157.8199 | 201.9912 | 112.1121 | 112.1121 | 112.1121 | 112.1121 | 278.1693 | 522.0527 | 525.7983 | 287.2122 | 447 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 25 | 18 | 4938 | 27.5 | 27.5 | 20.3083 | 17.1135 | 15 | 53 | 53 | 571.0751 | 124.3312 | 22.3634 | 273.7773 | 0 | 0 | 0 | 0 | 69.982 | 390.0138 | 481.5809 | 291.0444 | 244.6688 | 82.8623 | 82.8623 | 82.8623 | 82.8623 | 95.8158 | 155.0533 | 172.0023 | 136.7342 | 124.3312 | 82.8623 | 82.8623 | 82.8623 | 82.8623 | 165.7978 | 545.0671 | 653.5831 | 427.7786 | 369 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 19 | 4939 | 26.7 | 26.7 | 20.3083 | 17.1135 | 15 | 56 | 56 | 337.7745 | 111.5089 | 13.2901 | 285.1516 | 20.5784 | 0 | 0 | 0 | 0 | 205.8482 | 311.6917 | 234.9505 | 94.4911 | 70.1104 | 63.56 | 63.56 | 63.56 | 63.56 | 129.0839 | 162.7751 | 138.3475 | 111.5089 | 90.6888 | 63.56 | 63.56 | 63.56 | 63.56 | 334.9321 | 474.4668 | 373.298 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 20 | 4940 | 25.2 | 25.2 | 20.3083 | 17.1135 | 15 | 67 | 67 | 191.5019 | 58.0779 | 4.6906 | 296.495 | 48.7132 | 0 | 0 | 0 | 0 | 92.7591 | 179.8944 | 161.65 | 24.9221 | 51.2197 | 32.4316 | 32.4316 | 32.4316 | 32.4316 | 68.2076 | 101.8146 | 94.778 | 58.0779 | 99.9329 | 32.4316 | 32.4316 | 32.4316 | 32.4316 | 160.9667 | 281.709 | 256.428 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 21 | 4941 | 24.1 | 24.1 | 20.3083 | 17.1135 | 15 | 70 | 70 | 0 | 11 | -3.0809 | 308.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 11 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 5.2179 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 22 | 4942 | 20.7 | 20.7 | 20.3083 | 17.1135 | 15 | 90 | 90 | 0 | 0 | -9.6395 | 320.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 23 | 4943 | 19.8 | 19.8 | 20.3083 | 17.1135 | 15 | 92 | 92 | 0 | 0 | -14.5711 | 334.4021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 25 | 24 | 4944 | 19.7 | 19.7 | 22.1333 | 18.4797 | 15 | 91 | 91 | 0 | 0 | -17.4824 | 348.7763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 1 | 4945 | 18.5 | 18.5 | 22.1333 | 18.4797 | 15 | 93 | 93 | 0 | 0 | -18.0962 | 3.5895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 2 | 4946 | 18.1 | 18.1 | 22.1333 | 18.4797 | 15 | 96 | 96 | 0 | 0 | -16.5624 | 18.2988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 3 | 4947 | 18.5 | 18.5 | 22.1333 | 18.4797 | 15 | 95 | 95 | 0 | 0 | -12.6219 | 32.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 4 | 4948 | 19.9 | 19.9 | 22.1333 | 18.4797 | 15 | 87 | 87 | 0 | 0 | -6.8411 | 45.4224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 5 | 4949 | 18.1 | 18.1 | 22.1333 | 18.4797 | 15 | 94 | 94 | 0 | 0 | 0.36477 | 57.6088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 6 | 4950 | 18.4 | 18.4 | 22.1333 | 18.4797 | 15 | 94 | 94 | 1.9624 | 16.804 | 8.5911 | 69.1471 | 1.0512 | 1.915 | 1.657 | 0.42837 | 0 | 0 | 0 | 0 | 0.19599 | 32.986 | 54.4686 | 48.0522 | 17.4955 | 6.842 | 6.842 | 6.842 | 6.842 | 16.804 | 34.0372 | 56.3836 | 49.7093 | 17.9238 | 6.842 | 6.842 | 6.842 | 6.842 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 7 | 4951 | 20 | 20 | 22.1333 | 18.4797 | 15 | 91 | 91 | 14.1872 | 88.4714 | 17.4685 | 80.4495 | 4.9936 | 12.8005 | 13.1091 | 5.7386 | 0 | 0 | 0 | 0 | 3.5286 | 91.3243 | 177.591 | 181.001 | 99.5568 | 36.1458 | 36.1458 | 36.1458 | 36.1458 | 88.4714 | 96.3179 | 190.3916 | 194.1102 | 105.2954 | 36.1458 | 36.1458 | 36.1458 | 36.1458 | 92 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 26 | 8 | 4952 | 22.3 | 22.3 | 22.1333 | 18.4797 | 15 | 82 | 82 | 27.9846 | 157.8466 | 26.6469 | 92.0676 | 4.429 | 21.7456 | 26.324 | 15.4821 | 0 | 0 | 0 | 0 | 11.1534 | 86.1566 | 158.5524 | 177.6931 | 132.3665 | 67.6404 | 67.6404 | 67.6404 | 67.6404 | 157.8466 | 90.5856 | 180.298 | 204.0171 | 147.8486 | 67.6404 | 67.6404 | 67.6404 | 67.6404 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 9 | 4953 | 24.3 | 24.3 | 22.1333 | 18.4797 | 15 | 74 | 74 | 429.897 | 193.1936 | 35.7465 | 104.7454 | 0 | 261.7172 | 383.9866 | 281.3218 | 13.8625 | 0 | 0 | 0 | 231.8064 | 110.9726 | 197.028 | 237.2314 | 203.4742 | 115.5308 | 110.9726 | 110.9726 | 110.9726 | 193.1936 | 110.9726 | 458.7452 | 621.218 | 484.7959 | 129.3933 | 110.9726 | 110.9726 | 110.9726 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 10 | 4954 | 25.6 | 25.6 | 22.1333 | 18.4797 | 15 | 70 | 70 | 418.448 | 240.3557 | 44.2719 | 119.5226 | 0 | 171.1136 | 328.4316 | 293.3588 | 86.4404 | 0 | 0 | 0 | 276.6443 | 132.32 | 198.4507 | 259.2498 | 245.6951 | 165.7268 | 132.32 | 132.32 | 132.32 | 240.3557 | 132.32 | 369.5642 | 587.6813 | 539.0539 | 252.1673 | 132.32 | 132.32 | 132.32 | 517 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 11 | 4955 | 26 | 26 | 22.1333 | 18.4797 | 15 | 67 | 67 | 150.844 | 341.9682 | 51.4736 | 137.7511 | 0 | 28.8233 | 93.9858 | 104.0927 | 53.2235 | 0 | 0 | 0 | 114.0318 | 153.2469 | 187.7665 | 265.8071 | 277.9115 | 216.989 | 153.2469 | 153.2469 | 153.2469 | 341.9682 | 153.2469 | 216.5897 | 359.7929 | 382.0042 | 270.2125 | 153.2469 | 153.2469 | 153.2469 | 456 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 12 | 4956 | 27.7 | 27.7 | 22.1333 | 18.4797 | 15 | 62 | 62 | 468.8623 | 277.8375 | 56.2253 | 160.4559 | 0 | 0 | 196.3554 | 291.7059 | 216.179 | 14.0174 | 0 | 0 | 383.1625 | 148.4326 | 148.4326 | 230.168 | 269.8588 | 238.4198 | 154.2675 | 148.4326 | 148.4326 | 277.8375 | 148.4326 | 148.4326 | 426.5233 | 561.5646 | 454.5988 | 168.285 | 148.4326 | 148.4326 | 661 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 13 | 4957 | 28.4 | 28.4 | 22.1333 | 18.4797 | 15 | 61 | 61 | 547.4381 | 253.8043 | 57.2944 | 186.3235 | 0 | 0 | 101.8105 | 274.7902 | 286.8015 | 130.8084 | 0 | 0 | 460.1957 | 145.7543 | 145.7543 | 180.4787 | 239.4768 | 243.5735 | 190.369 | 145.7543 | 145.7543 | 253.8043 | 145.7543 | 145.7543 | 282.2892 | 514.267 | 530.375 | 321.1774 | 145.7543 | 145.7543 | 714 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 14 | 4958 | 27.5 | 27.5 | 22.1333 | 18.4797 | 15 | 65 | 65 | 56.8921 | 356.0892 | 54.3219 | 211.0642 | 0 | 0 | 0 | 19.2102 | 30.5531 | 23.9984 | 3.3858 | 0 | 46.9108 | 155.8179 | 155.8179 | 155.8179 | 198.477 | 223.6656 | 209.11 | 163.3366 | 155.8179 | 356.0892 | 155.8179 | 155.8179 | 155.8179 | 217.6871 | 254.2187 | 233.1084 | 166.7224 | 155.8179 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 15 | 4959 | 28.1 | 28.1 | 22.1333 | 18.4797 | 15 | 63 | 63 | 154.3394 | 348.1397 | 48.2248 | 231.5675 | 0 | 0 | 0 | 21.6788 | 77.1063 | 87.3659 | 46.4478 | 0 | 118.8603 | 155.4515 | 155.4515 | 155.4515 | 179.4555 | 240.8276 | 252.1876 | 206.8809 | 155.4515 | 348.1397 | 155.4515 | 155.4515 | 155.4515 | 201.1343 | 317.9339 | 339.5536 | 253.3287 | 155.4515 | 467 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 16 | 4960 | 21.6 | 21.6 | 22.1333 | 18.4797 | 15 | 75 | 75 | 0.36499 | 49.7514 | 40.268 | 247.9522 | 0 | 0 | 0 | 0 | 0.15115 | 0.24156 | 0.19048 | 0.027811 | 0.2486 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 49.7514 | 23.9643 | 23.9643 | 23.9643 | 23.9643 | 24.1155 | 24.2059 | 24.1548 | 23.9921 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 17 | 4961 | 18.3 | 18.3 | 22.1333 | 18.4797 | 15 | 97 | 97 | 0.025792 | 10.9855 | 31.3914 | 261.5637 | 0 | 0 | 0 | 0 | 0.0073876 | 0.018122 | 0.018241 | 0.0076746 | 0.014539 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 10.9855 | 5.1845 | 5.1845 | 5.1845 | 5.1845 | 5.1919 | 5.2026 | 5.2027 | 5.1922 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 26 | 18 | 4962 | 19.6 | 19.6 | 22.1333 | 18.4797 | 15 | 95 | 95 | 3.1613 | 90.6538 | 22.2016 | 273.621 | 0 | 0 | 0 | 0 | 0.39591 | 2.1675 | 2.6694 | 1.6076 | 1.3462 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 90.6538 | 44.5643 | 44.5643 | 44.5643 | 44.5643 | 44.9602 | 46.7318 | 47.2337 | 46.1719 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 19 | 4963 | 19.6 | 19.6 | 22.1333 | 18.4797 | 15 | 96 | 96 | 3.9639 | 65.9022 | 13.1244 | 285.0078 | 0.23179 | 0 | 0 | 0 | 0 | 2.426 | 3.6627 | 2.7538 | 1.0978 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 65.9022 | 32.4393 | 32.2075 | 32.2075 | 32.2075 | 32.2075 | 34.6335 | 35.8702 | 34.9613 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 20 | 4964 | 19.4 | 19.4 | 22.1333 | 18.4797 | 15 | 97 | 97 | 1.5124 | 18.8077 | 4.5171 | 296.3643 | 0.38141 | 0 | 0 | 0 | 0 | 0.73628 | 1.4227 | 1.2757 | 0.1923 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 18.8077 | 9.2701 | 8.8887 | 8.8887 | 8.8887 | 8.8887 | 9.625 | 10.3114 | 10.1644 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 21 | 4965 | 19.5 | 19.5 | 22.1333 | 18.4797 | 15 | 95 | 95 | 0 | 6 | -3.265 | 308.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 6 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 2.8021 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 22 | 4966 | 18.8 | 18.8 | 22.1333 | 18.4797 | 15 | 96 | 96 | 0 | 0 | -9.8353 | 320.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 23 | 4967 | 18.6 | 18.6 | 22.1333 | 18.4797 | 15 | 97 | 97 | 0 | 0 | -14.778 | 334.3344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 26 | 24 | 4968 | 17.8 | 17.8 | 21.4417 | 19.4146 | 15 | 97 | 97 | 0 | 0 | -17.697 | 348.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 1 | 4969 | 17.8 | 17.8 | 21.4417 | 19.4146 | 15 | 96 | 96 | 0 | 0 | -18.3132 | 3.5941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 2 | 4970 | 17.4 | 17.4 | 21.4417 | 19.4146 | 15 | 96 | 96 | 0 | 0 | -16.7805 | 18.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 3 | 4971 | 17.2 | 17.2 | 21.4417 | 19.4146 | 15 | 98 | 98 | 0 | 0 | -12.8311 | 32.4073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 4 | 4972 | 17.6 | 17.6 | 21.4417 | 19.4146 | 15 | 98 | 98 | 0 | 0 | -7.0391 | 45.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 5 | 4973 | 17.4 | 17.4 | 21.4417 | 19.4146 | 15 | 98 | 98 | 0 | 0 | 0.17785 | 57.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 6 | 4974 | 17.9 | 17.9 | 21.4417 | 19.4146 | 15 | 99 | 99 | 2.6105 | 18.7474 | 8.4133 | 69.2822 | 1.3938 | 2.5463 | 2.2072 | 0.5752 | 0 | 0 | 0 | 0 | 0.25262 | 45.9568 | 78.085 | 68.633 | 23.1378 | 7.1033 | 7.1033 | 7.1033 | 7.1033 | 18.7474 | 47.3506 | 80.6313 | 70.8402 | 23.713 | 7.1033 | 7.1033 | 7.1033 | 7.1033 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 7 | 4975 | 18.8 | 18.8 | 21.4417 | 19.4146 | 15 | 98 | 98 | 7.4311 | 76.1733 | 17.2966 | 80.5974 | 2.6006 | 6.7008 | 6.8758 | 3.023 | 0 | 0 | 0 | 0 | 1.8267 | 70.2285 | 129.7834 | 132.3249 | 76.3642 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 76.1733 | 72.8291 | 136.4842 | 139.2007 | 79.3872 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 78 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 27 | 8 | 4976 | 21.2 | 21.2 | 21.4417 | 19.4146 | 15 | 87 | 87 | 546.0489 | 119.8419 | 26.4765 | 92.2274 | 85.1745 | 423.9286 | 514.3511 | 303.4737 | 0 | 0 | 0 | 0 | 216.1581 | 96.0335 | 163.8741 | 181.9825 | 139.7512 | 78.976 | 78.976 | 78.976 | 78.976 | 119.8419 | 181.208 | 587.8026 | 696.3336 | 443.2249 | 78.976 | 78.976 | 78.976 | 78.976 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 9 | 4977 | 22 | 22 | 21.4417 | 19.4146 | 15 | 83 | 83 | 126.2513 | 243.24 | 35.5723 | 104.9155 | 0 | 76.7437 | 112.9243 | 82.9554 | 4.3923 | 0 | 0 | 0 | 67.76 | 111.5121 | 194.0722 | 232.995 | 200.7547 | 116.2373 | 111.5121 | 111.5121 | 111.5121 | 243.24 | 111.5121 | 270.816 | 345.9193 | 283.71 | 120.6296 | 111.5121 | 111.5121 | 111.5121 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 10 | 4978 | 23.3 | 23.3 | 21.4417 | 19.4146 | 15 | 78 | 78 | 368.4799 | 254.2534 | 44.0873 | 119.6956 | 0 | 150.24 | 289.6163 | 259.3394 | 77.1449 | 0 | 0 | 0 | 242.7466 | 134.0519 | 202.5923 | 266.1766 | 252.3641 | 169.2459 | 134.0519 | 134.0519 | 134.0519 | 254.2534 | 134.0519 | 352.8322 | 555.7929 | 511.7035 | 246.3909 | 134.0519 | 134.0519 | 134.0519 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 11 | 4979 | 24.2 | 24.2 | 21.4417 | 19.4146 | 15 | 71 | 71 | 621.9927 | 200.1765 | 51.2726 | 137.9036 | 0 | 117.9226 | 388.0913 | 430.9214 | 221.3235 | 0 | 0 | 0 | 468.8235 | 131.0948 | 157.5059 | 218.0155 | 227.6081 | 180.6646 | 131.0948 | 131.0948 | 131.0948 | 200.1765 | 131.0948 | 275.4285 | 606.1068 | 658.5295 | 401.9881 | 131.0948 | 131.0948 | 131.0948 | 669 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 12 | 4980 | 26.2 | 26.2 | 21.4417 | 19.4146 | 15 | 70 | 70 | 746.6002 | 169.4574 | 56.0078 | 160.5386 | 0 | 0 | 313.1239 | 466.4848 | 346.5852 | 23.6607 | 0 | 0 | 608.5426 | 132.7223 | 132.7223 | 185.5888 | 211.4816 | 191.2382 | 136.717 | 132.7223 | 132.7223 | 169.4574 | 132.7223 | 132.7223 | 498.7127 | 677.9663 | 537.8234 | 160.3778 | 132.7223 | 132.7223 | 778 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 13 | 4981 | 26.2 | 26.2 | 21.4417 | 19.4146 | 15 | 65 | 65 | 716.1549 | 185.4801 | 57.0727 | 186.29 | 0 | 0 | 133.3979 | 361.2681 | 377.5123 | 172.615 | 0 | 0 | 600.5199 | 136.0166 | 136.0166 | 161.202 | 204.2236 | 207.2905 | 168.6061 | 136.0166 | 136.0166 | 185.4801 | 136.0166 | 136.0166 | 294.5999 | 565.4916 | 584.8028 | 341.2211 | 136.0166 | 136.0166 | 786 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 14 | 4982 | 27.9 | 27.9 | 21.4417 | 19.4146 | 15 | 59 | 59 | 700.7762 | 187.657 | 54.1132 | 210.933 | 0 | 0 | 0 | 238.2216 | 378.6305 | 297.2428 | 41.7343 | 0 | 576.343 | 133.9717 | 133.9717 | 133.9717 | 180.4082 | 207.7781 | 191.9132 | 142.107 | 133.9717 | 187.657 | 133.9717 | 133.9717 | 133.9717 | 418.6298 | 586.4086 | 489.156 | 183.8413 | 133.9717 | 764 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 15 | 4983 | 27.4 | 27.4 | 21.4417 | 19.4146 | 15 | 64 | 64 | 561.8604 | 226.5316 | 48.0346 | 231.3948 | 0 | 0 | 0 | 80.0519 | 282.5102 | 319.4779 | 169.2997 | 0 | 431.4684 | 133.036 | 133.036 | 133.036 | 155.0011 | 210.5527 | 220.6961 | 179.4894 | 133.036 | 226.5316 | 133.036 | 133.036 | 133.036 | 235.053 | 493.0629 | 540.1739 | 348.7891 | 133.036 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 16 | 4984 | 27.8 | 27.8 | 21.4417 | 19.4146 | 15 | 61 | 61 | 736.4797 | 144.0667 | 40.092 | 247.7742 | 0 | 0 | 0 | 0 | 307.2773 | 489.4067 | 384.8482 | 54.8509 | 499.9333 | 114.4297 | 114.4297 | 114.4297 | 114.4297 | 150.1677 | 171.3502 | 159.1895 | 120.8091 | 144.0667 | 114.4297 | 114.4297 | 114.4297 | 114.4297 | 457.445 | 660.7569 | 544.0377 | 175.66 | 644 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 17 | 4985 | 26.8 | 26.8 | 21.4417 | 19.4146 | 15 | 67 | 67 | 392.5828 | 210.6725 | 31.2227 | 261.394 | 0 | 0 | 0 | 0 | 113.6021 | 276.9156 | 278.0157 | 116.258 | 220.3275 | 112.9956 | 112.9956 | 112.9956 | 112.9956 | 158.4377 | 223.7649 | 224.205 | 159.5001 | 210.6725 | 112.9956 | 112.9956 | 112.9956 | 112.9956 | 272.0398 | 500.6805 | 502.2207 | 275.7581 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 27 | 18 | 4986 | 26.5 | 26.5 | 21.4417 | 19.4146 | 15 | 69 | 69 | 165.8899 | 190.7974 | 22.0341 | 273.4631 | 0 | 0 | 0 | 0 | 21.2281 | 114.1928 | 140.2649 | 84.1718 | 70.2026 | 94.2404 | 94.2404 | 94.2404 | 94.2404 | 107.4832 | 165.4777 | 181.7423 | 146.7495 | 190.7974 | 94.2404 | 94.2404 | 94.2404 | 94.2404 | 128.7113 | 279.6705 | 322.0072 | 230.9213 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 19 | 4987 | 25.7 | 25.7 | 21.4417 | 19.4146 | 15 | 72 | 72 | 376.3032 | 104.8567 | 12.953 | 284.8623 | 21.0708 | 0 | 0 | 0 | 0 | 231.3021 | 348.1814 | 261.1008 | 103.1433 | 67.3732 | 61.5552 | 61.5552 | 61.5552 | 61.5552 | 125.4206 | 157.6924 | 133.6484 | 104.8567 | 88.444 | 61.5552 | 61.5552 | 61.5552 | 61.5552 | 356.7227 | 505.8738 | 394.7492 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 20 | 4988 | 24.7 | 24.7 | 21.4417 | 19.4146 | 15 | 74 | 74 | 152.0517 | 56.1328 | 4.3379 | 296.2322 | 38.0084 | 0 | 0 | 0 | 0 | 74.3995 | 143.2252 | 128.1515 | 18.8672 | 49.0983 | 30.8913 | 30.8913 | 30.8913 | 30.8913 | 66.5305 | 99.4997 | 92.279 | 56.1328 | 87.1066 | 30.8913 | 30.8913 | 30.8913 | 30.8913 | 140.93 | 242.7249 | 220.4305 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 21 | 4989 | 23.2 | 23.2 | 21.4417 | 19.4146 | 15 | 82 | 82 | 0 | 17 | -3.4548 | 308.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 17 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 8.2452 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 22 | 4990 | 22.3 | 22.3 | 21.4417 | 19.4146 | 15 | 83 | 83 | 0 | 0 | -10.037 | 320.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 23 | 4991 | 21.3 | 21.3 | 21.4417 | 19.4146 | 15 | 90 | 90 | 0 | 0 | -14.9907 | 334.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 27 | 24 | 4992 | 20.8 | 20.8 | 22.5667 | 20.5274 | 15 | 91 | 91 | 0 | 0 | -17.9173 | 348.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 1 | 4993 | 21 | 21 | 22.5667 | 20.5274 | 15 | 92 | 92 | 0 | 0 | -18.5354 | 3.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 2 | 4994 | 20.9 | 20.9 | 22.5667 | 20.5274 | 15 | 95 | 95 | 0 | 0 | -17.0035 | 18.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 3 | 4995 | 20.8 | 20.8 | 22.5667 | 20.5274 | 15 | 96 | 96 | 0 | 0 | -13.0446 | 32.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 4 | 4996 | 20.8 | 20.8 | 22.5667 | 20.5274 | 15 | 88 | 88 | 0 | 0 | -7.2408 | 45.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 5 | 4997 | 20.2 | 20.2 | 22.5667 | 20.5274 | 15 | 95 | 95 | 0 | 0 | -0.012329 | 57.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 6 | 4998 | 20.3 | 20.3 | 22.5667 | 20.5274 | 15 | 94 | 94 | 0.49467 | 7.9537 | 8.2326 | 69.4222 | 0.2632 | 0.48227 | 0.41884 | 0.11005 | 0 | 0 | 0 | 0 | 0.046295 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 7.9537 | 4.1419 | 4.361 | 4.2975 | 3.9887 | 3.8787 | 3.8787 | 3.8787 | 3.8787 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 7 | 4999 | 20.5 | 20.5 | 22.5667 | 20.5274 | 15 | 92 | 92 | 2.8701 | 49.303 | 17.1219 | 80.7504 | 0.99837 | 2.5863 | 2.6592 | 1.1744 | 0 | 0 | 0 | 0 | 0.69696 | 31.3315 | 44.1709 | 44.7605 | 32.7549 | 23.2592 | 23.2592 | 23.2592 | 23.2592 | 49.303 | 32.3298 | 46.7572 | 47.4197 | 33.9293 | 23.2592 | 23.2592 | 23.2592 | 23.2592 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 28 | 8 | 5000 | 21 | 21 | 22.5667 | 20.5274 | 15 | 86 | 86 | 6.1271 | 114.5915 | 26.3034 | 92.3926 | 0.9412 | 4.7522 | 5.7794 | 3.4211 | 0 | 0 | 0 | 0 | 2.4085 | 59.4377 | 86.4334 | 93.7099 | 77.0046 | 52.7705 | 52.7705 | 52.7705 | 52.7705 | 114.5915 | 60.3789 | 91.1856 | 99.4893 | 80.4258 | 52.7705 | 52.7705 | 52.7705 | 52.7705 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 9 | 5001 | 21.1 | 21.1 | 22.5667 | 20.5274 | 15 | 85 | 85 | 3.0839 | 112.3528 | 35.3951 | 105.0912 | 0 | 1.8715 | 2.7621 | 2.0347 | 0.11541 | 0 | 0 | 0 | 1.6472 | 56.0435 | 56.5874 | 56.8463 | 56.6348 | 56.077 | 56.0435 | 56.0435 | 56.0435 | 112.3528 | 56.0435 | 58.4589 | 59.6084 | 58.6696 | 56.1924 | 56.0435 | 56.0435 | 56.0435 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 10 | 5002 | 22.3 | 22.3 | 22.5667 | 20.5274 | 15 | 82 | 82 | 13.9413 | 232.8493 | 43.8993 | 119.8742 | 0 | 5.6667 | 10.9727 | 9.8511 | 2.9589 | 0 | 0 | 0 | 9.1507 | 107.8874 | 128.4296 | 147.6645 | 143.5986 | 118.6135 | 107.8874 | 107.8874 | 107.8874 | 232.8493 | 107.8874 | 134.0962 | 158.6373 | 153.4497 | 121.5724 | 107.8874 | 107.8874 | 107.8874 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 11 | 5003 | 23.4 | 23.4 | 22.5667 | 20.5274 | 15 | 78 | 78 | 221.9856 | 330.1855 | 51.0676 | 138.0617 | 0 | 41.7382 | 138.6993 | 154.4122 | 79.6726 | 0 | 0 | 0 | 166.8145 | 154.7079 | 187.2759 | 262.9337 | 275.1943 | 216.8757 | 154.7079 | 154.7079 | 154.7079 | 330.1855 | 154.7079 | 229.0141 | 401.633 | 429.6066 | 296.5483 | 154.7079 | 154.7079 | 154.7079 | 497 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 12 | 5004 | 24.5 | 24.5 | 22.5667 | 20.5274 | 15 | 78 | 78 | 254.07 | 349.4695 | 55.7854 | 160.6264 | 0 | 0 | 106.7045 | 159.4305 | 118.7643 | 8.5275 | 0 | 0 | 206.5305 | 157.7543 | 157.7543 | 248.7836 | 293.7641 | 259.0718 | 165.0291 | 157.7543 | 157.7543 | 349.4695 | 157.7543 | 157.7543 | 355.4881 | 453.1945 | 377.8361 | 173.5567 | 157.7543 | 157.7543 | 556 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 13 | 5005 | 26 | 26 | 22.5667 | 20.5274 | 15 | 74 | 74 | 100.5375 | 376.9136 | 56.8456 | 186.2602 | 0 | 0 | 18.7531 | 50.9708 | 53.3305 | 24.45 | 0 | 0 | 84.0864 | 166.6907 | 166.6907 | 192.7441 | 237.5039 | 240.7822 | 200.6588 | 166.6907 | 166.6907 | 376.9136 | 166.6907 | 166.6907 | 211.4972 | 288.4747 | 294.1128 | 225.1087 | 166.6907 | 166.6907 | 461 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 14 | 5006 | 27.1 | 27.1 | 22.5667 | 20.5274 | 15 | 75 | 75 | 316.7382 | 334.1959 | 53.8985 | 210.8036 | 0 | 0 | 0 | 108.4004 | 172.1903 | 135.1135 | 18.889 | 0 | 259.8041 | 155.0929 | 155.0929 | 155.0929 | 228.1285 | 271.1076 | 246.1267 | 167.8195 | 155.0929 | 334.1959 | 155.0929 | 155.0929 | 155.0929 | 336.5289 | 443.2979 | 381.2403 | 186.7085 | 155.0929 | 594 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 15 | 5007 | 26.8 | 26.8 | 22.5667 | 20.5274 | 15 | 73 | 73 | 337.4953 | 305.5904 | 47.8384 | 231.2222 | 0 | 0 | 0 | 48.7693 | 170.8047 | 192.7851 | 101.8346 | 0 | 258.4096 | 147.1044 | 147.1044 | 147.1044 | 175.5972 | 246.8948 | 259.7366 | 206.5999 | 147.1044 | 305.5904 | 147.1044 | 147.1044 | 147.1044 | 224.3665 | 417.6996 | 452.5216 | 308.4345 | 147.1044 | 564 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 16 | 5008 | 27.2 | 27.2 | 22.5667 | 20.5274 | 15 | 71 | 71 | 399.0764 | 252.0509 | 39.9102 | 247.5953 | 0 | 0 | 0 | 0 | 167.7673 | 266.2918 | 208.8261 | 29.0329 | 269.9491 | 130.0385 | 130.0385 | 130.0385 | 130.0385 | 205.903 | 250.4558 | 224.4698 | 143.1672 | 252.0509 | 130.0385 | 130.0385 | 130.0385 | 130.0385 | 373.6704 | 516.7476 | 433.2959 | 172.2001 | 522 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 17 | 5009 | 27.3 | 27.3 | 22.5667 | 20.5274 | 15 | 74 | 74 | 280.7598 | 235.1437 | 31.0483 | 261.2229 | 0 | 0 | 0 | 0 | 82.0826 | 198.8268 | 199.1009 | 82.7444 | 156.8563 | 117.3947 | 117.3947 | 117.3947 | 117.3947 | 163.8126 | 229.8317 | 229.9867 | 164.1869 | 235.1437 | 117.3947 | 117.3947 | 117.3947 | 117.3947 | 245.8952 | 428.6584 | 429.0876 | 246.9313 | 392 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 18 | 5010 | 26.3 | 26.3 | 22.5667 | 20.5274 | 15 | 78 | 78 | 16.7469 | 153.9586 | 21.8609 | 273.3037 | 0 | 0 | 0 | 0 | 2.1893 | 11.5746 | 14.1796 | 8.4784 | 7.0414 | 75.5879 | 75.5879 | 75.5879 | 75.5879 | 77.181 | 84.0106 | 85.9063 | 81.7575 | 153.9586 | 75.5879 | 75.5879 | 75.5879 | 75.5879 | 79.3703 | 95.5852 | 100.0858 | 90.236 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 19 | 5011 | 25.5 | 25.5 | 22.5667 | 20.5274 | 15 | 82 | 82 | 10.5131 | 91.1493 | 12.7759 | 284.7154 | 0.56229 | 0 | 0 | 0 | 0 | 6.4903 | 9.7409 | 7.2855 | 2.8507 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 91.1493 | 46.0951 | 45.5328 | 45.5328 | 45.5328 | 45.5328 | 52.0231 | 55.2737 | 52.8183 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 20 | 5012 | 24.3 | 24.3 | 22.5667 | 20.5274 | 15 | 87 | 87 | 18.0144 | 44.8213 | 4.153 | 296.0988 | 4.4627 | 0 | 0 | 0 | 0 | 8.8597 | 16.9922 | 15.1709 | 2.1787 | 26.4442 | 22.8548 | 22.8548 | 22.8548 | 22.8548 | 29.9807 | 36.5217 | 35.0568 | 44.8213 | 30.9069 | 22.8548 | 22.8548 | 22.8548 | 22.8548 | 38.8404 | 53.5139 | 50.2277 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 21 | 5013 | 23.2 | 23.2 | 22.5667 | 20.5274 | 15 | 90 | 90 | 0 | 17 | -3.6503 | 307.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 17 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 8.2608 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 22 | 5014 | 22.6 | 22.6 | 22.5667 | 20.5274 | 15 | 95 | 95 | 0 | 0 | -10.2444 | 320.5849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 23 | 5015 | 22 | 22 | 22.5667 | 20.5274 | 15 | 96 | 96 | 0 | 0 | -15.2091 | 334.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 28 | 24 | 5016 | 21.9 | 21.9 | 23.2083 | 21.5885 | 15 | 97 | 97 | 0 | 0 | -18.1432 | 348.6801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 1 | 5017 | 21.6 | 21.6 | 23.2083 | 21.5885 | 15 | 96 | 96 | 0 | 0 | -18.763 | 3.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 2 | 5018 | 21.4 | 21.4 | 23.2083 | 21.5885 | 15 | 96 | 96 | 0 | 0 | -17.2311 | 18.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 3 | 5019 | 20.3 | 20.3 | 23.2083 | 21.5885 | 15 | 98 | 98 | 0 | 0 | -13.2621 | 32.5745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 4 | 5020 | 18.9 | 18.9 | 23.2083 | 21.5885 | 15 | 98 | 98 | 0 | 0 | -7.4461 | 45.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 5 | 5021 | 18.2 | 18.2 | 23.2083 | 21.5885 | 15 | 99 | 99 | 0 | 0 | -0.20567 | 57.9846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 6 | 5022 | 20.1 | 20.1 | 23.2083 | 21.5885 | 15 | 99 | 99 | 4.0144 | 21.6374 | 8.049 | 69.5672 | 2.1282 | 3.9118 | 3.4038 | 0.902 | 0 | 0 | 0 | 0 | 0.36263 | 12.9471 | 15.297 | 14.6278 | 11.3315 | 10.1431 | 10.1431 | 10.1431 | 10.1431 | 21.6374 | 15.0754 | 19.2088 | 18.0317 | 12.2335 | 10.1431 | 10.1431 | 10.1431 | 10.1431 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 7 | 5023 | 21.4 | 21.4 | 23.2083 | 21.5885 | 15 | 94 | 94 | 14.378 | 85.5523 | 16.9445 | 80.9084 | 4.97 | 12.9476 | 13.3406 | 5.9189 | 0 | 0 | 0 | 0 | 3.4477 | 93.132 | 187.1081 | 191.738 | 104.3098 | 34.5848 | 34.5848 | 34.5848 | 34.5848 | 85.5523 | 98.102 | 200.0557 | 205.0787 | 110.2287 | 34.5848 | 34.5848 | 34.5848 | 34.5848 | 89 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 29 | 8 | 5024 | 22.3 | 22.3 | 23.2083 | 21.5885 | 15 | 88 | 88 | 36.9995 | 160.5609 | 26.1276 | 92.5631 | 5.5926 | 28.667 | 34.9486 | 20.7579 | 0 | 0 | 0 | 0 | 14.4391 | 90.2136 | 165.7844 | 186.3574 | 139.8812 | 71.8973 | 71.8973 | 71.8973 | 71.8973 | 160.5609 | 95.8062 | 194.4514 | 221.306 | 160.639 | 71.8973 | 71.8973 | 71.8973 | 71.8973 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 9 | 5025 | 22.6 | 22.6 | 23.2083 | 21.5885 | 15 | 82 | 82 | 35.2115 | 217.2855 | 35.215 | 105.2723 | 0 | 21.3321 | 31.5818 | 23.3314 | 1.4137 | 0 | 0 | 0 | 18.7145 | 97.55 | 165.5276 | 198.1899 | 171.8987 | 102.055 | 97.55 | 97.55 | 97.55 | 217.2855 | 97.55 | 186.8597 | 229.7717 | 195.2301 | 103.4687 | 97.55 | 97.55 | 97.55 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 10 | 5026 | 22.4 | 22.4 | 23.2083 | 21.5885 | 15 | 80 | 80 | 20.5629 | 247.554 | 43.7079 | 120.0584 | 0 | 8.3306 | 16.2065 | 14.5888 | 4.4252 | 0 | 0 | 0 | 13.446 | 113.2306 | 138.9404 | 163.2467 | 158.2541 | 126.8874 | 113.2306 | 113.2306 | 113.2306 | 247.554 | 113.2306 | 147.2711 | 179.4531 | 172.8429 | 131.3126 | 113.2306 | 113.2306 | 113.2306 | 261 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 11 | 5027 | 21.5 | 21.5 | 23.2083 | 21.5885 | 15 | 91 | 91 | 9.8773 | 248.6007 | 50.8586 | 138.2252 | 0 | 1.8409 | 6.1798 | 6.8986 | 3.5763 | 0 | 0 | 0 | 7.3993 | 118.3726 | 124.5613 | 139.1474 | 141.5639 | 130.3952 | 118.3726 | 118.3726 | 118.3726 | 248.6007 | 118.3726 | 126.4023 | 145.3273 | 148.4625 | 133.9715 | 118.3726 | 118.3726 | 118.3726 | 256 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 12 | 5028 | 21.2 | 21.2 | 23.2083 | 21.5885 | 15 | 88 | 88 | 3.2634 | 175.3546 | 55.5583 | 160.719 | 0 | 0 | 1.3724 | 2.0567 | 1.5363 | 0.1159 | 0 | 0 | 2.6454 | 88.5764 | 88.5764 | 88.5764 | 88.5764 | 88.5764 | 88.5764 | 88.5764 | 88.5764 | 175.3546 | 88.5764 | 88.5764 | 89.9488 | 90.6331 | 90.1127 | 88.6923 | 88.5764 | 88.5764 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 13 | 5029 | 21.7 | 21.7 | 23.2083 | 21.5885 | 15 | 79 | 79 | 5.7912 | 239.1693 | 56.613 | 186.2343 | 0 | 0 | 1.0815 | 2.9509 | 3.0916 | 1.4214 | 0 | 0 | 4.8307 | 118.9767 | 118.9767 | 120.9691 | 124.4129 | 124.6723 | 121.5952 | 118.9767 | 118.9767 | 239.1693 | 118.9767 | 118.9767 | 122.0506 | 127.3638 | 127.7639 | 123.0166 | 118.9767 | 118.9767 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 14 | 5030 | 22.4 | 22.4 | 23.2083 | 21.5885 | 15 | 68 | 68 | 195.9938 | 364.6775 | 53.678 | 210.6762 | 0 | 0 | 0 | 67.5313 | 107.2159 | 84.0949 | 11.7122 | 0 | 160.3225 | 164.6714 | 164.6714 | 164.6714 | 226.4969 | 262.8285 | 241.661 | 175.3941 | 164.6714 | 364.6775 | 164.6714 | 164.6714 | 164.6714 | 294.0282 | 370.0444 | 325.7559 | 187.1063 | 164.6714 | 525 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 15 | 5031 | 23.5 | 23.5 | 23.2083 | 21.5885 | 15 | 67 | 67 | 352.2791 | 300.0897 | 47.6362 | 231.0498 | 0 | 0 | 0 | 51.6236 | 179.4636 | 202.1763 | 106.4569 | 0 | 268.9103 | 146.4128 | 146.4128 | 146.4128 | 174.8804 | 245.377 | 257.9018 | 205.1179 | 146.4128 | 300.0897 | 146.4128 | 146.4128 | 146.4128 | 226.5039 | 424.8406 | 460.0781 | 311.5747 | 146.4128 | 569 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 16 | 5032 | 24 | 24 | 23.2083 | 21.5885 | 15 | 68 | 68 | 450.7247 | 235.2168 | 39.7224 | 247.4156 | 0 | 0 | 0 | 0 | 190.9283 | 302.0227 | 236.1964 | 32.0094 | 303.7832 | 127.6155 | 127.6155 | 127.6155 | 127.6155 | 200.551 | 242.9896 | 217.8436 | 139.8432 | 235.2168 | 127.6155 | 127.6155 | 127.6155 | 127.6155 | 391.4792 | 545.0123 | 454.04 | 171.8526 | 539 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 17 | 5033 | 24.3 | 24.3 | 23.2083 | 21.5885 | 15 | 64 | 64 | 615.9717 | 149.4727 | 30.8682 | 261.0505 | 0 | 0 | 0 | 0 | 181.9504 | 437.9772 | 437.4428 | 180.6604 | 342.5273 | 101.4158 | 101.4158 | 101.4158 | 101.4158 | 135.7925 | 184.1647 | 184.0638 | 135.5488 | 149.4727 | 101.4158 | 101.4158 | 101.4158 | 101.4158 | 317.743 | 622.1419 | 621.5066 | 316.2092 | 492 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 18 | 5034 | 23.3 | 23.3 | 23.2083 | 21.5885 | 15 | 64 | 64 | 276.6719 | 176.4457 | 21.682 | 273.1428 | 0 | 0 | 0 | 0 | 36.9434 | 192.0033 | 234.5902 | 139.7574 | 115.5543 | 92.3806 | 92.3806 | 92.3806 | 92.3806 | 109.8588 | 183.2188 | 203.367 | 158.5009 | 176.4457 | 92.3806 | 92.3806 | 92.3806 | 92.3806 | 146.8023 | 375.2221 | 437.9572 | 298.2582 | 292 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 19 | 5035 | 21.8 | 21.8 | 23.2083 | 21.5885 | 15 | 67 | 67 | 210.0187 | 118.6827 | 12.5933 | 284.567 | 10.6996 | 0 | 0 | 0 | 0 | 130.2253 | 194.866 | 145.3568 | 56.3173 | 68.4317 | 63.0768 | 63.0768 | 63.0768 | 63.0768 | 128.2514 | 160.6025 | 135.8243 | 118.6827 | 79.1312 | 63.0768 | 63.0768 | 63.0768 | 63.0768 | 258.4767 | 355.4685 | 281.1811 | 175 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 20 | 5036 | 21 | 21 | 23.2083 | 21.5885 | 15 | 66 | 66 | 8.6991 | 37.9759 | 3.9625 | 295.9643 | 2.1353 | 0 | 0 | 0 | 0 | 4.3003 | 8.2169 | 7.3201 | 1.0241 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 37.9759 | 20.6025 | 18.4672 | 18.4672 | 18.4672 | 18.4672 | 22.7675 | 26.6841 | 25.7873 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 21 | 5037 | 19.4 | 19.4 | 23.2083 | 21.5885 | 15 | 74 | 74 | 0 | 3 | -3.8515 | 307.8214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 3 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 22 | 5038 | 17.9 | 17.9 | 23.2083 | 21.5885 | 15 | 84 | 84 | 0 | 0 | -10.4576 | 320.4892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 23 | 5039 | 16.2 | 16.2 | 23.2083 | 21.5885 | 15 | 94 | 94 | 0 | 0 | -15.4332 | 334.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 29 | 24 | 5040 | 15.4 | 15.4 | 20.95 | 21.6792 | 15 | 97 | 97 | 0 | 0 | -18.3746 | 348.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 1 | 5041 | 15.4 | 15.4 | 20.95 | 21.6792 | 15 | 97 | 97 | 0 | 0 | -18.9957 | 3.6235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 2 | 5042 | 14.8 | 14.8 | 20.95 | 21.6792 | 15 | 97 | 97 | 0 | 0 | -17.4633 | 18.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 3 | 5043 | 15.8 | 15.8 | 20.95 | 21.6792 | 15 | 97 | 97 | 0 | 0 | -13.4838 | 32.6644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 4 | 5044 | 16.1 | 16.1 | 20.95 | 21.6792 | 15 | 96 | 96 | 0 | 0 | -7.6549 | 45.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 5 | 5045 | 16.6 | 16.6 | 20.95 | 21.6792 | 15 | 94 | 94 | 0 | 0 | -0.40209 | 58.1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 6 | 5046 | 16.7 | 16.7 | 20.95 | 21.6792 | 15 | 94 | 94 | 3.227 | 18.7192 | 7.8626 | 69.7171 | 1.7043 | 3.1427 | 2.7401 | 0.73245 | 0 | 0 | 0 | 0 | 0.28076 | 11.1871 | 13.2172 | 12.6491 | 9.8155 | 8.7817 | 8.7817 | 8.7817 | 8.7817 | 18.7192 | 12.8914 | 16.3599 | 15.3892 | 10.548 | 8.7817 | 8.7817 | 8.7817 | 8.7817 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 7 | 5047 | 19.1 | 19.1 | 20.95 | 21.6792 | 15 | 84 | 84 | 91.9105 | 106.2476 | 16.7645 | 81.0715 | 31.5618 | 82.7051 | 85.4009 | 38.07 | 0 | 0 | 0 | 0 | 21.7524 | 117.9704 | 234.936 | 241.1012 | 132.8546 | 45.788 | 45.788 | 45.788 | 45.788 | 106.2476 | 149.5322 | 317.6411 | 326.5021 | 170.9246 | 45.788 | 45.788 | 45.788 | 45.788 | 128 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 30 | 8 | 5048 | 20 | 20 | 20.95 | 21.6792 | 15 | 78 | 78 | 21.4872 | 147.6771 | 25.949 | 92.7387 | 3.1931 | 16.6296 | 20.3247 | 12.1138 | 0 | 0 | 0 | 0 | 8.3229 | 79.646 | 147.0398 | 165.5734 | 124.3899 | 63.6301 | 63.6301 | 63.6301 | 63.6301 | 147.6771 | 82.8391 | 163.6694 | 185.8981 | 136.5038 | 63.6301 | 63.6301 | 63.6301 | 63.6301 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 9 | 5049 | 21.6 | 21.6 | 20.95 | 21.6792 | 15 | 72 | 72 | 14.625 | 189.2666 | 35.0319 | 105.4587 | 0 | 8.8439 | 13.1355 | 9.7325 | 0.62834 | 0 | 0 | 0 | 7.7334 | 85.6996 | 124.6326 | 143.5253 | 128.5445 | 88.4657 | 85.6996 | 85.6996 | 85.6996 | 189.2666 | 85.6996 | 133.4765 | 156.6608 | 138.277 | 89.094 | 85.6996 | 85.6996 | 85.6996 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 10 | 5050 | 22.2 | 22.2 | 20.95 | 21.6792 | 15 | 75 | 75 | 14.4329 | 232.5991 | 43.5132 | 120.2481 | 0 | 5.8269 | 11.3906 | 10.2818 | 3.1501 | 0 | 0 | 0 | 9.4009 | 107.5867 | 128.5403 | 148.5472 | 144.56 | 118.9143 | 107.5867 | 107.5867 | 107.5867 | 232.5991 | 107.5867 | 134.3673 | 159.9378 | 154.8418 | 122.0644 | 107.5867 | 107.5867 | 107.5867 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 11 | 5051 | 23.1 | 23.1 | 20.95 | 21.6792 | 15 | 73 | 73 | 12.4775 | 259.6829 | 50.6456 | 138.3941 | 0 | 2.3042 | 7.8169 | 8.7506 | 4.5583 | 0 | 0 | 0 | 9.3171 | 122.5735 | 129.9804 | 147.7015 | 150.7029 | 137.2266 | 122.5735 | 122.5735 | 122.5735 | 259.6829 | 122.5735 | 132.2845 | 155.5184 | 159.4536 | 141.7849 | 122.5735 | 122.5735 | 122.5735 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 12 | 5052 | 25.4 | 25.4 | 20.95 | 21.6792 | 15 | 65 | 65 | 491.9956 | 266.3188 | 55.3266 | 160.8165 | 0 | 0 | 207.1571 | 311.4348 | 233.2782 | 18.4704 | 0 | 0 | 397.6812 | 146.4522 | 146.4522 | 226.1155 | 266.216 | 236.1605 | 153.5551 | 146.4522 | 146.4522 | 266.3188 | 146.4522 | 146.4522 | 433.2726 | 577.6508 | 469.4387 | 172.0254 | 146.4522 | 146.4522 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 13 | 5053 | 25.6 | 25.6 | 20.95 | 21.6792 | 15 | 59 | 59 | 178.1406 | 373.8145 | 56.375 | 186.2121 | 0 | 0 | 33.301 | 91.2291 | 95.7164 | 44.1343 | 0 | 0 | 148.1855 | 166.5837 | 166.5837 | 201.3677 | 261.8753 | 266.5625 | 212.6834 | 166.5837 | 166.5837 | 373.8145 | 166.5837 | 166.5837 | 234.6687 | 353.1044 | 362.2789 | 256.8178 | 166.5837 | 166.5837 | 522 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 14 | 5054 | 26.5 | 26.5 | 20.95 | 21.6792 | 15 | 54 | 54 | 604.4377 | 223.9704 | 53.4516 | 210.5509 | 0 | 0 | 0 | 209.6756 | 332.7447 | 260.8965 | 36.2186 | 0 | 493.0296 | 137.6109 | 137.6109 | 137.6109 | 191.0954 | 222.4881 | 204.1609 | 146.8496 | 137.6109 | 223.9704 | 137.6109 | 137.6109 | 137.6109 | 400.771 | 555.2328 | 465.0574 | 183.0682 | 137.6109 | 717 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 15 | 5055 | 26.3 | 26.3 | 20.95 | 21.6792 | 15 | 51 | 51 | 369.8407 | 293.5679 | 47.4282 | 230.8778 | 0 | 0 | 0 | 54.9544 | 189.6663 | 213.2743 | 111.949 | 0 | 281.4321 | 142.4132 | 142.4132 | 142.4132 | 172.7632 | 247.1615 | 260.1997 | 204.2401 | 142.4132 | 293.5679 | 142.4132 | 142.4132 | 142.4132 | 227.7177 | 436.8279 | 473.474 | 316.1891 | 142.4132 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 16 | 5056 | 26.6 | 26.6 | 20.95 | 21.6792 | 15 | 51 | 51 | 330.4492 | 270.1113 | 39.5289 | 247.2352 | 0 | 0 | 0 | 0 | 141.0569 | 222.3782 | 173.4334 | 22.8936 | 221.8887 | 134.1039 | 134.1039 | 134.1039 | 134.1039 | 209.6226 | 253.1602 | 226.9563 | 146.3607 | 270.1113 | 134.1039 | 134.1039 | 134.1039 | 134.1039 | 350.6795 | 475.5384 | 400.3896 | 169.2543 | 492 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 17 | 5057 | 26.4 | 26.4 | 20.95 | 21.6792 | 15 | 51 | 51 | 197.7193 | 246.5821 | 30.6823 | 260.877 | 0 | 0 | 0 | 0 | 59.0105 | 141.1615 | 140.622 | 57.708 | 109.4179 | 119.8217 | 119.8217 | 119.8217 | 119.8217 | 157.1467 | 209.1083 | 208.7671 | 156.3229 | 246.5821 | 119.8217 | 119.8217 | 119.8217 | 119.8217 | 216.1572 | 350.2698 | 349.3891 | 214.0309 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 30 | 18 | 5058 | 26.4 | 26.4 | 20.95 | 21.6792 | 15 | 50 | 50 | 447.1934 | 145.5093 | 21.4976 | 272.9806 | 0 | 0 | 0 | 0 | 60.9789 | 311.6251 | 379.7256 | 225.388 | 185.4907 | 86.154 | 86.154 | 86.154 | 86.154 | 102.983 | 172.1565 | 190.9509 | 148.3567 | 145.5093 | 86.154 | 86.154 | 86.154 | 86.154 | 163.9619 | 483.7816 | 570.6765 | 373.7447 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 19 | 5059 | 25.8 | 25.8 | 20.95 | 21.6792 | 15 | 51 | 51 | 298.192 | 109.9569 | 12.405 | 284.4174 | 14.4265 | 0 | 0 | 0 | 0 | 185.7186 | 277.0723 | 206.1208 | 79.0431 | 66.5648 | 61.3829 | 61.3829 | 61.3829 | 61.3829 | 128.0917 | 160.9053 | 135.4201 | 109.9569 | 80.9914 | 61.3829 | 61.3829 | 61.3829 | 61.3829 | 313.8104 | 437.9777 | 341.5409 | 189 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 20 | 5060 | 23.7 | 23.7 | 20.95 | 21.6792 | 15 | 60 | 60 | 67.5903 | 50.2653 | 3.7664 | 295.8287 | 16.436 | 0 | 0 | 0 | 0 | 33.5857 | 63.9334 | 56.8298 | 7.7347 | 35.7863 | 26.4356 | 26.4356 | 26.4356 | 26.4356 | 45.5431 | 62.8085 | 58.7671 | 50.2653 | 52.2224 | 26.4356 | 26.4356 | 26.4356 | 26.4356 | 79.1289 | 126.7419 | 115.5969 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 21 | 5061 | 22.5 | 22.5 | 20.95 | 21.6792 | 15 | 63 | 63 | 0 | 3 | -4.0583 | 307.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 3 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 22 | 5062 | 21.7 | 21.7 | 20.95 | 21.6792 | 15 | 68 | 68 | 0 | 0 | -10.6764 | 320.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 23 | 5063 | 21.2 | 21.2 | 20.95 | 21.6792 | 15 | 71 | 71 | 0 | 0 | -15.663 | 334.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 30 | 24 | 5064 | 20.5 | 20.5 | 21.6667 | 21.8193 | 15 | 71 | 71 | 0 | 0 | -18.6114 | 348.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 1 | 5065 | 20 | 20 | 21.6667 | 21.8193 | 15 | 70 | 70 | 0 | 0 | -19.2336 | 3.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 2 | 5066 | 19.2 | 19.2 | 21.6667 | 21.8193 | 15 | 74 | 74 | 0 | 0 | -17.7 | 18.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 3 | 5067 | 18.4 | 18.4 | 21.6667 | 21.8193 | 15 | 79 | 79 | 0 | 0 | -13.7093 | 32.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 4 | 5068 | 17.6 | 17.6 | 21.6667 | 21.8193 | 15 | 85 | 85 | 0 | 0 | -7.8672 | 45.9783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 5 | 5069 | 17.2 | 17.2 | 21.6667 | 21.8193 | 15 | 90 | 90 | 0 | 0 | -0.60151 | 58.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 6 | 5070 | 17.7 | 17.7 | 21.6667 | 21.8193 | 15 | 90 | 90 | 4.6846 | 21.6084 | 7.6735 | 69.8718 | 2.4643 | 4.5595 | 3.9838 | 1.0744 | 0 | 0 | 0 | 0 | 0.39163 | 12.9111 | 15.2733 | 14.6242 | 11.344 | 10.1326 | 10.1326 | 10.1326 | 10.1326 | 21.6084 | 15.3754 | 19.8328 | 18.608 | 12.4184 | 10.1326 | 10.1326 | 10.1326 | 10.1326 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 7 | 5071 | 20 | 20 | 21.6667 | 21.8193 | 15 | 86 | 86 | 116.4925 | 105.8016 | 16.5819 | 81.2395 | 39.7286 | 104.7415 | 108.3983 | 48.5568 | 0 | 0 | 0 | 0 | 27.1984 | 119.9656 | 240.2075 | 246.9707 | 136.2935 | 46.4874 | 46.4874 | 46.4874 | 46.4874 | 105.8016 | 159.6942 | 344.949 | 355.369 | 184.8503 | 46.4874 | 46.4874 | 46.4874 | 46.4874 | 133 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2008 | 7 | 31 | 8 | 5072 | 21.9 | 21.9 | 21.6667 | 21.8193 | 15 | 79 | 79 | 376.7588 | 147.1878 | 25.7679 | 92.9194 | 54.9955 | 291.2385 | 356.8779 | 213.4631 | 0 | 0 | 0 | 0 | 144.8122 | 101.0157 | 178.2771 | 199.7439 | 152.8412 | 83.0298 | 83.0298 | 83.0298 | 83.0298 | 147.1878 | 156.0112 | 469.5156 | 556.6218 | 366.3043 | 83.0298 | 83.0298 | 83.0298 | 83.0298 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 9 | 5073 | 24 | 24 | 21.6667 | 21.8193 | 15 | 73 | 73 | 558.047 | 156.4683 | 34.846 | 105.6505 | 0 | 336.801 | 501.9042 | 372.9987 | 25.5956 | 0 | 0 | 0 | 293.5317 | 101.939 | 179.4054 | 217.3802 | 187.7311 | 107.8262 | 101.939 | 101.939 | 101.939 | 156.4683 | 101.939 | 516.2064 | 719.2843 | 560.7298 | 133.4218 | 101.939 | 101.939 | 101.939 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 10 | 5074 | 25.5 | 25.5 | 21.6667 | 21.8193 | 15 | 68 | 68 | 627.384 | 170.9865 | 43.3153 | 120.4431 | 0 | 252.3653 | 495.799 | 448.8004 | 138.9005 | 0 | 0 | 0 | 407.0135 | 116.2006 | 166.707 | 215.426 | 206.02 | 143.9991 | 116.2006 | 116.2006 | 116.2006 | 170.9865 | 116.2006 | 419.0724 | 711.225 | 654.8204 | 282.8996 | 116.2006 | 116.2006 | 116.2006 | 578 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 11 | 5075 | 27 | 27 | 21.6667 | 21.8193 | 15 | 62 | 62 | 673.6323 | 179.6578 | 50.4287 | 138.5682 | 0 | 123.1891 | 422.5554 | 474.3945 | 248.3397 | 0 | 0 | 0 | 501.3422 | 127.5693 | 151.4599 | 209.5172 | 219.5706 | 175.7309 | 127.5693 | 127.5693 | 127.5693 | 179.6578 | 127.5693 | 274.6489 | 632.0726 | 693.965 | 424.0706 | 127.5693 | 127.5693 | 127.5693 | 681 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 12 | 5076 | 28.1 | 28.1 | 21.6667 | 21.8193 | 15 | 62 | 62 | 727.5812 | 174.633 | 55.0902 | 160.9188 | 0 | 0 | 306.7088 | 462.5979 | 347.5035 | 28.8462 | 0 | 0 | 586.367 | 132.5845 | 132.5845 | 186.8692 | 214.4602 | 194.0895 | 137.69 | 132.5845 | 132.5845 | 174.633 | 132.5845 | 132.5845 | 493.578 | 677.0581 | 541.5929 | 166.5362 | 132.5845 | 132.5845 | 761 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 13 | 5077 | 27.3 | 27.3 | 21.6667 | 21.8193 | 15 | 63 | 63 | 218.8043 | 365.5043 | 56.1318 | 186.1937 | 0 | 0 | 40.935 | 112.6235 | 118.3386 | 54.7326 | 0 | 0 | 181.4957 | 167.3 | 167.3 | 201.1674 | 260.4786 | 265.207 | 212.5828 | 167.3 | 167.3 | 365.5043 | 167.3 | 167.3 | 242.1024 | 373.102 | 383.5456 | 267.3155 | 167.3 | 167.3 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 14 | 5078 | 28 | 28 | 21.6667 | 21.8193 | 15 | 61 | 61 | 167.2915 | 366.9411 | 53.2195 | 210.4278 | 0 | 0 | 0 | 58.4256 | 92.6848 | 72.6504 | 10.0585 | 0 | 136.0589 | 163.0677 | 163.0677 | 163.0677 | 226.3291 | 263.4238 | 241.7313 | 173.9587 | 163.0677 | 366.9411 | 163.0677 | 163.0677 | 163.0677 | 284.7547 | 356.1086 | 314.3817 | 184.0172 | 163.0677 | 503 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 15 | 5079 | 28.7 | 28.7 | 21.6667 | 21.8193 | 15 | 54 | 54 | 609.959 | 206.3455 | 47.2142 | 230.7064 | 0 | 0 | 0 | 91.8877 | 314.9118 | 353.4648 | 184.9629 | 0 | 462.6545 | 130.089 | 130.089 | 130.089 | 151.917 | 204.8967 | 214.055 | 174.0272 | 130.089 | 206.3455 | 130.089 | 130.089 | 130.089 | 243.8048 | 519.8085 | 567.5198 | 358.9901 | 130.089 | 669 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 16 | 5080 | 29.6 | 29.6 | 21.6667 | 21.8193 | 15 | 50 | 50 | 589.5683 | 188.6392 | 39.3295 | 247.0542 | 0 | 0 | 0 | 0 | 253.6151 | 398.485 | 309.9278 | 39.8191 | 394.3608 | 119.091 | 119.091 | 119.091 | 119.091 | 177.2746 | 210.5102 | 190.1937 | 128.2262 | 188.6392 | 119.091 | 119.091 | 119.091 | 119.091 | 430.8897 | 608.9952 | 500.1215 | 168.0453 | 583 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 17 | 5081 | 29.3 | 29.3 | 21.6667 | 21.8193 | 15 | 54 | 54 | 550.5837 | 165.8175 | 30.4908 | 260.7023 | 0 | 0 | 0 | 0 | 166.035 | 394.7217 | 392.1857 | 159.9127 | 303.1825 | 103.5467 | 103.5467 | 103.5467 | 103.5467 | 141.0023 | 192.5915 | 192.0194 | 139.6212 | 165.8175 | 103.5467 | 103.5467 | 103.5467 | 103.5467 | 307.0373 | 587.3131 | 584.2051 | 299.5339 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2008 | 7 | 31 | 18 | 5082 | 28.7 | 28.7 | 21.6667 | 21.8193 | 15 | 53 | 53 | 546.8862 | 124.7649 | 21.3076 | 272.8171 | 0 | 0 | 0 | 0 | 76.1381 | 382.6892 | 465.0662 | 275.0137 | 225.2351 | 81.1605 | 81.1605 | 81.1605 | 81.1605 | 95.9689 | 155.5913 | 171.6131 | 134.649 | 124.7649 | 81.1605 | 81.1605 | 81.1605 | 81.1605 | 172.107 | 538.2805 | 636.6794 | 409.6628 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 19 | 5083 | 27.3 | 27.3 | 21.6667 | 21.8193 | 15 | 55 | 55 | 330.7381 | 105.3717 | 12.2113 | 284.2666 | 15.1439 | 0 | 0 | 0 | 0 | 206.909 | 307.7575 | 228.3258 | 86.6283 | 64.9553 | 60.1624 | 60.1624 | 60.1624 | 60.1624 | 125.647 | 157.5644 | 132.4251 | 105.3717 | 80.0992 | 60.1624 | 60.1624 | 60.1624 | 60.1624 | 332.556 | 465.3219 | 360.7509 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 20 | 5084 | 23.9 | 23.9 | 21.6667 | 21.8193 | 15 | 76 | 76 | 122.6561 | 50.3765 | 3.5648 | 295.692 | 29.5427 | 0 | 0 | 0 | 0 | 61.2645 | 116.1837 | 103.0442 | 13.6235 | 44.2013 | 27.5855 | 27.5855 | 27.5855 | 27.5855 | 62.0425 | 92.9308 | 85.5407 | 50.3765 | 73.744 | 27.5855 | 27.5855 | 27.5855 | 27.5855 | 123.307 | 209.1146 | 188.5849 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 21 | 5085 | 22.2 | 22.2 | 21.6667 | 21.8193 | 15 | 73 | 73 | 0 | 3 | -4.2708 | 307.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 3 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 22 | 5086 | 21.3 | 21.3 | 21.6667 | 21.8193 | 15 | 72 | 72 | 0 | 0 | -10.9008 | 320.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 23 | 5087 | 19.9 | 19.9 | 21.6667 | 21.8193 | 15 | 75 | 75 | 0 | 0 | -15.8983 | 334.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2008 | 7 | 31 | 24 | 5088 | 19.9 | 19.9 | 23.4458 | 22.3261 | 15 | 76 | 76 | 0 | 0 | -18.8536 | 348.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 1 | 5089 | 18.6 | 18.6 | 23.4458 | 22.3261 | 15 | 79 | 79 | 0 | 0 | -19.4764 | 3.6565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 2 | 5090 | 18.6 | 18.6 | 23.4458 | 22.3261 | 15 | 89 | 89 | 0 | 0 | -17.9412 | 18.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 3 | 5091 | 17.8 | 17.8 | 23.4458 | 22.3261 | 15 | 89 | 89 | 0 | 0 | -13.9388 | 32.8572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 4 | 5092 | 17.6 | 17.6 | 23.4458 | 22.3261 | 15 | 89 | 89 | 0 | 0 | -8.0827 | 46.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 5 | 5093 | 16.5 | 16.5 | 23.4458 | 22.3261 | 15 | 92 | 92 | 0 | 0 | -0.80384 | 58.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 6 | 5094 | 15.4 | 15.4 | 23.4458 | 22.3261 | 15 | 94 | 94 | 0.37922 | 5.9696 | 7.4818 | 70.0314 | 0.19867 | 0.36885 | 0.32297 | 0.087898 | 0 | 0 | 0 | 0 | 0.030384 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 5.9696 | 3.1078 | 3.2779 | 3.2321 | 2.997 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 7 | 5095 | 16.4 | 16.4 | 23.4458 | 22.3261 | 15 | 86 | 86 | 3.1899 | 49.2656 | 16.3968 | 81.4125 | 1.0801 | 2.8657 | 2.9726 | 1.3382 | 0 | 0 | 0 | 0 | 0.73436 | 34.6084 | 54.0806 | 55.2465 | 37.4232 | 22.8299 | 22.8299 | 22.8299 | 22.8299 | 49.2656 | 35.6885 | 56.9463 | 58.2191 | 38.7614 | 22.8299 | 22.8299 | 22.8299 | 22.8299 | 50 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 1 | 8 | 5096 | 17.6 | 17.6 | 23.4458 | 22.3261 | 15 | 80 | 80 | 6.6524 | 114.4633 | 25.5841 | 93.1052 | 0.95294 | 5.1359 | 6.3103 | 3.7882 | 0 | 0 | 0 | 0 | 2.5367 | 59.4235 | 91.0392 | 99.9158 | 80.8534 | 52.221 | 52.221 | 52.221 | 52.221 | 114.4633 | 60.3764 | 96.1751 | 106.2261 | 84.6416 | 52.221 | 52.221 | 52.221 | 52.221 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 9 | 5097 | 18.3 | 18.3 | 23.4458 | 22.3261 | 15 | 69 | 69 | 146.8081 | 237.1971 | 34.6573 | 105.8474 | 0 | 88.4214 | 132.2195 | 98.5652 | 7.1727 | 0 | 0 | 0 | 76.8029 | 109.7316 | 208.7883 | 257.8544 | 220.1521 | 117.767 | 109.7316 | 109.7316 | 109.7316 | 237.1971 | 109.7316 | 297.2098 | 390.0739 | 318.7173 | 124.9397 | 109.7316 | 109.7316 | 109.7316 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 10 | 5098 | 18.3 | 18.3 | 23.4458 | 22.3261 | 15 | 61 | 61 | 50.0273 | 275.6786 | 43.1141 | 120.6435 | 0 | 20.0461 | 39.5869 | 35.9381 | 11.2373 | 0 | 0 | 0 | 32.3214 | 122.9023 | 171.6516 | 219.1718 | 210.2986 | 150.2299 | 122.9023 | 122.9023 | 122.9023 | 275.6786 | 122.9023 | 191.6978 | 258.7587 | 246.2368 | 161.4672 | 122.9023 | 122.9023 | 122.9023 | 308 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 11 | 5099 | 18.8 | 18.8 | 23.4458 | 22.3261 | 15 | 59 | 59 | 153.8682 | 335.8763 | 50.2081 | 138.7474 | 0 | 27.8511 | 96.6377 | 108.8153 | 57.2503 | 0 | 0 | 0 | 114.1237 | 151.2343 | 183.5956 | 263.5214 | 277.671 | 217.7557 | 151.2343 | 151.2343 | 151.2343 | 335.8763 | 151.2343 | 211.4466 | 360.1591 | 386.4862 | 275.006 | 151.2343 | 151.2343 | 151.2343 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 12 | 5100 | 20 | 20 | 23.4458 | 22.3261 | 15 | 62 | 62 | 547.0541 | 243.4645 | 54.8493 | 161.0256 | 0 | 0 | 230.8593 | 349.3668 | 263.22 | 22.8825 | 0 | 0 | 439.5355 | 143.0168 | 143.0168 | 218.0183 | 256.5189 | 228.5316 | 150.4509 | 143.0168 | 143.0168 | 243.4645 | 143.0168 | 143.0168 | 448.8776 | 605.8858 | 491.7517 | 173.3334 | 143.0168 | 143.0168 | 683 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 13 | 5101 | 19.9 | 19.9 | 23.4458 | 22.3261 | 15 | 58 | 58 | 159.5264 | 374.0609 | 55.8834 | 186.1791 | 0 | 0 | 29.8626 | 82.5307 | 86.8535 | 40.2987 | 0 | 0 | 131.9391 | 165.118 | 165.118 | 200.0498 | 261.6584 | 266.715 | 212.2574 | 165.118 | 165.118 | 374.0609 | 165.118 | 165.118 | 229.9124 | 344.1892 | 353.5685 | 252.5561 | 165.118 | 165.118 | 506 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 14 | 5102 | 19.7 | 19.7 | 23.4458 | 22.3261 | 15 | 58 | 58 | 472.1841 | 275.1244 | 52.9818 | 210.3069 | 0 | 0 | 0 | 166.024 | 263.2997 | 206.338 | 28.5063 | 0 | 382.8756 | 145.3003 | 145.3003 | 145.3003 | 214.8017 | 255.5235 | 231.678 | 157.2336 | 145.3003 | 275.1244 | 145.3003 | 145.3003 | 145.3003 | 380.8257 | 518.8232 | 438.016 | 185.7399 | 145.3003 | 658 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 15 | 5103 | 20.6 | 20.6 | 23.4458 | 22.3261 | 15 | 50 | 50 | 473.5329 | 256.0177 | 46.9945 | 230.5356 | 0 | 0 | 0 | 72.3128 | 246.136 | 275.7761 | 143.8703 | 0 | 357.9823 | 137.9044 | 137.9044 | 137.9044 | 166.2794 | 234.4863 | 246.1169 | 194.3581 | 137.9044 | 256.0177 | 137.9044 | 137.9044 | 137.9044 | 238.5922 | 480.6224 | 521.893 | 338.2284 | 137.9044 | 614 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 16 | 5104 | 21.8 | 21.8 | 23.4458 | 22.3261 | 15 | 50 | 50 | 813.1767 | 122.2182 | 39.1244 | 246.8729 | 0 | 0 | 0 | 0 | 352.5293 | 552.0553 | 428.1948 | 53.5036 | 541.7818 | 110.7018 | 110.7018 | 110.7018 | 110.7018 | 143.7585 | 162.4681 | 150.8537 | 115.7188 | 122.2182 | 110.7018 | 110.7018 | 110.7018 | 110.7018 | 496.2879 | 714.5235 | 579.0485 | 169.2224 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 17 | 5105 | 21.1 | 21.1 | 23.4458 | 22.3261 | 15 | 52 | 52 | 807.8176 | 101.4405 | 30.2937 | 260.5268 | 0 | 0 | 0 | 0 | 246.1449 | 581.573 | 576.3234 | 233.4714 | 442.5595 | 94.0089 | 94.0089 | 94.0089 | 94.0089 | 114.9863 | 143.5728 | 143.1254 | 113.9062 | 101.4405 | 94.0089 | 94.0089 | 94.0089 | 94.0089 | 361.1313 | 725.1457 | 719.4488 | 347.3777 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 1 | 18 | 5106 | 20.7 | 20.7 | 23.4458 | 22.3261 | 15 | 54 | 54 | 506.2623 | 132.0183 | 21.1121 | 272.6525 | 0 | 0 | 0 | 0 | 71.9462 | 355.7578 | 431.1713 | 254.0105 | 206.9817 | 82.7478 | 82.7478 | 82.7478 | 82.7478 | 99.2061 | 164.1307 | 181.3822 | 140.855 | 132.0183 | 82.7478 | 82.7478 | 82.7478 | 82.7478 | 171.1524 | 519.8885 | 612.5535 | 394.8655 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 19 | 5107 | 20 | 20 | 23.4458 | 22.3261 | 15 | 57 | 57 | 569.9344 | 48.3475 | 12.012 | 284.1146 | 24.6051 | 0 | 0 | 0 | 0 | 358.1527 | 531.1095 | 392.9495 | 207.6525 | 49.9957 | 47.8366 | 47.8366 | 47.8366 | 47.8366 | 79.2634 | 94.4398 | 82.3167 | 48.3475 | 74.6007 | 47.8366 | 47.8366 | 47.8366 | 47.8366 | 437.4161 | 625.5492 | 475.2662 | 256 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 20 | 5108 | 18.6 | 18.6 | 23.4458 | 22.3261 | 15 | 63 | 63 | 200.6041 | 22.3187 | 3.3576 | 295.5544 | 47.8486 | 0 | 0 | 0 | 0 | 100.7199 | 190.2881 | 168.388 | 80.6813 | 31.4628 | 20.6343 | 20.6343 | 20.6343 | 20.6343 | 43.4279 | 63.6978 | 58.7417 | 22.3187 | 79.3114 | 20.6343 | 20.6343 | 20.6343 | 20.6343 | 144.1478 | 253.9858 | 227.1297 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 21 | 5109 | 17.4 | 17.4 | 23.4458 | 22.3261 | 15 | 69 | 69 | 0 | 8 | -4.4887 | 307.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 8 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 3.784 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 22 | 5110 | 15.3 | 15.3 | 23.4458 | 22.3261 | 15 | 79 | 79 | 0 | 0 | -11.1308 | 320.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 23 | 5111 | 14.8 | 14.8 | 23.4458 | 22.3261 | 15 | 81 | 81 | 0 | 0 | -16.1391 | 333.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 1 | 24 | 5112 | 14.3 | 14.3 | 18.2542 | 21.2704 | 15 | 83 | 83 | 0 | 0 | -19.1012 | 348.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 1 | 5113 | 14.2 | 14.2 | 18.2542 | 21.2704 | 15 | 83 | 83 | 0 | 0 | -19.7242 | 3.6771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 2 | 5114 | 12.8 | 12.8 | 18.2542 | 21.2704 | 15 | 87 | 87 | 0 | 0 | -18.1867 | 18.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 3 | 5115 | 12.3 | 12.3 | 18.2542 | 21.2704 | 15 | 91 | 91 | 0 | 0 | -14.172 | 32.9599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 4 | 5116 | 12.8 | 12.8 | 18.2542 | 21.2704 | 15 | 88 | 88 | 0 | 0 | -8.3015 | 46.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 5 | 5117 | 12.3 | 12.3 | 18.2542 | 21.2704 | 15 | 91 | 91 | 0 | 0 | -1.009 | 58.5527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 6 | 5118 | 12.8 | 12.8 | 18.2542 | 21.2704 | 15 | 89 | 89 | 4.1619 | 18.6813 | 7.2875 | 70.1958 | 2.171 | 4.0454 | 3.5501 | 0.97515 | 0 | 0 | 0 | 0 | 0.3187 | 11.1387 | 13.1856 | 12.6447 | 9.8328 | 8.768 | 8.768 | 8.768 | 8.768 | 18.6813 | 13.3097 | 17.231 | 16.1947 | 10.808 | 8.768 | 8.768 | 8.768 | 8.768 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 7 | 5119 | 14.3 | 14.3 | 18.2542 | 21.2704 | 15 | 83 | 83 | 24.6964 | 88.3968 | 16.2092 | 81.5904 | 8.2997 | 22.1662 | 23.048 | 10.4286 | 0 | 0 | 0 | 0 | 5.6032 | 93.7134 | 186.4833 | 192.383 | 107.9565 | 38.1865 | 38.1865 | 38.1865 | 38.1865 | 88.3968 | 102.0131 | 208.6495 | 215.431 | 118.3851 | 38.1865 | 38.1865 | 38.1865 | 38.1865 | 94 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 2 | 8 | 5120 | 15.7 | 15.7 | 18.2542 | 21.2704 | 15 | 78 | 78 | 105.7484 | 171.0059 | 25.3979 | 93.2959 | 14.8509 | 81.5321 | 100.453 | 60.5298 | 0 | 0 | 0 | 0 | 39.9941 | 98.0417 | 191.1786 | 217.6063 | 161.8437 | 77.2988 | 77.2988 | 77.2988 | 77.2988 | 171.0059 | 112.8926 | 272.7108 | 318.0593 | 222.3736 | 77.2988 | 77.2988 | 77.2988 | 77.2988 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 9 | 5121 | 17.8 | 17.8 | 18.2542 | 21.2704 | 15 | 71 | 71 | 117.405 | 235.9215 | 34.4658 | 106.0494 | 0 | 70.5586 | 105.8825 | 79.1818 | 6.0976 | 0 | 0 | 0 | 61.0785 | 107.7795 | 189.3916 | 230.2492 | 199.3657 | 114.8323 | 107.7795 | 107.7795 | 107.7795 | 235.9215 | 107.7795 | 259.9501 | 336.1317 | 278.5476 | 120.9299 | 107.7795 | 107.7795 | 107.7795 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 10 | 5122 | 18.6 | 18.6 | 18.2542 | 21.2704 | 15 | 70 | 70 | 90.4721 | 288.7962 | 42.9097 | 120.8489 | 0 | 36.1061 | 71.6837 | 65.2699 | 20.6219 | 0 | 0 | 0 | 58.2038 | 129.918 | 182.9181 | 235.1424 | 225.7277 | 160.1888 | 129.918 | 129.918 | 129.918 | 288.7962 | 129.918 | 219.0243 | 306.8261 | 290.9976 | 180.8108 | 129.918 | 129.918 | 129.918 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 11 | 5123 | 20.4 | 20.4 | 18.2542 | 21.2704 | 15 | 65 | 65 | 196.3927 | 329.8475 | 49.9836 | 138.9315 | 0 | 35.1668 | 123.4928 | 139.4783 | 73.7594 | 0 | 0 | 0 | 145.1525 | 152.3795 | 183.7114 | 262.4056 | 276.6479 | 218.0955 | 152.3795 | 152.3795 | 152.3795 | 329.8475 | 152.3795 | 218.8783 | 385.8983 | 416.1262 | 291.8549 | 152.3795 | 152.3795 | 152.3795 | 475 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 12 | 5124 | 22.9 | 22.9 | 18.2542 | 21.2704 | 15 | 60 | 60 | 226.6476 | 351.4688 | 54.604 | 161.137 | 0 | 0 | 95.7427 | 145.3929 | 109.8739 | 9.9922 | 0 | 0 | 181.5312 | 163.2503 | 163.2503 | 238.1843 | 277.0435 | 249.2442 | 171.0708 | 163.2503 | 163.2503 | 351.4688 | 163.2503 | 163.2503 | 333.927 | 422.4364 | 359.1181 | 181.0631 | 163.2503 | 163.2503 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 13 | 5125 | 25.2 | 25.2 | 18.2542 | 21.2704 | 15 | 52 | 52 | 478.5164 | 277.4242 | 55.6298 | 186.1683 | 0 | 0 | 89.6101 | 248.8258 | 262.2828 | 122.0981 | 0 | 0 | 394.5758 | 147.9006 | 147.9006 | 184.9342 | 250.734 | 256.2954 | 198.3606 | 147.9006 | 147.9006 | 277.4242 | 147.9006 | 147.9006 | 274.5442 | 499.5598 | 518.5782 | 320.4587 | 147.9006 | 147.9006 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 14 | 5126 | 25.9 | 25.9 | 18.2542 | 21.2704 | 15 | 45 | 45 | 775.2846 | 159.2965 | 52.7385 | 210.1885 | 0 | 0 | 0 | 274.4391 | 435.1434 | 340.9466 | 47.0279 | 0 | 626.7035 | 130.1275 | 130.1275 | 130.1275 | 162.515 | 181.4803 | 170.3638 | 135.6774 | 130.1275 | 159.2965 | 130.1275 | 130.1275 | 130.1275 | 436.954 | 616.6236 | 511.3104 | 182.7054 | 130.1275 | 786 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 15 | 5127 | 26.3 | 26.3 | 18.2542 | 21.2704 | 15 | 52 | 52 | 18.2875 | 280.2222 | 46.7691 | 230.3657 | 0 | 0 | 0 | 2.8305 | 9.5706 | 10.7043 | 5.5676 | 0 | 13.7778 | 135.287 | 135.287 | 135.287 | 140.0145 | 151.2717 | 153.1653 | 144.586 | 135.287 | 280.2222 | 135.287 | 135.287 | 135.287 | 142.845 | 160.8423 | 163.8697 | 150.1537 | 135.287 | 294 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 16 | 5128 | 27.2 | 27.2 | 18.2542 | 21.2704 | 15 | 49 | 49 | 546.5397 | 201.3471 | 38.9137 | 246.6913 | 0 | 0 | 0 | 0 | 238.7905 | 372.7068 | 288.2965 | 35.0061 | 362.6529 | 120.3005 | 120.3005 | 120.3005 | 120.3005 | 181.7953 | 216.2823 | 194.5444 | 129.3154 | 201.3471 | 120.3005 | 120.3005 | 120.3005 | 120.3005 | 420.5858 | 588.9891 | 482.8409 | 164.3215 | 564 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 17 | 5129 | 26.3 | 26.3 | 18.2542 | 21.2704 | 15 | 56 | 56 | 117.2034 | 247.1279 | 30.091 | 260.3504 | 0 | 0 | 0 | 0 | 36.0845 | 84.7375 | 83.7524 | 33.7063 | 63.8721 | 115.4539 | 115.4539 | 115.4539 | 115.4539 | 154.3866 | 206.8798 | 205.8169 | 151.8206 | 247.1279 | 115.4539 | 115.4539 | 115.4539 | 115.4539 | 190.4711 | 291.6173 | 289.5693 | 185.5269 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 2 | 18 | 5130 | 26.8 | 26.8 | 18.2542 | 21.2704 | 15 | 53 | 53 | 120.5197 | 184.097 | 20.911 | 272.4868 | 0 | 0 | 0 | 0 | 17.4792 | 85.0515 | 102.8018 | 60.3322 | 48.903 | 89.3999 | 89.3999 | 89.3999 | 89.3999 | 104.0843 | 160.8519 | 175.764 | 140.0852 | 184.097 | 89.3999 | 89.3999 | 89.3999 | 89.3999 | 121.5635 | 245.9035 | 278.5659 | 200.4174 | 233 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 19 | 5131 | 25.2 | 25.2 | 18.2542 | 21.2704 | 15 | 59 | 59 | 56.8444 | 110.4811 | 11.8073 | 283.9616 | 2.304 | 0 | 0 | 0 | 0 | 35.8831 | 53.0504 | 39.1415 | 14.5189 | 56.0364 | 54.2914 | 54.2914 | 54.2914 | 54.2914 | 81.4676 | 94.4693 | 83.9353 | 110.4811 | 58.3404 | 54.2914 | 54.2914 | 54.2914 | 54.2914 | 117.3507 | 147.5197 | 123.0768 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 20 | 5132 | 24.3 | 24.3 | 18.2542 | 21.2704 | 15 | 65 | 65 | 197.3483 | 46.4502 | 3.145 | 295.4158 | 46.6069 | 0 | 0 | 0 | 0 | 99.6023 | 187.4659 | 165.5145 | 20.5498 | 43.9274 | 26.4902 | 26.4902 | 26.4902 | 26.4902 | 63.7549 | 96.6277 | 88.4149 | 46.4502 | 90.5344 | 26.4902 | 26.4902 | 26.4902 | 26.4902 | 163.3572 | 284.0936 | 253.9294 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 21 | 5133 | 22.6 | 22.6 | 18.2542 | 21.2704 | 15 | 73 | 73 | 0 | 3 | -4.7121 | 307.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 3 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 1.3902 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 22 | 5134 | 20.3 | 20.3 | 18.2542 | 21.2704 | 15 | 87 | 87 | 0 | 0 | -11.3662 | 320.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 23 | 5135 | 20 | 20 | 18.2542 | 21.2704 | 15 | 94 | 94 | 0 | 0 | -16.3853 | 333.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 2 | 24 | 5136 | 19.2 | 19.2 | 19.8417 | 20.8425 | 15 | 98 | 98 | 0 | 0 | -19.3539 | 348.5517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 1 | 5137 | 19.5 | 19.5 | 19.8417 | 20.8425 | 15 | 92 | 92 | 0 | 0 | -19.9769 | 3.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 2 | 5138 | 18.8 | 18.8 | 19.8417 | 20.8425 | 15 | 92 | 92 | 0 | 0 | -18.4365 | 18.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 3 | 5139 | 18.2 | 18.2 | 19.8417 | 20.8425 | 15 | 95 | 95 | 0 | 0 | -14.4089 | 33.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 4 | 5140 | 18.7 | 18.7 | 19.8417 | 20.8425 | 15 | 94 | 94 | 0 | 0 | -8.5235 | 46.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 5 | 5141 | 18.7 | 18.7 | 19.8417 | 20.8425 | 15 | 95 | 95 | 0 | 0 | -1.2169 | 58.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 6 | 5142 | 19.2 | 19.2 | 19.8417 | 20.8425 | 15 | 93 | 93 | 0.11427 | 2.9917 | 7.0907 | 70.365 | 0.059339 | 0.11099 | 0.09762 | 0.027069 | 0 | 0 | 0 | 0 | 0.0083368 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 1.456 | 2.9917 | 1.5153 | 1.567 | 1.5536 | 1.4831 | 1.456 | 1.456 | 1.456 | 1.456 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 7 | 5143 | 18.5 | 18.5 | 19.8417 | 20.8425 | 15 | 96 | 96 | 0.086602 | 7.9806 | 16.0192 | 81.773 | 0.028878 | 0.077655 | 0.080943 | 0.036815 | 0 | 0 | 0 | 0 | 0.019354 | 3.728 | 3.728 | 3.728 | 3.728 | 3.728 | 3.728 | 3.728 | 3.728 | 7.9806 | 3.7568 | 3.8056 | 3.8089 | 3.7648 | 3.728 | 3.728 | 3.728 | 3.728 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 3 | 8 | 5144 | 18.3 | 18.3 | 19.8417 | 20.8425 | 15 | 88 | 88 | 0.84769 | 41.6821 | 25.2093 | 93.4916 | 0.11659 | 0.65265 | 0.80639 | 0.48776 | 0 | 0 | 0 | 0 | 0.3179 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 41.6821 | 20.2273 | 20.7634 | 20.9172 | 20.5985 | 20.1108 | 20.1108 | 20.1108 | 20.1108 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 9 | 5145 | 18.3 | 18.3 | 19.8417 | 20.8425 | 15 | 86 | 86 | 0.63149 | 49.6734 | 34.2717 | 106.2565 | 0 | 0.37865 | 0.57029 | 0.42786 | 0.034796 | 0 | 0 | 0 | 0.32664 | 23.8874 | 23.8874 | 23.8874 | 23.8874 | 23.8874 | 23.8874 | 23.8874 | 23.8874 | 49.6734 | 23.8874 | 24.2661 | 24.4577 | 24.3153 | 23.9222 | 23.8874 | 23.8874 | 23.8874 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 10 | 5146 | 17.5 | 17.5 | 19.8417 | 20.8425 | 15 | 94 | 94 | 1.0808 | 80.3077 | 42.7023 | 121.0594 | 0 | 0.42949 | 0.85741 | 0.78307 | 0.25002 | 0 | 0 | 0 | 0.69227 | 39.1608 | 39.1608 | 39.1608 | 39.1608 | 39.1608 | 39.1608 | 39.1608 | 39.1608 | 80.3077 | 39.1608 | 39.5903 | 40.0182 | 39.9439 | 39.4108 | 39.1608 | 39.1608 | 39.1608 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 11 | 5147 | 17.7 | 17.7 | 19.8417 | 20.8425 | 15 | 90 | 90 | 1.0548 | 91.2232 | 49.7555 | 139.1205 | 0 | 0.18675 | 0.66401 | 0.75231 | 0.39992 | 0 | 0 | 0 | 0.77677 | 44.639 | 44.639 | 44.639 | 44.639 | 44.639 | 44.639 | 44.639 | 44.639 | 91.2232 | 44.639 | 44.8257 | 45.303 | 45.3913 | 45.0389 | 44.639 | 44.639 | 44.639 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 12 | 5148 | 19.3 | 19.3 | 19.8417 | 20.8425 | 15 | 78 | 78 | 30.0782 | 319.9868 | 54.3543 | 161.2529 | 0 | 0 | 12.7177 | 19.3818 | 14.6924 | 1.3963 | 0 | 0 | 24.0132 | 140.6829 | 140.6829 | 189.0575 | 214.4061 | 196.5685 | 145.9939 | 140.6829 | 140.6829 | 319.9868 | 140.6829 | 140.6829 | 201.7753 | 233.7879 | 211.2609 | 147.3902 | 140.6829 | 140.6829 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 13 | 5149 | 20.9 | 20.9 | 19.8417 | 20.8425 | 15 | 72 | 72 | 60.8042 | 358.017 | 55.3712 | 186.1612 | 0 | 0 | 11.3885 | 31.7799 | 33.555 | 15.6741 | 0 | 0 | 49.983 | 156.8422 | 156.8422 | 181.2423 | 224.9312 | 228.7345 | 190.4242 | 156.8422 | 156.8422 | 358.017 | 156.8422 | 156.8422 | 192.6308 | 256.7111 | 262.2895 | 206.0983 | 156.8422 | 156.8422 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 14 | 5150 | 21.8 | 21.8 | 19.8417 | 20.8425 | 15 | 65 | 65 | 190.164 | 360.7695 | 52.4896 | 210.0725 | 0 | 0 | 0 | 67.7691 | 107.4379 | 84.171 | 11.5979 | 0 | 153.2305 | 162.9341 | 162.9341 | 162.9341 | 226.3014 | 263.3937 | 241.638 | 173.7787 | 162.9341 | 360.7695 | 162.9341 | 162.9341 | 162.9341 | 294.0705 | 370.8315 | 325.809 | 185.3766 | 162.9341 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 15 | 5151 | 22.9 | 22.9 | 19.8417 | 20.8425 | 15 | 64 | 64 | 649.8958 | 190.0913 | 46.5379 | 230.1967 | 0 | 0 | 0 | 101.9373 | 342.4571 | 382.3702 | 198.296 | 0 | 487.9087 | 127.4751 | 127.4751 | 127.4751 | 148.9549 | 199.636 | 208.0463 | 169.2591 | 127.4751 | 190.0913 | 127.4751 | 127.4751 | 127.4751 | 250.8922 | 542.0931 | 590.4165 | 367.5551 | 127.4751 | 678 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 16 | 5152 | 21.5 | 21.5 | 19.8417 | 20.8425 | 15 | 70 | 70 | 89.8946 | 296.6005 | 38.6973 | 246.5096 | 0 | 0 | 0 | 0 | 39.5847 | 61.582 | 47.5054 | 5.6008 | 59.3995 | 135.5484 | 135.5484 | 135.5484 | 135.5484 | 182.0919 | 207.9563 | 191.4051 | 142.1338 | 296.6005 | 135.5484 | 135.5484 | 135.5484 | 135.5484 | 221.6766 | 269.5383 | 238.9106 | 147.7346 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 17 | 5153 | 21.5 | 21.5 | 19.8417 | 20.8425 | 15 | 69 | 69 | 140.047 | 246.0911 | 29.8828 | 260.1733 | 0 | 0 | 0 | 0 | 43.567 | 101.689 | 100.2429 | 40.076 | 75.9089 | 116.2726 | 116.2726 | 116.2726 | 116.2726 | 155.5144 | 207.8663 | 206.5639 | 152.37 | 246.0911 | 116.2726 | 116.2726 | 116.2726 | 116.2726 | 199.0814 | 309.5553 | 306.8068 | 192.446 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 3 | 18 | 5154 | 21.6 | 21.6 | 19.8417 | 20.8425 | 15 | 60 | 60 | 637.3911 | 104.3705 | 20.7046 | 272.3202 | 0 | 0 | 0 | 0 | 94.3197 | 451.7415 | 544.5393 | 318.3533 | 256.6295 | 76.0922 | 76.0922 | 76.0922 | 76.0922 | 90.2262 | 143.7862 | 157.6921 | 123.7979 | 104.3705 | 76.0922 | 76.0922 | 76.0922 | 76.0922 | 184.5459 | 595.5277 | 702.2314 | 442.1512 | 361 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 19 | 5155 | 20.7 | 20.7 | 19.8417 | 20.8425 | 15 | 64 | 64 | 459.9023 | 87.0788 | 11.5972 | 283.8075 | 17.4163 | 0 | 0 | 0 | 0 | 291.6326 | 429.8471 | 316.263 | 115.9212 | 58.2583 | 54.7776 | 54.7776 | 54.7776 | 54.7776 | 113.0616 | 140.6843 | 117.9841 | 87.0788 | 75.6746 | 54.7776 | 54.7776 | 54.7776 | 54.7776 | 404.6942 | 570.5315 | 434.2471 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 20 | 5156 | 19.7 | 19.7 | 19.8417 | 20.8425 | 15 | 71 | 71 | 188.3983 | 45.0558 | 2.9271 | 295.2764 | 44.0454 | 0 | 0 | 0 | 0 | 95.5822 | 179.2191 | 157.8719 | 18.9442 | 42.6922 | 25.6465 | 25.6465 | 25.6465 | 25.6465 | 62.637 | 95.0047 | 86.7433 | 45.0558 | 86.7376 | 25.6465 | 25.6465 | 25.6465 | 25.6465 | 158.2193 | 274.2238 | 244.6151 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 21 | 5157 | 16.9 | 16.9 | 19.8417 | 20.8425 | 15 | 84 | 84 | 0 | 6 | -4.9409 | 307.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 6 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 2.8208 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 22 | 5158 | 14.8 | 14.8 | 19.8417 | 20.8425 | 15 | 94 | 94 | 0 | 0 | -11.607 | 320.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 23 | 5159 | 13.7 | 13.7 | 19.8417 | 20.8425 | 15 | 96 | 96 | 0 | 0 | -16.6368 | 333.8135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 3 | 24 | 5160 | 15.2 | 15.2 | 18.9125 | 20.2775 | 15 | 94 | 94 | 0 | 0 | -19.6118 | 348.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 1 | 5161 | 16 | 16 | 18.9125 | 20.2775 | 15 | 96 | 96 | 0 | 0 | -20.2343 | 3.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 2 | 5162 | 16.4 | 16.4 | 18.9125 | 20.2775 | 15 | 91 | 91 | 0 | 0 | -18.6904 | 18.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 3 | 5163 | 17.1 | 17.1 | 18.9125 | 20.2775 | 15 | 84 | 84 | 0 | 0 | -14.6493 | 33.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 4 | 5164 | 16.5 | 16.5 | 18.9125 | 20.2775 | 15 | 89 | 89 | 0 | 0 | -8.7486 | 46.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 5 | 5165 | 16.2 | 16.2 | 18.9125 | 20.2775 | 15 | 89 | 89 | 0 | 0 | -1.4275 | 58.8651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 6 | 5166 | 15.9 | 15.9 | 18.9125 | 20.2775 | 15 | 94 | 94 | 0 | 0 | 6.8916 | 70.5389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 7 | 5167 | 15.7 | 15.7 | 18.9125 | 20.2775 | 15 | 96 | 96 | 0.50385 | 18.8891 | 15.827 | 81.9605 | 0.16665 | 0.45134 | 0.47163 | 0.21565 | 0 | 0 | 0 | 0 | 0.11086 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 18.8891 | 9.2215 | 9.5061 | 9.5264 | 9.2705 | 9.0548 | 9.0548 | 9.0548 | 9.0548 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 4 | 8 | 5168 | 16.3 | 16.3 | 18.9125 | 20.2775 | 15 | 93 | 93 | 3.6154 | 84.6559 | 25.0182 | 93.6921 | 0.48647 | 2.7794 | 3.4442 | 2.0914 | 0 | 0 | 0 | 0 | 1.3441 | 42.6896 | 51.8841 | 54.5498 | 49.1253 | 40.7389 | 40.7389 | 40.7389 | 40.7389 | 84.6559 | 43.1761 | 54.6634 | 57.994 | 51.2168 | 40.7389 | 40.7389 | 40.7389 | 40.7389 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 9 | 5169 | 16.7 | 16.7 | 18.9125 | 20.2775 | 15 | 93 | 93 | 2.9804 | 106.4675 | 34.075 | 106.4684 | 0 | 1.7828 | 2.6951 | 2.0287 | 0.17391 | 0 | 0 | 0 | 1.5325 | 53.136 | 53.3547 | 53.4666 | 53.3849 | 53.1573 | 53.136 | 53.136 | 53.136 | 106.4675 | 53.136 | 55.1375 | 56.1617 | 55.4136 | 53.3312 | 53.136 | 53.136 | 53.136 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 10 | 5170 | 17.5 | 17.5 | 18.9125 | 20.2775 | 15 | 87 | 87 | 7.8716 | 200.9806 | 42.4917 | 121.2748 | 0 | 3.1143 | 6.2526 | 5.7282 | 1.8484 | 0 | 0 | 0 | 5.0194 | 95.169 | 107.8959 | 120.7212 | 118.5783 | 102.7226 | 95.169 | 95.169 | 95.169 | 200.9806 | 95.169 | 111.0102 | 126.9738 | 124.3065 | 104.5709 | 95.169 | 95.169 | 95.169 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 11 | 5171 | 18.2 | 18.2 | 18.9125 | 20.2775 | 15 | 69 | 69 | 31.4411 | 295.932 | 49.5237 | 139.3142 | 0 | 5.5007 | 19.815 | 22.5218 | 12.0357 | 0 | 0 | 0 | 23.068 | 131.1543 | 150.8788 | 202.2066 | 211.9129 | 174.3119 | 131.1543 | 131.1543 | 131.1543 | 295.932 | 131.1543 | 156.3796 | 222.0216 | 234.4348 | 186.3477 | 131.1543 | 131.1543 | 131.1543 | 319 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 12 | 5172 | 20 | 20 | 18.9125 | 20.2775 | 15 | 59 | 59 | 38.9509 | 330.0064 | 54.1003 | 161.373 | 0 | 0 | 16.4831 | 25.2127 | 19.173 | 1.902 | 0 | 0 | 30.9936 | 144.9214 | 144.9214 | 195.9264 | 222.9391 | 204.25 | 150.807 | 144.9214 | 144.9214 | 330.0064 | 144.9214 | 144.9214 | 212.4095 | 248.1518 | 223.423 | 152.7091 | 144.9214 | 144.9214 | 361 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 13 | 5173 | 19.9 | 19.9 | 18.9125 | 20.2775 | 15 | 53 | 53 | 229.098 | 359.2732 | 55.1077 | 186.1579 | 0 | 0 | 42.9076 | 120.3543 | 127.299 | 59.6738 | 0 | 0 | 187.7268 | 157.4649 | 157.4649 | 199.3471 | 274.9429 | 281.7217 | 215.7126 | 157.4649 | 157.4649 | 359.2732 | 157.4649 | 157.4649 | 242.2547 | 395.2972 | 409.0208 | 275.3864 | 157.4649 | 157.4649 | 547 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 14 | 5174 | 21.2 | 21.2 | 18.9125 | 20.2775 | 15 | 52 | 52 | 602.8336 | 221.8379 | 52.2353 | 209.959 | 0 | 0 | 0 | 216.2771 | 342.8528 | 268.59 | 36.9908 | 0 | 484.1621 | 136.549 | 136.549 | 136.549 | 191.3411 | 223.4081 | 204.5942 | 145.9203 | 136.549 | 221.8379 | 136.549 | 136.549 | 136.549 | 407.6182 | 566.2609 | 473.1842 | 182.9111 | 136.549 | 706 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 15 | 5175 | 21 | 21 | 18.9125 | 20.2775 | 15 | 53 | 53 | 683.7702 | 177.5156 | 46.3012 | 230.0287 | 0 | 0 | 0 | 108.6706 | 362.8013 | 404.4079 | 209.1178 | 0 | 511.4844 | 125.5988 | 125.5988 | 125.5988 | 146.3379 | 194.837 | 202.7774 | 165.5076 | 125.5988 | 177.5156 | 125.5988 | 125.5988 | 125.5988 | 255.0085 | 557.6384 | 607.1853 | 374.6254 | 125.5988 | 689 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 16 | 5176 | 20.7 | 20.7 | 18.9125 | 20.2775 | 15 | 53 | 53 | 206.133 | 292.3794 | 38.4753 | 246.3278 | 0 | 0 | 0 | 0 | 91.4851 | 141.8624 | 109.1387 | 12.483 | 135.6206 | 138.9087 | 138.9087 | 138.9087 | 138.9087 | 202.9711 | 238.2478 | 215.3331 | 147.6499 | 292.3794 | 138.9087 | 138.9087 | 138.9087 | 138.9087 | 294.4561 | 380.1103 | 324.4718 | 160.1329 | 428 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 17 | 5177 | 20.6 | 20.6 | 18.9125 | 20.2775 | 15 | 57 | 57 | 768.2991 | 107.8753 | 29.6691 | 259.9956 | 0 | 0 | 0 | 0 | 241.4974 | 560.2905 | 550.873 | 218.7616 | 414.1247 | 93.9515 | 93.9515 | 93.9515 | 93.9515 | 116.6798 | 146.6826 | 145.7963 | 114.54 | 107.8753 | 93.9515 | 93.9515 | 93.9515 | 93.9515 | 358.1771 | 706.9731 | 696.6693 | 333.3016 | 522 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 18 | 5178 | 20.2 | 20.2 | 18.9125 | 20.2775 | 15 | 49 | 49 | 543.413 | 121.9523 | 20.4927 | 272.1527 | 0 | 0 | 0 | 0 | 82.0274 | 386.8004 | 464.991 | 270.7962 | 217.0477 | 79.2783 | 79.2783 | 79.2783 | 79.2783 | 95.1748 | 154.2385 | 169.3915 | 131.7574 | 121.9523 | 79.2783 | 79.2783 | 79.2783 | 79.2783 | 177.2022 | 541.039 | 634.3825 | 402.5535 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 19 | 5179 | 19.5 | 19.5 | 18.9125 | 20.2775 | 15 | 54 | 54 | 594.7227 | 53.2063 | 11.3818 | 283.6526 | 20.9261 | 0 | 0 | 0 | 0 | 378.8448 | 556.6935 | 408.4387 | 182.7937 | 49.6798 | 47.7652 | 47.7652 | 47.7652 | 47.7652 | 82.4271 | 98.6992 | 85.1348 | 53.2063 | 70.6059 | 47.7652 | 47.7652 | 47.7652 | 47.7652 | 461.2719 | 655.3926 | 493.5735 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 20 | 5180 | 17.9 | 17.9 | 18.9125 | 20.2775 | 15 | 61 | 61 | 200.6053 | 28.8704 | 2.7038 | 295.1362 | 46.4186 | 0 | 0 | 0 | 0 | 102.3077 | 191.1035 | 167.9535 | 54.1296 | 34.6118 | 21.3672 | 21.3672 | 21.3672 | 21.3672 | 50.5586 | 75.8946 | 69.2892 | 28.8704 | 81.0304 | 21.3672 | 21.3672 | 21.3672 | 21.3672 | 152.8663 | 266.9981 | 237.2427 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 21 | 5181 | 16.2 | 16.2 | 18.9125 | 20.2775 | 15 | 76 | 76 | 0 | 6 | -5.175 | 307.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 6 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 2.8247 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 22 | 5182 | 12.9 | 12.9 | 18.9125 | 20.2775 | 15 | 92 | 92 | 0 | 0 | -11.8532 | 319.9126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 23 | 5183 | 11.5 | 11.5 | 18.9125 | 20.2775 | 15 | 92 | 92 | 0 | 0 | -16.8936 | 333.7517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 4 | 24 | 5184 | 13.9 | 13.9 | 17.4167 | 19.3808 | 15 | 91 | 91 | 0 | 0 | -19.8748 | 348.5127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 1 | 5185 | 13.8 | 13.8 | 17.4167 | 19.3808 | 15 | 87 | 87 | 0 | 0 | -20.4965 | 3.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 2 | 5186 | 14.2 | 14.2 | 17.4167 | 19.3808 | 15 | 83 | 83 | 0 | 0 | -18.9484 | 18.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 3 | 5187 | 14.7 | 14.7 | 17.4167 | 19.3808 | 15 | 84 | 84 | 0 | 0 | -14.8933 | 33.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 4 | 5188 | 14.8 | 14.8 | 17.4167 | 19.3808 | 15 | 87 | 87 | 0 | 0 | -8.9766 | 46.6491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 5 | 5189 | 14.8 | 14.8 | 17.4167 | 19.3808 | 15 | 89 | 89 | 0 | 0 | -1.6406 | 59.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 6 | 5190 | 14.3 | 14.3 | 17.4167 | 19.3808 | 15 | 96 | 96 | 0 | 0 | 6.69 | 70.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 7 | 5191 | 14.7 | 14.7 | 17.4167 | 19.3808 | 15 | 94 | 94 | 0.52027 | 18.8874 | 15.6324 | 82.1527 | 0.17064 | 0.46555 | 0.48774 | 0.22423 | 0 | 0 | 0 | 0 | 0.11263 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 18.8874 | 9.2338 | 9.5287 | 9.5509 | 9.2874 | 9.0632 | 9.0632 | 9.0632 | 9.0632 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 5 | 8 | 5192 | 14.5 | 14.5 | 17.4167 | 19.3808 | 15 | 96 | 96 | 0.96319 | 43.6451 | 24.8249 | 93.8974 | 0.12664 | 0.73929 | 0.91888 | 0.56019 | 0 | 0 | 0 | 0 | 0.35489 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 43.6451 | 21.244 | 21.8567 | 22.0363 | 21.6776 | 21.1174 | 21.1174 | 21.1174 | 21.1174 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 9 | 5193 | 15.8 | 15.8 | 17.4167 | 19.3808 | 15 | 96 | 96 | 5.8997 | 146.9847 | 33.8757 | 106.6852 | 0 | 3.5201 | 5.3421 | 4.0348 | 0.36394 | 0 | 0 | 0 | 3.0153 | 69.5283 | 86.4714 | 95.2411 | 88.9487 | 71.2801 | 69.5283 | 69.5283 | 69.5283 | 146.9847 | 69.5283 | 89.9915 | 100.5833 | 92.9835 | 71.644 | 69.5283 | 69.5283 | 69.5283 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 10 | 5194 | 17.2 | 17.2 | 17.4167 | 19.3808 | 15 | 91 | 91 | 92.1956 | 285.4813 | 42.2782 | 121.495 | 0 | 36.3066 | 73.3225 | 67.387 | 21.9771 | 0 | 0 | 0 | 58.5187 | 128.6095 | 180.8287 | 234.0679 | 225.531 | 160.2188 | 128.6095 | 128.6095 | 128.6095 | 285.4813 | 128.6095 | 217.1353 | 307.3904 | 292.918 | 182.196 | 128.6095 | 128.6095 | 128.6095 | 344 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 11 | 5195 | 19.1 | 19.1 | 17.4167 | 19.3808 | 15 | 76 | 76 | 667.364 | 179.2303 | 49.2884 | 139.5125 | 0 | 115.3115 | 421.0342 | 480.1207 | 257.959 | 0 | 0 | 0 | 487.7697 | 126.2843 | 148.8163 | 208.555 | 220.1005 | 176.6898 | 126.2843 | 126.2843 | 126.2843 | 179.2303 | 126.2843 | 264.1278 | 629.5891 | 700.2212 | 434.6489 | 126.2843 | 126.2843 | 126.2843 | 667 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 12 | 5196 | 18.2 | 18.2 | 17.4167 | 19.3808 | 15 | 80 | 80 | 42.9709 | 332.9241 | 53.842 | 161.4974 | 0 | 0 | 18.198 | 27.941 | 21.3165 | 2.2051 | 0 | 0 | 34.0759 | 146.2416 | 146.2416 | 198.1595 | 225.9558 | 207.0566 | 152.5327 | 146.2416 | 146.2416 | 332.9241 | 146.2416 | 146.2416 | 216.3575 | 253.8968 | 228.3731 | 154.7379 | 146.2416 | 146.2416 | 367 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 13 | 5197 | 19.3 | 19.3 | 17.4167 | 19.3808 | 15 | 70 | 70 | 367.7799 | 316.6201 | 54.8393 | 186.1583 | 0 | 0 | 68.8629 | 194.2008 | 205.7785 | 96.8139 | 0 | 0 | 300.3799 | 155.0633 | 155.0633 | 193.0419 | 262.167 | 268.5522 | 208.4572 | 155.0633 | 155.0633 | 316.6201 | 155.0633 | 155.0633 | 261.9048 | 456.3679 | 474.3307 | 305.2711 | 155.0633 | 155.0633 | 617 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 14 | 5198 | 19.2 | 19.2 | 17.4167 | 19.3808 | 15 | 66 | 66 | 199.9139 | 356.9804 | 51.9757 | 209.8482 | 0 | 0 | 0 | 72.203 | 114.4605 | 89.6686 | 12.35 | 0 | 160.0196 | 162.4764 | 162.4764 | 162.4764 | 225.9832 | 263.1512 | 241.3453 | 173.339 | 162.4764 | 356.9804 | 162.4764 | 162.4764 | 162.4764 | 298.1862 | 377.6117 | 331.0138 | 185.6891 | 162.4764 | 517 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 15 | 5199 | 17.6 | 17.6 | 17.4167 | 19.3808 | 15 | 74 | 74 | 179.2539 | 335.4097 | 46.0589 | 229.8619 | 0 | 0 | 0 | 28.8612 | 95.7721 | 106.581 | 54.9562 | 0 | 133.5903 | 153.0584 | 153.0584 | 153.0584 | 179.6108 | 241.169 | 251.1132 | 203.6183 | 153.0584 | 335.4097 | 153.0584 | 153.0584 | 153.0584 | 208.472 | 336.9411 | 357.6942 | 258.5744 | 153.0584 | 469 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 16 | 5200 | 19 | 19 | 17.4167 | 19.3808 | 15 | 64 | 64 | 144.3322 | 297.4592 | 38.2478 | 246.1462 | 0 | 0 | 0 | 0 | 64.563 | 99.7945 | 76.5677 | 8.4886 | 94.5408 | 136.587 | 136.587 | 136.587 | 136.587 | 202.7263 | 238.8179 | 215.0241 | 145.2829 | 297.4592 | 136.587 | 136.587 | 136.587 | 136.587 | 267.2893 | 338.6124 | 291.5918 | 153.7715 | 392 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 17 | 5201 | 18.5 | 18.5 | 17.4167 | 19.3808 | 15 | 62 | 62 | 190.0782 | 240.1295 | 29.45 | 259.8174 | 0 | 0 | 0 | 0 | 60.368 | 139.2244 | 136.525 | 53.8511 | 101.8705 | 116.6684 | 116.6684 | 116.6684 | 116.6684 | 155.7243 | 206.7415 | 204.9951 | 151.5081 | 240.1295 | 116.6684 | 116.6684 | 116.6684 | 116.6684 | 216.0923 | 345.9659 | 341.5201 | 205.3592 | 342 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 18 | 5202 | 19.2 | 19.2 | 17.4167 | 19.3808 | 15 | 61 | 61 | 801.7948 | 74.3768 | 20.2755 | 271.9845 | 0 | 0 | 0 | 0 | 123.4306 | 573.1981 | 687.194 | 398.6409 | 317.6232 | 70.8633 | 70.8633 | 70.8633 | 70.8633 | 80.0654 | 113.5971 | 122.0959 | 100.5833 | 74.3768 | 70.8633 | 70.8633 | 70.8633 | 70.8633 | 203.4961 | 686.7953 | 809.2899 | 499.2242 | 392 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 19 | 5203 | 18.1 | 18.1 | 17.4167 | 19.3808 | 15 | 66 | 66 | 526.6344 | 76.9019 | 11.1611 | 283.4969 | 17.1067 | 0 | 0 | 0 | 0 | 337.0068 | 493.7063 | 361.1994 | 129.0981 | 54.533 | 51.7312 | 51.7312 | 51.7312 | 51.7312 | 106.9262 | 132.5904 | 110.8885 | 76.9019 | 71.6397 | 51.7312 | 51.7312 | 51.7312 | 51.7312 | 443.933 | 626.2967 | 472.0878 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 20 | 5204 | 16.5 | 16.5 | 17.4167 | 19.3808 | 15 | 73 | 73 | 146.8988 | 42.3092 | 2.4752 | 294.9954 | 33.6366 | 0 | 0 | 0 | 0 | 75.3095 | 140.1403 | 122.8788 | 13.6908 | 38.0805 | 23.6373 | 23.6373 | 23.6373 | 23.6373 | 55.9745 | 83.8122 | 76.4003 | 42.3092 | 71.7171 | 23.6373 | 23.6373 | 23.6373 | 23.6373 | 131.284 | 223.9525 | 199.2791 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 21 | 5205 | 13.9 | 13.9 | 17.4167 | 19.3808 | 15 | 87 | 87 | 0 | 3 | -5.4144 | 306.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 3 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 1.3927 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 22 | 5206 | 12.2 | 12.2 | 17.4167 | 19.3808 | 15 | 97 | 97 | 0 | 0 | -12.1046 | 319.8165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 23 | 5207 | 11.4 | 11.4 | 17.4167 | 19.3808 | 15 | 99 | 99 | 0 | 0 | -17.1556 | 333.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 5 | 24 | 5208 | 11 | 11 | 15.9167 | 18.365 | 15 | 99 | 99 | 0 | 0 | -20.1427 | 348.4959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 1 | 5209 | 11.9 | 11.9 | 15.9167 | 18.365 | 15 | 97 | 97 | 0 | 0 | -20.7632 | 3.7882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 2 | 5210 | 12.6 | 12.6 | 15.9167 | 18.365 | 15 | 95 | 95 | 0 | 0 | -19.2104 | 18.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 3 | 5211 | 12.4 | 12.4 | 15.9167 | 18.365 | 15 | 93 | 93 | 0 | 0 | -15.1407 | 33.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 4 | 5212 | 11.5 | 11.5 | 15.9167 | 18.365 | 15 | 95 | 95 | 0 | 0 | -9.2075 | 46.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 5 | 5213 | 11 | 11 | 15.9167 | 18.365 | 15 | 98 | 98 | 0 | 0 | -1.8563 | 59.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 6 | 5214 | 11.2 | 11.2 | 15.9167 | 18.365 | 15 | 99 | 99 | 3.4759 | 13.7855 | 6.4863 | 70.9006 | 1.7791 | 3.3679 | 2.9839 | 0.85197 | 0 | 0 | 0 | 0 | 0.21447 | 9.3459 | 12.2278 | 11.5313 | 7.6644 | 6.1191 | 6.1191 | 6.1191 | 6.1191 | 13.7855 | 11.125 | 15.5958 | 14.5152 | 8.5164 | 6.1191 | 6.1191 | 6.1191 | 6.1191 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 7 | 5215 | 14.1 | 14.1 | 15.9167 | 18.365 | 15 | 92 | 92 | 46.2175 | 90.1612 | 15.4358 | 82.3495 | 15.0259 | 41.3089 | 43.3938 | 20.0591 | 0 | 0 | 0 | 0 | 9.8388 | 107.8263 | 229.9853 | 239.6752 | 131.2198 | 37.9886 | 37.9886 | 37.9886 | 37.9886 | 90.1612 | 122.8522 | 271.2942 | 283.0689 | 151.279 | 37.9886 | 37.9886 | 37.9886 | 37.9886 | 100 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 6 | 8 | 5216 | 17.3 | 17.3 | 15.9167 | 18.365 | 15 | 86 | 86 | 183.243 | 164.1038 | 24.6292 | 94.1073 | 23.5153 | 140.4147 | 175.061 | 107.159 | 0 | 0 | 0 | 0 | 66.8962 | 98.9816 | 204.9119 | 236.3073 | 174.7768 | 77.6728 | 77.6728 | 77.6728 | 77.6728 | 164.1038 | 122.4968 | 345.3266 | 411.3684 | 281.9358 | 77.6728 | 77.6728 | 77.6728 | 77.6728 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 9 | 5217 | 17.9 | 17.9 | 15.9167 | 18.365 | 15 | 84 | 84 | 91.6524 | 228.4477 | 33.6738 | 106.9067 | 0 | 54.5411 | 83.1002 | 62.9803 | 5.9674 | 0 | 0 | 0 | 46.5523 | 103.3766 | 182.7786 | 224.3554 | 195.0645 | 112.0641 | 103.3766 | 103.3766 | 103.3766 | 228.4477 | 103.3766 | 237.3197 | 307.4557 | 258.0449 | 118.0315 | 103.3766 | 103.3766 | 103.3766 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 10 | 5218 | 18.7 | 18.7 | 15.9167 | 18.365 | 15 | 78 | 78 | 46.4103 | 267.6815 | 42.0617 | 121.7198 | 0 | 18.1879 | 36.9537 | 34.0725 | 11.2321 | 0 | 0 | 0 | 29.3185 | 119.5054 | 166.1929 | 214.3637 | 206.9679 | 148.3377 | 119.5054 | 119.5054 | 119.5054 | 267.6815 | 119.5054 | 184.3808 | 251.3175 | 241.0404 | 159.5698 | 119.5054 | 119.5054 | 119.5054 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 11 | 5219 | 20.1 | 20.1 | 15.9167 | 18.365 | 15 | 74 | 74 | 69.7077 | 321.251 | 49.0495 | 139.7153 | 0 | 11.8883 | 44.0223 | 50.3687 | 27.2098 | 0 | 0 | 0 | 50.749 | 142.6993 | 164.9429 | 225.0676 | 236.942 | 193.6103 | 142.6993 | 142.6993 | 142.6993 | 321.251 | 142.6993 | 176.8312 | 269.0899 | 287.3107 | 220.8201 | 142.6993 | 142.6993 | 142.6993 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 12 | 5220 | 21.3 | 21.3 | 15.9167 | 18.365 | 15 | 69 | 69 | 192.6278 | 353.7813 | 53.5796 | 161.6258 | 0 | 0 | 81.6314 | 125.8224 | 96.3084 | 10.3782 | 0 | 0 | 152.2187 | 161.1343 | 161.1343 | 237.4619 | 278.7817 | 251.1853 | 170.8382 | 161.1343 | 161.1343 | 353.7813 | 161.1343 | 161.1343 | 319.0933 | 404.6041 | 347.4937 | 181.2164 | 161.1343 | 161.1343 | 506 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 13 | 5221 | 20.1 | 20.1 | 15.9167 | 18.365 | 15 | 75 | 75 | 17.1853 | 300.0113 | 54.5661 | 186.1623 | 0 | 0 | 3.2162 | 9.121 | 9.6828 | 4.5726 | 0 | 0 | 13.9887 | 143.1816 | 143.1816 | 150.3922 | 163.6306 | 164.8902 | 153.4332 | 143.1816 | 143.1816 | 300.0113 | 143.1816 | 143.1816 | 153.6084 | 172.7515 | 174.573 | 158.0058 | 143.1816 | 143.1816 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 14 | 5222 | 20.6 | 20.6 | 15.9167 | 18.365 | 15 | 79 | 79 | 82.2344 | 356.4036 | 51.7108 | 209.7399 | 0 | 0 | 0 | 29.8987 | 47.401 | 37.1364 | 5.1178 | 0 | 65.5964 | 157.8793 | 157.8793 | 157.8793 | 204.7914 | 232.2531 | 216.1476 | 165.9094 | 157.8793 | 356.4036 | 157.8793 | 157.8793 | 157.8793 | 234.6901 | 279.6541 | 253.284 | 171.0272 | 157.8793 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 15 | 5223 | 20.4 | 20.4 | 15.9167 | 18.365 | 15 | 74 | 74 | 57.0688 | 321.6313 | 45.8111 | 229.6964 | 0 | 0 | 0 | 9.3072 | 30.704 | 34.1148 | 17.5416 | 0 | 42.3687 | 143.2259 | 143.2259 | 143.2259 | 161.6193 | 203.905 | 210.6457 | 177.8928 | 143.2259 | 321.6313 | 143.2259 | 143.2259 | 143.2259 | 170.9265 | 234.609 | 244.7605 | 195.4344 | 143.2259 | 364 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 16 | 5224 | 19.3 | 19.3 | 15.9167 | 18.365 | 15 | 90 | 90 | 24.0455 | 253.3211 | 38.0148 | 245.9647 | 0 | 0 | 0 | 0 | 10.8412 | 16.7041 | 12.7819 | 1.3723 | 15.6789 | 122.0872 | 122.0872 | 122.0872 | 122.0872 | 135.8734 | 143.3289 | 138.3413 | 123.8322 | 253.3211 | 122.0872 | 122.0872 | 122.0872 | 122.0872 | 146.7147 | 160.033 | 151.1232 | 125.2045 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 17 | 5225 | 18.7 | 18.7 | 15.9167 | 18.365 | 15 | 95 | 95 | 4.0817 | 128.8253 | 29.2255 | 259.6388 | 0 | 0 | 0 | 0 | 1.3098 | 3.0029 | 2.9369 | 1.1506 | 2.1747 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 128.8253 | 64.2414 | 64.2414 | 64.2414 | 64.2414 | 65.5511 | 67.2442 | 67.1783 | 65.3919 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 6 | 18 | 5226 | 18.6 | 18.6 | 15.9167 | 18.365 | 15 | 93 | 93 | 1.7924 | 63.2959 | 20.0531 | 271.8155 | 0 | 0 | 0 | 0 | 0.28134 | 1.287 | 1.5387 | 0.88912 | 0.70406 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 63.2959 | 30.6624 | 30.6624 | 30.6624 | 30.6624 | 30.9438 | 31.9494 | 32.2012 | 31.5516 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 19 | 5227 | 18.9 | 18.9 | 15.9167 | 18.365 | 15 | 90 | 90 | 4.7387 | 62.8552 | 10.9352 | 283.3403 | 0.14103 | 0 | 0 | 0 | 0 | 3.0463 | 4.4492 | 3.2458 | 1.1448 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 62.8552 | 30.8933 | 30.7523 | 30.7523 | 30.7523 | 30.7523 | 33.7986 | 35.2015 | 33.9981 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 20 | 5228 | 18.9 | 18.9 | 15.9167 | 18.365 | 15 | 89 | 89 | 3.0483 | 18.7274 | 2.2415 | 294.8538 | 0.69057 | 0 | 0 | 0 | 0 | 1.5709 | 2.9121 | 2.5475 | 0.27258 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 18.7274 | 9.5735 | 8.8829 | 8.8829 | 8.8829 | 8.8829 | 10.4538 | 11.7951 | 11.4304 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 21 | 5229 | 18.9 | 18.9 | 15.9167 | 18.365 | 15 | 90 | 90 | 0 | 0 | -5.6591 | 306.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 22 | 5230 | 18.8 | 18.8 | 15.9167 | 18.365 | 15 | 87 | 87 | 0 | 0 | -12.3613 | 319.7206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 23 | 5231 | 18.7 | 18.7 | 15.9167 | 18.365 | 15 | 89 | 89 | 0 | 0 | -17.4228 | 333.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 6 | 24 | 5232 | 18.3 | 18.3 | 17.0917 | 17.8509 | 15 | 90 | 90 | 0 | 0 | -20.4156 | 348.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 1 | 5233 | 17.3 | 17.3 | 17.0917 | 17.8509 | 15 | 98 | 98 | 0 | 0 | -21.0344 | 3.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 2 | 5234 | 17.6 | 17.6 | 17.0917 | 17.8509 | 15 | 96 | 96 | 0 | 0 | -19.4763 | 19.0818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 3 | 5235 | 17.6 | 17.6 | 17.0917 | 17.8509 | 15 | 98 | 98 | 0 | 0 | -15.3914 | 33.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 4 | 5236 | 17.5 | 17.5 | 17.0917 | 17.8509 | 15 | 96 | 96 | 0 | 0 | -9.4412 | 46.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 5 | 5237 | 17.2 | 17.2 | 17.0917 | 17.8509 | 15 | 96 | 96 | 0 | 0 | -2.0744 | 59.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 6 | 5238 | 16.7 | 16.7 | 17.0917 | 17.8509 | 15 | 98 | 98 | 0 | 0 | 6.2803 | 71.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 7 | 5239 | 16.8 | 16.8 | 17.0917 | 17.8509 | 15 | 97 | 97 | 1.6793 | 32.6487 | 15.2369 | 82.5509 | 0.541 | 1.4991 | 1.5791 | 0.73404 | 0 | 0 | 0 | 0 | 0.35133 | 18.2567 | 22.5526 | 22.9111 | 19.1222 | 15.831 | 15.831 | 15.831 | 15.831 | 32.6487 | 18.7977 | 24.0517 | 24.4902 | 19.8563 | 15.831 | 15.831 | 15.831 | 15.831 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 7 | 8 | 5240 | 17.1 | 17.1 | 17.0917 | 17.8509 | 15 | 94 | 94 | 2.1141 | 63.2355 | 24.4314 | 94.3219 | 0.26445 | 1.6172 | 2.0226 | 1.2432 | 0 | 0 | 0 | 0 | 0.7645 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 63.2355 | 31.5409 | 32.8936 | 33.299 | 32.5196 | 31.2764 | 31.2764 | 31.2764 | 31.2764 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 9 | 5241 | 17.5 | 17.5 | 17.0917 | 17.8509 | 15 | 94 | 94 | 2.8114 | 101.5812 | 33.4695 | 107.1328 | 0 | 1.6684 | 2.5523 | 1.9412 | 0.19289 | 0 | 0 | 0 | 1.4188 | 50.6588 | 50.6588 | 50.6588 | 50.6588 | 50.6588 | 50.6588 | 50.6588 | 50.6588 | 101.5812 | 50.6588 | 52.3272 | 53.2112 | 52.6 | 50.8517 | 50.6588 | 50.6588 | 50.6588 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 10 | 5242 | 18.4 | 18.4 | 17.0917 | 17.8509 | 15 | 89 | 89 | 15.0282 | 226.5524 | 41.8423 | 121.9492 | 0 | 5.8597 | 11.9799 | 11.0825 | 3.693 | 0 | 0 | 0 | 9.4476 | 104.4432 | 125.5196 | 147.533 | 144.3049 | 117.7264 | 104.4432 | 104.4432 | 104.4432 | 226.5524 | 104.4432 | 131.3794 | 159.5129 | 155.3874 | 121.4194 | 104.4432 | 104.4432 | 104.4432 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 11 | 5243 | 18.8 | 18.8 | 17.0917 | 17.8509 | 15 | 88 | 88 | 26.9307 | 286.4726 | 48.8071 | 139.9223 | 0 | 4.5305 | 17.0237 | 19.5447 | 10.6166 | 0 | 0 | 0 | 19.5274 | 132.0227 | 142.7039 | 172.1583 | 178.1018 | 157.0528 | 132.0227 | 132.0227 | 132.0227 | 286.4726 | 132.0227 | 147.2344 | 189.182 | 197.6465 | 167.6695 | 132.0227 | 132.0227 | 132.0227 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 12 | 5244 | 18.9 | 18.9 | 17.0917 | 17.8509 | 15 | 82 | 82 | 15.3798 | 284.8902 | 53.3131 | 161.7583 | 0 | 0 | 6.5214 | 10.0917 | 7.7505 | 0.86912 | 0 | 0 | 12.1098 | 135.0369 | 135.0369 | 152.2736 | 161.7105 | 155.5223 | 137.334 | 135.0369 | 135.0369 | 284.8902 | 135.0369 | 135.0369 | 158.795 | 171.8022 | 163.2728 | 138.2032 | 135.0369 | 135.0369 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 13 | 5245 | 21.9 | 21.9 | 17.0917 | 17.8509 | 15 | 72 | 72 | 490.7828 | 268.8835 | 54.2882 | 186.1699 | 0 | 0 | 91.7839 | 261.815 | 278.4785 | 132.0131 | 0 | 0 | 398.1165 | 146.1149 | 146.1149 | 182.1378 | 248.8709 | 255.4109 | 197.9268 | 146.1149 | 146.1149 | 268.8835 | 146.1149 | 146.1149 | 273.9217 | 510.6859 | 533.8894 | 329.9398 | 146.1149 | 146.1149 | 667 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 14 | 5246 | 21.4 | 21.4 | 17.0917 | 17.8509 | 15 | 66 | 66 | 496.6988 | 261.2009 | 51.4407 | 209.6344 | 0 | 0 | 0 | 181.7882 | 288.2481 | 225.8562 | 31.1608 | 0 | 394.7991 | 142.7269 | 142.7269 | 142.7269 | 212.07 | 252.6791 | 228.8797 | 154.6132 | 142.7269 | 261.2009 | 142.7269 | 142.7269 | 142.7269 | 393.8582 | 540.9272 | 454.7359 | 185.774 | 142.7269 | 656 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 15 | 5247 | 20.4 | 20.4 | 17.0917 | 17.8509 | 15 | 70 | 70 | 37.3657 | 305.3678 | 45.5579 | 229.5323 | 0 | 0 | 0 | 6.1716 | 20.2444 | 22.4584 | 11.5165 | 0 | 27.6322 | 135.8632 | 135.8632 | 135.8632 | 153.0737 | 192.3184 | 198.4924 | 167.9791 | 135.8632 | 305.3678 | 135.8632 | 135.8632 | 135.8632 | 159.2453 | 212.5628 | 220.9508 | 179.4956 | 135.8632 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 16 | 5248 | 19.2 | 19.2 | 17.0917 | 17.8509 | 15 | 76 | 76 | 3.4626 | 144.7527 | 37.7765 | 245.7836 | 0 | 0 | 0 | 0 | 1.5735 | 2.4169 | 1.8444 | 0.19158 | 2.2473 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 144.7527 | 72.4013 | 72.4013 | 72.4013 | 72.4013 | 73.9748 | 74.8182 | 74.2457 | 72.5929 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 17 | 5249 | 18.3 | 18.3 | 17.0917 | 17.8509 | 15 | 86 | 86 | 0.80955 | 57.5713 | 28.9957 | 259.4598 | 0 | 0 | 0 | 0 | 0.26247 | 0.59824 | 0.58357 | 0.22705 | 0.42873 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 57.5713 | 27.7552 | 27.7552 | 27.7552 | 27.7552 | 28.0177 | 28.3534 | 28.3388 | 27.9823 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 7 | 18 | 5250 | 18.3 | 18.3 | 17.0917 | 17.8509 | 15 | 93 | 93 | 0.98331 | 46.6171 | 19.8254 | 271.646 | 0 | 0 | 0 | 0 | 0.15733 | 0.70914 | 0.84555 | 0.48665 | 0.3829 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 46.6171 | 22.3551 | 22.3551 | 22.3551 | 22.3551 | 22.5124 | 23.0642 | 23.2006 | 22.8417 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 19 | 5251 | 18.1 | 18.1 | 17.0917 | 17.8509 | 15 | 95 | 95 | 1.1455 | 30.7274 | 10.7041 | 283.1831 | 0.030954 | 0 | 0 | 0 | 0 | 0.73979 | 1.0772 | 0.78357 | 0.27258 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 30.7274 | 14.6506 | 14.6196 | 14.6196 | 14.6196 | 14.6196 | 15.3594 | 15.6968 | 15.4032 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 20 | 5252 | 17.8 | 17.8 | 17.0917 | 17.8509 | 15 | 98 | 98 | 0.33178 | 5.9716 | 2.0026 | 294.7117 | 0.074351 | 0 | 0 | 0 | 0 | 0.17187 | 0.31742 | 0.27702 | 0.028393 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 5.9716 | 2.8478 | 2.7734 | 2.7734 | 2.7734 | 2.7734 | 2.9453 | 3.0909 | 3.0505 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 21 | 5253 | 17.8 | 17.8 | 17.0917 | 17.8509 | 15 | 97 | 97 | 0 | 0 | -5.9088 | 306.7341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 22 | 5254 | 18 | 18 | 17.0917 | 17.8509 | 15 | 97 | 97 | 0 | 0 | -12.623 | 319.6249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 23 | 5255 | 18.1 | 18.1 | 17.0917 | 17.8509 | 15 | 96 | 96 | 0 | 0 | -17.6949 | 333.5716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 7 | 24 | 5256 | 18 | 18 | 18.2792 | 17.7314 | 15 | 96 | 96 | 0 | 0 | -20.6933 | 348.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 1 | 5257 | 15.1 | 15.1 | 18.2792 | 17.7314 | 15 | 98 | 98 | 0 | 0 | -21.3101 | 3.8612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 2 | 5258 | 15.2 | 15.2 | 18.2792 | 17.7314 | 15 | 99 | 99 | 0 | 0 | -19.7459 | 19.1715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 3 | 5259 | 14.4 | 14.4 | 18.2792 | 17.7314 | 15 | 97 | 97 | 0 | 0 | -15.6453 | 33.6673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 4 | 5260 | 14.2 | 14.2 | 18.2792 | 17.7314 | 15 | 97 | 97 | 0 | 0 | -9.6776 | 47.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 5 | 5261 | 14.6 | 14.6 | 18.2792 | 17.7314 | 15 | 96 | 96 | 0 | 0 | -2.2948 | 59.5455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 6 | 5262 | 14.6 | 14.6 | 18.2792 | 17.7314 | 15 | 94 | 94 | 0.20924 | 2.9887 | 6.0723 | 71.2808 | 0.10597 | 0.20237 | 0.18023 | 0.052509 | 0 | 0 | 0 | 0 | 0.011272 | 1.7662 | 2.0928 | 2.0177 | 1.5851 | 1.4072 | 1.4072 | 1.4072 | 1.4072 | 2.9887 | 1.8722 | 2.2951 | 2.198 | 1.6376 | 1.4072 | 1.4072 | 1.4072 | 1.4072 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 7 | 5263 | 15.1 | 15.1 | 18.2792 | 17.7314 | 15 | 92 | 92 | 4.4887 | 52.0776 | 15.0361 | 82.7568 | 1.4325 | 4.0021 | 4.2274 | 1.9763 | 0 | 0 | 0 | 0 | 0.92235 | 49.9155 | 98.7142 | 102.992 | 60.2431 | 22.7123 | 22.7123 | 22.7123 | 22.7123 | 52.0776 | 51.3479 | 102.7163 | 107.2194 | 62.2194 | 22.7123 | 22.7123 | 22.7123 | 22.7123 | 53 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 8 | 8 | 5264 | 15.9 | 15.9 | 18.2792 | 17.7314 | 15 | 89 | 89 | 9.6529 | 118.5432 | 24.2314 | 94.541 | 1.1754 | 7.3705 | 9.2481 | 5.7082 | 0 | 0 | 0 | 0 | 3.4568 | 61.6563 | 109.7567 | 124.3346 | 96.8505 | 52.5303 | 52.5303 | 52.5303 | 52.5303 | 118.5432 | 62.8317 | 117.1271 | 133.5826 | 102.5588 | 52.5303 | 52.5303 | 52.5303 | 52.5303 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 9 | 5265 | 16.6 | 16.6 | 18.2792 | 17.7314 | 15 | 84 | 84 | 36.679 | 206.6101 | 33.2627 | 107.3635 | 0 | 21.7042 | 33.3424 | 25.4492 | 2.6481 | 0 | 0 | 0 | 18.3899 | 92.8699 | 159.7812 | 195.6607 | 171.3267 | 101.0338 | 92.8699 | 92.8699 | 92.8699 | 206.6101 | 92.8699 | 181.4854 | 229.0031 | 196.7759 | 103.6819 | 92.8699 | 92.8699 | 92.8699 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 10 | 5266 | 17.4 | 17.4 | 18.2792 | 17.7314 | 15 | 80 | 80 | 13.8721 | 222.3226 | 41.6201 | 122.1831 | 0 | 5.3805 | 11.0707 | 10.2759 | 3.4616 | 0 | 0 | 0 | 8.6774 | 102.7589 | 122.7271 | 143.8451 | 140.8953 | 115.6058 | 102.7589 | 102.7589 | 102.7589 | 222.3226 | 102.7589 | 128.1076 | 154.9158 | 151.1713 | 119.0674 | 102.7589 | 102.7589 | 102.7589 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 11 | 5267 | 18.1 | 18.1 | 18.2792 | 17.7314 | 15 | 76 | 76 | 28.3814 | 287.5057 | 48.5613 | 140.1335 | 0 | 4.7067 | 17.957 | 20.6883 | 11.3007 | 0 | 0 | 0 | 20.4943 | 132.3156 | 143.118 | 173.5292 | 179.7979 | 158.2522 | 132.3156 | 132.3156 | 132.3156 | 287.5057 | 132.3156 | 147.8247 | 191.4861 | 200.4862 | 169.5529 | 132.3156 | 132.3156 | 132.3156 | 308 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 12 | 5268 | 19.1 | 19.1 | 18.2792 | 17.7314 | 15 | 72 | 72 | 132.7319 | 356.8751 | 53.0426 | 161.8946 | 0 | 0 | 56.3084 | 87.4921 | 67.4241 | 7.8601 | 0 | 0 | 104.1249 | 157.344 | 157.344 | 234.9134 | 277.8716 | 250.2264 | 168.1719 | 157.344 | 157.344 | 356.8751 | 157.344 | 157.344 | 291.2218 | 365.3637 | 317.6505 | 176.0319 | 157.344 | 157.344 | 461 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 13 | 5269 | 13.7 | 13.7 | 18.2792 | 17.7314 | 15 | 93 | 93 | 1.2724 | 109.9715 | 54.0056 | 186.1811 | 0 | 0 | 0.23773 | 0.68223 | 0.72709 | 0.34603 | 0 | 0 | 1.0285 | 54.2433 | 54.2433 | 54.2433 | 54.2433 | 54.2433 | 54.2433 | 54.2433 | 54.2433 | 109.9715 | 54.2433 | 54.2433 | 54.481 | 54.9255 | 54.9703 | 54.5893 | 54.2433 | 54.2433 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 14 | 5270 | 14.9 | 14.9 | 18.2792 | 17.7314 | 15 | 96 | 96 | 0.79565 | 85.3699 | 51.1655 | 209.5316 | 0 | 0 | 0 | 0.29313 | 0.46489 | 0.36433 | 0.050349 | 0 | 0.63012 | 41.7492 | 41.7492 | 41.7492 | 41.7492 | 41.7492 | 41.7492 | 41.7492 | 41.7492 | 85.3699 | 41.7492 | 41.7492 | 41.7492 | 42.0423 | 42.2141 | 42.1135 | 41.7995 | 41.7492 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 15 | 5271 | 16.6 | 16.6 | 18.2792 | 17.7314 | 15 | 87 | 87 | 6.8013 | 222.9906 | 45.2994 | 229.3696 | 0 | 0 | 0 | 1.1375 | 3.7108 | 4.1104 | 2.1022 | 0 | 5.0094 | 110.9889 | 110.9889 | 110.9889 | 112.546 | 116.0686 | 116.6156 | 113.8665 | 110.9889 | 222.9906 | 110.9889 | 110.9889 | 110.9889 | 113.6834 | 119.7794 | 120.726 | 115.9687 | 110.9889 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 16 | 5272 | 16.9 | 16.9 | 18.2792 | 17.7314 | 15 | 93 | 93 | 5.595 | 182.3861 | 37.5328 | 245.6029 | 0 | 0 | 0 | 0 | 2.5627 | 3.9241 | 2.9868 | 0.29984 | 3.6139 | 91.903 | 91.903 | 91.903 | 91.903 | 92.8142 | 93.2982 | 92.9649 | 92.0097 | 182.3861 | 91.903 | 91.903 | 91.903 | 91.903 | 95.3769 | 97.2222 | 95.9517 | 92.3095 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 17 | 5273 | 18.1 | 18.1 | 18.2792 | 17.7314 | 15 | 81 | 81 | 364.7813 | 205.0066 | 28.7606 | 259.2807 | 0 | 0 | 0 | 0 | 119.4869 | 270.772 | 263.4425 | 101.792 | 191.9934 | 108.8001 | 108.8001 | 108.8001 | 108.8001 | 159.1405 | 222.8777 | 219.7898 | 151.6856 | 205.0066 | 108.8001 | 108.8001 | 108.8001 | 108.8001 | 278.6274 | 493.6497 | 483.2323 | 253.4776 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 8 | 18 | 5274 | 19 | 19 | 18.2792 | 17.7314 | 15 | 71 | 71 | 513.8511 | 123.6926 | 19.5925 | 271.4759 | 0 | 0 | 0 | 0 | 83.7847 | 372.2107 | 442.6008 | 253.7213 | 198.3074 | 78.1186 | 78.1186 | 78.1186 | 78.1186 | 95.4838 | 155.263 | 169.852 | 130.7049 | 123.6926 | 78.1186 | 78.1186 | 78.1186 | 78.1186 | 179.2685 | 527.4737 | 612.4528 | 384.4262 | 322 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 19 | 5275 | 18.1 | 18.1 | 18.2792 | 17.7314 | 15 | 72 | 72 | 530.7355 | 53.1523 | 10.4678 | 283.0253 | 12.8785 | 0 | 0 | 0 | 0 | 344.3343 | 499.8407 | 362.5473 | 165.8477 | 46.2377 | 44.5786 | 44.5786 | 44.5786 | 44.5786 | 88.9382 | 108.9716 | 91.2845 | 53.1523 | 59.1162 | 44.5786 | 44.5786 | 44.5786 | 44.5786 | 433.2724 | 608.8123 | 453.8318 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 20 | 5276 | 16.9 | 16.9 | 18.2792 | 17.7314 | 15 | 75 | 75 | 127.0935 | 34.2073 | 1.7586 | 294.569 | 28.1678 | 0 | 0 | 0 | 0 | 66.1815 | 121.7626 | 106.0168 | 23.7927 | 34.7769 | 20.7445 | 20.7445 | 20.7445 | 20.7445 | 53.7143 | 81.4033 | 73.5592 | 34.2073 | 62.9447 | 20.7445 | 20.7445 | 20.7445 | 20.7445 | 119.8959 | 203.166 | 179.576 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 21 | 5277 | 15.9 | 15.9 | 18.2792 | 17.7314 | 15 | 82 | 82 | 0 | 0 | -6.1636 | 306.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 22 | 5278 | 15.5 | 15.5 | 18.2792 | 17.7314 | 15 | 87 | 87 | 0 | 0 | -12.8898 | 319.5294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 23 | 5279 | 15.2 | 15.2 | 18.2792 | 17.7314 | 15 | 88 | 88 | 0 | 0 | -17.9721 | 333.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 8 | 24 | 5280 | 14.8 | 14.8 | 16.0792 | 17.2433 | 15 | 86 | 86 | 0 | 0 | -20.9757 | 348.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 1 | 5281 | 14.6 | 14.6 | 16.0792 | 17.2433 | 15 | 92 | 92 | 0 | 0 | -21.5901 | 3.9022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 2 | 5282 | 14.4 | 14.4 | 16.0792 | 17.2433 | 15 | 94 | 94 | 0 | 0 | -20.0193 | 19.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 3 | 5283 | 14.3 | 14.3 | 16.0792 | 17.2433 | 15 | 94 | 94 | 0 | 0 | -15.9024 | 33.8003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 4 | 5284 | 14 | 14 | 16.0792 | 17.2433 | 15 | 96 | 96 | 0 | 0 | -9.9167 | 47.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 5 | 5285 | 13.8 | 13.8 | 16.0792 | 17.2433 | 15 | 99 | 99 | 0 | 0 | -2.5174 | 59.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 6 | 5286 | 14 | 14 | 16.0792 | 17.2433 | 15 | 99 | 99 | 0 | 0 | 5.8621 | 71.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 7 | 5287 | 14.2 | 14.2 | 16.0792 | 17.2433 | 15 | 98 | 98 | 0.47917 | 16.9034 | 14.8332 | 82.9672 | 0.15143 | 0.42667 | 0.45198 | 0.21252 | 0 | 0 | 0 | 0 | 0.096645 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 16.9034 | 8.2596 | 8.5349 | 8.5602 | 8.3207 | 8.1082 | 8.1082 | 8.1082 | 8.1082 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 9 | 8 | 5288 | 14 | 14 | 16.0792 | 17.2433 | 15 | 97 | 97 | 0.51567 | 30.8172 | 24.0293 | 94.7646 | 0.061033 | 0.39299 | 0.49473 | 0.30667 | 0 | 0 | 0 | 0 | 0.18282 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 30.8172 | 14.7839 | 15.1159 | 15.2176 | 15.0296 | 14.7229 | 14.7229 | 14.7229 | 14.7229 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 9 | 5289 | 13.8 | 13.8 | 16.0792 | 17.2433 | 15 | 96 | 96 | 1.6546 | 77.176 | 33.0536 | 107.5986 | 0 | 0.97613 | 1.506 | 1.1536 | 0.12552 | 0 | 0 | 0 | 0.824 | 37.8682 | 37.8682 | 37.8682 | 37.8682 | 37.8682 | 37.8682 | 37.8682 | 37.8682 | 77.176 | 37.8682 | 38.8444 | 39.3742 | 39.0219 | 37.9937 | 37.8682 | 37.8682 | 37.8682 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 10 | 5290 | 17.1 | 17.1 | 16.0792 | 17.2433 | 15 | 87 | 87 | 291.1302 | 260.8192 | 41.395 | 122.4213 | 0 | 112.3005 | 232.5936 | 216.6365 | 73.7767 | 0 | 0 | 0 | 181.1808 | 130.6901 | 196.5312 | 267.0582 | 257.7027 | 173.9449 | 130.6901 | 130.6901 | 130.6901 | 260.8192 | 130.6901 | 308.8317 | 499.6518 | 474.3392 | 247.7216 | 130.6901 | 130.6901 | 130.6901 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 11 | 5291 | 15.5 | 15.5 | 16.0792 | 17.2433 | 15 | 88 | 88 | 5.2181 | 196.2479 | 48.3121 | 140.3488 | 0 | 0.8525 | 3.3043 | 3.8205 | 2.0987 | 0 | 0 | 0 | 3.7521 | 96.5299 | 98.4621 | 104.0193 | 105.1892 | 101.2867 | 96.5299 | 96.5299 | 96.5299 | 196.2479 | 96.5299 | 99.3146 | 107.3236 | 109.0098 | 103.3854 | 96.5299 | 96.5299 | 96.5299 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 12 | 5292 | 17.7 | 17.7 | 16.0792 | 17.2433 | 15 | 78 | 78 | 309.4532 | 322.1608 | 52.7681 | 162.0346 | 0 | 0 | 131.3292 | 204.9126 | 158.461 | 19.1851 | 0 | 0 | 241.8392 | 153.722 | 153.722 | 239.7735 | 287.9879 | 257.5512 | 166.2928 | 153.722 | 153.722 | 322.1608 | 153.722 | 153.722 | 371.1027 | 492.9005 | 416.0122 | 185.4778 | 153.722 | 153.722 | 564 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 13 | 5293 | 18.3 | 18.3 | 16.0792 | 17.2433 | 15 | 73 | 73 | 264.3981 | 345.0597 | 53.7186 | 186.1959 | 0 | 0 | 49.3423 | 142.4924 | 152.1724 | 72.7118 | 0 | 0 | 212.9403 | 156.2101 | 156.2101 | 196.5359 | 272.6644 | 280.5755 | 215.6351 | 156.2101 | 156.2101 | 345.0597 | 156.2101 | 156.2101 | 245.8783 | 415.1568 | 432.7479 | 288.3469 | 156.2101 | 156.2101 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 14 | 5294 | 18.3 | 18.3 | 16.0792 | 17.2433 | 15 | 74 | 74 | 28.1157 | 313.8169 | 50.8853 | 209.4316 | 0 | 0 | 0 | 10.4261 | 16.5403 | 12.9655 | 1.7956 | 0 | 22.1831 | 138.4351 | 138.4351 | 138.4351 | 177.9052 | 201.0521 | 187.5188 | 145.2329 | 138.4351 | 313.8169 | 138.4351 | 138.4351 | 138.4351 | 188.3313 | 217.5924 | 200.4843 | 147.0286 | 138.4351 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 15 | 5295 | 19.6 | 19.6 | 16.0792 | 17.2433 | 15 | 64 | 64 | 437.8857 | 261.8115 | 45.0357 | 229.2084 | 0 | 0 | 0 | 74.1427 | 240.5989 | 266.1155 | 135.7453 | 0 | 321.1885 | 137.222 | 137.222 | 137.222 | 168.9556 | 240.2001 | 251.1214 | 195.322 | 137.222 | 261.8115 | 137.222 | 137.222 | 137.222 | 243.0982 | 480.799 | 517.2369 | 331.0673 | 137.222 | 583 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 16 | 5296 | 17.9 | 17.9 | 16.0792 | 17.2433 | 15 | 73 | 73 | 6.3183 | 189.9389 | 37.2838 | 245.4227 | 0 | 0 | 0 | 0 | 2.917 | 4.4529 | 3.3803 | 0.32766 | 4.0611 | 95.1191 | 95.1191 | 95.1191 | 95.1191 | 97.2595 | 98.3866 | 97.5996 | 95.3595 | 189.9389 | 95.1191 | 95.1191 | 95.1191 | 95.1191 | 100.1765 | 102.8394 | 100.9799 | 95.6872 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 17 | 5297 | 15 | 15 | 16.0792 | 17.2433 | 15 | 93 | 93 | 0.77331 | 55.5956 | 28.5204 | 259.1014 | 0 | 0 | 0 | 0 | 0.25591 | 0.57661 | 0.55954 | 0.2147 | 0.40444 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 55.5956 | 26.7756 | 26.7756 | 26.7756 | 26.7756 | 27.0315 | 27.3522 | 27.3352 | 26.9903 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 9 | 18 | 5298 | 15.7 | 15.7 | 16.0792 | 17.2433 | 15 | 91 | 91 | 3.9042 | 90.5071 | 19.3545 | 271.3054 | 0 | 0 | 0 | 0 | 0.64859 | 2.8405 | 3.3685 | 1.9233 | 1.4929 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 90.5071 | 44.5999 | 44.5999 | 44.5999 | 44.5999 | 45.2485 | 47.4404 | 47.9684 | 46.5232 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 19 | 5299 | 15.7 | 15.7 | 16.0792 | 17.2433 | 15 | 92 | 92 | 45.4264 | 97.5283 | 10.2266 | 282.8669 | 0.97639 | 0 | 0 | 0 | 0 | 29.6078 | 42.8481 | 30.9886 | 10.4717 | 48.9216 | 48.1126 | 48.1126 | 48.1126 | 48.1126 | 72.6448 | 83.6154 | 73.7889 | 97.5283 | 49.898 | 48.1126 | 48.1126 | 48.1126 | 48.1126 | 102.2526 | 126.4635 | 104.7775 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 20 | 5300 | 14.8 | 14.8 | 16.0792 | 17.2433 | 15 | 96 | 96 | 0.71496 | 7.9444 | 1.5096 | 294.4258 | 0.15668 | 0 | 0 | 0 | 0 | 0.37424 | 0.68594 | 0.59582 | 0.055554 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 7.9444 | 3.86 | 3.7034 | 3.7034 | 3.7034 | 3.7034 | 4.0776 | 4.3893 | 4.2992 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 21 | 5301 | 14.1 | 14.1 | 16.0792 | 17.2433 | 15 | 96 | 96 | 0 | 0 | -6.4234 | 306.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 22 | 5302 | 13.3 | 13.3 | 16.0792 | 17.2433 | 15 | 98 | 98 | 0 | 0 | -13.1616 | 319.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 23 | 5303 | 12 | 12 | 16.0792 | 17.2433 | 15 | 98 | 98 | 0 | 0 | -18.2541 | 333.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 9 | 24 | 5304 | 11.6 | 11.6 | 15.1542 | 16.5539 | 15 | 99 | 99 | 0 | 0 | -21.2627 | 348.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 1 | 5305 | 11.8 | 11.8 | 15.1542 | 16.5539 | 15 | 99 | 99 | 0 | 0 | -21.8744 | 3.9463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 2 | 5306 | 12.3 | 12.3 | 15.1542 | 16.5539 | 15 | 99 | 99 | 0 | 0 | -20.2963 | 19.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 3 | 5307 | 12.7 | 12.7 | 15.1542 | 16.5539 | 15 | 99 | 99 | 0 | 0 | -16.1625 | 33.9377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 4 | 5308 | 12.8 | 12.8 | 15.1542 | 16.5539 | 15 | 98 | 98 | 0 | 0 | -10.1583 | 47.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 5 | 5309 | 13 | 13 | 15.1542 | 16.5539 | 15 | 96 | 96 | 0 | 0 | -2.7423 | 59.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 6 | 5310 | 12.6 | 12.6 | 15.1542 | 16.5539 | 15 | 96 | 96 | 0 | 0 | 5.65 | 71.6789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 7 | 5311 | 13 | 13 | 15.1542 | 16.5539 | 15 | 97 | 97 | 3.3351 | 43.3402 | 14.6284 | 83.1819 | 1.0433 | 2.9655 | 3.1506 | 1.4901 | 0 | 0 | 0 | 0 | 0.6598 | 37.428 | 70.4474 | 73.6269 | 45.1042 | 19.5077 | 19.5077 | 19.5077 | 19.5077 | 43.3402 | 38.4713 | 73.4129 | 76.7776 | 46.5943 | 19.5077 | 19.5077 | 19.5077 | 19.5077 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 10 | 8 | 5312 | 13.4 | 13.4 | 15.1542 | 16.5539 | 15 | 93 | 93 | 10.5039 | 118.3142 | 23.8251 | 94.9925 | 1.2066 | 7.9889 | 10.0915 | 6.2826 | 0 | 0 | 0 | 0 | 3.6858 | 61.3891 | 113.6556 | 129.8584 | 100.5062 | 52.0911 | 52.0911 | 52.0911 | 52.0911 | 118.3142 | 62.5957 | 121.6445 | 139.9499 | 106.7887 | 52.0911 | 52.0911 | 52.0911 | 52.0911 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 9 | 5313 | 13.4 | 13.4 | 15.1542 | 16.5539 | 15 | 93 | 93 | 4.5162 | 125.7664 | 32.8421 | 107.838 | 0 | 2.656 | 4.1157 | 3.1644 | 0.35953 | 0 | 0 | 0 | 2.2336 | 60.7634 | 69.7463 | 74.6832 | 71.466 | 61.9794 | 60.7634 | 60.7634 | 60.7634 | 125.7664 | 60.7634 | 72.4023 | 78.7988 | 74.6304 | 62.3389 | 60.7634 | 60.7634 | 60.7634 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 10 | 5314 | 14.5 | 14.5 | 15.1542 | 16.5539 | 15 | 87 | 87 | 9.0976 | 202.3679 | 41.1671 | 122.6636 | 0 | 3.4893 | 7.276 | 6.8006 | 2.3414 | 0 | 0 | 0 | 5.6321 | 95.067 | 109.465 | 125.0903 | 123.1283 | 104.7284 | 95.067 | 95.067 | 95.067 | 202.3679 | 95.067 | 112.9543 | 132.3663 | 129.9288 | 107.0698 | 95.067 | 95.067 | 95.067 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 11 | 5315 | 17.3 | 17.3 | 15.1542 | 16.5539 | 15 | 77 | 77 | 237.6033 | 312.8935 | 48.0596 | 140.5679 | 0 | 38.2148 | 150.579 | 174.7361 | 96.5351 | 0 | 0 | 0 | 170.1065 | 149.1998 | 176.0258 | 254.9033 | 271.8611 | 216.9655 | 149.1998 | 149.1998 | 149.1998 | 312.8935 | 149.1998 | 214.2406 | 405.4823 | 446.5972 | 313.5007 | 149.1998 | 149.1998 | 149.1998 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 12 | 5316 | 16.9 | 16.9 | 15.1542 | 16.5539 | 15 | 82 | 82 | 26.5989 | 307.2935 | 52.4897 | 162.1782 | 0 | 0 | 11.2917 | 17.6937 | 13.731 | 1.7249 | 0 | 0 | 20.7065 | 143.5149 | 143.5149 | 167.1873 | 180.6089 | 172.3013 | 147.1311 | 143.5149 | 143.5149 | 307.2935 | 143.5149 | 143.5149 | 178.479 | 198.3026 | 186.0323 | 148.8559 | 143.5149 | 143.5149 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 13 | 5317 | 17.2 | 17.2 | 15.1542 | 16.5539 | 15 | 78 | 78 | 87.8754 | 360.4909 | 53.4271 | 186.214 | 0 | 0 | 16.3764 | 47.5999 | 50.94 | 24.4401 | 0 | 0 | 70.5091 | 159.7257 | 159.7257 | 184.6946 | 232.3006 | 237.3932 | 196.9892 | 159.7257 | 159.7257 | 360.4909 | 159.7257 | 159.7257 | 201.0711 | 279.9005 | 288.3332 | 221.4293 | 159.7257 | 159.7257 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 14 | 5318 | 16.9 | 16.9 | 15.1542 | 16.5539 | 15 | 84 | 84 | 20.3425 | 298.0115 | 50.6002 | 209.3343 | 0 | 0 | 0 | 7.5927 | 12.0498 | 9.4482 | 1.312 | 0 | 15.9885 | 142.6085 | 142.6085 | 142.6085 | 156.6623 | 164.912 | 160.0966 | 145.037 | 142.6085 | 298.0115 | 142.6085 | 142.6085 | 142.6085 | 164.255 | 176.9618 | 169.5448 | 146.349 | 142.6085 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 15 | 5319 | 16.7 | 16.7 | 15.1542 | 16.5539 | 15 | 70 | 70 | 81.4003 | 326.5453 | 44.7667 | 229.0489 | 0 | 0 | 0 | 13.9513 | 45.0421 | 49.7478 | 25.312 | 0 | 59.4547 | 146.6719 | 146.6719 | 146.6719 | 166.6971 | 211.3237 | 218.0782 | 183.0038 | 146.6719 | 326.5453 | 146.6719 | 146.6719 | 146.6719 | 180.6485 | 256.3658 | 267.826 | 208.3158 | 146.6719 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 16 | 5320 | 17.2 | 17.2 | 15.1542 | 16.5539 | 15 | 68 | 68 | 184.9679 | 287.7083 | 37.0296 | 245.2431 | 0 | 0 | 0 | 0 | 86.0713 | 130.9957 | 99.1846 | 9.2725 | 118.2917 | 135.6191 | 135.6191 | 135.6191 | 135.6191 | 202.3258 | 237.143 | 212.4888 | 142.8054 | 287.7083 | 135.6191 | 135.6191 | 135.6191 | 135.6191 | 288.3971 | 368.1387 | 311.6734 | 152.0779 | 406 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 17 | 5321 | 16.6 | 16.6 | 15.1542 | 16.5539 | 15 | 70 | 70 | 127.9432 | 236.5213 | 28.275 | 258.9221 | 0 | 0 | 0 | 0 | 42.7732 | 95.8313 | 92.7527 | 35.3409 | 66.4787 | 111.7499 | 111.7499 | 111.7499 | 111.7499 | 152.7945 | 203.7084 | 200.7543 | 145.6626 | 236.5213 | 111.7499 | 111.7499 | 111.7499 | 111.7499 | 195.5677 | 299.5397 | 293.507 | 181.0035 | 303 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 10 | 18 | 5322 | 17.8 | 17.8 | 15.1542 | 16.5539 | 15 | 63 | 63 | 447.0408 | 133.6633 | 19.1115 | 271.1345 | 0 | 0 | 0 | 0 | 75.6469 | 326.6925 | 386.366 | 219.7116 | 169.3367 | 79.9904 | 79.9904 | 79.9904 | 79.9904 | 99.9059 | 165.9985 | 181.7087 | 137.8337 | 133.6633 | 79.9904 | 79.9904 | 79.9904 | 79.9904 | 175.5528 | 492.6909 | 568.0747 | 357.5452 | 303 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 19 | 5323 | 16.1 | 16.1 | 15.1542 | 16.5539 | 15 | 72 | 72 | 419.5606 | 82.8828 | 9.9804 | 282.708 | 7.8491 | 0 | 0 | 0 | 0 | 274.7173 | 396.358 | 285.8176 | 95.1172 | 52.8113 | 51.0834 | 51.0834 | 51.0834 | 51.0834 | 111.559 | 138.3366 | 114.0025 | 82.8828 | 60.6604 | 51.0834 | 51.0834 | 51.0834 | 51.0834 | 386.2763 | 534.6946 | 399.8201 | 178 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 20 | 5324 | 15.3 | 15.3 | 15.1542 | 16.5539 | 15 | 77 | 77 | 9.4755 | 24.3019 | 1.2557 | 294.2822 | 2.0529 | 0 | 0 | 0 | 0 | 4.9855 | 9.1035 | 7.8888 | 0.69807 | 13.8357 | 12.6827 | 12.6827 | 12.6827 | 12.6827 | 15.4829 | 17.7959 | 17.1136 | 24.3019 | 15.8887 | 12.6827 | 12.6827 | 12.6827 | 12.6827 | 20.4685 | 26.8994 | 25.0024 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 21 | 5325 | 14.8 | 14.8 | 15.1542 | 16.5539 | 15 | 78 | 78 | 0 | 3 | -6.6882 | 306.3648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 3 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 1.4003 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 22 | 5326 | 13.9 | 13.9 | 15.1542 | 16.5539 | 15 | 84 | 84 | 0 | 0 | -13.4383 | 319.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 23 | 5327 | 12.6 | 12.6 | 15.1542 | 16.5539 | 15 | 88 | 88 | 0 | 0 | -18.5409 | 333.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 10 | 24 | 5328 | 11.6 | 11.6 | 14.6 | 15.9488 | 15 | 92 | 92 | 0 | 0 | -21.5544 | 348.4413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 1 | 5329 | 10.4 | 10.4 | 14.6 | 15.9488 | 15 | 97 | 97 | 0 | 0 | -22.1628 | 3.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 2 | 5330 | 9.9 | 9.9 | 14.6 | 15.9488 | 15 | 99 | 99 | 0 | 0 | -20.5769 | 19.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 3 | 5331 | 10.6 | 10.6 | 14.6 | 15.9488 | 15 | 99 | 99 | 0 | 0 | -16.4255 | 34.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 4 | 5332 | 10 | 10 | 14.6 | 15.9488 | 15 | 99 | 99 | 0 | 0 | -10.4023 | 47.6044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 5 | 5333 | 9.5 | 9.5 | 14.6 | 15.9488 | 15 | 99 | 99 | 0 | 0 | -2.9692 | 60.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 6 | 5334 | 8.9 | 8.9 | 14.6 | 15.9488 | 15 | 99 | 99 | 0.34957 | 2.9854 | 5.436 | 71.8845 | 0.174 | 0.33704 | 0.30264 | 0.090962 | 0 | 0 | 0 | 0 | 0.014562 | 1.7584 | 2.0887 | 2.019 | 1.5902 | 1.406 | 1.406 | 1.406 | 1.406 | 2.9854 | 1.9324 | 2.4257 | 2.3216 | 1.6812 | 1.406 | 1.406 | 1.406 | 1.406 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 7 | 5335 | 12.3 | 12.3 | 14.6 | 15.9488 | 15 | 100 | 100 | 25.4182 | 76.0709 | 14.4217 | 83.401 | 7.8678 | 22.569 | 24.0496 | 11.4423 | 0 | 0 | 0 | 0 | 4.9291 | 96.9094 | 218.2991 | 230.5245 | 126.4241 | 31.944 | 31.944 | 31.944 | 31.944 | 76.0709 | 104.7772 | 240.8681 | 254.5741 | 137.8664 | 31.944 | 31.944 | 31.944 | 31.944 | 81 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 11 | 8 | 5336 | 16.2 | 16.2 | 14.6 | 15.9488 | 15 | 84 | 84 | 270.0977 | 148.2218 | 23.6189 | 95.2247 | 30.0614 | 205.0008 | 259.8536 | 162.4876 | 0 | 0 | 0 | 0 | 93.7782 | 90.8689 | 169.2219 | 193.7897 | 150.1808 | 77.4048 | 77.4048 | 77.4048 | 77.4048 | 148.2218 | 120.9303 | 374.2227 | 453.6433 | 312.6685 | 77.4048 | 77.4048 | 77.4048 | 77.4048 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 9 | 5337 | 18.2 | 18.2 | 14.6 | 15.9488 | 15 | 75 | 75 | 432.1118 | 176.8 | 32.6283 | 108.0816 | 0 | 253.2973 | 394.2692 | 304.2835 | 36.0527 | 0 | 0 | 0 | 212.2 | 102.6326 | 181.8022 | 225.8638 | 197.7382 | 113.9011 | 102.6326 | 102.6326 | 102.6326 | 176.8 | 102.6326 | 435.0995 | 620.1329 | 502.0218 | 149.9538 | 102.6326 | 102.6326 | 102.6326 | 389 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 10 | 5338 | 19.3 | 19.3 | 14.6 | 15.9488 | 15 | 66 | 66 | 567.377 | 181.6328 | 40.9365 | 122.9101 | 0 | 216.3268 | 454.2392 | 426.0645 | 148.307 | 0 | 0 | 0 | 349.3672 | 116.6913 | 170.6786 | 230.0529 | 223.0215 | 153.7033 | 116.6913 | 116.6913 | 116.6913 | 181.6328 | 116.6913 | 387.0053 | 684.2921 | 649.086 | 302.0103 | 116.6913 | 116.6913 | 116.6913 | 531 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 11 | 5339 | 19.3 | 19.3 | 14.6 | 15.9488 | 15 | 73 | 73 | 294.4908 | 298.1042 | 47.8039 | 140.7908 | 0 | 46.5954 | 186.7681 | 217.5346 | 120.8722 | 0 | 0 | 0 | 209.8958 | 145.0753 | 174.9612 | 264.8666 | 284.6 | 222.6016 | 145.0753 | 145.0753 | 145.0753 | 298.1042 | 145.0753 | 221.5566 | 451.6348 | 502.1345 | 343.4738 | 145.0753 | 145.0753 | 145.0753 | 508 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 12 | 5340 | 19 | 19 | 14.6 | 15.9488 | 15 | 73 | 73 | 22.8105 | 299.3134 | 52.2075 | 162.3253 | 0 | 0 | 9.6853 | 15.243 | 11.8715 | 1.5458 | 0 | 0 | 17.6866 | 140.2697 | 140.2697 | 162.1309 | 174.6754 | 167.0654 | 143.7589 | 140.2697 | 140.2697 | 299.3134 | 140.2697 | 140.2697 | 171.8163 | 189.9183 | 178.9369 | 145.3048 | 140.2697 | 140.2697 | 317 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 13 | 5341 | 20.7 | 20.7 | 14.6 | 15.9488 | 15 | 62 | 62 | 17.8066 | 296.767 | 53.1312 | 186.2356 | 0 | 0 | 3.313 | 9.6943 | 10.3968 | 5.009 | 0 | 0 | 14.233 | 141.3961 | 141.3961 | 148.7216 | 162.8316 | 164.385 | 152.4718 | 141.3961 | 141.3961 | 296.767 | 141.3961 | 141.3961 | 152.0346 | 172.5259 | 174.7818 | 157.4808 | 141.3961 | 141.3961 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 14 | 5342 | 19.3 | 19.3 | 14.6 | 15.9488 | 15 | 59 | 59 | 141.2788 | 356.3956 | 50.3102 | 209.2399 | 0 | 0 | 0 | 53.0731 | 84.2636 | 66.0936 | 9.2069 | 0 | 110.6044 | 157.6168 | 157.6168 | 157.6168 | 224.0534 | 263.0976 | 240.3525 | 169.142 | 157.6168 | 356.3956 | 157.6168 | 157.6168 | 157.6168 | 277.1265 | 347.3612 | 306.4461 | 178.3489 | 157.6168 | 467 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 15 | 5343 | 21.1 | 21.1 | 14.6 | 15.9488 | 15 | 54 | 54 | 852.2623 | 127.2059 | 44.4927 | 228.8911 | 0 | 0 | 0 | 147.8321 | 474.9298 | 523.82 | 265.8636 | 0 | 619.7941 | 119.5951 | 119.5951 | 119.5951 | 133.1155 | 163.0311 | 167.5025 | 143.9104 | 119.5951 | 127.2059 | 119.5951 | 119.5951 | 119.5951 | 280.9476 | 637.9609 | 691.3226 | 409.774 | 119.5951 | 747 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 16 | 5344 | 19.3 | 19.3 | 14.6 | 15.9488 | 15 | 59 | 59 | 828.8249 | 114.6725 | 36.7703 | 245.0642 | 0 | 0 | 0 | 0 | 388.7317 | 589.8707 | 445.4715 | 40.1211 | 527.3275 | 106.8893 | 106.8893 | 106.8893 | 106.8893 | 141.3269 | 159.1457 | 146.3535 | 110.4436 | 114.6725 | 106.8893 | 106.8893 | 106.8893 | 106.8893 | 530.0586 | 749.0165 | 591.825 | 150.5648 | 642 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 17 | 5345 | 20.2 | 20.2 | 14.6 | 15.9488 | 15 | 59 | 59 | 362.6794 | 201.8079 | 28.0245 | 258.7429 | 0 | 0 | 0 | 0 | 122.4846 | 272.8892 | 263.4391 | 99.6699 | 187.1921 | 107.3217 | 107.3217 | 107.3217 | 107.3217 | 158.6605 | 221.7018 | 217.7408 | 149.0978 | 201.8079 | 107.3217 | 107.3217 | 107.3217 | 107.3217 | 281.145 | 494.591 | 481.1799 | 248.7677 | 389 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 18 | 5346 | 19.6 | 19.6 | 14.6 | 15.9488 | 15 | 55 | 55 | 826.8441 | 67.8202 | 18.8636 | 270.9633 | 0 | 0 | 0 | 0 | 142.4841 | 606.9348 | 715.8513 | 405.4318 | 310.1798 | 69.0147 | 69.0147 | 69.0147 | 69.0147 | 77.665 | 105.8622 | 112.4746 | 93.6288 | 67.8202 | 69.0147 | 69.0147 | 69.0147 | 69.0147 | 220.1491 | 712.7969 | 828.3259 | 499.0606 | 378 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 19 | 5347 | 18.2 | 18.2 | 14.6 | 15.9488 | 15 | 58 | 58 | 216.6886 | 98.7146 | 9.7293 | 282.5487 | 3.4472 | 0 | 0 | 0 | 0 | 142.5346 | 205.0215 | 147.4096 | 48.2854 | 55.083 | 53.5588 | 53.5588 | 53.5588 | 53.5588 | 116.5805 | 144.2091 | 118.736 | 98.7146 | 58.5301 | 53.5588 | 53.5588 | 53.5588 | 53.5588 | 259.1151 | 349.2306 | 266.1456 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 20 | 5348 | 17 | 17 | 14.6 | 15.9488 | 15 | 70 | 70 | 148.8024 | 31.6463 | 0.9969 | 294.1382 | 31.8652 | 0 | 0 | 0 | 0 | 78.6964 | 143.1587 | 123.7606 | 10.3537 | 31.4009 | 18.098 | 18.098 | 18.098 | 18.098 | 50.9517 | 77.8631 | 69.7649 | 31.6463 | 63.2662 | 18.098 | 18.098 | 18.098 | 18.098 | 129.6481 | 221.0219 | 193.5256 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 21 | 5349 | 16.8 | 16.8 | 14.6 | 15.9488 | 15 | 66 | 66 | 0 | 0 | -6.9577 | 306.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 22 | 5350 | 16.9 | 16.9 | 14.6 | 15.9488 | 15 | 75 | 75 | 0 | 0 | -13.7197 | 319.2444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 23 | 5351 | 16.4 | 16.4 | 14.6 | 15.9488 | 15 | 80 | 80 | 0 | 0 | -18.8324 | 333.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 11 | 24 | 5352 | 16.3 | 16.3 | 16.0583 | 15.9192 | 15 | 80 | 80 | 0 | 0 | -21.8505 | 348.4364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 1 | 5353 | 15.7 | 15.7 | 16.0583 | 15.9192 | 15 | 71 | 71 | 0 | 0 | -22.4553 | 4.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 2 | 5354 | 15.3 | 15.3 | 16.0583 | 15.9192 | 15 | 74 | 74 | 0 | 0 | -20.8608 | 19.5688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 3 | 5355 | 15.6 | 15.6 | 16.0583 | 15.9192 | 15 | 73 | 73 | 0 | 0 | -16.6914 | 34.2255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 4 | 5356 | 15.1 | 15.1 | 16.0583 | 15.9192 | 15 | 77 | 77 | 0 | 0 | -10.6488 | 47.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 5 | 5357 | 14.7 | 14.7 | 16.0583 | 15.9192 | 15 | 77 | 77 | 0 | 0 | -3.1982 | 60.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 6 | 5358 | 15 | 15 | 16.0583 | 15.9192 | 15 | 78 | 78 | 0 | 0 | 5.2201 | 72.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 7 | 5359 | 15.4 | 15.4 | 16.0583 | 15.9192 | 15 | 79 | 79 | 1.1671 | 24.7783 | 14.2132 | 83.6244 | 0.35734 | 1.0347 | 1.106 | 0.52937 | 0 | 0 | 0 | 0 | 0.22169 | 12.219 | 12.2362 | 12.238 | 12.2233 | 12.2099 | 12.2099 | 12.2099 | 12.2099 | 24.7783 | 12.5763 | 13.2709 | 13.3439 | 12.7527 | 12.2099 | 12.2099 | 12.2099 | 12.2099 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 12 | 8 | 5360 | 16 | 16 | 16.0583 | 15.9192 | 15 | 79 | 79 | 1.7913 | 55.3848 | 23.4108 | 95.4611 | 0.19282 | 1.3566 | 1.7257 | 1.0839 | 0 | 0 | 0 | 0 | 0.61519 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 55.3848 | 27.4451 | 28.6089 | 28.978 | 28.3362 | 27.2523 | 27.2523 | 27.2523 | 27.2523 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 9 | 5361 | 15.6 | 15.6 | 16.0583 | 15.9192 | 15 | 86 | 86 | 1.9528 | 82.048 | 32.4123 | 108.3294 | 0 | 1.1408 | 1.7839 | 1.382 | 0.17055 | 0 | 0 | 0 | 0.95203 | 40.4338 | 40.4338 | 40.4338 | 40.4338 | 40.4338 | 40.4338 | 40.4338 | 40.4338 | 82.048 | 40.4338 | 41.5746 | 42.2177 | 41.8158 | 40.6043 | 40.4338 | 40.4338 | 40.4338 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 10 | 5362 | 15.8 | 15.8 | 16.0583 | 15.9192 | 15 | 88 | 88 | 3.8823 | 144.6226 | 40.7032 | 123.1604 | 0 | 1.4711 | 3.1112 | 2.9287 | 1.0307 | 0 | 0 | 0 | 2.3774 | 71.8132 | 73.5089 | 75.3994 | 75.1891 | 73.0013 | 71.8132 | 71.8132 | 71.8132 | 144.6226 | 71.8132 | 74.9801 | 78.5106 | 78.1179 | 74.0319 | 71.8132 | 71.8132 | 71.8132 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 11 | 5363 | 15.3 | 15.3 | 16.0583 | 15.9192 | 15 | 84 | 84 | 2.1929 | 126.4442 | 47.545 | 141.0173 | 0 | 0.34108 | 1.3917 | 1.627 | 0.90931 | 0 | 0 | 0 | 1.5558 | 62.8415 | 62.8415 | 62.8415 | 62.8415 | 62.8415 | 62.8415 | 62.8415 | 62.8415 | 126.4442 | 62.8415 | 63.1826 | 64.2332 | 64.4686 | 63.7508 | 62.8415 | 62.8415 | 62.8415 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 12 | 5364 | 14.6 | 14.6 | 16.0583 | 15.9192 | 15 | 95 | 95 | 1.8511 | 126.5705 | 51.9216 | 162.4757 | 0 | 0 | 0.78606 | 1.2426 | 0.97131 | 0.13099 | 0 | 0 | 1.4295 | 62.799 | 62.799 | 62.799 | 62.799 | 62.799 | 62.799 | 62.799 | 62.799 | 126.5705 | 62.799 | 62.799 | 63.5851 | 64.0417 | 63.7703 | 62.93 | 62.799 | 62.799 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 13 | 5365 | 15.6 | 15.6 | 16.0583 | 15.9192 | 15 | 96 | 96 | 1.9658 | 134.4349 | 52.8311 | 186.2604 | 0 | 0 | 0.36506 | 1.0756 | 1.1561 | 0.55936 | 0 | 0 | 1.5651 | 66.8874 | 66.8874 | 66.8874 | 66.8874 | 66.8874 | 66.8874 | 66.8874 | 66.8874 | 134.4349 | 66.8874 | 66.8874 | 67.2524 | 67.963 | 68.0435 | 67.4467 | 66.8874 | 66.8874 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 14 | 5366 | 16.4 | 16.4 | 16.0583 | 15.9192 | 15 | 96 | 96 | 0.6742 | 77.4743 | 50.0155 | 209.1483 | 0 | 0 | 0 | 0.2549 | 0.4049 | 0.31772 | 0.044418 | 0 | 0.52569 | 37.765 | 37.765 | 37.765 | 37.765 | 37.765 | 37.765 | 37.765 | 37.765 | 77.4743 | 37.765 | 37.765 | 37.765 | 38.0198 | 38.1699 | 38.0827 | 37.8094 | 37.765 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 15 | 5367 | 17.1 | 17.1 | 16.0583 | 15.9192 | 15 | 91 | 91 | 0.88544 | 82.3589 | 44.2137 | 228.735 | 0 | 0 | 0 | 0.15541 | 0.49691 | 0.54733 | 0.27713 | 0 | 0.64106 | 40.1911 | 40.1911 | 40.1911 | 40.1911 | 40.1911 | 40.1911 | 40.1911 | 40.1911 | 82.3589 | 40.1911 | 40.1911 | 40.1911 | 40.3465 | 40.688 | 40.7384 | 40.4682 | 40.1911 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 16 | 5368 | 17.5 | 17.5 | 16.0583 | 15.9192 | 15 | 87 | 87 | 10.2652 | 212.5033 | 36.506 | 244.8861 | 0 | 0 | 0 | 0 | 4.8526 | 7.3419 | 5.5304 | 0.47929 | 6.4967 | 104.4949 | 104.4949 | 104.4949 | 104.4949 | 111.1739 | 114.6 | 112.1068 | 105.1546 | 212.5033 | 104.4949 | 104.4949 | 104.4949 | 104.4949 | 116.0265 | 121.9419 | 117.6372 | 105.6339 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 17 | 5369 | 18.3 | 18.3 | 16.0583 | 15.9192 | 15 | 82 | 82 | 55.1406 | 221.7341 | 27.7691 | 258.5637 | 0 | 0 | 0 | 0 | 18.811 | 41.6789 | 40.1318 | 15.0761 | 28.2659 | 103.2268 | 103.2268 | 103.2268 | 103.2268 | 130.2595 | 163.122 | 160.8988 | 124.8921 | 221.7341 | 103.2268 | 103.2268 | 103.2268 | 103.2268 | 149.0705 | 204.8009 | 201.0306 | 139.9682 | 250 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 18 | 5370 | 18.4 | 18.4 | 16.0583 | 15.9192 | 15 | 79 | 79 | 7.1653 | 114.3387 | 18.6107 | 270.7918 | 0 | 0 | 0 | 0 | 1.2571 | 5.283 | 6.2142 | 3.5052 | 2.6613 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 114.3387 | 57.2474 | 57.2474 | 57.2474 | 57.2474 | 58.5045 | 62.5305 | 63.4617 | 60.7527 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 19 | 5371 | 18.2 | 18.2 | 16.0583 | 15.9192 | 15 | 70 | 70 | 2.1386 | 38.5319 | 9.4733 | 282.389 | 0.028008 | 0 | 0 | 0 | 0 | 1.4132 | 2.0266 | 1.4528 | 0.46813 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 38.5319 | 18.5123 | 18.4843 | 18.4843 | 18.4843 | 18.4843 | 19.8975 | 20.5108 | 19.9371 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 20 | 5372 | 18.4 | 18.4 | 16.0583 | 15.9192 | 15 | 63 | 63 | 1.0072 | 7.9341 | 0.73333 | 293.9938 | 0.21314 | 0 | 0 | 0 | 0 | 0.53541 | 0.97032 | 0.83684 | 0.065901 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 3.701 | 7.9341 | 3.9141 | 3.701 | 3.701 | 3.701 | 3.701 | 4.2364 | 4.6713 | 4.5378 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 21 | 5373 | 17.1 | 17.1 | 16.0583 | 15.9192 | 15 | 66 | 66 | 0 | 0 | -7.2321 | 306.1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 22 | 5374 | 16.1 | 16.1 | 16.0583 | 15.9192 | 15 | 83 | 83 | 0 | 0 | -14.0059 | 319.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 23 | 5375 | 16.5 | 16.5 | 16.0583 | 15.9192 | 15 | 84 | 84 | 0 | 0 | -19.1285 | 333.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 12 | 24 | 5376 | 17.2 | 17.2 | 16.2875 | 16.0013 | 15 | 92 | 92 | 0 | 0 | -22.151 | 348.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 1 | 5377 | 17.2 | 17.2 | 16.2875 | 16.0013 | 15 | 94 | 94 | 0 | 0 | -22.7517 | 4.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 2 | 5378 | 17 | 17 | 16.2875 | 16.0013 | 15 | 92 | 92 | 0 | 0 | -21.1481 | 19.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 3 | 5379 | 17.1 | 17.1 | 16.2875 | 16.0013 | 15 | 93 | 93 | 0 | 0 | -16.9601 | 34.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 4 | 5380 | 17.3 | 17.3 | 16.2875 | 16.0013 | 15 | 93 | 93 | 0 | 0 | -10.8975 | 47.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 5 | 5381 | 17.5 | 17.5 | 16.2875 | 16.0013 | 15 | 92 | 92 | 0 | 0 | -3.4292 | 60.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 6 | 5382 | 17.7 | 17.7 | 16.2875 | 16.0013 | 15 | 92 | 92 | 0 | 0 | 5.0025 | 72.3088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 7 | 5383 | 17.6 | 17.6 | 16.2875 | 16.0013 | 15 | 94 | 94 | 0 | 0 | 14.0029 | 83.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 13 | 8 | 5384 | 17.7 | 17.7 | 16.2875 | 16.0013 | 15 | 96 | 96 | 0.36493 | 24.8761 | 23.2007 | 95.7016 | 0.037922 | 0.27575 | 0.35205 | 0.22212 | 0 | 0 | 0 | 0 | 0.12394 | 11.816 | 11.816 | 11.816 | 11.816 | 11.816 | 11.816 | 11.816 | 11.816 | 24.8761 | 11.8539 | 12.0917 | 12.168 | 12.0381 | 11.816 | 11.816 | 11.816 | 11.816 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 9 | 5385 | 18 | 18 | 16.2875 | 16.0013 | 15 | 92 | 92 | 0.31321 | 32.8484 | 32.194 | 108.5811 | 0 | 0.18233 | 0.28646 | 0.22278 | 0.0286 | 0 | 0 | 0 | 0.15156 | 15.6195 | 15.6195 | 15.6195 | 15.6195 | 15.6195 | 15.6195 | 15.6195 | 15.6195 | 32.8484 | 15.6195 | 15.8018 | 15.9059 | 15.8422 | 15.6481 | 15.6195 | 15.6195 | 15.6195 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 10 | 5386 | 17.9 | 17.9 | 16.2875 | 16.0013 | 15 | 95 | 95 | 0.35163 | 43.7859 | 40.4673 | 123.4145 | 0 | 0.1324 | 0.28206 | 0.26649 | 0.094819 | 0 | 0 | 0 | 0.21412 | 20.946 | 20.946 | 20.946 | 20.946 | 20.946 | 20.946 | 20.946 | 20.946 | 43.7859 | 20.946 | 21.0783 | 21.228 | 21.2124 | 21.0408 | 20.946 | 20.946 | 20.946 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 11 | 5387 | 18.2 | 18.2 | 16.2875 | 16.0013 | 15 | 96 | 96 | 0.75964 | 74.4636 | 47.2829 | 141.2472 | 0 | 0.11606 | 0.48239 | 0.56614 | 0.31826 | 0 | 0 | 0 | 0.53645 | 36.1697 | 36.1697 | 36.1697 | 36.1697 | 36.1697 | 36.1697 | 36.1697 | 36.1697 | 74.4636 | 36.1697 | 36.2858 | 36.6521 | 36.7359 | 36.488 | 36.1697 | 36.1697 | 36.1697 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 12 | 5388 | 18.6 | 18.6 | 16.2875 | 16.0013 | 15 | 94 | 94 | 0.84233 | 85.3523 | 51.632 | 162.6294 | 0 | 0 | 0.35769 | 0.56803 | 0.44562 | 0.062181 | 0 | 0 | 0.64774 | 41.672 | 41.672 | 41.672 | 41.672 | 41.672 | 41.672 | 41.672 | 41.672 | 85.3523 | 41.672 | 41.672 | 42.0297 | 42.24 | 42.1176 | 41.7342 | 41.672 | 41.672 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 13 | 5389 | 19.5 | 19.5 | 16.2875 | 16.0013 | 15 | 89 | 89 | 3.7052 | 183.0618 | 52.5268 | 186.2885 | 0 | 0 | 0.68663 | 2.0376 | 2.195 | 1.0666 | 0 | 0 | 2.9382 | 92.6886 | 92.6886 | 92.6886 | 92.6886 | 92.6886 | 92.6886 | 92.6886 | 92.6886 | 183.0618 | 92.6886 | 92.6886 | 93.3753 | 94.7262 | 94.8836 | 93.7552 | 92.6886 | 92.6886 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 14 | 5390 | 19.1 | 19.1 | 16.2875 | 16.0013 | 15 | 89 | 89 | 0.73281 | 80.431 | 49.7161 | 209.0595 | 0 | 0 | 0 | 0.27883 | 0.44315 | 0.34789 | 0.048835 | 0 | 0.56904 | 39.2446 | 39.2446 | 39.2446 | 39.2446 | 39.2446 | 39.2446 | 39.2446 | 39.2446 | 80.431 | 39.2446 | 39.2446 | 39.2446 | 39.5234 | 39.6877 | 39.5925 | 39.2934 | 39.2446 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 15 | 5391 | 19.7 | 19.7 | 16.2875 | 16.0013 | 15 | 88 | 88 | 2.2935 | 131.3471 | 43.9297 | 228.5808 | 0 | 0 | 0 | 0.40727 | 1.2962 | 1.4259 | 0.72028 | 0 | 1.6529 | 65.2906 | 65.2906 | 65.2906 | 65.2906 | 65.2906 | 65.2906 | 65.2906 | 65.2906 | 131.3471 | 65.2906 | 65.2906 | 65.2906 | 65.6979 | 66.5869 | 66.7165 | 66.0109 | 65.2906 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 16 | 5392 | 19.7 | 19.7 | 16.2875 | 16.0013 | 15 | 88 | 88 | 1.2571 | 85.2087 | 36.2367 | 244.7088 | 0 | 0 | 0 | 0 | 0.59895 | 0.90359 | 0.67892 | 0.056545 | 0.79131 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 85.2087 | 41.5976 | 41.5976 | 41.5976 | 41.5976 | 42.1966 | 42.5012 | 42.2766 | 41.6542 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 17 | 5393 | 20.7 | 20.7 | 16.2875 | 16.0013 | 15 | 81 | 81 | 11.5595 | 175.1159 | 27.5088 | 258.3848 | 0 | 0 | 0 | 0 | 3.9833 | 8.7775 | 8.43 | 3.1443 | 5.8841 | 86.1895 | 86.1895 | 86.1895 | 86.1895 | 90.1105 | 94.8298 | 94.4878 | 89.2847 | 175.1159 | 86.1895 | 86.1895 | 86.1895 | 86.1895 | 94.0937 | 103.6073 | 102.9177 | 92.429 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 13 | 18 | 5394 | 20.5 | 20.5 | 16.2875 | 16.0013 | 15 | 83 | 83 | 10.5284 | 124.1294 | 18.353 | 270.6202 | 0 | 0 | 0 | 0 | 1.8801 | 7.7972 | 9.1468 | 5.1383 | 3.8706 | 61.6972 | 61.6972 | 61.6972 | 61.6972 | 62.4141 | 64.6702 | 65.1848 | 63.6564 | 124.1294 | 61.6972 | 61.6972 | 61.6972 | 61.6972 | 64.2942 | 72.4674 | 74.3316 | 68.7948 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 19 | 5395 | 20.4 | 20.4 | 16.2875 | 16.0013 | 15 | 84 | 84 | 17.1154 | 79.3218 | 9.2126 | 282.2289 | 0.17583 | 0 | 0 | 0 | 0 | 11.3618 | 16.2438 | 11.6105 | 3.6782 | 39.6068 | 39.3268 | 39.3268 | 39.3268 | 39.3268 | 57.4139 | 65.1857 | 57.8097 | 79.3218 | 39.7826 | 39.3268 | 39.3268 | 39.3268 | 39.3268 | 68.7757 | 81.4296 | 69.4202 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 20 | 5396 | 19.9 | 19.9 | 16.2875 | 16.0013 | 15 | 87 | 87 | 12.1281 | 21.2575 | 0.46506 | 293.8491 | 2.5358 | 0 | 0 | 0 | 0 | 6.4801 | 11.7 | 10.0663 | 0.74251 | 12.0533 | 11.1521 | 11.1521 | 11.1521 | 11.1521 | 13.4552 | 15.3104 | 14.7298 | 21.2575 | 14.5891 | 11.1521 | 11.1521 | 11.1521 | 11.1521 | 19.9352 | 27.0104 | 24.796 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 21 | 5397 | 19.7 | 19.7 | 16.2875 | 16.0013 | 15 | 88 | 88 | 0 | 0 | -7.5111 | 305.9939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 22 | 5398 | 18.8 | 18.8 | 16.2875 | 16.0013 | 15 | 90 | 90 | 0 | 0 | -14.2968 | 319.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 23 | 5399 | 19.2 | 19.2 | 16.2875 | 16.0013 | 15 | 89 | 89 | 0 | 0 | -19.4292 | 333.2383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 13 | 24 | 5400 | 19 | 19 | 18.6667 | 16.6245 | 15 | 91 | 91 | 0 | 0 | -22.4558 | 348.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 1 | 5401 | 18.8 | 18.8 | 18.6667 | 16.6245 | 15 | 91 | 91 | 0 | 0 | -23.0521 | 4.1532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 2 | 5402 | 17.1 | 17.1 | 18.6667 | 16.6245 | 15 | 96 | 96 | 0 | 0 | -21.4387 | 19.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 3 | 5403 | 16.1 | 16.1 | 18.6667 | 16.6245 | 15 | 98 | 98 | 0 | 0 | -17.2315 | 34.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 4 | 5404 | 15.7 | 15.7 | 18.6667 | 16.6245 | 15 | 99 | 99 | 0 | 0 | -11.1484 | 48.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 5 | 5405 | 14.5 | 14.5 | 18.6667 | 16.6245 | 15 | 99 | 99 | 0 | 0 | -3.662 | 60.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 6 | 5406 | 14.7 | 14.7 | 18.6667 | 16.6245 | 15 | 100 | 100 | 0.72483 | 2.979 | 4.7831 | 72.5272 | 0.35398 | 0.69635 | 0.63082 | 0.19575 | 0 | 0 | 0 | 0 | 0.020956 | 1.9876 | 2.6275 | 2.505 | 1.6919 | 1.3261 | 1.3261 | 1.3261 | 1.3261 | 2.979 | 2.3416 | 3.3238 | 3.1358 | 1.8876 | 1.3261 | 1.3261 | 1.3261 | 1.3261 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 7 | 5407 | 16 | 16 | 18.6667 | 16.6245 | 15 | 99 | 99 | 9.0034 | 59.363 | 13.7909 | 84.0835 | 2.6939 | 7.9564 | 8.5581 | 4.1466 | 0 | 0 | 0 | 0 | 1.637 | 89.027 | 218.1281 | 232.8903 | 124.6661 | 22.9394 | 22.9394 | 22.9394 | 22.9394 | 59.363 | 91.7209 | 226.0845 | 241.4484 | 128.8127 | 22.9394 | 22.9394 | 22.9394 | 22.9394 | 61 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 14 | 8 | 5408 | 18.2 | 18.2 | 18.6667 | 16.6245 | 15 | 92 | 92 | 100.8559 | 152.1384 | 22.9888 | 95.9461 | 10.0965 | 76.0303 | 97.4267 | 61.7518 | 0 | 0 | 0 | 0 | 33.8616 | 83.8004 | 184.5915 | 217.2994 | 162.7643 | 68.3663 | 68.3663 | 68.3663 | 68.3663 | 152.1384 | 93.8969 | 260.6218 | 314.726 | 224.5161 | 68.3663 | 68.3663 | 68.3663 | 68.3663 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 9 | 5409 | 20 | 20 | 18.6667 | 16.6245 | 15 | 85 | 85 | 347.4577 | 191.1437 | 31.9736 | 108.8367 | 0 | 201.5304 | 318.1422 | 248.3907 | 33.1353 | 0 | 0 | 0 | 166.8563 | 103.5558 | 185.4363 | 232.815 | 204.4754 | 117.0184 | 103.5558 | 103.5558 | 103.5558 | 191.1437 | 103.5558 | 386.9667 | 550.9572 | 452.8661 | 150.1537 | 103.5558 | 103.5558 | 103.5558 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 10 | 5410 | 21.6 | 21.6 | 18.6667 | 16.6245 | 15 | 80 | 80 | 539.898 | 187.1339 | 40.2288 | 123.6723 | 0 | 201.9425 | 433.4625 | 411.066 | 147.8726 | 0 | 0 | 0 | 326.8661 | 116.6873 | 170.4751 | 232.1409 | 226.1755 | 156.0735 | 116.6873 | 116.6873 | 116.6873 | 187.1339 | 116.6873 | 372.4176 | 665.6033 | 637.2415 | 303.9461 | 116.6873 | 116.6873 | 116.6873 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 11 | 5411 | 23.3 | 23.3 | 18.6667 | 16.6245 | 15 | 75 | 75 | 670.9897 | 172.4245 | 47.0177 | 141.4805 | 0 | 100.6221 | 426.3318 | 502.3021 | 284.0306 | 0 | 0 | 0 | 471.5755 | 122.6725 | 141.778 | 203.6219 | 218.0467 | 176.6026 | 122.6725 | 122.6725 | 122.6725 | 172.4245 | 122.6725 | 242.4002 | 629.9537 | 720.3488 | 460.6332 | 122.6725 | 122.6725 | 122.6725 | 644 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 12 | 5412 | 25.5 | 25.5 | 18.6667 | 16.6245 | 15 | 67 | 67 | 746.1016 | 161.7152 | 51.3388 | 162.7861 | 0 | 0 | 316.7912 | 505.4215 | 397.9827 | 57.411 | 0 | 0 | 571.2848 | 127.3981 | 127.3981 | 179.2515 | 210.127 | 192.5411 | 136.7953 | 127.3981 | 127.3981 | 161.7152 | 127.3981 | 127.3981 | 496.0426 | 715.5485 | 590.5238 | 194.2063 | 127.3981 | 127.3981 | 733 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 13 | 5413 | 25.9 | 25.9 | 18.6667 | 16.6245 | 15 | 61 | 61 | 769.9049 | 158.984 | 52.2183 | 186.3198 | 0 | 0 | 142.3381 | 425.5116 | 459.4262 | 224.2152 | 0 | 0 | 608.016 | 129.6219 | 129.6219 | 146.5508 | 180.2299 | 184.2635 | 156.2888 | 129.6219 | 129.6219 | 158.984 | 129.6219 | 129.6219 | 288.8889 | 605.7416 | 643.6898 | 380.504 | 129.6219 | 129.6219 | 767 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 14 | 5414 | 26.9 | 26.9 | 18.6667 | 16.6245 | 15 | 55 | 55 | 791.0288 | 149.3505 | 49.4122 | 208.9735 | 0 | 0 | 0 | 302.8791 | 481.6821 | 378.3224 | 53.3465 | 0 | 611.6495 | 126.3572 | 126.3572 | 126.3572 | 159.8827 | 179.6742 | 168.2334 | 132.2621 | 126.3572 | 149.3505 | 126.3572 | 126.3572 | 126.3572 | 462.7617 | 661.3564 | 546.5558 | 185.6086 | 126.3572 | 761 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 15 | 5415 | 27.8 | 27.8 | 18.6667 | 16.6245 | 15 | 56 | 56 | 824.5331 | 130.513 | 43.641 | 228.4284 | 0 | 0 | 0 | 148.1047 | 469.3118 | 515.6024 | 259.8601 | 0 | 591.487 | 118.2716 | 118.2716 | 118.2716 | 132.5794 | 163.61 | 168.082 | 143.3757 | 118.2716 | 130.513 | 118.2716 | 118.2716 | 118.2716 | 280.6841 | 632.9218 | 683.6843 | 403.2358 | 118.2716 | 722 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 16 | 5416 | 27.9 | 27.9 | 18.6667 | 16.6245 | 15 | 55 | 55 | 793.3464 | 120.376 | 35.9625 | 244.5324 | 0 | 0 | 0 | 0 | 380.9656 | 573.1003 | 429.5206 | 34.3336 | 496.624 | 106.2787 | 106.2787 | 106.2787 | 106.2787 | 142.9644 | 161.4663 | 147.6401 | 109.5849 | 120.376 | 106.2787 | 106.2787 | 106.2787 | 106.2787 | 523.93 | 734.5665 | 577.1607 | 143.9185 | 617 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 17 | 5417 | 28.1 | 28.1 | 18.6667 | 16.6245 | 15 | 54 | 54 | 789.7922 | 97.848 | 27.2436 | 258.2061 | 0 | 0 | 0 | 0 | 274.8818 | 602.4715 | 577.1416 | 213.73 | 399.152 | 88.6756 | 88.6756 | 88.6756 | 88.6756 | 112.5537 | 141.0104 | 138.8101 | 107.2417 | 97.848 | 88.6756 | 88.6756 | 88.6756 | 88.6756 | 387.4355 | 743.4819 | 715.9517 | 320.9716 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 14 | 18 | 5418 | 27.4 | 27.4 | 18.6667 | 16.6245 | 15 | 54 | 54 | 658.6087 | 91.3984 | 18.0906 | 270.4484 | 0 | 0 | 0 | 0 | 119.6812 | 489.9316 | 573.1866 | 320.6768 | 239.6016 | 69.0671 | 69.0671 | 69.0671 | 69.0671 | 85.3119 | 135.5676 | 146.8681 | 112.5939 | 91.3984 | 69.0671 | 69.0671 | 69.0671 | 69.0671 | 204.9931 | 625.4991 | 720.0548 | 433.2707 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 19 | 5419 | 26.9 | 26.9 | 18.6667 | 16.6245 | 15 | 63 | 63 | 475.4158 | 71.7555 | 8.9473 | 282.0686 | 3.5367 | 0 | 0 | 0 | 0 | 317.0412 | 451.9007 | 322.0429 | 100.2445 | 47.1133 | 46.4784 | 46.4784 | 46.4784 | 46.4784 | 103.3994 | 127.6118 | 104.2973 | 71.7555 | 50.6501 | 46.4784 | 46.4784 | 46.4784 | 46.4784 | 420.4405 | 579.5124 | 426.3402 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 20 | 5420 | 23.4 | 23.4 | 18.6667 | 16.6245 | 15 | 77 | 77 | 55.7404 | 18.8871 | 0.19216 | 293.7041 | 11.5125 | 0 | 0 | 0 | 0 | 29.9337 | 53.8451 | 46.2148 | 28.1129 | 20.7156 | 13.1452 | 13.1452 | 13.1452 | 13.1452 | 32.829 | 48.5528 | 43.5353 | 18.8871 | 32.2281 | 13.1452 | 13.1452 | 13.1452 | 13.1452 | 62.7627 | 102.3979 | 89.7501 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 21 | 5421 | 20.7 | 20.7 | 18.6667 | 16.6245 | 15 | 87 | 87 | 0 | 0 | -7.7947 | 305.8701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 22 | 5422 | 21 | 21 | 18.6667 | 16.6245 | 15 | 84 | 84 | 0 | 0 | -14.5922 | 318.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 23 | 5423 | 20.1 | 20.1 | 18.6667 | 16.6245 | 15 | 84 | 84 | 0 | 0 | -19.7344 | 333.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 14 | 24 | 5424 | 19.9 | 19.9 | 21.5625 | 17.8683 | 15 | 84 | 84 | 0 | 0 | -22.7648 | 348.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 1 | 5425 | 19 | 19 | 21.5625 | 17.8683 | 15 | 88 | 88 | 0 | 0 | -23.3562 | 4.2127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 2 | 5426 | 19.1 | 19.1 | 21.5625 | 17.8683 | 15 | 86 | 86 | 0 | 0 | -21.7324 | 19.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 3 | 5427 | 18.6 | 18.6 | 21.5625 | 17.8683 | 15 | 88 | 88 | 0 | 0 | -17.5054 | 34.6896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 4 | 5428 | 18.7 | 18.7 | 21.5625 | 17.8683 | 15 | 85 | 85 | 0 | 0 | -11.4014 | 48.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 5 | 5429 | 17.7 | 17.7 | 21.5625 | 17.8683 | 15 | 92 | 92 | 0 | 0 | -3.8966 | 60.9091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 6 | 5430 | 17.8 | 17.8 | 21.5625 | 17.8683 | 15 | 92 | 92 | 0 | 0 | 4.5621 | 72.7498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 7 | 5431 | 20.3 | 20.3 | 21.5625 | 17.8683 | 15 | 85 | 85 | 21.6839 | 68.1474 | 13.5772 | 84.3191 | 6.4099 | 19.1292 | 20.643 | 10.0643 | 0 | 0 | 0 | 0 | 3.8526 | 90.7216 | 214.656 | 229.4053 | 126.3294 | 28.2652 | 28.2652 | 28.2652 | 28.2652 | 68.1474 | 97.1315 | 233.7853 | 250.0482 | 136.3937 | 28.2652 | 28.2652 | 28.2652 | 28.2652 | 72 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 15 | 8 | 5432 | 22.6 | 22.6 | 21.5625 | 17.8683 | 15 | 78 | 78 | 185.1364 | 149.5709 | 22.775 | 96.1944 | 17.8141 | 139.2243 | 179.0788 | 114.0313 | 0 | 0 | 0 | 0 | 61.4291 | 87.0031 | 197.7362 | 234.0858 | 174.7587 | 70.7556 | 70.7556 | 70.7556 | 70.7556 | 149.5709 | 104.8173 | 336.9605 | 413.1645 | 288.7901 | 70.7556 | 70.7556 | 70.7556 | 70.7556 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 9 | 5433 | 24.8 | 24.8 | 21.5625 | 17.8683 | 15 | 74 | 74 | 390.4566 | 180.955 | 31.751 | 109.0961 | 0 | 225.6131 | 357.9116 | 280.5504 | 38.8466 | 0 | 0 | 0 | 186.045 | 101.5738 | 180.8069 | 227.2688 | 200.1003 | 115.2164 | 101.5738 | 101.5738 | 101.5738 | 180.955 | 101.5738 | 406.4199 | 585.1803 | 480.6507 | 154.0629 | 101.5738 | 101.5738 | 101.5738 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 10 | 5434 | 26.3 | 26.3 | 21.5625 | 17.8683 | 15 | 66 | 66 | 549.308 | 183.3976 | 39.9878 | 123.9337 | 0 | 204.0587 | 441.396 | 420.1695 | 152.8134 | 0 | 0 | 0 | 330.6024 | 115.6621 | 168.4761 | 229.9032 | 224.4094 | 155.2129 | 115.6621 | 115.6621 | 115.6621 | 183.3976 | 115.6621 | 372.5348 | 671.2992 | 644.5789 | 308.0264 | 115.6621 | 115.6621 | 115.6621 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 11 | 5435 | 28.1 | 28.1 | 21.5625 | 17.8683 | 15 | 63 | 63 | 657.3134 | 176.296 | 46.7494 | 141.7169 | 0 | 96.6678 | 417.847 | 494.257 | 281.138 | 0 | 0 | 0 | 459.704 | 122.89 | 141.8684 | 204.9241 | 219.9254 | 178.0846 | 122.89 | 122.89 | 122.89 | 176.296 | 122.89 | 238.5362 | 622.7711 | 714.1825 | 459.2227 | 122.89 | 122.89 | 122.89 | 636 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 12 | 5436 | 29.2 | 29.2 | 21.5625 | 17.8683 | 15 | 60 | 60 | 681.615 | 183.3781 | 51.0421 | 162.9458 | 0 | 0 | 289.3509 | 463.8302 | 366.604 | 54.6262 | 0 | 0 | 519.6219 | 130.0034 | 130.0034 | 186.4622 | 220.5069 | 201.536 | 140.6622 | 130.0034 | 130.0034 | 183.3781 | 130.0034 | 130.0034 | 475.8131 | 684.3371 | 568.14 | 195.2884 | 130.0034 | 130.0034 | 703 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 13 | 5437 | 30.2 | 30.2 | 21.5625 | 17.8683 | 15 | 52 | 52 | 666.6714 | 194.7249 | 51.9059 | 186.3541 | 0 | 0 | 122.9323 | 370.2906 | 400.7377 | 196.4381 | 0 | 0 | 524.2751 | 133.1753 | 133.1753 | 158.8235 | 210.4316 | 216.784 | 174.1595 | 133.1753 | 133.1753 | 194.7249 | 133.1753 | 133.1753 | 281.7558 | 580.7222 | 617.5217 | 370.5976 | 133.1753 | 133.1753 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 14 | 5438 | 30.5 | 30.5 | 21.5625 | 17.8683 | 15 | 57 | 57 | 487.4012 | 257.7549 | 49.1037 | 208.8903 | 0 | 0 | 0 | 187.7917 | 298.8574 | 234.8564 | 33.2798 | 0 | 375.2451 | 140.8089 | 140.8089 | 140.8089 | 212.5714 | 255.0139 | 230.5566 | 153.5264 | 140.8089 | 257.7549 | 140.8089 | 140.8089 | 140.8089 | 400.3631 | 553.8712 | 465.4131 | 186.8062 | 140.8089 | 633 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 15 | 5439 | 31.2 | 31.2 | 21.5625 | 17.8683 | 15 | 46 | 46 | 717.0475 | 160.0694 | 43.3475 | 228.2779 | 0 | 0 | 0 | 130.2601 | 411.0206 | 451.0108 | 226.805 | 0 | 511.9306 | 120.3403 | 120.3403 | 120.3403 | 142.3486 | 189.7851 | 196.5417 | 158.6606 | 120.3403 | 160.0694 | 120.3403 | 120.3403 | 120.3403 | 272.6088 | 600.8057 | 647.5525 | 385.4656 | 120.3403 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 16 | 5440 | 30.1 | 30.1 | 21.5625 | 17.8683 | 15 | 50 | 50 | 386.3513 | 237.5172 | 35.6835 | 244.357 | 0 | 0 | 0 | 0 | 186.9815 | 280.4968 | 209.7008 | 16.065 | 240.4828 | 123.8115 | 123.8115 | 123.8115 | 123.8115 | 206.7538 | 248.2358 | 216.8318 | 130.9377 | 237.5172 | 123.8115 | 123.8115 | 123.8115 | 123.8115 | 393.7353 | 528.7326 | 426.5326 | 147.0027 | 478 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 17 | 5441 | 31.4 | 31.4 | 21.5625 | 17.8683 | 15 | 49 | 49 | 602.2608 | 139.8552 | 26.9737 | 258.0277 | 0 | 0 | 0 | 0 | 211.7018 | 461.5344 | 441.0065 | 162.1429 | 302.1448 | 94.3495 | 94.3495 | 94.3495 | 94.3495 | 133.9303 | 180.6402 | 176.8022 | 124.6645 | 139.8552 | 94.3495 | 94.3495 | 94.3495 | 94.3495 | 345.6321 | 642.1747 | 617.8087 | 286.8075 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 15 | 18 | 5442 | 29.9 | 29.9 | 21.5625 | 17.8683 | 15 | 55 | 55 | 450.8195 | 126.7492 | 17.8234 | 270.2766 | 0 | 0 | 0 | 0 | 83.3439 | 336.8526 | 393.0377 | 218.9866 | 162.2508 | 76.5357 | 76.5357 | 76.5357 | 76.5357 | 97.6756 | 161.9772 | 176.2283 | 132.0809 | 126.7492 | 76.5357 | 76.5357 | 76.5357 | 76.5357 | 181.0195 | 498.8298 | 569.266 | 351.0674 | 289 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 19 | 5443 | 27.2 | 27.2 | 21.5625 | 17.8683 | 15 | 75 | 75 | 5.9441 | 59.7711 | 8.6773 | 281.908 | 0.027317 | 0 | 0 | 0 | 0 | 3.982 | 5.6587 | 4.0206 | 1.2289 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 59.7711 | 29.329 | 29.3017 | 29.3017 | 29.3017 | 29.3017 | 33.2837 | 34.9604 | 33.3223 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 20 | 5444 | 24.9 | 24.9 | 21.5625 | 17.8683 | 15 | 78 | 78 | 33.1571 | 24.0097 | -0.08528 | 293.5589 | 6.7633 | 0 | 0 | 0 | 0 | 17.896 | 32.0722 | 27.4609 | 6.9903 | 17.6365 | 13.4431 | 13.4431 | 13.4431 | 13.4431 | 24.539 | 33.3284 | 30.4693 | 24.0097 | 24.3999 | 13.4431 | 13.4431 | 13.4431 | 13.4431 | 42.435 | 65.4006 | 57.9302 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 21 | 5445 | 25.1 | 25.1 | 21.5625 | 17.8683 | 15 | 73 | 73 | 0 | 0 | -8.0828 | 305.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 22 | 5446 | 21.5 | 21.5 | 21.5625 | 17.8683 | 15 | 88 | 88 | 0 | 0 | -14.8921 | 318.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 23 | 5447 | 20.1 | 20.1 | 21.5625 | 17.8683 | 15 | 94 | 94 | 0 | 0 | -20.0439 | 333.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 15 | 24 | 5448 | 20.4 | 20.4 | 24.3625 | 19.6817 | 15 | 94 | 94 | 0 | 0 | -23.0779 | 348.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 1 | 5449 | 20.5 | 20.5 | 24.3625 | 19.6817 | 15 | 91 | 91 | 0 | 0 | -23.6641 | 4.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 2 | 5450 | 20.1 | 20.1 | 24.3625 | 19.6817 | 15 | 93 | 93 | 0 | 0 | -22.0291 | 20.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 3 | 5451 | 21.7 | 21.7 | 24.3625 | 19.6817 | 15 | 83 | 83 | 0 | 0 | -17.7819 | 34.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 4 | 5452 | 22.3 | 22.3 | 24.3625 | 19.6817 | 15 | 84 | 84 | 0 | 0 | -11.6565 | 48.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 5 | 5453 | 21.5 | 21.5 | 24.3625 | 19.6817 | 15 | 84 | 84 | 0 | 0 | -4.133 | 61.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 6 | 5454 | 20.8 | 20.8 | 24.3625 | 19.6817 | 15 | 86 | 86 | 0 | 0 | 4.3395 | 72.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 7 | 5455 | 19 | 19 | 24.3625 | 19.6817 | 15 | 95 | 95 | 0.14307 | 7.9752 | 13.362 | 84.5587 | 0.041767 | 0.12599 | 0.13641 | 0.066924 | 0 | 0 | 0 | 0 | 0.024818 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 7.9752 | 3.7955 | 3.8797 | 3.8902 | 3.8207 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 16 | 8 | 5456 | 20.6 | 20.6 | 24.3625 | 19.6817 | 15 | 90 | 90 | 48.566 | 140.0796 | 22.5595 | 96.4467 | 4.4807 | 36.4295 | 47.0384 | 30.0928 | 0 | 0 | 0 | 0 | 15.9204 | 75.0206 | 165.7508 | 195.8787 | 147.7556 | 62.296 | 62.296 | 62.296 | 62.296 | 140.0796 | 79.5012 | 202.1803 | 242.917 | 177.8484 | 62.296 | 62.296 | 62.296 | 62.296 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 9 | 5457 | 21.2 | 21.2 | 24.3625 | 19.6817 | 15 | 85 | 85 | 45.4953 | 200.4952 | 31.5264 | 109.3592 | 0 | 26.185 | 41.7484 | 32.8562 | 4.7173 | 0 | 0 | 0 | 21.5048 | 90.1713 | 158.1721 | 198.5894 | 175.4968 | 102.4217 | 90.1713 | 90.1713 | 90.1713 | 200.4952 | 90.1713 | 184.357 | 240.3378 | 208.353 | 107.139 | 90.1713 | 90.1713 | 90.1713 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 10 | 5458 | 20.4 | 20.4 | 24.3625 | 19.6817 | 15 | 89 | 89 | 1.7685 | 95.942 | 39.7442 | 124.1984 | 0 | 0.65234 | 1.4223 | 1.3591 | 0.49972 | 0 | 0 | 0 | 1.058 | 47.2376 | 47.2376 | 47.2376 | 47.2376 | 47.2376 | 47.2376 | 47.2376 | 47.2376 | 95.942 | 47.2376 | 47.89 | 48.6599 | 48.5967 | 47.7374 | 47.2376 | 47.2376 | 47.2376 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 11 | 5459 | 21.7 | 21.7 | 24.3625 | 19.6817 | 15 | 82 | 82 | 24.4968 | 271.9535 | 46.4782 | 141.9563 | 0 | 3.53 | 15.579 | 18.502 | 10.5868 | 0 | 0 | 0 | 17.0465 | 125.4365 | 134.2061 | 164.1397 | 171.4015 | 151.7376 | 125.4365 | 125.4365 | 125.4365 | 271.9535 | 125.4365 | 137.7361 | 179.7187 | 189.9035 | 162.3244 | 125.4365 | 125.4365 | 125.4365 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 12 | 5460 | 20.7 | 20.7 | 24.3625 | 19.6817 | 15 | 82 | 82 | 4.8128 | 199.3475 | 50.7419 | 163.1083 | 0 | 0 | 2.0424 | 3.2898 | 2.6101 | 0.4014 | 0 | 0 | 3.6525 | 99.5396 | 99.5396 | 102.1164 | 103.6901 | 102.8325 | 100.046 | 99.5396 | 99.5396 | 199.3475 | 99.5396 | 99.5396 | 104.1588 | 106.9799 | 105.4426 | 100.4474 | 99.5396 | 99.5396 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 13 | 5461 | 20.9 | 20.9 | 24.3625 | 19.6817 | 15 | 71 | 71 | 35.5135 | 322.1922 | 51.5895 | 186.3914 | 0 | 0 | 6.53 | 19.8229 | 21.5039 | 10.5882 | 0 | 0 | 27.8078 | 142.0206 | 142.0206 | 162.9872 | 205.6686 | 211.0658 | 176.0173 | 142.0206 | 142.0206 | 322.1922 | 142.0206 | 142.0206 | 169.5171 | 225.4915 | 232.5697 | 186.6055 | 142.0206 | 142.0206 | 350 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 14 | 5462 | 22.3 | 22.3 | 24.3625 | 19.6817 | 15 | 68 | 68 | 336.9523 | 308.7318 | 48.791 | 208.8099 | 0 | 0 | 0 | 130.6309 | 208.0443 | 163.5881 | 23.3043 | 0 | 258.2682 | 149.4079 | 149.4079 | 149.4079 | 226.1535 | 271.6339 | 245.5159 | 163.0992 | 149.4079 | 308.7318 | 149.4079 | 149.4079 | 149.4079 | 356.7845 | 479.6782 | 409.104 | 186.4034 | 149.4079 | 567 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 15 | 5463 | 22.5 | 22.5 | 24.3625 | 19.6817 | 15 | 60 | 60 | 389.4986 | 270.276 | 43.0493 | 228.1294 | 0 | 0 | 0 | 71.5478 | 224.8431 | 246.4284 | 123.6593 | 0 | 276.724 | 136.6358 | 136.6358 | 136.6358 | 171.5302 | 246.2933 | 256.8206 | 196.9453 | 136.6358 | 270.276 | 136.6358 | 136.6358 | 136.6358 | 243.0779 | 471.1364 | 503.249 | 320.6046 | 136.6358 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 16 | 5464 | 21.5 | 21.5 | 24.3625 | 19.6817 | 15 | 65 | 65 | 537.7444 | 192.2202 | 35.3998 | 244.1827 | 0 | 0 | 0 | 0 | 262.285 | 392.3797 | 292.6236 | 21.4526 | 332.7798 | 116.4531 | 116.4531 | 116.4531 | 116.4531 | 188.8843 | 224.8106 | 197.2625 | 122.3773 | 192.2202 | 116.4531 | 116.4531 | 116.4531 | 116.4531 | 451.1694 | 617.1903 | 489.8861 | 143.83 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 17 | 5465 | 20.9 | 20.9 | 24.3625 | 19.6817 | 15 | 59 | 59 | 750.0459 | 104.5369 | 26.6991 | 257.8497 | 0 | 0 | 0 | 0 | 266.2602 | 577.4384 | 550.361 | 200.8896 | 373.4631 | 88.9989 | 88.9989 | 88.9989 | 88.9989 | 114.6304 | 144.586 | 141.9794 | 108.3375 | 104.5369 | 88.9989 | 88.9989 | 88.9989 | 88.9989 | 380.8906 | 722.0244 | 692.3405 | 309.2272 | 478 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 16 | 18 | 5466 | 21 | 21 | 24.3625 | 19.6817 | 15 | 59 | 59 | 751.4799 | 74.5135 | 17.5517 | 270.1047 | 0 | 0 | 0 | 0 | 141.3043 | 564.0033 | 656.3168 | 364.1688 | 267.4865 | 66.1232 | 66.1232 | 66.1232 | 66.1232 | 77.7981 | 112.7224 | 120.3496 | 96.2116 | 74.5135 | 66.1232 | 66.1232 | 66.1232 | 66.1232 | 219.1024 | 676.7258 | 776.6664 | 460.3805 | 342 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 19 | 5467 | 20.4 | 20.4 | 24.3625 | 19.6817 | 15 | 62 | 62 | 407.5748 | 75.4313 | 8.4028 | 281.7472 | 0.71045 | 0 | 0 | 0 | 0 | 274.279 | 388.5995 | 275.2837 | 82.5687 | 46.6121 | 46.4572 | 46.4572 | 46.4572 | 46.4572 | 106.266 | 131.1946 | 106.4851 | 75.4313 | 47.3226 | 46.4572 | 46.4572 | 46.4572 | 46.4572 | 380.545 | 519.7941 | 381.7688 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 20 | 5468 | 18.4 | 18.4 | 24.3625 | 19.6817 | 15 | 69 | 69 | 48.2127 | 9.57 | -0.36718 | 293.4134 | 9.7105 | 0 | 0 | 0 | 0 | 26.1528 | 46.6962 | 39.8855 | 48.43 | 15.3335 | 10.2478 | 10.2478 | 10.2478 | 10.2478 | 23.9448 | 34.7039 | 31.1369 | 9.57 | 25.0439 | 10.2478 | 10.2478 | 10.2478 | 10.2478 | 50.0976 | 81.4 | 71.0224 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 21 | 5469 | 16.7 | 16.7 | 24.3625 | 19.6817 | 15 | 77 | 77 | 0 | 0 | -8.3754 | 305.6224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 22 | 5470 | 14.5 | 14.5 | 24.3625 | 19.6817 | 15 | 86 | 86 | 0 | 0 | -15.1963 | 318.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 23 | 5471 | 12.6 | 12.6 | 24.3625 | 19.6817 | 15 | 93 | 93 | 0 | 0 | -20.3576 | 333.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 16 | 24 | 5472 | 12.4 | 12.4 | 19.775 | 19.9443 | 15 | 96 | 96 | 0 | 0 | -23.3951 | 348.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 1 | 5473 | 13.5 | 13.5 | 19.775 | 19.9443 | 15 | 91 | 91 | 0 | 0 | -23.9755 | 4.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 2 | 5474 | 13.4 | 13.4 | 19.775 | 19.9443 | 15 | 91 | 91 | 0 | 0 | -22.3288 | 20.1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 3 | 5475 | 11.7 | 11.7 | 19.775 | 19.9443 | 15 | 95 | 95 | 0 | 0 | -18.0607 | 35.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 4 | 5476 | 11.5 | 11.5 | 19.775 | 19.9443 | 15 | 97 | 97 | 0 | 0 | -11.9136 | 48.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 5 | 5477 | 11.3 | 11.3 | 19.775 | 19.9443 | 15 | 96 | 96 | 0 | 0 | -4.371 | 61.3374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 6 | 5478 | 11.8 | 11.8 | 19.775 | 19.9443 | 15 | 97 | 97 | 0 | 0 | 4.1154 | 73.2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 7 | 5479 | 14.6 | 14.6 | 19.775 | 19.9443 | 15 | 89 | 89 | 22.3026 | 65.2263 | 13.1451 | 84.8021 | 6.4269 | 19.6034 | 21.2965 | 10.5144 | 0 | 0 | 0 | 0 | 3.7737 | 87.3225 | 211.5651 | 227.5295 | 125.8639 | 26.7225 | 26.7225 | 26.7225 | 26.7225 | 65.2263 | 93.7494 | 231.1685 | 248.8259 | 136.3782 | 26.7225 | 26.7225 | 26.7225 | 26.7225 | 69 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 17 | 8 | 5480 | 16 | 16 | 19.775 | 19.9443 | 15 | 83 | 83 | 251.4648 | 140.5863 | 22.3422 | 96.7026 | 22.1849 | 188.1283 | 243.8687 | 156.7541 | 0 | 0 | 0 | 0 | 81.4137 | 82.9689 | 160.1539 | 186.0803 | 145.5609 | 72.6501 | 72.6501 | 72.6501 | 72.6501 | 140.5863 | 105.1537 | 348.2821 | 429.949 | 302.315 | 72.6501 | 72.6501 | 72.6501 | 72.6501 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 9 | 5481 | 18.1 | 18.1 | 19.775 | 19.9443 | 15 | 81 | 81 | 476.4216 | 159.6425 | 31.2997 | 109.6258 | 0 | 273.0942 | 437.645 | 345.8293 | 51.4315 | 0 | 0 | 0 | 223.3575 | 96.163 | 168.5639 | 212.1886 | 187.847 | 109.7982 | 96.163 | 96.163 | 96.163 | 159.6425 | 96.163 | 441.6581 | 649.8335 | 533.6763 | 161.2297 | 96.163 | 96.163 | 96.163 | 383 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 10 | 5482 | 19.6 | 19.6 | 19.775 | 19.9443 | 15 | 75 | 75 | 660.7361 | 149.172 | 39.4981 | 124.4664 | 0 | 241.9361 | 531.7755 | 510.108 | 189.6261 | 0 | 0 | 0 | 392.828 | 107.2049 | 150.1289 | 201.5518 | 197.7076 | 140.8481 | 107.2049 | 107.2049 | 107.2049 | 149.172 | 107.2049 | 392.065 | 733.3274 | 707.8156 | 330.4743 | 107.2049 | 107.2049 | 107.2049 | 542 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 11 | 5483 | 20.4 | 20.4 | 19.775 | 19.9443 | 15 | 67 | 67 | 360.988 | 272.086 | 46.204 | 142.1986 | 0 | 50.9233 | 229.6569 | 273.8606 | 157.6405 | 0 | 0 | 0 | 249.914 | 140.4159 | 165.3866 | 253.0302 | 274.7059 | 217.7163 | 140.4159 | 140.4159 | 140.4159 | 272.086 | 140.4159 | 216.3099 | 482.6871 | 548.5665 | 375.3568 | 140.4159 | 140.4159 | 140.4159 | 522 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 12 | 5484 | 21.4 | 21.4 | 19.775 | 19.9443 | 15 | 61 | 61 | 735.1724 | 163.6196 | 50.4383 | 163.2735 | 0 | 0 | 311.8611 | 504.7967 | 402.0292 | 63.7585 | 0 | 0 | 555.3804 | 126.7104 | 126.7104 | 178.9777 | 211.3133 | 194.0897 | 137.3962 | 126.7104 | 126.7104 | 163.6196 | 126.7104 | 126.7104 | 490.8388 | 716.11 | 596.1189 | 201.1546 | 126.7104 | 126.7104 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 13 | 5485 | 21.8 | 21.8 | 19.775 | 19.9443 | 15 | 58 | 58 | 523.8673 | 247.6071 | 51.2693 | 186.4316 | 0 | 0 | 96.0272 | 293.8494 | 319.5386 | 158.0464 | 0 | 0 | 408.3929 | 141.3236 | 141.3236 | 174.3688 | 242.444 | 251.2842 | 195.711 | 141.3236 | 141.3236 | 247.6071 | 141.3236 | 141.3236 | 270.3959 | 536.2933 | 570.8228 | 353.7575 | 141.3236 | 141.3236 | 656 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 14 | 5486 | 22.7 | 22.7 | 19.775 | 19.9443 | 15 | 56 | 56 | 473.0765 | 261.0364 | 48.4739 | 208.7323 | 0 | 0 | 0 | 184.5316 | 294.1225 | 231.4203 | 33.1553 | 0 | 360.9636 | 140.8084 | 140.8084 | 140.8084 | 213.9454 | 257.3804 | 232.5291 | 153.9492 | 140.8084 | 261.0364 | 140.8084 | 140.8084 | 140.8084 | 398.477 | 551.5028 | 463.9495 | 187.1045 | 140.8084 | 622 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 15 | 5487 | 22.9 | 22.9 | 19.775 | 19.9443 | 15 | 53 | 53 | 760.3012 | 145.5281 | 42.7466 | 227.9829 | 0 | 0 | 0 | 141.1974 | 441.9891 | 483.8697 | 242.3059 | 0 | 537.4719 | 118.6813 | 118.6813 | 118.6813 | 134.7244 | 168.901 | 173.6596 | 146.2126 | 118.6813 | 145.5281 | 118.6813 | 118.6813 | 118.6813 | 275.9218 | 610.8902 | 657.5293 | 388.5185 | 118.6813 | 683 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 16 | 5488 | 22.3 | 22.3 | 19.775 | 19.9443 | 15 | 52 | 52 | 65.1743 | 270.906 | 35.1114 | 244.0094 | 0 | 0 | 0 | 0 | 32.0363 | 47.7967 | 35.5585 | 2.4906 | 40.094 | 123.8894 | 123.8894 | 123.8894 | 123.8894 | 171.408 | 194.7851 | 176.6324 | 127.5836 | 270.906 | 123.8894 | 123.8894 | 123.8894 | 123.8894 | 203.4442 | 242.5818 | 212.1909 | 130.0742 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 17 | 5489 | 23.7 | 23.7 | 19.775 | 19.9443 | 15 | 49 | 49 | 779.3443 | 97.9282 | 26.4199 | 257.6722 | 0 | 0 | 0 | 0 | 279.381 | 602.7634 | 573.0552 | 207.659 | 385.0718 | 87.4267 | 87.4267 | 87.4267 | 87.4267 | 112.2022 | 140.8797 | 138.2452 | 105.8419 | 97.9282 | 87.4267 | 87.4267 | 87.4267 | 87.4267 | 391.5831 | 743.6431 | 711.3004 | 313.5009 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 17 | 18 | 5490 | 22.3 | 22.3 | 19.775 | 19.9443 | 15 | 55 | 55 | 650.7073 | 89.9943 | 17.2755 | 269.933 | 0 | 0 | 0 | 0 | 124.4188 | 490.5393 | 569.3086 | 314.5846 | 229.0057 | 67.4444 | 67.4444 | 67.4444 | 67.4444 | 84.4996 | 134.6871 | 145.4847 | 110.5673 | 89.9943 | 67.4444 | 67.4444 | 67.4444 | 67.4444 | 208.9183 | 625.2264 | 714.7933 | 425.152 | 319 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 19 | 5491 | 21.4 | 21.4 | 19.775 | 19.9443 | 15 | 58 | 58 | 466.2868 | 68.5041 | 8.1239 | 281.5863 | 0 | 0 | 0 | 0 | 0.52104 | 315.2086 | 445.2512 | 314.4717 | 92.4959 | 44.2169 | 44.2169 | 44.2169 | 44.2169 | 44.311 | 101.136 | 124.6185 | 101.0029 | 68.5041 | 44.2169 | 44.2169 | 44.2169 | 44.2169 | 44.832 | 416.3445 | 569.8697 | 415.4746 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 20 | 5492 | 19.5 | 19.5 | 19.775 | 19.9443 | 15 | 71 | 71 | 44.5164 | 14.7568 | -0.65346 | 293.2678 | 8.8511 | 0 | 0 | 0 | 0 | 24.2683 | 43.1716 | 36.7856 | 21.2432 | 16.5251 | 10.2682 | 10.2682 | 10.2682 | 10.2682 | 27.4237 | 40.7866 | 36.2723 | 14.7568 | 25.3762 | 10.2682 | 10.2682 | 10.2682 | 10.2682 | 51.692 | 83.9583 | 73.0579 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 21 | 5493 | 18.2 | 18.2 | 19.775 | 19.9443 | 15 | 78 | 78 | 0 | 0 | -8.6723 | 305.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 22 | 5494 | 17.2 | 17.2 | 19.775 | 19.9443 | 15 | 78 | 78 | 0 | 0 | -15.5049 | 318.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 23 | 5495 | 16.4 | 16.4 | 19.775 | 19.9443 | 15 | 83 | 83 | 0 | 0 | -20.6756 | 333.0378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 17 | 24 | 5496 | 15.8 | 15.8 | 17.8125 | 19.6305 | 15 | 87 | 87 | 0 | 0 | -23.7162 | 348.4506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 1 | 5497 | 15.3 | 15.3 | 17.8125 | 19.6305 | 15 | 88 | 88 | 0 | 0 | -24.2905 | 4.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 2 | 5498 | 15.9 | 15.9 | 17.8125 | 19.6305 | 15 | 85 | 85 | 0 | 0 | -22.6314 | 20.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 3 | 5499 | 16 | 16 | 17.8125 | 19.6305 | 15 | 83 | 83 | 0 | 0 | -18.3419 | 35.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 4 | 5500 | 15.7 | 15.7 | 17.8125 | 19.6305 | 15 | 83 | 83 | 0 | 0 | -12.1725 | 48.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 5 | 5501 | 15.7 | 15.7 | 17.8125 | 19.6305 | 15 | 80 | 80 | 0 | 0 | -4.6106 | 61.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 6 | 5502 | 16.5 | 16.5 | 17.8125 | 19.6305 | 15 | 74 | 74 | 0 | 0 | 3.8897 | 73.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 7 | 5503 | 16.5 | 16.5 | 17.8125 | 19.6305 | 15 | 76 | 76 | 0.088988 | 5.9853 | 12.9267 | 85.0493 | 0.025302 | 0.078067 | 0.085102 | 0.042284 | 0 | 0 | 0 | 0 | 0.014674 | 2.802 | 2.802 | 2.802 | 2.802 | 2.802 | 2.802 | 2.802 | 2.802 | 5.9853 | 2.8273 | 2.8801 | 2.8871 | 2.8443 | 2.802 | 2.802 | 2.802 | 2.802 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 18 | 8 | 5504 | 16.4 | 16.4 | 17.8125 | 19.6305 | 15 | 78 | 78 | 0.85249 | 35.7275 | 22.1232 | 96.9621 | 0.071705 | 0.63604 | 0.82779 | 0.53463 | 0 | 0 | 0 | 0 | 0.2725 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 35.7275 | 17.3065 | 17.8709 | 18.0626 | 17.7695 | 17.2348 | 17.2348 | 17.2348 | 17.2348 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 9 | 5505 | 16.6 | 16.6 | 17.8125 | 19.6305 | 15 | 89 | 89 | 3.8313 | 109.2188 | 31.071 | 109.8958 | 0 | 2.187 | 3.5231 | 2.7954 | 0.43022 | 0 | 0 | 0 | 1.7812 | 53.3633 | 58.4483 | 61.5549 | 59.8629 | 54.3636 | 53.3633 | 53.3633 | 53.3633 | 109.2188 | 53.3633 | 60.6353 | 65.0779 | 62.6583 | 54.7938 | 53.3633 | 53.3633 | 53.3633 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 10 | 5506 | 17.7 | 17.7 | 17.8125 | 19.6305 | 15 | 90 | 90 | 3.3047 | 129.0477 | 39.2496 | 124.7375 | 0 | 1.2009 | 2.6616 | 2.5632 | 0.96326 | 0 | 0 | 0 | 1.9523 | 64.7206 | 64.7206 | 64.7206 | 64.7206 | 64.7206 | 64.7206 | 64.7206 | 64.7206 | 129.0477 | 64.7206 | 65.9215 | 67.3822 | 67.2837 | 65.6838 | 64.7206 | 64.7206 | 64.7206 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 11 | 5507 | 20.7 | 20.7 | 17.8125 | 19.6305 | 15 | 82 | 82 | 96.0485 | 311.8532 | 45.9269 | 142.4437 | 0 | 13.2514 | 61.1231 | 73.1897 | 42.3828 | 0 | 0 | 0 | 66.1468 | 140.3929 | 158.5791 | 224.2787 | 240.839 | 198.5594 | 140.3929 | 140.3929 | 140.3929 | 311.8532 | 140.3929 | 171.8305 | 285.4017 | 314.0287 | 240.9422 | 140.3929 | 140.3929 | 140.3929 | 378 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 12 | 5508 | 22 | 22 | 17.8125 | 19.6305 | 15 | 76 | 76 | 211.2497 | 335.1614 | 50.1314 | 163.4412 | 0 | 0 | 89.566 | 145.7017 | 116.4873 | 19.0363 | 0 | 0 | 158.8386 | 155.8729 | 155.8729 | 228.9812 | 274.802 | 250.9558 | 171.4113 | 155.8729 | 155.8729 | 335.1614 | 155.8729 | 155.8729 | 318.5472 | 420.5037 | 367.4431 | 190.4475 | 155.8729 | 155.8729 | 494 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 13 | 5509 | 22.2 | 22.2 | 17.8125 | 19.6305 | 15 | 77 | 77 | 586.3819 | 222.9316 | 50.9454 | 186.4746 | 0 | 0 | 107.1274 | 330.5205 | 360.2991 | 179.0194 | 0 | 0 | 455.0684 | 135.6964 | 135.6964 | 163.3242 | 220.9363 | 228.6161 | 181.8648 | 135.6964 | 135.6964 | 222.9316 | 135.6964 | 135.6964 | 270.4516 | 551.4568 | 588.9152 | 360.8842 | 135.6964 | 135.6964 | 678 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 14 | 5510 | 23.5 | 23.5 | 17.8125 | 19.6305 | 15 | 71 | 71 | 631.371 | 201.4859 | 48.1527 | 208.6574 | 0 | 0 | 0 | 247.7759 | 395.2652 | 311.2135 | 44.8572 | 0 | 479.5141 | 130.9997 | 130.9997 | 130.9997 | 186.8429 | 220.0838 | 201.1404 | 141.1095 | 130.9997 | 201.4859 | 130.9997 | 130.9997 | 130.9997 | 434.6188 | 615.349 | 512.3539 | 185.9667 | 130.9997 | 681 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 15 | 5511 | 24.2 | 24.2 | 17.8125 | 19.6305 | 15 | 67 | 67 | 713.212 | 159.3871 | 42.4394 | 227.8384 | 0 | 0 | 0 | 133.8858 | 417.5317 | 456.5932 | 228.1886 | 0 | 501.6129 | 119.3164 | 119.3164 | 119.3164 | 142.0051 | 190.0728 | 196.6923 | 157.986 | 119.3164 | 159.3871 | 119.3164 | 119.3164 | 119.3164 | 275.8909 | 607.6045 | 653.2855 | 386.1746 | 119.3164 | 661 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 16 | 5512 | 24.2 | 24.2 | 17.8125 | 19.6305 | 15 | 69 | 69 | 731.9623 | 133.436 | 34.8185 | 243.8373 | 0 | 0 | 0 | 0 | 362.5833 | 539.5191 | 400.412 | 26.7489 | 447.564 | 105.3453 | 105.3453 | 105.3453 | 105.3453 | 158.4311 | 184.3362 | 163.9696 | 109.2616 | 133.436 | 105.3453 | 105.3453 | 105.3453 | 105.3453 | 521.0144 | 723.8554 | 564.3815 | 136.0105 | 581 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 17 | 5513 | 24.4 | 24.4 | 17.8125 | 19.6305 | 15 | 70 | 70 | 474.1082 | 167.5849 | 26.1363 | 257.4951 | 0 | 0 | 0 | 0 | 171.6181 | 368.3788 | 349.3482 | 125.6741 | 232.4151 | 99.0618 | 99.0618 | 99.0618 | 99.0618 | 147.9415 | 203.9822 | 198.562 | 134.8559 | 167.5849 | 99.0618 | 99.0618 | 99.0618 | 99.0618 | 319.5596 | 572.361 | 547.9101 | 260.53 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 18 | 5514 | 24.6 | 24.6 | 17.8125 | 19.6305 | 15 | 71 | 71 | 394.7208 | 131.6906 | 16.9949 | 269.7612 | 0 | 0 | 0 | 0 | 76.7269 | 298.8805 | 345.9539 | 190.3722 | 137.3094 | 76.2236 | 76.2236 | 76.2236 | 76.2236 | 99.0533 | 165.154 | 179.1605 | 132.8679 | 131.6906 | 76.2236 | 76.2236 | 76.2236 | 76.2236 | 175.7802 | 464.0345 | 525.1144 | 323.2401 | 269 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 19 | 5515 | 23.4 | 23.4 | 17.8125 | 19.6305 | 15 | 77 | 77 | 71.2782 | 86.1653 | 7.8407 | 281.4252 | 0 | 0 | 0 | 0 | 0.28406 | 48.4007 | 68.1649 | 47.999 | 13.8347 | 43.8068 | 43.8068 | 43.8068 | 43.8068 | 44.0409 | 83.6907 | 99.9771 | 83.3597 | 86.1653 | 43.8068 | 43.8068 | 43.8068 | 43.8068 | 44.3249 | 132.0914 | 168.142 | 131.3587 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 20 | 5516 | 22.4 | 22.4 | 17.8125 | 19.6305 | 15 | 82 | 82 | 51.9311 | 16.9559 | -0.94403 | 293.1221 | 10.1908 | 0 | 0 | 0 | 0 | 28.4507 | 50.4261 | 42.8626 | 2.0441 | 16.6966 | 9.5227 | 9.5227 | 9.5227 | 9.5227 | 29.5509 | 45.0207 | 39.6963 | 16.9559 | 26.8873 | 9.5227 | 9.5227 | 9.5227 | 9.5227 | 58.0015 | 95.4468 | 82.5589 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 21 | 5517 | 22.1 | 22.1 | 17.8125 | 19.6305 | 15 | 84 | 84 | 0 | 0 | -8.9734 | 305.3746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 22 | 5518 | 21.4 | 21.4 | 17.8125 | 19.6305 | 15 | 84 | 84 | 0 | 0 | -15.8176 | 318.5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 23 | 5519 | 20.4 | 20.4 | 17.8125 | 19.6305 | 15 | 87 | 87 | 0 | 0 | -20.9977 | 332.9905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 18 | 24 | 5520 | 19.2 | 19.2 | 19.875 | 19.9089 | 15 | 93 | 93 | 0 | 0 | -24.0412 | 348.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 1 | 5521 | 17.2 | 17.2 | 19.875 | 19.9089 | 15 | 98 | 98 | 0 | 0 | -24.6089 | 4.4819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 2 | 5522 | 17.9 | 17.9 | 19.875 | 19.9089 | 15 | 98 | 98 | 0 | 0 | -22.9368 | 20.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 3 | 5523 | 19.5 | 19.5 | 19.875 | 19.9089 | 15 | 89 | 89 | 0 | 0 | -18.6253 | 35.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 4 | 5524 | 18.9 | 18.9 | 19.875 | 19.9089 | 15 | 92 | 92 | 0 | 0 | -12.4332 | 49.1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 5 | 5525 | 19.1 | 19.1 | 19.875 | 19.9089 | 15 | 91 | 91 | 0 | 0 | -4.8518 | 61.7821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 6 | 5526 | 18.2 | 18.2 | 19.875 | 19.9089 | 15 | 90 | 90 | 0 | 0 | 3.6627 | 73.6802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 7 | 5527 | 18.6 | 18.6 | 19.875 | 19.9089 | 15 | 89 | 89 | 1.2618 | 21.7974 | 12.7069 | 85.3001 | 0.35384 | 1.1047 | 1.2085 | 0.60433 | 0 | 0 | 0 | 0 | 0.20255 | 12.9459 | 18.1872 | 18.9115 | 14.6943 | 10.476 | 10.476 | 10.476 | 10.476 | 21.7974 | 13.2997 | 19.292 | 20.12 | 15.2986 | 10.476 | 10.476 | 10.476 | 10.476 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 19 | 8 | 5528 | 19.6 | 19.6 | 19.875 | 19.9089 | 15 | 84 | 84 | 17.0569 | 116.6187 | 21.9026 | 97.2252 | 1.3634 | 12.6901 | 16.5832 | 10.7621 | 0 | 0 | 0 | 0 | 5.3813 | 58.9302 | 136.1028 | 162.6274 | 122.9663 | 49.6413 | 49.6413 | 49.6413 | 49.6413 | 116.6187 | 60.2936 | 148.7929 | 179.2106 | 133.7284 | 49.6413 | 49.6413 | 49.6413 | 49.6413 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 9 | 5529 | 20.1 | 20.1 | 19.875 | 19.9089 | 15 | 82 | 82 | 32.7892 | 187.8864 | 30.8403 | 110.1691 | 0 | 18.6356 | 30.1809 | 24.0466 | 3.8262 | 0 | 0 | 0 | 15.1136 | 82.1974 | 140.2367 | 176.1939 | 157.0892 | 94.1139 | 82.1974 | 82.1974 | 82.1974 | 187.8864 | 82.1974 | 158.8723 | 206.3748 | 181.1359 | 97.9402 | 82.1974 | 82.1974 | 82.1974 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 10 | 5530 | 20.8 | 20.8 | 19.875 | 19.9089 | 15 | 74 | 74 | 187.7822 | 264.7778 | 38.9987 | 125.0116 | 0 | 67.707 | 151.3429 | 146.3242 | 55.5907 | 0 | 0 | 0 | 110.2222 | 124.7879 | 183.3087 | 255.5974 | 251.2596 | 172.8363 | 124.7879 | 124.7879 | 124.7879 | 264.7778 | 124.7879 | 251.0157 | 406.9403 | 397.5837 | 228.4271 | 124.7879 | 124.7879 | 124.7879 | 375 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 11 | 5531 | 21.7 | 21.7 | 19.875 | 19.9089 | 15 | 67 | 67 | 184.8593 | 309.3721 | 45.647 | 142.6913 | 0 | 24.9186 | 117.6671 | 141.4877 | 82.4268 | 0 | 0 | 0 | 126.6279 | 143.4551 | 166.2983 | 251.322 | 273.1587 | 219.0168 | 143.4551 | 143.4551 | 143.4551 | 309.3721 | 143.4551 | 191.217 | 368.989 | 414.6464 | 301.4436 | 143.4551 | 143.4551 | 143.4551 | 436 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 12 | 5532 | 21.1 | 21.1 | 19.875 | 19.9089 | 15 | 68 | 68 | 15.3003 | 271.5508 | 49.8212 | 163.6114 | 0 | 0 | 6.483 | 10.5999 | 8.5075 | 1.4315 | 0 | 0 | 11.4492 | 128.5136 | 128.5136 | 145.6519 | 156.5351 | 151.0037 | 132.2979 | 128.5136 | 128.5136 | 271.5508 | 128.5136 | 128.5136 | 152.1349 | 167.135 | 159.5112 | 133.7294 | 128.5136 | 128.5136 | 283 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 13 | 5533 | 21.8 | 21.8 | 19.875 | 19.9089 | 15 | 65 | 65 | 175.9731 | 350.0631 | 50.6178 | 186.5203 | 0 | 0 | 32.0335 | 99.6695 | 108.9205 | 54.3673 | 0 | 0 | 135.9369 | 158.4386 | 158.4386 | 190.544 | 258.3318 | 267.6034 | 212.9279 | 158.4386 | 158.4386 | 350.0631 | 158.4386 | 158.4386 | 222.5776 | 358.0013 | 376.5239 | 267.2951 | 158.4386 | 158.4386 | 486 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 14 | 5534 | 21.9 | 21.9 | 19.875 | 19.9089 | 15 | 65 | 65 | 26.4292 | 299.0225 | 47.8274 | 208.5852 | 0 | 0 | 0 | 10.4344 | 16.6607 | 13.1273 | 1.9042 | 0 | 19.9775 | 132.8492 | 132.8492 | 132.8492 | 172.884 | 196.773 | 183.2164 | 140.1553 | 132.8492 | 299.0225 | 132.8492 | 132.8492 | 132.8492 | 183.3183 | 213.4337 | 196.3437 | 142.0595 | 132.8492 | 319 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 15 | 5535 | 23.3 | 23.3 | 19.875 | 19.9089 | 15 | 60 | 60 | 433.4857 | 252.712 | 42.1279 | 227.6958 | 0 | 0 | 0 | 82.2414 | 255.5535 | 279.1659 | 139.2467 | 0 | 303.288 | 133.7287 | 133.7287 | 133.7287 | 168.1148 | 240.5788 | 250.4514 | 191.9495 | 133.7287 | 252.712 | 133.7287 | 133.7287 | 133.7287 | 250.3562 | 496.1323 | 529.6174 | 331.1962 | 133.7287 | 556 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 16 | 5536 | 23.4 | 23.4 | 19.875 | 19.9089 | 15 | 62 | 62 | 376.9431 | 234.9413 | 34.5212 | 243.6664 | 0 | 0 | 0 | 0 | 188.1622 | 279.2503 | 206.7573 | 13.1488 | 229.0587 | 122.191 | 122.191 | 122.191 | 122.191 | 206.864 | 247.8536 | 215.2318 | 128.108 | 234.9413 | 122.191 | 122.191 | 122.191 | 122.191 | 395.0261 | 527.1038 | 421.9891 | 141.2567 | 464 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 17 | 5537 | 20.9 | 20.9 | 19.875 | 19.9089 | 15 | 72 | 72 | 209.6538 | 217.0504 | 25.8482 | 257.3186 | 0 | 0 | 0 | 0 | 76.6257 | 163.6509 | 154.8116 | 55.2858 | 101.9496 | 107.8907 | 107.8907 | 107.8907 | 107.8907 | 149.709 | 197.2028 | 192.3788 | 138.0628 | 217.0504 | 107.8907 | 107.8907 | 107.8907 | 107.8907 | 226.3347 | 360.8537 | 347.1904 | 193.3485 | 319 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 18 | 5538 | 22 | 22 | 19.875 | 19.9089 | 15 | 65 | 65 | 663.3316 | 85.9861 | 16.71 | 269.5896 | 0 | 0 | 0 | 0 | 131.0518 | 504.4897 | 582.4044 | 319.1545 | 228.0139 | 65.6324 | 65.6324 | 65.6324 | 65.6324 | 82.8298 | 131.8347 | 142.0592 | 107.5139 | 85.9861 | 65.6324 | 65.6324 | 65.6324 | 65.6324 | 213.8816 | 636.3244 | 724.4636 | 426.6684 | 314 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 19 | 5539 | 21.7 | 21.7 | 19.875 | 19.9089 | 15 | 66 | 66 | 273.3913 | 81.1185 | 7.5532 | 281.264 | 0 | 0 | 0 | 0 | 1.8754 | 186.4749 | 261.8399 | 183.8227 | 51.8815 | 45.9833 | 45.9833 | 45.9833 | 45.9833 | 46.6268 | 109.9612 | 135.8183 | 109.0513 | 81.1185 | 45.9833 | 45.9833 | 45.9833 | 45.9833 | 48.5021 | 296.4361 | 397.6583 | 292.874 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 20 | 5540 | 20.4 | 20.4 | 19.875 | 19.9089 | 15 | 73 | 73 | 54.7145 | 15.0941 | -1.2388 | 292.9761 | 10.5947 | 0 | 0 | 0 | 0 | 30.1229 | 53.195 | 45.1061 | 1.9059 | 15.0769 | 8.5188 | 8.5188 | 8.5188 | 8.5188 | 27.1647 | 41.4461 | 36.4391 | 15.0941 | 25.6715 | 8.5188 | 8.5188 | 8.5188 | 8.5188 | 57.2876 | 94.6411 | 81.5452 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 21 | 5541 | 17.9 | 17.9 | 19.875 | 19.9089 | 15 | 85 | 85 | 0 | 0 | -9.2787 | 305.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 22 | 5542 | 17.8 | 17.8 | 19.875 | 19.9089 | 15 | 83 | 83 | 0 | 0 | -16.1345 | 318.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 23 | 5543 | 17.7 | 17.7 | 19.875 | 19.9089 | 15 | 82 | 82 | 0 | 0 | -21.3237 | 332.9443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 19 | 24 | 5544 | 17 | 17 | 19.9375 | 20.0946 | 15 | 86 | 86 | 0 | 0 | -24.3699 | 348.4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 1 | 5545 | 16.8 | 16.8 | 19.9375 | 20.0946 | 15 | 88 | 88 | 0 | 0 | -24.9306 | 4.5571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 2 | 5546 | 16.2 | 16.2 | 19.9375 | 20.0946 | 15 | 90 | 90 | 0 | 0 | -23.2448 | 20.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 3 | 5547 | 16.9 | 16.9 | 19.9375 | 20.0946 | 15 | 87 | 87 | 0 | 0 | -18.9109 | 35.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 4 | 5548 | 16 | 16 | 19.9375 | 20.0946 | 15 | 90 | 90 | 0 | 0 | -12.6956 | 49.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 5 | 5549 | 15.4 | 15.4 | 19.9375 | 20.0946 | 15 | 92 | 92 | 0 | 0 | -5.0944 | 62.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 6 | 5550 | 15.4 | 15.4 | 19.9375 | 20.0946 | 15 | 93 | 93 | 0 | 0 | 3.4343 | 73.9224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 7 | 5551 | 15.8 | 15.8 | 19.9375 | 20.0946 | 15 | 91 | 91 | 0.79631 | 16.8757 | 12.4857 | 85.5546 | 0.22013 | 0.69573 | 0.76379 | 0.38442 | 0 | 0 | 0 | 0 | 0.12431 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 16.8757 | 8.4966 | 8.9722 | 9.0403 | 8.6609 | 8.2765 | 8.2765 | 8.2765 | 8.2765 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 20 | 8 | 5552 | 16.3 | 16.3 | 19.9375 | 20.0946 | 15 | 91 | 91 | 0.89823 | 35.7204 | 21.6803 | 97.4917 | 0.067975 | 0.66632 | 0.87435 | 0.57019 | 0 | 0 | 0 | 0 | 0.27959 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 35.7204 | 17.3196 | 17.9179 | 18.126 | 17.8218 | 17.2516 | 17.2516 | 17.2516 | 17.2516 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 9 | 5553 | 17.6 | 17.6 | 19.9375 | 20.0946 | 15 | 89 | 89 | 4.5552 | 116.9187 | 30.6077 | 110.4456 | 0 | 2.5774 | 4.1968 | 3.3579 | 0.5519 | 0 | 0 | 0 | 2.0813 | 56.3056 | 65.5714 | 71.3935 | 68.3774 | 58.2897 | 56.3056 | 56.3056 | 56.3056 | 116.9187 | 56.3056 | 68.1487 | 75.5904 | 71.7352 | 58.8416 | 56.3056 | 56.3056 | 56.3056 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 10 | 5554 | 20.1 | 20.1 | 19.9375 | 20.0946 | 15 | 76 | 76 | 266.1437 | 250.8119 | 38.7454 | 125.2885 | 0 | 95.1886 | 214.633 | 208.3482 | 80.0159 | 0 | 0 | 0 | 155.1881 | 124.5322 | 178.6981 | 246.6664 | 243.0901 | 170.0643 | 124.5322 | 124.5322 | 124.5322 | 250.8119 | 124.5322 | 273.8867 | 461.2993 | 451.4383 | 250.0802 | 124.5322 | 124.5322 | 124.5322 | 406 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 11 | 5555 | 20.2 | 20.2 | 19.9375 | 20.0946 | 15 | 79 | 79 | 31.096 | 275.8159 | 45.3643 | 142.9413 | 0 | 4.0911 | 19.7965 | 23.9053 | 14.0107 | 0 | 0 | 0 | 21.1841 | 126.445 | 135.418 | 169.8638 | 178.8755 | 157.1742 | 126.445 | 126.445 | 126.445 | 275.8159 | 126.445 | 139.5091 | 189.6603 | 202.7808 | 171.1849 | 126.445 | 126.445 | 126.445 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 12 | 5556 | 21.8 | 21.8 | 19.9375 | 20.0946 | 15 | 75 | 75 | 426.1945 | 271.6438 | 49.5079 | 163.7838 | 0 | 0 | 180.4542 | 296.5711 | 238.9607 | 41.3704 | 0 | 0 | 317.3562 | 142.6306 | 142.6306 | 222.1073 | 273.2481 | 247.875 | 160.8512 | 142.6306 | 142.6306 | 271.6438 | 142.6306 | 142.6306 | 402.5614 | 569.8193 | 486.8358 | 202.2215 | 142.6306 | 142.6306 | 589 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 13 | 5557 | 20.9 | 20.9 | 19.9375 | 20.0946 | 15 | 76 | 76 | 179.2815 | 348.1594 | 50.2866 | 186.5686 | 0 | 0 | 32.5105 | 102.0313 | 111.7836 | 56.0545 | 0 | 0 | 137.8406 | 158.0352 | 158.0352 | 189.8642 | 257.9278 | 267.4757 | 212.9148 | 158.0352 | 158.0352 | 348.1594 | 158.0352 | 158.0352 | 222.3747 | 359.9591 | 379.2592 | 268.9693 | 158.0352 | 158.0352 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 14 | 5558 | 22.9 | 22.9 | 19.9375 | 20.0946 | 15 | 67 | 67 | 241.3199 | 329.4724 | 47.4981 | 208.5157 | 0 | 0 | 0 | 95.8416 | 153.1787 | 120.7858 | 17.6382 | 0 | 181.5276 | 149.3185 | 149.3185 | 149.3185 | 231.7085 | 280.9982 | 253.1517 | 164.4811 | 149.3185 | 329.4724 | 149.3185 | 149.3185 | 149.3185 | 327.5501 | 434.177 | 373.9376 | 182.1194 | 149.3185 | 511 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 15 | 5559 | 22.2 | 22.2 | 19.9375 | 20.0946 | 15 | 68 | 68 | 45.9875 | 295.9963 | 41.8121 | 227.5553 | 0 | 0 | 0 | 8.8162 | 27.3006 | 29.7928 | 14.8327 | 0 | 32.0037 | 132.8041 | 132.8041 | 132.8041 | 152.6533 | 194.2702 | 199.8811 | 166.1992 | 132.8041 | 295.9963 | 132.8041 | 132.8041 | 132.8041 | 161.4695 | 221.5708 | 229.6739 | 181.0319 | 132.8041 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 16 | 5560 | 21.7 | 21.7 | 19.9375 | 20.0946 | 15 | 70 | 70 | 70.9351 | 268.1671 | 34.2195 | 243.4967 | 0 | 0 | 0 | 0 | 35.6811 | 52.8179 | 39.0147 | 2.3572 | 42.8329 | 123.0553 | 123.0553 | 123.0553 | 123.0553 | 171.6693 | 195.0175 | 176.2112 | 126.2669 | 268.1671 | 123.0553 | 123.0553 | 123.0553 | 123.0553 | 207.3504 | 247.8354 | 215.2259 | 128.6241 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 17 | 5561 | 21.3 | 21.3 | 19.9375 | 20.0946 | 15 | 70 | 70 | 511.0197 | 156.5458 | 25.5558 | 257.1427 | 0 | 0 | 0 | 0 | 188.5658 | 400.7281 | 378.1494 | 134.0558 | 246.4542 | 96.1632 | 96.1632 | 96.1632 | 96.1632 | 143.8024 | 197.403 | 191.6987 | 130.031 | 156.5458 | 96.1632 | 96.1632 | 96.1632 | 96.1632 | 332.3681 | 598.1311 | 569.848 | 264.0868 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 20 | 18 | 5562 | 21.1 | 21.1 | 19.9375 | 20.0946 | 15 | 69 | 69 | 700.7504 | 79.0519 | 16.4208 | 269.4182 | 0 | 0 | 0 | 0 | 140.6783 | 535.2942 | 616.342 | 336.345 | 237.9481 | 65.2652 | 65.2652 | 65.2652 | 65.2652 | 78.4382 | 115.3898 | 122.979 | 96.7603 | 79.0519 | 65.2652 | 65.2652 | 65.2652 | 65.2652 | 219.1165 | 650.684 | 739.3211 | 433.1054 | 317 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 19 | 5563 | 20 | 20 | 19.9375 | 20.0946 | 15 | 73 | 73 | 325.1076 | 75.727 | 7.2615 | 281.1028 | 0 | 0 | 0 | 0 | 3.1665 | 222.7368 | 311.8308 | 218.2586 | 60.273 | 44.3688 | 44.3688 | 44.3688 | 44.3688 | 45.2505 | 106.3883 | 131.1958 | 105.1414 | 75.727 | 44.3688 | 44.3688 | 44.3688 | 44.3688 | 48.417 | 329.125 | 443.0267 | 323.4 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 20 | 5564 | 16.4 | 16.4 | 19.9375 | 20.0946 | 15 | 91 | 91 | 41.9411 | 12.7309 | -1.5376 | 292.8301 | 8.0118 | 0 | 0 | 0 | 0 | 23.2031 | 40.826 | 34.5336 | 1.2691 | 12.9024 | 7.1884 | 7.1884 | 7.1884 | 7.1884 | 23.737 | 36.3057 | 31.8179 | 12.7309 | 20.9143 | 7.1884 | 7.1884 | 7.1884 | 7.1884 | 46.9401 | 77.1318 | 66.3515 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 21 | 5565 | 14.9 | 14.9 | 19.9375 | 20.0946 | 15 | 94 | 94 | 0 | 0 | -9.5881 | 305.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 22 | 5566 | 15.2 | 15.2 | 19.9375 | 20.0946 | 15 | 97 | 97 | 0 | 0 | -16.4554 | 318.4087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 23 | 5567 | 13.4 | 13.4 | 19.9375 | 20.0946 | 15 | 98 | 98 | 0 | 0 | -21.6537 | 332.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 20 | 24 | 5568 | 11.9 | 11.9 | 17.9333 | 19.5384 | 15 | 98 | 98 | 0 | 0 | -24.7022 | 348.4863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 1 | 5569 | 12.2 | 12.2 | 17.9333 | 19.5384 | 15 | 99 | 99 | 0 | 0 | -25.2556 | 4.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 2 | 5570 | 12.2 | 12.2 | 17.9333 | 19.5384 | 15 | 99 | 99 | 0 | 0 | -23.5555 | 20.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 3 | 5571 | 10.5 | 10.5 | 17.9333 | 19.5384 | 15 | 99 | 99 | 0 | 0 | -19.1985 | 35.7323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 4 | 5572 | 11.1 | 11.1 | 17.9333 | 19.5384 | 15 | 100 | 100 | 0 | 0 | -12.9597 | 49.5487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 5 | 5573 | 9.6 | 9.6 | 17.9333 | 19.5384 | 15 | 100 | 100 | 0 | 0 | -5.3384 | 62.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 6 | 5574 | 10.2 | 10.2 | 17.9333 | 19.5384 | 15 | 100 | 100 | 0 | 0 | 3.2045 | 74.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 7 | 5575 | 13.4 | 13.4 | 17.9333 | 19.5384 | 15 | 100 | 100 | 13.6034 | 53.9371 | 12.263 | 85.8126 | 3.7054 | 11.8598 | 13.0669 | 6.6196 | 0 | 0 | 0 | 0 | 2.0629 | 94.7398 | 262.3439 | 287.1548 | 154.6387 | 18.5807 | 18.5807 | 18.5807 | 18.5807 | 53.9371 | 98.4451 | 274.2037 | 300.2218 | 161.2584 | 18.5807 | 18.5807 | 18.5807 | 18.5807 | 56 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 21 | 8 | 5576 | 16.3 | 16.3 | 17.9333 | 19.5384 | 15 | 99 | 99 | 190.7452 | 138.4408 | 21.4564 | 97.7615 | 13.6103 | 141.0719 | 185.8954 | 121.824 | 0 | 0 | 0 | 0 | 58.5592 | 77.8 | 191.842 | 231.9464 | 174.6206 | 65.6226 | 65.6226 | 65.6226 | 65.6226 | 138.4408 | 91.4103 | 332.9139 | 417.8419 | 296.4445 | 65.6226 | 65.6226 | 65.6226 | 65.6226 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 9 | 5577 | 19.4 | 19.4 | 17.9333 | 19.5384 | 15 | 84 | 84 | 350.1236 | 180.4581 | 30.3731 | 110.7252 | 0 | 197.1884 | 322.8735 | 259.4236 | 44.0069 | 0 | 0 | 0 | 158.5419 | 98.4754 | 175.6624 | 224.8602 | 200.0236 | 115.7014 | 98.4754 | 98.4754 | 98.4754 | 180.4581 | 98.4754 | 372.8508 | 547.7337 | 459.4472 | 159.7083 | 98.4754 | 98.4754 | 98.4754 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 10 | 5578 | 21.1 | 21.1 | 17.9333 | 19.5384 | 15 | 75 | 75 | 527.4508 | 183.5161 | 38.4899 | 125.5682 | 0 | 187.0807 | 425.6112 | 414.8245 | 161.0392 | 0 | 0 | 0 | 305.4839 | 113.4211 | 163.6994 | 227.805 | 224.906 | 156.7007 | 113.4211 | 113.4211 | 113.4211 | 183.5161 | 113.4211 | 350.78 | 653.4162 | 639.7305 | 317.7399 | 113.4211 | 113.4211 | 113.4211 | 489 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 11 | 5579 | 22 | 22 | 17.9333 | 19.5384 | 15 | 69 | 69 | 657.2012 | 171.7834 | 45.0789 | 143.1935 | 0 | 84.2974 | 418.4282 | 507.4493 | 299.2136 | 0 | 0 | 0 | 445.2166 | 120.0998 | 136.4051 | 201.0344 | 218.2534 | 177.9753 | 120.0998 | 120.0998 | 120.0998 | 171.7834 | 120.0998 | 220.7025 | 619.4626 | 725.7027 | 477.1889 | 120.0998 | 120.0998 | 120.0998 | 617 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 12 | 5580 | 22.5 | 22.5 | 17.9333 | 19.5384 | 15 | 68 | 68 | 505.0182 | 242.8326 | 49.1915 | 163.9583 | 0 | 0 | 213.65 | 352.9698 | 285.5247 | 50.8231 | 0 | 0 | 374.1674 | 138.4728 | 138.4728 | 212.5012 | 260.7747 | 237.4054 | 156.0827 | 138.4728 | 138.4728 | 242.8326 | 138.4728 | 138.4728 | 426.1512 | 613.7445 | 522.9301 | 206.9058 | 138.4728 | 138.4728 | 617 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 13 | 5581 | 23.3 | 23.3 | 17.9333 | 19.5384 | 15 | 66 | 66 | 432.4432 | 277.1158 | 49.9519 | 186.6194 | 0 | 0 | 78.0974 | 247.2813 | 271.6112 | 136.8349 | 0 | 0 | 330.8842 | 144.2048 | 144.2048 | 179.1494 | 254.8506 | 265.737 | 205.4315 | 144.2048 | 144.2048 | 277.1158 | 144.2048 | 144.2048 | 257.2468 | 502.1319 | 537.3482 | 342.2664 | 144.2048 | 144.2048 | 608 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 14 | 5582 | 23.8 | 23.8 | 17.9333 | 19.5384 | 15 | 62 | 62 | 473.3101 | 256.7231 | 47.1649 | 208.4487 | 0 | 0 | 0 | 189.085 | 302.512 | 238.7316 | 35.1054 | 0 | 354.2769 | 139.2999 | 139.2999 | 139.2999 | 213.0482 | 257.2878 | 232.4117 | 152.9919 | 139.2999 | 256.7231 | 139.2999 | 139.2999 | 139.2999 | 402.1332 | 559.7998 | 471.1433 | 188.0974 | 139.2999 | 611 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 15 | 5583 | 24.5 | 24.5 | 17.9333 | 19.5384 | 15 | 62 | 62 | 288.1103 | 292.5889 | 41.4922 | 227.4169 | 0 | 0 | 0 | 55.802 | 172.2294 | 187.7672 | 93.3135 | 0 | 199.4111 | 140.0007 | 140.0007 | 140.0007 | 176.5005 | 252.6552 | 262.8184 | 201.0366 | 140.0007 | 292.5889 | 140.0007 | 140.0007 | 140.0007 | 232.3025 | 424.8846 | 450.5855 | 294.3501 | 140.0007 | 492 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 16 | 5584 | 24.5 | 24.5 | 17.9333 | 19.5384 | 15 | 60 | 60 | 330.0017 | 244.0219 | 33.9136 | 243.3282 | 0 | 0 | 0 | 0 | 167.261 | 246.9667 | 182.0026 | 10.4239 | 197.9781 | 124.4647 | 124.4647 | 124.4647 | 124.4647 | 207.3397 | 246.8326 | 214.644 | 129.6296 | 244.0219 | 124.4647 | 124.4647 | 124.4647 | 124.4647 | 374.6007 | 493.7992 | 396.6466 | 140.0535 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 17 | 5585 | 24.5 | 24.5 | 17.9333 | 19.5384 | 15 | 60 | 60 | 301.5191 | 199.8056 | 25.2592 | 256.9673 | 0 | 0 | 0 | 0 | 112.3206 | 237.5309 | 223.5988 | 78.6856 | 144.1944 | 104.1119 | 104.1119 | 104.1119 | 104.1119 | 157.1119 | 216.194 | 209.62 | 141.2407 | 199.8056 | 104.1119 | 104.1119 | 104.1119 | 104.1119 | 269.4325 | 453.7249 | 433.2188 | 219.9263 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 21 | 18 | 5586 | 23.9 | 23.9 | 17.9333 | 19.5384 | 15 | 63 | 63 | 100.358 | 152.347 | 16.1275 | 269.247 | 0 | 0 | 0 | 0 | 20.4675 | 76.9983 | 88.4245 | 48.0528 | 33.653 | 74.7341 | 74.7341 | 74.7341 | 74.7341 | 93.0165 | 143.5121 | 153.7184 | 117.6568 | 152.347 | 74.7341 | 74.7341 | 74.7341 | 74.7341 | 113.484 | 220.5104 | 242.143 | 165.7096 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 19 | 5587 | 21.7 | 21.7 | 17.9333 | 19.5384 | 15 | 80 | 80 | 35.4506 | 74.5846 | 6.9658 | 280.9415 | 0 | 0 | 0 | 0 | 0.44757 | 24.3952 | 34.0525 | 23.7623 | 6.4154 | 37.2232 | 37.2232 | 37.2232 | 37.2232 | 37.586 | 56.9963 | 64.8239 | 56.4833 | 74.5846 | 37.2232 | 37.2232 | 37.2232 | 37.2232 | 38.0335 | 81.3916 | 98.8764 | 80.2456 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 20 | 5588 | 20.3 | 20.3 | 17.9333 | 19.5384 | 15 | 84 | 84 | 28.6467 | 10.2656 | -1.8405 | 292.684 | 5.3972 | 0 | 0 | 0 | 0 | 15.9249 | 27.9184 | 23.5577 | 0.73436 | 10.5772 | 5.8004 | 5.8004 | 5.8004 | 5.8004 | 19.8947 | 30.5096 | 26.6501 | 10.2656 | 15.9745 | 5.8004 | 5.8004 | 5.8004 | 5.8004 | 35.8196 | 58.428 | 50.2078 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 21 | 5589 | 19.6 | 19.6 | 17.9333 | 19.5384 | 15 | 81 | 81 | 0 | 0 | -9.9014 | 305.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 22 | 5590 | 18.1 | 18.1 | 17.9333 | 19.5384 | 15 | 89 | 89 | 0 | 0 | -16.7801 | 318.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 23 | 5591 | 18 | 18 | 17.9333 | 19.5384 | 15 | 87 | 87 | 0 | 0 | -21.9874 | 332.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 21 | 24 | 5592 | 17.5 | 17.5 | 18.3417 | 19.0838 | 15 | 90 | 90 | 0 | 0 | -25.0382 | 348.5024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 1 | 5593 | 16.1 | 16.1 | 18.3417 | 19.0838 | 15 | 94 | 94 | 0 | 0 | -25.5837 | 4.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 2 | 5594 | 15.5 | 15.5 | 18.3417 | 19.0838 | 15 | 97 | 97 | 0 | 0 | -23.8687 | 20.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 3 | 5595 | 15.3 | 15.3 | 18.3417 | 19.0838 | 15 | 98 | 98 | 0 | 0 | -19.4881 | 35.9207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 4 | 5596 | 15 | 15 | 18.3417 | 19.0838 | 15 | 99 | 99 | 0 | 0 | -13.2254 | 49.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 5 | 5597 | 15.1 | 15.1 | 18.3417 | 19.0838 | 15 | 99 | 99 | 0 | 0 | -5.5837 | 62.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 6 | 5598 | 15.2 | 15.2 | 18.3417 | 19.0838 | 15 | 99 | 99 | 0 | 0 | 2.9736 | 74.4179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 7 | 5599 | 15.9 | 15.9 | 18.3417 | 19.0838 | 15 | 99 | 99 | 1.5 | 21.7793 | 12.039 | 86.0739 | 0.40239 | 1.3048 | 1.4429 | 0.73578 | 0 | 0 | 0 | 0 | 0.2207 | 15.1604 | 26.3283 | 28.0373 | 19.2861 | 10.1808 | 10.1808 | 10.1808 | 10.1808 | 21.7793 | 15.5627 | 27.6332 | 29.4802 | 20.0219 | 10.1808 | 10.1808 | 10.1808 | 10.1808 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 22 | 8 | 5600 | 19.3 | 19.3 | 18.3417 | 19.0838 | 15 | 85 | 85 | 44.7831 | 128.445 | 21.231 | 98.0344 | 2.9988 | 33.0178 | 43.6954 | 28.7768 | 0 | 0 | 0 | 0 | 13.555 | 66.3399 | 159.5481 | 192.7018 | 146.38 | 57.0286 | 57.0286 | 57.0286 | 57.0286 | 128.445 | 69.3387 | 192.5659 | 236.3972 | 175.1568 | 57.0286 | 57.0286 | 57.0286 | 57.0286 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 9 | 5601 | 21.7 | 21.7 | 18.3417 | 19.0838 | 15 | 75 | 75 | 373.3245 | 174.4983 | 30.1367 | 111.0077 | 0 | 209.2562 | 344.5705 | 278.04 | 48.6375 | 0 | 0 | 0 | 167.5017 | 97.0609 | 172.594 | 221.437 | 197.4222 | 114.6171 | 97.0609 | 97.0609 | 97.0609 | 174.4983 | 97.0609 | 381.8502 | 566.0075 | 475.4622 | 163.2546 | 97.0609 | 97.0609 | 97.0609 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 10 | 5602 | 22.6 | 22.6 | 18.3417 | 19.0838 | 15 | 75 | 75 | 248.831 | 250.8763 | 38.232 | 125.8504 | 0 | 87.5018 | 200.8929 | 196.6037 | 77.1467 | 0 | 0 | 0 | 143.1237 | 123.203 | 177.1342 | 247.0223 | 244.3787 | 170.752 | 123.203 | 123.203 | 123.203 | 250.8763 | 123.203 | 264.636 | 447.9152 | 440.9824 | 247.8987 | 123.203 | 123.203 | 123.203 | 394 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 11 | 5603 | 24 | 24 | 18.3417 | 19.0838 | 15 | 63 | 63 | 527.795 | 213.4895 | 44.7907 | 143.4479 | 0 | 65.9252 | 336.0449 | 409.314 | 242.8126 | 0 | 0 | 0 | 355.5105 | 128.2058 | 147.9593 | 228.8964 | 250.8504 | 200.9608 | 128.2058 | 128.2058 | 128.2058 | 213.4895 | 128.2058 | 213.8845 | 564.9413 | 660.1644 | 443.7734 | 128.2058 | 128.2058 | 128.2058 | 569 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 12 | 5604 | 25.2 | 25.2 | 18.3417 | 19.0838 | 15 | 56 | 56 | 637.4875 | 194.1023 | 48.872 | 164.1348 | 0 | 0 | 269.4374 | 447.5066 | 363.4326 | 66.4646 | 0 | 0 | 469.8977 | 129.1957 | 129.1957 | 187.3518 | 225.7868 | 207.64 | 143.5416 | 129.1957 | 129.1957 | 194.1023 | 129.1957 | 129.1957 | 456.7892 | 673.2934 | 571.0725 | 210.0063 | 129.1957 | 129.1957 | 664 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 13 | 5605 | 26.3 | 26.3 | 18.3417 | 19.0838 | 15 | 55 | 55 | 361.0052 | 300.1343 | 49.6138 | 186.6725 | 0 | 0 | 64.9127 | 207.4061 | 228.4039 | 115.6057 | 0 | 0 | 274.8657 | 149.4367 | 149.4367 | 184.0912 | 260.1631 | 271.373 | 211.1543 | 149.4367 | 149.4367 | 300.1343 | 149.4367 | 149.4367 | 249.0039 | 467.5693 | 499.7769 | 326.7599 | 149.4367 | 149.4367 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 14 | 5606 | 27.4 | 27.4 | 18.3417 | 19.0838 | 15 | 50 | 50 | 731.1491 | 163.4924 | 46.8279 | 208.3844 | 0 | 0 | 0 | 293.7909 | 470.5289 | 371.6374 | 55.0458 | 0 | 544.5076 | 124.7414 | 124.7414 | 124.7414 | 174.2109 | 203.9707 | 187.319 | 134.0102 | 124.7414 | 163.4924 | 124.7414 | 124.7414 | 124.7414 | 468.0018 | 674.4996 | 558.9564 | 189.056 | 124.7414 | 708 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 15 | 5607 | 27.7 | 27.7 | 18.3417 | 19.0838 | 15 | 55 | 55 | 580.6578 | 200.3411 | 41.1682 | 227.2805 | 0 | 0 | 0 | 113.6025 | 349.5194 | 380.6925 | 188.8612 | 0 | 399.6589 | 123.7877 | 123.7877 | 123.7877 | 151.3285 | 208.5223 | 216.0797 | 169.5737 | 123.7877 | 200.3411 | 123.7877 | 123.7877 | 123.7877 | 264.931 | 558.0417 | 596.7722 | 358.4349 | 123.7877 | 600 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 16 | 5608 | 27 | 27 | 18.3417 | 19.0838 | 15 | 59 | 59 | 236.2796 | 262.1843 | 33.6035 | 243.161 | 0 | 0 | 0 | 0 | 120.6665 | 177.7258 | 130.6757 | 7.0776 | 140.8157 | 125.5075 | 125.5075 | 125.5075 | 125.5075 | 213.6538 | 255.3353 | 220.9655 | 130.6777 | 262.1843 | 125.5075 | 125.5075 | 125.5075 | 125.5075 | 334.3204 | 433.0612 | 351.6412 | 137.7552 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 17 | 5609 | 25.2 | 25.2 | 18.3417 | 19.0838 | 15 | 64 | 64 | 34.3798 | 194.6999 | 24.9585 | 256.7926 | 0 | 0 | 0 | 0 | 12.928 | 27.2081 | 25.55 | 8.925 | 16.3001 | 91.087 | 91.087 | 91.087 | 91.087 | 116.8498 | 145.3066 | 142.0024 | 108.8727 | 194.6999 | 91.087 | 91.087 | 91.087 | 91.087 | 129.7778 | 172.5147 | 167.5524 | 117.7977 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 22 | 18 | 5610 | 23.3 | 23.3 | 18.3417 | 19.0838 | 15 | 79 | 79 | 122.7492 | 151.3645 | 15.8301 | 269.076 | 0 | 0 | 0 | 0 | 25.4262 | 94.5888 | 108.3426 | 58.6307 | 40.6355 | 74.9931 | 74.9931 | 74.9931 | 74.9931 | 93.5771 | 144.128 | 154.1806 | 117.8462 | 151.3645 | 74.9931 | 74.9931 | 74.9931 | 74.9931 | 119.0034 | 238.7168 | 262.5231 | 176.4769 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 19 | 5611 | 22.5 | 22.5 | 18.3417 | 19.0838 | 15 | 82 | 82 | 33.1927 | 72.1418 | 6.6661 | 280.7803 | 0 | 0 | 0 | 0 | 0.515 | 22.9419 | 31.9297 | 22.2135 | 5.8582 | 36.0431 | 36.0431 | 36.0431 | 36.0431 | 36.4717 | 55.135 | 62.6146 | 54.529 | 72.1418 | 36.0431 | 36.0431 | 36.0431 | 36.0431 | 36.9867 | 78.0769 | 94.5443 | 76.7425 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 20 | 5612 | 21.5 | 21.5 | 18.3417 | 19.0838 | 15 | 86 | 86 | 5.1915 | 9.3811 | -2.1473 | 292.5378 | 0.96447 | 0 | 0 | 0 | 0 | 2.8998 | 5.0654 | 4.2638 | 1.6189 | 5.221 | 5.1609 | 5.1609 | 5.1609 | 5.1609 | 5.3416 | 5.4767 | 5.4267 | 9.3811 | 6.1855 | 5.1609 | 5.1609 | 5.1609 | 5.1609 | 8.2415 | 10.5421 | 9.6905 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 21 | 5613 | 21.4 | 21.4 | 18.3417 | 19.0838 | 15 | 85 | 85 | 0 | 0 | -10.2186 | 304.8792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 22 | 5614 | 20.9 | 20.9 | 18.3417 | 19.0838 | 15 | 88 | 88 | 0 | 0 | -17.1088 | 318.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 23 | 5615 | 20.5 | 20.5 | 18.3417 | 19.0838 | 15 | 88 | 88 | 0 | 0 | -22.3249 | 332.8126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 22 | 24 | 5616 | 19.8 | 19.8 | 21.0167 | 19.3862 | 15 | 91 | 91 | 0 | 0 | -25.3776 | 348.5206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 1 | 5617 | 19.9 | 19.9 | 21.0167 | 19.3862 | 15 | 91 | 91 | 0 | 0 | -25.9148 | 4.8015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 2 | 5618 | 18.7 | 18.7 | 21.0167 | 19.3862 | 15 | 95 | 95 | 0 | 0 | -24.1843 | 20.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 3 | 5619 | 18.1 | 18.1 | 21.0167 | 19.3862 | 15 | 98 | 98 | 0 | 0 | -19.7796 | 36.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 4 | 5620 | 18.2 | 18.2 | 21.0167 | 19.3862 | 15 | 97 | 97 | 0 | 0 | -13.4926 | 49.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 5 | 5621 | 18.4 | 18.4 | 21.0167 | 19.3862 | 15 | 94 | 94 | 0 | 0 | -5.8304 | 62.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 6 | 5622 | 18.2 | 18.2 | 21.0167 | 19.3862 | 15 | 96 | 96 | 0 | 0 | 2.7413 | 74.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 7 | 5623 | 19.1 | 19.1 | 21.0167 | 19.3862 | 15 | 90 | 90 | 0.64663 | 13.9078 | 11.8137 | 86.3386 | 0.17075 | 0.56121 | 0.62292 | 0.31973 | 0 | 0 | 0 | 0 | 0.092193 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 13.9078 | 6.9719 | 7.3623 | 7.4241 | 7.1209 | 6.8011 | 6.8011 | 6.8011 | 6.8011 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 23 | 8 | 5624 | 20.3 | 20.3 | 21.0167 | 19.3862 | 15 | 80 | 80 | 18.164 | 111.5815 | 21.0041 | 98.3105 | 1.1354 | 13.349 | 17.7429 | 11.7433 | 0 | 0 | 0 | 0 | 5.4185 | 54.9282 | 138.9406 | 169.1648 | 127.8959 | 47.1184 | 47.1184 | 47.1184 | 47.1184 | 111.5815 | 56.0635 | 152.2896 | 186.9077 | 139.6393 | 47.1184 | 47.1184 | 47.1184 | 47.1184 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 9 | 5625 | 22.2 | 22.2 | 21.0167 | 19.3862 | 15 | 73 | 73 | 136.2765 | 203.4278 | 29.8984 | 111.2931 | 0 | 76.0121 | 125.8857 | 102.0172 | 18.3884 | 0 | 0 | 0 | 60.5722 | 94.41 | 183.7006 | 242.2866 | 214.2485 | 116.0106 | 94.41 | 94.41 | 94.41 | 203.4278 | 94.41 | 259.7127 | 368.1723 | 316.2657 | 134.399 | 94.41 | 94.41 | 94.41 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 10 | 5626 | 23.4 | 23.4 | 21.0167 | 19.3862 | 15 | 70 | 70 | 301.2157 | 238.9634 | 37.9719 | 126.135 | 0 | 104.9884 | 243.3014 | 239.0918 | 94.8254 | 0 | 0 | 0 | 172.0366 | 122.2328 | 178.5099 | 252.65 | 250.3935 | 173.0622 | 122.2328 | 122.2328 | 122.2328 | 238.9634 | 122.2328 | 283.4982 | 495.9514 | 489.4853 | 267.8877 | 122.2328 | 122.2328 | 122.2328 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 11 | 5627 | 24.9 | 24.9 | 21.0167 | 19.3862 | 15 | 66 | 66 | 442.3257 | 239.7962 | 44.4999 | 143.7043 | 0 | 53.7358 | 281.6134 | 344.5257 | 205.6196 | 0 | 0 | 0 | 296.2038 | 131.8955 | 152.3913 | 239.3081 | 263.304 | 210.3226 | 131.8955 | 131.8955 | 131.8955 | 239.7962 | 131.8955 | 206.1271 | 520.9215 | 607.8298 | 415.9422 | 131.8955 | 131.8955 | 131.8955 | 536 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 12 | 5628 | 26.1 | 26.1 | 21.0167 | 19.3862 | 15 | 60 | 60 | 337.8137 | 296.2954 | 48.5495 | 164.3131 | 0 | 0 | 142.6288 | 238.1711 | 194.196 | 36.4636 | 0 | 0 | 247.7046 | 147.1661 | 147.1661 | 227.1713 | 280.7642 | 256.0971 | 167.6197 | 147.1661 | 147.1661 | 296.2954 | 147.1661 | 147.1661 | 369.8001 | 518.9353 | 450.2932 | 204.0833 | 147.1661 | 147.1661 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 13 | 5629 | 27.1 | 27.1 | 21.0167 | 19.3862 | 15 | 58 | 58 | 248.6246 | 330.6502 | 49.2725 | 186.728 | 0 | 0 | 44.4999 | 143.509 | 158.4525 | 80.5767 | 0 | 0 | 188.3498 | 151.2176 | 151.2176 | 188.2893 | 270.7713 | 283.2203 | 218.3439 | 151.2176 | 151.2176 | 330.6502 | 151.2176 | 151.2176 | 232.7893 | 414.2803 | 441.6728 | 298.9206 | 151.2176 | 151.2176 | 519 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 14 | 5630 | 28 | 28 | 21.0167 | 19.3862 | 15 | 52 | 52 | 228.4428 | 327.7497 | 46.4873 | 208.3225 | 0 | 0 | 0 | 92.3211 | 148.0239 | 117.0163 | 17.4622 | 0 | 169.2503 | 148.022 | 148.022 | 148.022 | 231.3405 | 281.6115 | 253.6276 | 163.7814 | 148.022 | 327.7497 | 148.022 | 148.022 | 148.022 | 323.6616 | 429.6354 | 370.6439 | 181.2435 | 148.022 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 15 | 5631 | 28.7 | 28.7 | 21.0167 | 19.3862 | 15 | 52 | 52 | 558.3764 | 206.8591 | 40.8402 | 227.1461 | 0 | 0 | 0 | 110.3313 | 338.4284 | 368.2788 | 182.3965 | 0 | 382.1409 | 124.2723 | 124.2723 | 124.2723 | 152.6061 | 211.183 | 218.8488 | 171.1129 | 124.2723 | 206.8591 | 124.2723 | 124.2723 | 124.2723 | 262.9373 | 549.6114 | 587.1276 | 353.5094 | 124.2723 | 589 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 16 | 5632 | 27.6 | 27.6 | 21.0167 | 19.3862 | 15 | 55 | 55 | 209.994 | 264.6934 | 33.2894 | 242.9951 | 0 | 0 | 0 | 0 | 108.0511 | 158.7565 | 116.4646 | 5.9492 | 124.3066 | 128.1073 | 128.1073 | 128.1073 | 128.1073 | 197.2417 | 229.6847 | 202.6249 | 131.9138 | 264.6934 | 128.1073 | 128.1073 | 128.1073 | 128.1073 | 305.2928 | 388.4412 | 319.0895 | 137.8631 | 389 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 17 | 5633 | 27.3 | 27.3 | 21.0167 | 19.3862 | 15 | 55 | 55 | 100.6119 | 213.717 | 24.6537 | 256.6186 | 0 | 0 | 0 | 0 | 38.1881 | 79.9883 | 74.9325 | 25.9822 | 47.283 | 101.0664 | 101.0664 | 101.0664 | 101.0664 | 144.6066 | 192.2651 | 186.5007 | 130.6901 | 213.717 | 101.0664 | 101.0664 | 101.0664 | 101.0664 | 182.7946 | 272.2534 | 261.4332 | 156.6723 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 23 | 18 | 5634 | 25.8 | 25.8 | 21.0167 | 19.3862 | 15 | 63 | 63 | 5.5515 | 92.1863 | 15.5288 | 268.9052 | 0 | 0 | 0 | 0 | 1.1677 | 4.2965 | 4.9085 | 2.6452 | 1.8137 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 92.1863 | 45.7102 | 45.7102 | 45.7102 | 45.7102 | 46.8779 | 50.0068 | 50.6188 | 48.3554 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 19 | 5635 | 23.8 | 23.8 | 21.0167 | 19.3862 | 15 | 71 | 71 | 1.4173 | 24.7563 | 6.3625 | 280.619 | 0 | 0 | 0 | 0 | 0.026092 | 0.98388 | 1.3653 | 0.94698 | 0.24373 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 24.7563 | 11.7489 | 11.7489 | 11.7489 | 11.7489 | 11.775 | 12.7328 | 13.1142 | 12.6959 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 20 | 5636 | 22.7 | 22.7 | 21.0167 | 19.3862 | 15 | 79 | 79 | 0 | 0 | -2.4579 | 292.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 21 | 5637 | 22 | 22 | 21.0167 | 19.3862 | 15 | 87 | 87 | 0 | 0 | -10.5395 | 304.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 22 | 5638 | 21.1 | 21.1 | 21.0167 | 19.3862 | 15 | 88 | 88 | 0 | 0 | -17.4411 | 318.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 23 | 5639 | 20.7 | 20.7 | 21.0167 | 19.3862 | 15 | 90 | 90 | 0 | 0 | -22.666 | 332.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 23 | 24 | 5640 | 19.8 | 19.8 | 22.5875 | 20.2296 | 15 | 94 | 94 | 0 | 0 | -25.7203 | 348.5409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 1 | 5641 | 19.3 | 19.3 | 22.5875 | 20.2296 | 15 | 98 | 98 | 0 | 0 | -26.2489 | 4.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 2 | 5642 | 19.7 | 19.7 | 22.5875 | 20.2296 | 15 | 99 | 99 | 0 | 0 | -24.5022 | 21.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 3 | 5643 | 19.6 | 19.6 | 22.5875 | 20.2296 | 15 | 98 | 98 | 0 | 0 | -20.0729 | 36.3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 4 | 5644 | 18.7 | 18.7 | 22.5875 | 20.2296 | 15 | 98 | 98 | 0 | 0 | -13.7612 | 50.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 5 | 5645 | 18.2 | 18.2 | 22.5875 | 20.2296 | 15 | 99 | 99 | 0 | 0 | -6.0782 | 62.9626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 6 | 5646 | 18.2 | 18.2 | 22.5875 | 20.2296 | 15 | 100 | 100 | 0 | 0 | 2.508 | 74.9276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 7 | 5647 | 19.2 | 19.2 | 22.5875 | 20.2296 | 15 | 100 | 100 | 0.69023 | 13.9048 | 11.5872 | 86.6066 | 0.17931 | 0.59762 | 0.66584 | 0.34403 | 0 | 0 | 0 | 0 | 0.095228 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 13.9048 | 7.0039 | 7.4222 | 7.4904 | 7.1686 | 6.8245 | 6.8245 | 6.8245 | 6.8245 | 14 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 24 | 8 | 5648 | 20.8 | 20.8 | 22.5875 | 20.2296 | 15 | 95 | 95 | 4.3656 | 73.717 | 20.7756 | 98.5896 | 0.25314 | 3.1977 | 4.2691 | 2.8397 | 0 | 0 | 0 | 0 | 1.283 | 36.2462 | 57.8674 | 65.7344 | 55.2388 | 34.3875 | 34.3875 | 34.3875 | 34.3875 | 73.717 | 36.4994 | 61.0651 | 70.0035 | 58.0785 | 34.3875 | 34.3875 | 34.3875 | 34.3875 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 9 | 5649 | 22.9 | 22.9 | 22.5875 | 20.2296 | 15 | 79 | 79 | 24.2649 | 172.3178 | 29.6582 | 111.5811 | 0 | 13.4663 | 22.4326 | 18.2582 | 3.3884 | 0 | 0 | 0 | 10.6822 | 75.9059 | 126.3588 | 159.9523 | 144.3125 | 88.6011 | 75.9059 | 75.9059 | 75.9059 | 172.3178 | 75.9059 | 139.825 | 182.3849 | 162.5707 | 91.9895 | 75.9059 | 75.9059 | 75.9059 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 10 | 5650 | 24.9 | 24.9 | 22.5875 | 20.2296 | 15 | 75 | 75 | 120.905 | 259.4419 | 37.7095 | 126.4219 | 0 | 41.7583 | 97.7002 | 96.4106 | 38.645 | 0 | 0 | 0 | 68.5581 | 119.0446 | 164.0812 | 224.4149 | 223.0241 | 160.7235 | 119.0446 | 119.0446 | 119.0446 | 259.4419 | 119.0446 | 205.8395 | 322.1151 | 319.4347 | 199.3685 | 119.0446 | 119.0446 | 119.0446 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 11 | 5651 | 26.9 | 26.9 | 22.5875 | 20.2296 | 15 | 62 | 62 | 508.3202 | 217.6285 | 44.2065 | 143.9625 | 0 | 59.9827 | 323.5914 | 397.6446 | 238.763 | 0 | 0 | 0 | 338.3715 | 128.1712 | 147.022 | 229.8663 | 253.139 | 203.2073 | 128.1712 | 128.1712 | 128.1712 | 217.6285 | 128.1712 | 207.0047 | 553.4576 | 650.7836 | 441.9703 | 128.1712 | 128.1712 | 128.1712 | 556 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 12 | 5652 | 28.2 | 28.2 | 22.5875 | 20.2296 | 15 | 59 | 59 | 662.8928 | 183.5214 | 48.2241 | 164.4931 | 0 | 0 | 279.557 | 469.3807 | 384.2475 | 74.0274 | 0 | 0 | 483.4786 | 127.0794 | 127.0794 | 183.1437 | 221.2122 | 204.139 | 141.9254 | 127.0794 | 127.0794 | 183.5214 | 127.0794 | 127.0794 | 462.7006 | 690.5929 | 588.3866 | 215.9528 | 127.0794 | 127.0794 | 667 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 13 | 5653 | 28.6 | 28.6 | 22.5875 | 20.2296 | 15 | 54 | 54 | 682.4387 | 182.6569 | 48.9279 | 186.7856 | 0 | 0 | 121.5533 | 395.7368 | 438.103 | 223.8344 | 0 | 0 | 514.3431 | 128.9073 | 128.9073 | 152.5963 | 206.0306 | 214.2871 | 172.5293 | 128.9073 | 128.9073 | 182.6569 | 128.9073 | 128.9073 | 274.1496 | 601.7674 | 652.3901 | 396.3637 | 128.9073 | 128.9073 | 697 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 14 | 5654 | 29.6 | 29.6 | 22.5875 | 20.2296 | 15 | 50 | 50 | 743.2211 | 158.2574 | 46.1431 | 208.2631 | 0 | 0 | 0 | 302.0664 | 484.8818 | 383.66 | 57.6954 | 0 | 547.7426 | 123.3451 | 123.3451 | 123.3451 | 172.2324 | 201.8199 | 185.4378 | 132.6827 | 123.3451 | 158.2574 | 123.3451 | 123.3451 | 123.3451 | 474.2989 | 686.7017 | 569.0978 | 190.3781 | 123.3451 | 706 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 15 | 5655 | 29.6 | 29.6 | 22.5875 | 20.2296 | 15 | 47 | 47 | 678.9949 | 166.0038 | 40.5085 | 227.0137 | 0 | 0 | 0 | 135.4784 | 414.3624 | 450.5185 | 222.767 | 0 | 461.9962 | 118.288 | 118.288 | 118.288 | 143.1437 | 194.3094 | 200.9428 | 159.1582 | 118.288 | 166.0038 | 118.288 | 118.288 | 118.288 | 278.6221 | 608.6718 | 651.4614 | 381.9252 | 118.288 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 16 | 5656 | 29.2 | 29.2 | 22.5875 | 20.2296 | 15 | 47 | 47 | 727.5441 | 130.292 | 32.9714 | 242.8305 | 0 | 0 | 0 | 0 | 377.1566 | 552.8175 | 404.6454 | 19.4375 | 427.708 | 102.5014 | 102.5014 | 102.5014 | 102.5014 | 157.4546 | 183.049 | 161.4598 | 105.3335 | 130.292 | 102.5014 | 102.5014 | 102.5014 | 102.5014 | 534.6112 | 735.8665 | 566.1051 | 124.771 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 17 | 5657 | 29.2 | 29.2 | 22.5875 | 20.2296 | 15 | 46 | 46 | 646.6855 | 120.8147 | 24.345 | 256.4453 | 0 | 0 | 0 | 0 | 247.7331 | 516.4722 | 482.6688 | 166.1246 | 301.1853 | 87.0978 | 87.0978 | 87.0978 | 87.0978 | 126.7996 | 169.8678 | 164.4504 | 113.721 | 120.8147 | 87.0978 | 87.0978 | 87.0978 | 87.0978 | 374.5327 | 686.34 | 647.1193 | 279.8456 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 24 | 18 | 5658 | 28.6 | 28.6 | 22.5875 | 20.2296 | 15 | 51 | 51 | 543.2612 | 99.8948 | 15.2236 | 268.7347 | 0 | 0 | 0 | 0 | 116.0043 | 422.2646 | 481.168 | 258.2097 | 175.1052 | 66.2704 | 66.2704 | 66.2704 | 66.2704 | 86.9453 | 141.5286 | 152.0267 | 112.2899 | 99.8948 | 66.2704 | 66.2704 | 66.2704 | 66.2704 | 202.9496 | 563.7932 | 633.1947 | 370.4996 | 275 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 19 | 5659 | 26.1 | 26.1 | 22.5875 | 20.2296 | 15 | 58 | 58 | 376.6798 | 64.9448 | 6.0552 | 280.4577 | 0 | 0 | 0 | 0 | 8.026 | 262.6187 | 363.3729 | 251.2682 | 63.0552 | 39.6471 | 39.6471 | 39.6471 | 39.6471 | 41.4402 | 98.3192 | 120.8289 | 95.7834 | 64.9448 | 39.6471 | 39.6471 | 39.6471 | 39.6471 | 49.4661 | 360.9379 | 484.2018 | 347.0516 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 20 | 5660 | 21.8 | 21.8 | 22.5875 | 20.2296 | 15 | 83 | 83 | 1.0305 | 2.31 | -2.7722 | 292.2451 | 0.186 | 0 | 0 | 0 | 0 | 0.58104 | 1.0077 | 0.84408 | 11.69 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.31 | 2.5877 | 2.4017 | 2.4017 | 2.4017 | 2.4017 | 2.9827 | 3.4094 | 3.2458 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 21 | 5661 | 19.8 | 19.8 | 22.5875 | 20.2296 | 15 | 91 | 91 | 0 | 0 | -10.8641 | 304.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 22 | 5662 | 18.7 | 18.7 | 22.5875 | 20.2296 | 15 | 94 | 94 | 0 | 0 | -17.777 | 318.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 23 | 5663 | 18.2 | 18.2 | 22.5875 | 20.2296 | 15 | 96 | 96 | 0 | 0 | -23.0106 | 332.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 24 | 24 | 5664 | 17.7 | 17.7 | 23.0708 | 21.0661 | 15 | 98 | 98 | 0 | 0 | -26.0664 | 348.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 1 | 5665 | 17.8 | 17.8 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | -26.5859 | 4.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 2 | 5666 | 18 | 18 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | -24.8223 | 21.2896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 3 | 5667 | 17.5 | 17.5 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | -20.3679 | 36.5101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 4 | 5668 | 17.9 | 17.9 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | -14.0311 | 50.4425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 5 | 5669 | 17.1 | 17.1 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | -6.3272 | 63.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 6 | 5670 | 16.2 | 16.2 | 23.0708 | 21.0661 | 15 | 99 | 99 | 0 | 0 | 2.2735 | 75.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 7 | 5671 | 18.3 | 18.3 | 23.0708 | 21.0661 | 15 | 99 | 99 | 4.8857 | 35.3487 | 11.3594 | 86.8776 | 1.2481 | 4.2198 | 4.7197 | 2.4548 | 0 | 0 | 0 | 0 | 0.65134 | 48.0976 | 130.5146 | 144.3766 | 81.5634 | 13.4839 | 13.4839 | 13.4839 | 13.4839 | 35.3487 | 49.3457 | 134.7344 | 149.0962 | 84.0182 | 13.4839 | 13.4839 | 13.4839 | 13.4839 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 25 | 8 | 5672 | 22.1 | 22.1 | 23.0708 | 21.0661 | 15 | 84 | 84 | 72.4735 | 129.025 | 20.5457 | 98.8715 | 3.8702 | 52.9047 | 70.9484 | 47.4314 | 0 | 0 | 0 | 0 | 20.975 | 65.5784 | 170.9814 | 209.7674 | 159.2161 | 57.2591 | 57.2591 | 57.2591 | 57.2591 | 129.025 | 69.4487 | 223.8862 | 280.7158 | 206.6475 | 57.2591 | 57.2591 | 57.2591 | 57.2591 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 9 | 5673 | 24.6 | 24.6 | 23.0708 | 21.0661 | 15 | 73 | 73 | 242.5054 | 191.2846 | 29.4163 | 111.8717 | 0 | 133.886 | 224.3635 | 183.412 | 35.0201 | 0 | 0 | 0 | 105.7154 | 94.6237 | 177.2281 | 233.0506 | 207.7845 | 116.2303 | 94.6237 | 94.6237 | 94.6237 | 191.2846 | 94.6237 | 311.1141 | 457.4141 | 391.1964 | 151.2504 | 94.6237 | 94.6237 | 94.6237 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 10 | 5674 | 26.8 | 26.8 | 23.0708 | 21.0661 | 15 | 68 | 68 | 403.5506 | 211.8472 | 37.445 | 126.7109 | 0 | 138.0749 | 326.2199 | 323.2697 | 130.9525 | 0 | 0 | 0 | 227.1528 | 117.6973 | 168.9645 | 238.8226 | 237.7272 | 166.32 | 117.6973 | 117.6973 | 117.6973 | 211.8472 | 117.6973 | 307.0393 | 565.0425 | 560.997 | 297.2725 | 117.6973 | 117.6973 | 117.6973 | 439 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 11 | 5675 | 28.7 | 28.7 | 23.0708 | 21.0661 | 15 | 57 | 57 | 532.4404 | 208.7252 | 43.9106 | 144.2223 | 0 | 60.9431 | 338.8818 | 418.3082 | 252.6953 | 0 | 0 | 0 | 352.2748 | 126.3338 | 144.1624 | 225.4718 | 248.7075 | 200.2584 | 126.3338 | 126.3338 | 126.3338 | 208.7252 | 126.3338 | 205.1055 | 564.3536 | 667.0157 | 452.9537 | 126.3338 | 126.3338 | 126.3338 | 561 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 12 | 5676 | 30 | 30 | 23.0708 | 21.0661 | 15 | 53 | 53 | 610.6278 | 201.0656 | 47.8959 | 164.6747 | 0 | 0 | 257.1901 | 434.2241 | 356.8955 | 70.5024 | 0 | 0 | 442.9344 | 129.0305 | 129.0305 | 188.1034 | 228.7657 | 211.0044 | 145.2239 | 129.0305 | 129.0305 | 201.0656 | 129.0305 | 129.0305 | 445.2936 | 662.9898 | 567.8999 | 215.7262 | 129.0305 | 129.0305 | 644 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 13 | 5677 | 30.3 | 30.3 | 23.0708 | 21.0661 | 15 | 49 | 49 | 650.4655 | 193.32 | 48.5802 | 186.8453 | 0 | 0 | 115.2669 | 378.926 | 420.6153 | 215.9139 | 0 | 0 | 487.68 | 129.9888 | 129.9888 | 154.4431 | 210.3793 | 219.2238 | 175.7957 | 129.9888 | 129.9888 | 193.32 | 129.9888 | 129.9888 | 269.71 | 589.3052 | 639.8391 | 391.7096 | 129.9888 | 129.9888 | 681 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 14 | 5678 | 30.9 | 30.9 | 23.0708 | 21.0661 | 15 | 49 | 49 | 730.12 | 161.8056 | 45.7954 | 208.2061 | 0 | 0 | 0 | 298.4071 | 479.583 | 379.8257 | 57.5717 | 0 | 535.1944 | 123.4837 | 123.4837 | 123.4837 | 173.4564 | 203.797 | 187.0912 | 133.1249 | 123.4837 | 161.8056 | 123.4837 | 123.4837 | 123.4837 | 471.8635 | 683.38 | 566.9169 | 190.6966 | 123.4837 | 697 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 15 | 5679 | 30.8 | 30.8 | 23.0708 | 21.0661 | 15 | 47 | 47 | 672.0816 | 167.4133 | 40.1729 | 226.8834 | 0 | 0 | 0 | 135.39 | 412.9467 | 448.6048 | 221.4763 | 0 | 454.5867 | 118.1438 | 118.1438 | 118.1438 | 143.3901 | 195.1462 | 201.7954 | 159.4426 | 118.1438 | 167.4133 | 118.1438 | 118.1438 | 118.1438 | 278.7801 | 608.0929 | 650.4002 | 380.919 | 118.1438 | 622 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 16 | 5680 | 30.8 | 30.8 | 23.0708 | 21.0661 | 15 | 46 | 46 | 695.3262 | 138.1043 | 32.6495 | 242.6673 | 0 | 0 | 0 | 0 | 363.1354 | 531.0122 | 387.8292 | 17.4611 | 405.8957 | 103.4429 | 103.4429 | 103.4429 | 103.4429 | 161.2023 | 187.9043 | 165.13 | 106.2202 | 138.1043 | 103.4429 | 103.4429 | 103.4429 | 103.4429 | 524.3377 | 718.9165 | 552.9592 | 123.6813 | 544 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 17 | 5681 | 30.6 | 30.6 | 23.0708 | 21.0661 | 15 | 46 | 46 | 649.8104 | 119.1343 | 24.0325 | 256.2727 | 0 | 0 | 0 | 0 | 251.2195 | 521.3263 | 486.0472 | 166.0483 | 299.8657 | 86.3224 | 86.3224 | 86.3224 | 86.3224 | 126.0904 | 168.8482 | 163.2635 | 112.6078 | 119.1343 | 86.3224 | 86.3224 | 86.3224 | 86.3224 | 377.3099 | 690.1745 | 649.3108 | 278.656 | 419 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 18 | 5682 | 29.4 | 29.4 | 23.0708 | 21.0661 | 15 | 52 | 52 | 462.4392 | 110.997 | 14.9147 | 268.5645 | 0 | 0 | 0 | 0 | 100.2248 | 360.9873 | 410.2884 | 219.248 | 147.003 | 68.5513 | 68.5513 | 68.5513 | 68.5513 | 91.6916 | 151.8975 | 163.2803 | 119.1722 | 110.997 | 68.5513 | 68.5513 | 68.5513 | 68.5513 | 191.9164 | 512.8848 | 573.5686 | 338.4202 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 19 | 5683 | 27 | 27 | 23.0708 | 21.0661 | 15 | 60 | 60 | 108.6582 | 74.3125 | 5.7442 | 280.2965 | 0 | 0 | 0 | 0 | 2.6304 | 76.0811 | 104.9646 | 72.3612 | 17.6875 | 38.6852 | 38.6852 | 38.6852 | 38.6852 | 40.0004 | 76.7247 | 91.166 | 74.8648 | 74.3125 | 38.6852 | 38.6852 | 38.6852 | 38.6852 | 42.6307 | 152.8058 | 196.1306 | 147.226 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 20 | 5684 | 24.1 | 24.1 | 23.0708 | 21.0661 | 15 | 73 | 73 | 0.72844 | 2.805 | -3.0901 | 292.0987 | 0.12955 | 0 | 0 | 0 | 0 | 0.41264 | 0.71311 | 0.59585 | 14.195 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 2.805 | 2.8438 | 2.7142 | 2.7142 | 2.7142 | 2.7142 | 3.1269 | 3.4274 | 3.3101 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 21 | 5685 | 23.6 | 23.6 | 23.0708 | 21.0661 | 15 | 76 | 76 | 0 | 0 | -11.1923 | 304.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 22 | 5686 | 22.2 | 22.2 | 23.0708 | 21.0661 | 15 | 80 | 80 | 0 | 0 | -18.1165 | 317.9586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 23 | 5687 | 20.4 | 20.4 | 23.0708 | 21.0661 | 15 | 85 | 85 | 0 | 0 | -23.3587 | 332.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 25 | 24 | 5688 | 18.8 | 18.8 | 23.9125 | 21.8774 | 15 | 93 | 93 | 0 | 0 | -26.4156 | 348.5878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 1 | 5689 | 19.6 | 19.6 | 23.9125 | 21.8774 | 15 | 90 | 90 | 0 | 0 | -26.9256 | 5.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 2 | 5690 | 18.7 | 18.7 | 23.9125 | 21.8774 | 15 | 94 | 94 | 0 | 0 | -25.1446 | 21.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 3 | 5691 | 19.7 | 19.7 | 23.9125 | 21.8774 | 15 | 88 | 88 | 0 | 0 | -20.6646 | 36.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 4 | 5692 | 20.2 | 20.2 | 23.9125 | 21.8774 | 15 | 84 | 84 | 0 | 0 | -14.3024 | 50.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 5 | 5693 | 18.7 | 18.7 | 23.9125 | 21.8774 | 15 | 89 | 89 | 0 | 0 | -6.5773 | 63.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 6 | 5694 | 18.9 | 18.9 | 23.9125 | 21.8774 | 15 | 88 | 88 | 0 | 0 | 2.0379 | 75.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 7 | 5695 | 19.4 | 19.4 | 23.9125 | 21.8774 | 15 | 87 | 87 | 4.4085 | 32.433 | 11.1304 | 87.1517 | 1.1068 | 3.798 | 4.2645 | 2.2328 | 0 | 0 | 0 | 0 | 0.56702 | 42.5413 | 115.5861 | 128.2456 | 73.1039 | 12.5019 | 12.5019 | 12.5019 | 12.5019 | 32.433 | 43.6481 | 119.3842 | 132.51 | 75.3368 | 12.5019 | 12.5019 | 12.5019 | 12.5019 | 33 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 26 | 8 | 5696 | 21.2 | 21.2 | 23.9125 | 21.8774 | 15 | 84 | 84 | 3.9282 | 67.8809 | 20.3144 | 99.1562 | 0.19153 | 2.8575 | 3.8496 | 2.5866 | 0 | 0 | 0 | 0 | 1.1191 | 33.2178 | 50.9814 | 57.5918 | 49.1766 | 31.9416 | 31.9416 | 31.9416 | 31.9416 | 67.8809 | 33.4094 | 53.8389 | 61.4414 | 51.7633 | 31.9416 | 31.9416 | 31.9416 | 31.9416 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 9 | 5697 | 23.1 | 23.1 | 23.9125 | 21.8774 | 15 | 75 | 75 | 4.43 | 109.0881 | 29.1726 | 112.1647 | 0 | 2.4328 | 4.1015 | 3.3677 | 0.66109 | 0 | 0 | 0 | 1.9119 | 52.588 | 61.0274 | 66.8165 | 64.2707 | 54.8813 | 52.588 | 52.588 | 52.588 | 109.0881 | 52.588 | 63.4602 | 70.918 | 67.6384 | 55.5424 | 52.588 | 52.588 | 52.588 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 10 | 5698 | 26.4 | 26.4 | 23.9125 | 21.8774 | 15 | 63 | 63 | 294.2754 | 235.5957 | 37.1783 | 127.002 | 0 | 99.7171 | 237.9603 | 236.8096 | 96.939 | 0 | 0 | 0 | 164.4043 | 120.284 | 174.5187 | 249.7072 | 249.0814 | 173.0078 | 120.284 | 120.284 | 120.284 | 235.5957 | 120.284 | 274.2358 | 487.6675 | 485.8909 | 269.9468 | 120.284 | 120.284 | 120.284 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 11 | 5699 | 26.4 | 26.4 | 23.9125 | 21.8774 | 15 | 66 | 66 | 42.7085 | 277.9182 | 43.6121 | 144.4836 | 0 | 4.7347 | 27.1756 | 33.6974 | 20.4797 | 0 | 0 | 0 | 28.0818 | 124.2764 | 136.8942 | 196.6982 | 214.0786 | 178.854 | 124.2764 | 124.2764 | 124.2764 | 277.9182 | 124.2764 | 141.6288 | 223.8738 | 247.776 | 199.3338 | 124.2764 | 124.2764 | 124.2764 | 306 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 12 | 5700 | 28.1 | 28.1 | 23.9125 | 21.8774 | 15 | 60 | 60 | 253.2569 | 314.3145 | 47.565 | 164.8577 | 0 | 0 | 106.5229 | 180.8584 | 149.2495 | 30.2122 | 0 | 0 | 182.6855 | 147.1761 | 147.1761 | 230.2209 | 288.1724 | 263.5302 | 170.7294 | 147.1761 | 147.1761 | 314.3145 | 147.1761 | 147.1761 | 336.7438 | 469.0308 | 412.7797 | 200.9416 | 147.1761 | 147.1761 | 497 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 13 | 5701 | 29.8 | 29.8 | 23.9125 | 21.8774 | 15 | 54 | 54 | 672.1522 | 184.7518 | 48.2295 | 186.907 | 0 | 0 | 118.4717 | 393.3366 | 437.7903 | 225.7924 | 0 | 0 | 501.2482 | 128.508 | 128.508 | 152.1218 | 206.9078 | 215.7683 | 173.5129 | 128.508 | 128.508 | 184.7518 | 128.508 | 128.508 | 270.5934 | 600.2444 | 653.5586 | 399.3053 | 128.508 | 128.508 | 686 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 14 | 5702 | 29.4 | 29.4 | 23.9125 | 21.8774 | 15 | 60 | 60 | 609.5124 | 202.6651 | 45.4444 | 208.1513 | 0 | 0 | 0 | 250.4938 | 403.0794 | 319.5466 | 48.8277 | 0 | 444.3349 | 128.6994 | 128.6994 | 128.6994 | 187.167 | 222.782 | 203.2846 | 140.0962 | 128.6994 | 202.6651 | 128.6994 | 128.6994 | 128.6994 | 437.6608 | 625.8614 | 522.8312 | 188.924 | 128.6994 | 647 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 15 | 5703 | 29 | 29 | 23.9125 | 21.8774 | 15 | 64 | 64 | 563.7836 | 201.9669 | 39.8338 | 226.755 | 0 | 0 | 0 | 114.6484 | 348.7592 | 378.5715 | 186.6219 | 0 | 379.0331 | 122.6218 | 122.6218 | 122.6218 | 151.3242 | 209.9343 | 217.3979 | 169.3429 | 122.6218 | 201.9669 | 122.6218 | 122.6218 | 122.6218 | 265.9726 | 558.6935 | 595.9695 | 355.9648 | 122.6218 | 581 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 16 | 5704 | 27.1 | 27.1 | 23.9125 | 21.8774 | 15 | 71 | 71 | 52.3317 | 250.6705 | 32.3239 | 242.5053 | 0 | 0 | 0 | 0 | 27.5321 | 40.167 | 29.2726 | 1.2307 | 30.3295 | 115.0445 | 115.0445 | 115.0445 | 115.0445 | 162.2734 | 183.9474 | 165.259 | 117.1557 | 250.6705 | 115.0445 | 115.0445 | 115.0445 | 115.0445 | 189.8055 | 224.1144 | 194.5316 | 118.3864 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 17 | 5705 | 23.7 | 23.7 | 23.9125 | 21.8774 | 15 | 83 | 83 | 0.48742 | 38.7772 | 23.7163 | 256.1008 | 0 | 0 | 0 | 0 | 0.19015 | 0.39281 | 0.36536 | 0.12389 | 0.22282 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 38.7772 | 18.5024 | 18.5024 | 18.5024 | 18.5024 | 18.6925 | 18.8952 | 18.8678 | 18.6263 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 18 | 5706 | 21.5 | 21.5 | 23.9125 | 21.8774 | 15 | 93 | 93 | 0.024546 | 5.9923 | 14.6021 | 268.3946 | 0 | 0 | 0 | 0 | 0.0053983 | 0.019243 | 0.021815 | 0.011608 | 0.0076927 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 5.9923 | 2.7932 | 2.7932 | 2.7932 | 2.7932 | 2.7986 | 2.8125 | 2.815 | 2.8048 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 19 | 5707 | 21.5 | 21.5 | 23.9125 | 21.8774 | 15 | 93 | 93 | 6.0096 | 46.0498 | 5.4296 | 280.1353 | 0 | 0 | 0 | 0 | 0.16293 | 4.2258 | 5.8132 | 3.9954 | 0.95025 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 46.0498 | 22.4392 | 22.4392 | 22.4392 | 22.4392 | 22.6021 | 26.665 | 28.2524 | 26.4346 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 20 | 5708 | 21 | 21 | 23.9125 | 21.8774 | 15 | 95 | 95 | 0.20158 | 0.495 | -3.4115 | 291.9522 | 0.035314 | 0 | 0 | 0 | 0 | 0.11472 | 0.19755 | 0.16466 | 2.505 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.495 | 0.54964 | 0.51433 | 0.51433 | 0.51433 | 0.51433 | 0.62904 | 0.71187 | 0.67898 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 21 | 5709 | 20.6 | 20.6 | 23.9125 | 21.8774 | 15 | 96 | 96 | 0 | 0 | -11.5239 | 304.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 22 | 5710 | 19.7 | 19.7 | 23.9125 | 21.8774 | 15 | 94 | 94 | 0 | 0 | -18.4594 | 317.8698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 23 | 5711 | 18.9 | 18.9 | 23.9125 | 21.8774 | 15 | 96 | 96 | 0 | 0 | -23.71 | 332.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 26 | 24 | 5712 | 18.6 | 18.6 | 22.55 | 22.1874 | 15 | 99 | 99 | 0 | 0 | -26.7679 | 348.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 1 | 5713 | 18.5 | 18.5 | 22.55 | 22.1874 | 15 | 97 | 97 | 0 | 0 | -27.268 | 5.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 2 | 5714 | 18.5 | 18.5 | 22.55 | 22.1874 | 15 | 98 | 98 | 0 | 0 | -25.469 | 21.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 3 | 5715 | 18.5 | 18.5 | 22.55 | 22.1874 | 15 | 98 | 98 | 0 | 0 | -20.9629 | 36.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 4 | 5716 | 18.4 | 18.4 | 22.55 | 22.1874 | 15 | 97 | 97 | 0 | 0 | -14.5748 | 50.9126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 5 | 5717 | 17.8 | 17.8 | 22.55 | 22.1874 | 15 | 95 | 95 | 0 | 0 | -6.8284 | 63.7152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 6 | 5718 | 17 | 17 | 22.55 | 22.1874 | 15 | 91 | 91 | 0 | 0 | 1.8013 | 75.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 7 | 5719 | 16.6 | 16.6 | 22.55 | 22.1874 | 15 | 82 | 82 | 4.1917 | 30.4807 | 10.9003 | 87.4287 | 1.0336 | 3.6018 | 4.0601 | 2.14 | 0 | 0 | 0 | 0 | 0.51926 | 39.598 | 108.8429 | 121.1999 | 69.4306 | 11.7293 | 11.7293 | 11.7293 | 11.7293 | 30.4807 | 40.6316 | 112.4446 | 125.26 | 71.5706 | 11.7293 | 11.7293 | 11.7293 | 11.7293 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 27 | 8 | 5720 | 17.2 | 17.2 | 22.55 | 22.1874 | 15 | 79 | 79 | 84.0163 | 126.4475 | 20.0817 | 99.4436 | 3.7012 | 60.8951 | 82.4174 | 55.6607 | 0 | 0 | 0 | 0 | 23.5525 | 63.299 | 172.9704 | 214.2403 | 162.9333 | 56.2017 | 56.2017 | 56.2017 | 56.2017 | 126.4475 | 67.0003 | 233.8655 | 296.6577 | 218.594 | 56.2017 | 56.2017 | 56.2017 | 56.2017 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 9 | 5721 | 17.9 | 17.9 | 22.55 | 22.1874 | 15 | 75 | 75 | 401.9308 | 161.306 | 28.9272 | 112.4601 | 0 | 219.5151 | 372.3791 | 307.1085 | 61.9378 | 0 | 0 | 0 | 171.694 | 92.1991 | 162.9971 | 212.2988 | 191.2477 | 112.1753 | 92.1991 | 92.1991 | 92.1991 | 161.306 | 92.1991 | 382.5122 | 584.6779 | 498.3562 | 174.1131 | 92.1991 | 92.1991 | 92.1991 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 10 | 5722 | 18.2 | 18.2 | 22.55 | 22.1874 | 15 | 69 | 69 | 766.6054 | 113.9863 | 36.9096 | 127.2948 | 0 | 257.197 | 620.0646 | 619.7068 | 256.3332 | 0 | 0 | 0 | 425.0137 | 97.0037 | 131.1968 | 179.4382 | 179.3907 | 131.0819 | 97.0037 | 97.0037 | 97.0037 | 113.9863 | 97.0037 | 388.3937 | 799.5029 | 799.0975 | 387.4151 | 97.0037 | 97.0037 | 97.0037 | 539 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 11 | 5723 | 19.3 | 19.3 | 22.55 | 22.1874 | 15 | 64 | 64 | 519.4562 | 210.6059 | 43.3113 | 144.7463 | 0 | 55.6882 | 330.4219 | 411.5989 | 251.6669 | 0 | 0 | 0 | 339.3941 | 125.8941 | 142.6624 | 225.3876 | 249.8308 | 201.6736 | 125.8941 | 125.8941 | 125.8941 | 210.6059 | 125.8941 | 198.3507 | 555.8095 | 661.4297 | 453.3405 | 125.8941 | 125.8941 | 125.8941 | 550 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 12 | 5724 | 19.5 | 19.5 | 22.55 | 22.1874 | 15 | 61 | 61 | 703.6504 | 167.3031 | 47.2313 | 165.042 | 0 | 0 | 295.5267 | 504.613 | 418.1038 | 86.6751 | 0 | 0 | 504.6969 | 123.6721 | 123.6721 | 176.328 | 213.5823 | 198.1684 | 139.1155 | 123.6721 | 123.6721 | 167.3031 | 123.6721 | 123.6721 | 471.8548 | 718.1953 | 616.2722 | 225.7906 | 123.6721 | 123.6721 | 672 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 13 | 5725 | 20.1 | 20.1 | 22.55 | 22.1874 | 15 | 56 | 56 | 865.8776 | 129.8022 | 47.8758 | 186.9704 | 0 | 0 | 151.7606 | 508.9777 | 568.0425 | 294.3557 | 0 | 0 | 642.1978 | 123.7006 | 123.7006 | 137.7028 | 170.6614 | 176.111 | 150.8593 | 123.7006 | 123.7006 | 129.8022 | 123.7006 | 123.7006 | 289.4634 | 679.639 | 744.1535 | 445.215 | 123.7006 | 123.7006 | 772 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 14 | 5726 | 19.1 | 19.1 | 22.55 | 22.1874 | 15 | 63 | 63 | 463.113 | 253.2803 | 45.0901 | 208.0989 | 0 | 0 | 0 | 191.3682 | 308.3325 | 244.6798 | 37.697 | 0 | 335.7197 | 137.2066 | 137.2066 | 137.2066 | 212.319 | 258.2277 | 233.2439 | 152.0028 | 137.2066 | 253.2803 | 137.2066 | 137.2066 | 137.2066 | 403.6872 | 566.5602 | 477.9237 | 189.6998 | 137.2066 | 589 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 15 | 5727 | 19.8 | 19.8 | 22.55 | 22.1874 | 15 | 56 | 56 | 813.2422 | 125.623 | 39.4912 | 226.6285 | 0 | 0 | 0 | 166.9158 | 506.4731 | 549.3453 | 270.4185 | 0 | 543.377 | 112.7327 | 112.7327 | 112.7327 | 128.8474 | 161.6297 | 165.7687 | 138.84 | 112.7327 | 125.623 | 112.7327 | 112.7327 | 112.7327 | 295.7632 | 668.1027 | 715.114 | 409.2585 | 112.7327 | 669 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 16 | 5728 | 19.2 | 19.2 | 22.55 | 22.1874 | 15 | 57 | 57 | 738.3821 | 125.1931 | 31.9946 | 242.3447 | 0 | 0 | 0 | 0 | 391.3143 | 569.5961 | 414.2163 | 16.1942 | 424.8069 | 100.3676 | 100.3676 | 100.3676 | 100.3676 | 155.1622 | 180.1265 | 158.3691 | 102.6352 | 125.1931 | 100.3676 | 100.3676 | 100.3676 | 100.3676 | 546.4764 | 749.7226 | 572.5854 | 118.8294 | 550 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 17 | 5729 | 19.4 | 19.4 | 22.55 | 22.1874 | 15 | 57 | 57 | 434.5702 | 164.2401 | 23.3965 | 255.9297 | 0 | 0 | 0 | 0 | 171.0666 | 351.7991 | 326.4525 | 109.8745 | 196.7599 | 94.7575 | 94.7575 | 94.7575 | 94.7575 | 147.3579 | 202.9305 | 195.1368 | 128.5423 | 164.2401 | 94.7575 | 94.7575 | 94.7575 | 94.7575 | 318.4245 | 554.7296 | 521.5893 | 238.4167 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 27 | 18 | 5730 | 18.3 | 18.3 | 22.55 | 22.1874 | 15 | 65 | 65 | 313.8848 | 128.0507 | 14.286 | 268.225 | 0 | 0 | 0 | 0 | 70.0351 | 247.112 | 279.434 | 148.0674 | 96.9493 | 71.1869 | 71.1869 | 71.1869 | 71.1869 | 95.5803 | 157.2567 | 168.5146 | 122.7592 | 128.0507 | 71.1869 | 71.1869 | 71.1869 | 71.1869 | 165.6153 | 404.3687 | 447.9486 | 270.8266 | 225 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 19 | 5731 | 17.3 | 17.3 | 22.55 | 22.1874 | 15 | 63 | 63 | 403.5595 | 28.38 | 5.1116 | 279.9742 | 0 | 0 | 0 | 0 | 12.1134 | 284.968 | 390.8922 | 267.837 | 143.62 | 31.135 | 31.135 | 31.135 | 31.135 | 32.3738 | 60.2787 | 71.1115 | 58.5267 | 28.38 | 31.135 | 31.135 | 31.135 | 31.135 | 44.4873 | 345.2467 | 462.0037 | 326.3637 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 20 | 5732 | 14.7 | 14.7 | 22.55 | 22.1874 | 15 | 81 | 81 | 0 | 14 | -3.7363 | 291.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 14 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 6.6823 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 21 | 5733 | 14.7 | 14.7 | 22.55 | 22.1874 | 15 | 77 | 77 | 0 | 0 | -11.8589 | 304.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 22 | 5734 | 12.1 | 12.1 | 22.55 | 22.1874 | 15 | 89 | 89 | 0 | 0 | -18.8056 | 317.7813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 23 | 5735 | 11.6 | 11.6 | 22.55 | 22.1874 | 15 | 93 | 93 | 0 | 0 | -24.0646 | 332.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 27 | 24 | 5736 | 11.1 | 11.1 | 17.2833 | 21.1091 | 15 | 94 | 94 | 0 | 0 | -27.1232 | 348.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 1 | 5737 | 10.3 | 10.3 | 17.2833 | 21.1091 | 15 | 96 | 96 | 0 | 0 | -27.613 | 5.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 2 | 5738 | 9.9 | 9.9 | 17.2833 | 21.1091 | 15 | 97 | 97 | 0 | 0 | -25.7953 | 21.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 3 | 5739 | 8.5 | 8.5 | 17.2833 | 21.1091 | 15 | 98 | 98 | 0 | 0 | -21.2627 | 37.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 4 | 5740 | 9 | 9 | 17.2833 | 21.1091 | 15 | 99 | 99 | 0 | 0 | -14.8484 | 51.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 5 | 5741 | 8.4 | 8.4 | 17.2833 | 21.1091 | 15 | 99 | 99 | 0 | 0 | -7.0805 | 63.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 6 | 5742 | 7.8 | 7.8 | 17.2833 | 21.1091 | 15 | 99 | 99 | 0 | 0 | 1.5637 | 75.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 7 | 5743 | 11.3 | 11.3 | 17.2833 | 21.1091 | 15 | 99 | 99 | 18.5512 | 44.7905 | 10.669 | 87.7085 | 4.4904 | 15.8978 | 17.9924 | 9.5474 | 0 | 0 | 0 | 0 | 2.2095 | 61.0073 | 173.5674 | 194.2359 | 110.9055 | 16.6986 | 16.6986 | 16.6986 | 16.6986 | 44.7905 | 65.4977 | 189.4652 | 212.2284 | 120.4529 | 16.6986 | 16.6986 | 16.6986 | 16.6986 | 47 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 28 | 8 | 5744 | 15.1 | 15.1 | 17.2833 | 21.1091 | 15 | 84 | 84 | 232.0273 | 122.025 | 19.8476 | 99.7334 | 9.117 | 167.5497 | 227.834 | 154.6562 | 0 | 0 | 0 | 0 | 63.975 | 66.7203 | 140.3654 | 168.3877 | 134.3721 | 62.4824 | 62.4824 | 62.4824 | 62.4824 | 122.025 | 75.8374 | 307.9151 | 396.2217 | 289.0283 | 62.4824 | 62.4824 | 62.4824 | 62.4824 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 9 | 5745 | 16.7 | 16.7 | 17.2833 | 21.1091 | 15 | 73 | 73 | 456.0543 | 149.217 | 28.6801 | 112.7576 | 0 | 247.676 | 422.7894 | 350.2385 | 72.5226 | 0 | 0 | 0 | 192.783 | 88.8118 | 154.0483 | 200.1723 | 181.0627 | 107.9139 | 88.8118 | 88.8118 | 88.8118 | 149.217 | 88.8118 | 401.7244 | 622.9617 | 531.3012 | 180.4365 | 88.8118 | 88.8118 | 88.8118 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 10 | 5746 | 17.3 | 17.3 | 17.2833 | 21.1091 | 15 | 72 | 72 | 698.4698 | 129.7777 | 36.6387 | 127.5894 | 0 | 231.9519 | 565.0717 | 567.1802 | 237.0422 | 0 | 0 | 0 | 384.2223 | 99.1527 | 135.5796 | 187.8945 | 188.2256 | 136.379 | 99.1527 | 99.1527 | 99.1527 | 129.7777 | 99.1527 | 367.5315 | 752.9662 | 755.4058 | 373.4213 | 99.1527 | 99.1527 | 99.1527 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 11 | 5747 | 17.2 | 17.2 | 17.2833 | 21.1091 | 15 | 67 | 67 | 123.7515 | 297.6667 | 43.008 | 145.0102 | 0 | 12.8076 | 78.6856 | 98.4706 | 60.5729 | 0 | 0 | 0 | 80.3333 | 136.2443 | 149.697 | 218.893 | 239.6745 | 199.868 | 136.2443 | 136.2443 | 136.2443 | 297.6667 | 136.2443 | 162.5046 | 297.5786 | 338.1451 | 260.4409 | 136.2443 | 136.2443 | 136.2443 | 378 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 12 | 5748 | 18.3 | 18.3 | 17.2833 | 21.1091 | 15 | 64 | 64 | 126.1162 | 327.0656 | 46.895 | 165.2274 | 0 | 0 | 52.8838 | 90.8196 | 75.5546 | 16.0307 | 0 | 0 | 89.9344 | 146.2822 | 146.2822 | 218.5063 | 270.3159 | 249.4682 | 168.1755 | 146.2822 | 146.2822 | 327.0656 | 146.2822 | 146.2822 | 271.3901 | 361.1355 | 325.0227 | 184.2062 | 146.2822 | 146.2822 | 417 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 13 | 5749 | 19 | 19 | 17.2833 | 21.1091 | 15 | 64 | 64 | 537.7757 | 231.3634 | 47.5193 | 187.0356 | 0 | 0 | 93.702 | 317.5171 | 355.335 | 185.0025 | 0 | 0 | 396.6366 | 135.9826 | 135.9826 | 165.6934 | 236.6602 | 248.6514 | 194.6428 | 135.9826 | 135.9826 | 231.3634 | 135.9826 | 135.9826 | 259.3954 | 554.1773 | 603.9864 | 379.6453 | 135.9826 | 135.9826 | 628 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 14 | 5750 | 19.1 | 19.1 | 17.2833 | 21.1091 | 15 | 65 | 65 | 259.4388 | 313.0016 | 44.7327 | 208.0485 | 0 | 0 | 0 | 107.7842 | 173.8907 | 138.1344 | 21.4608 | 0 | 186.9984 | 145.676 | 145.676 | 145.676 | 228.1602 | 278.7497 | 251.3864 | 162.0993 | 145.676 | 313.0016 | 145.676 | 145.676 | 145.676 | 335.9444 | 452.6404 | 389.5207 | 183.5602 | 145.676 | 500 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 15 | 5751 | 18.9 | 18.9 | 17.2833 | 21.1091 | 15 | 63 | 63 | 438.5869 | 239.7944 | 39.1451 | 226.504 | 0 | 0 | 0 | 90.8422 | 274.9772 | 298.0342 | 146.5069 | 0 | 291.2056 | 129.2802 | 129.2802 | 129.2802 | 165.232 | 238.1054 | 247.2305 | 187.2619 | 129.2802 | 239.7944 | 129.2802 | 129.2802 | 129.2802 | 256.0741 | 513.0826 | 545.2647 | 333.7688 | 129.2802 | 531 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 16 | 5752 | 19.7 | 19.7 | 17.2833 | 21.1091 | 15 | 60 | 60 | 870.8333 | 99.7315 | 31.6619 | 242.1854 | 0 | 0 | 0 | 0 | 464.8628 | 675.1419 | 489.932 | 17.7266 | 497.2685 | 98.8322 | 98.8322 | 98.8322 | 98.8322 | 135.2134 | 151.6703 | 137.1754 | 100.2195 | 99.7315 | 98.8322 | 98.8322 | 98.8322 | 98.8322 | 600.0762 | 826.8122 | 627.1074 | 117.9461 | 597 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 17 | 5753 | 19.1 | 19.1 | 17.2833 | 21.1091 | 15 | 57 | 57 | 495.5262 | 149.8338 | 23.0732 | 255.7593 | 0 | 0 | 0 | 0 | 196.8039 | 402.9417 | 373.0417 | 124.619 | 222.1662 | 91.5216 | 91.5216 | 91.5216 | 91.5216 | 141.5888 | 194.0306 | 186.424 | 123.2249 | 149.8338 | 91.5216 | 91.5216 | 91.5216 | 91.5216 | 338.3927 | 596.9723 | 559.4657 | 247.8438 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 28 | 18 | 5754 | 18.7 | 18.7 | 17.2833 | 21.1091 | 15 | 57 | 57 | 772.6599 | 61.887 | 13.9665 | 268.0558 | 0 | 0 | 0 | 0 | 174.8662 | 610.8507 | 689.0071 | 363.5525 | 235.113 | 57.1736 | 57.1736 | 57.1736 | 57.1736 | 70.2376 | 102.8095 | 108.6485 | 84.3341 | 61.887 | 57.1736 | 57.1736 | 57.1736 | 57.1736 | 245.1038 | 713.6602 | 797.6556 | 447.8867 | 297 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 19 | 5755 | 17.2 | 17.2 | 17.2833 | 21.1091 | 15 | 64 | 64 | 436.233 | 45.2857 | 4.7902 | 279.8131 | 0 | 0 | 0 | 0 | 14.3624 | 309.3277 | 423.093 | 289.0162 | 82.7143 | 32.4163 | 32.4163 | 32.4163 | 32.4163 | 34.7484 | 82.6439 | 101.1168 | 79.3458 | 45.2857 | 32.4163 | 32.4163 | 32.4163 | 32.4163 | 49.1108 | 391.9716 | 524.2098 | 368.362 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 20 | 5756 | 14.9 | 14.9 | 17.2833 | 21.1091 | 15 | 76 | 76 | 0 | 17 | -4.0643 | 291.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 17 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 8.2058 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 21 | 5757 | 12.6 | 12.6 | 17.2833 | 21.1091 | 15 | 89 | 89 | 0 | 0 | -12.1972 | 304.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 22 | 5758 | 10.9 | 10.9 | 17.2833 | 21.1091 | 15 | 92 | 92 | 0 | 0 | -19.155 | 317.6931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 23 | 5759 | 11 | 11 | 17.2833 | 21.1091 | 15 | 95 | 95 | 0 | 0 | -24.4222 | 332.5785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 28 | 24 | 5760 | 9.6 | 9.6 | 14.1875 | 19.3969 | 15 | 97 | 97 | 0 | 0 | -27.4814 | 348.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 1 | 5761 | 9.5 | 9.5 | 14.1875 | 19.3969 | 15 | 98 | 98 | 0 | 0 | -27.9605 | 5.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 2 | 5762 | 8.4 | 8.4 | 14.1875 | 19.3969 | 15 | 99 | 99 | 0 | 0 | -26.1235 | 21.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 3 | 5763 | 8.7 | 8.7 | 14.1875 | 19.3969 | 15 | 99 | 99 | 0 | 0 | -21.5638 | 37.3511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 4 | 5764 | 8.7 | 8.7 | 14.1875 | 19.3969 | 15 | 99 | 99 | 0 | 0 | -15.1232 | 51.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 5 | 5765 | 8.4 | 8.4 | 14.1875 | 19.3969 | 15 | 99 | 99 | 0 | 0 | -7.3336 | 64.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 6 | 5766 | 8.1 | 8.1 | 14.1875 | 19.3969 | 15 | 99 | 99 | 0 | 0 | 1.3251 | 76.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 7 | 5767 | 10.5 | 10.5 | 14.1875 | 19.3969 | 15 | 100 | 100 | 5.4023 | 41.2017 | 10.4366 | 87.991 | 1.2829 | 4.6168 | 5.2463 | 2.8026 | 0 | 0 | 0 | 0 | 0.79829 | 80.8746 | 260.2537 | 294.1225 | 162.6409 | 11.852 | 11.852 | 11.852 | 11.852 | 41.2017 | 82.1575 | 264.8705 | 299.3687 | 165.4435 | 11.852 | 11.852 | 11.852 | 11.852 | 42 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 29 | 8 | 5768 | 13.6 | 13.6 | 14.1875 | 19.3969 | 15 | 91 | 91 | 100.9699 | 138.3666 | 19.6121 | 100.0257 | 3.4811 | 72.6336 | 99.2384 | 67.7106 | 0 | 0 | 0 | 0 | 30.6334 | 67.0258 | 210.7676 | 266.0686 | 200.5344 | 59.7899 | 59.7899 | 59.7899 | 59.7899 | 138.3666 | 70.507 | 283.4012 | 365.307 | 268.245 | 59.7899 | 59.7899 | 59.7899 | 59.7899 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 9 | 5769 | 15.5 | 15.5 | 14.1875 | 19.3969 | 15 | 82 | 82 | 73.799 | 199.9985 | 28.4313 | 113.0571 | 0 | 39.8481 | 68.4561 | 56.9634 | 12.1023 | 0 | 0 | 0 | 33.0015 | 89.1818 | 167.5001 | 223.7268 | 201.1388 | 112.968 | 89.1818 | 89.1818 | 89.1818 | 199.9985 | 89.1818 | 207.3483 | 292.1829 | 258.1023 | 125.0703 | 89.1818 | 89.1818 | 89.1818 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 10 | 5770 | 17 | 17 | 14.1875 | 19.3969 | 15 | 73 | 73 | 568.9387 | 170.0742 | 36.3658 | 127.8855 | 0 | 186.9598 | 460.3502 | 464.0737 | 195.9491 | 0 | 0 | 0 | 323.9258 | 110.2958 | 154.895 | 220.1121 | 221.0004 | 157.0394 | 110.2958 | 110.2958 | 110.2958 | 170.0742 | 110.2958 | 341.8548 | 680.4623 | 685.074 | 352.9884 | 110.2958 | 110.2958 | 110.2958 | 494 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 11 | 5771 | 18 | 18 | 14.1875 | 19.3969 | 15 | 68 | 68 | 717.097 | 150.5964 | 42.7023 | 145.2752 | 0 | 71.5174 | 455.739 | 572.9949 | 354.5981 | 0 | 0 | 0 | 474.4036 | 115.6307 | 127.3966 | 190.6083 | 209.8991 | 173.9687 | 115.6307 | 115.6307 | 115.6307 | 150.5964 | 115.6307 | 198.9141 | 646.3474 | 782.894 | 528.5669 | 115.6307 | 115.6307 | 115.6307 | 625 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 12 | 5772 | 18.8 | 18.8 | 14.1875 | 19.3969 | 15 | 66 | 66 | 778.5305 | 144.415 | 46.5562 | 165.4138 | 0 | 0 | 325.9066 | 562.9562 | 470.2336 | 102.0546 | 0 | 0 | 558.585 | 120.69 | 120.69 | 168.2175 | 202.7869 | 189.265 | 135.5728 | 120.69 | 120.69 | 144.415 | 120.69 | 120.69 | 494.1242 | 765.7431 | 659.4986 | 237.6274 | 120.69 | 120.69 | 703 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 13 | 5773 | 19.6 | 19.6 | 14.1875 | 19.3969 | 15 | 60 | 60 | 779.758 | 147.2336 | 47.16 | 187.1024 | 0 | 0 | 135.0337 | 462.4103 | 518.9131 | 271.4437 | 0 | 0 | 571.7664 | 123.303 | 123.303 | 138.458 | 175.1999 | 181.5413 | 153.7675 | 123.303 | 123.303 | 147.2336 | 123.303 | 123.303 | 273.4917 | 637.6102 | 700.4545 | 425.2113 | 123.303 | 123.303 | 719 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 14 | 5774 | 20.6 | 20.6 | 14.1875 | 19.3969 | 15 | 56 | 56 | 876.7069 | 123.4756 | 44.3722 | 208.0003 | 0 | 0 | 0 | 366.168 | 591.5458 | 470.4041 | 73.706 | 0 | 620.5244 | 119.1263 | 119.1263 | 119.1263 | 151.2931 | 171.0918 | 160.4499 | 125.6011 | 119.1263 | 123.4756 | 119.1263 | 119.1263 | 119.1263 | 517.4611 | 762.6377 | 630.854 | 199.3071 | 119.1263 | 744 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 15 | 5775 | 20.5 | 20.5 | 14.1875 | 19.3969 | 15 | 58 | 58 | 452.3401 | 228.2172 | 38.7957 | 226.3814 | 0 | 0 | 0 | 94.5333 | 285.4899 | 309.2104 | 151.7997 | 0 | 290.7828 | 125.2281 | 125.2281 | 125.2281 | 160.3141 | 231.1876 | 239.9914 | 181.5685 | 125.2281 | 228.2172 | 125.2281 | 125.2281 | 125.2281 | 254.8474 | 516.6775 | 549.2019 | 333.3681 | 125.2281 | 519 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 16 | 5776 | 20.5 | 20.5 | 14.1875 | 19.3969 | 15 | 61 | 61 | 262.8846 | 235.2814 | 31.3257 | 242.0275 | 0 | 0 | 0 | 0 | 141.3431 | 204.8286 | 148.3283 | 4.9393 | 142.7186 | 116.5104 | 116.5104 | 116.5104 | 116.5104 | 202.2507 | 240.7617 | 206.488 | 119.5067 | 235.2814 | 116.5104 | 116.5104 | 116.5104 | 116.5104 | 343.5938 | 445.5903 | 354.8163 | 124.446 | 378 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 17 | 5777 | 20 | 20 | 14.1875 | 19.3969 | 15 | 57 | 57 | 348.5521 | 166.4215 | 22.7465 | 255.5897 | 0 | 0 | 0 | 0 | 139.6554 | 284.6904 | 262.9576 | 87.1878 | 144.5785 | 90.5341 | 90.5341 | 90.5341 | 90.5341 | 144.5217 | 200.5888 | 192.1874 | 124.2389 | 166.4215 | 90.5341 | 90.5341 | 90.5341 | 90.5341 | 284.1771 | 485.2792 | 455.145 | 211.4267 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 29 | 18 | 5778 | 19.3 | 19.3 | 14.1875 | 19.3969 | 15 | 61 | 61 | 190.7304 | 121.0204 | 13.6436 | 267.8869 | 0 | 0 | 0 | 0 | 43.7742 | 151.4174 | 170.3623 | 89.5113 | 50.9796 | 63.5919 | 63.5919 | 63.5919 | 63.5919 | 87.8403 | 147.4683 | 157.9627 | 113.176 | 121.0204 | 63.5919 | 63.5919 | 63.5919 | 63.5919 | 131.6145 | 298.8857 | 328.325 | 202.6873 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 19 | 5779 | 17.9 | 17.9 | 14.1875 | 19.3969 | 15 | 69 | 69 | 201.7019 | 49.7324 | 4.4656 | 279.6521 | 0 | 0 | 0 | 0 | 7.2275 | 143.6165 | 195.877 | 133.3953 | 22.2676 | 28.3062 | 28.3062 | 28.3062 | 28.3062 | 30.9366 | 80.5754 | 99.5956 | 76.8554 | 49.7324 | 28.3062 | 28.3062 | 28.3062 | 28.3062 | 38.1641 | 224.192 | 295.4726 | 210.2507 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 20 | 5780 | 16.2 | 16.2 | 14.1875 | 19.3969 | 15 | 76 | 76 | 0 | 11 | -4.3956 | 291.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 11 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 5.2222 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 21 | 5781 | 14.6 | 14.6 | 14.1875 | 19.3969 | 15 | 84 | 84 | 0 | 0 | -12.5385 | 304.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 22 | 5782 | 14.5 | 14.5 | 14.1875 | 19.3969 | 15 | 83 | 83 | 0 | 0 | -19.5075 | 317.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 23 | 5783 | 14.4 | 14.4 | 14.1875 | 19.3969 | 15 | 83 | 83 | 0 | 0 | -24.7829 | 332.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 29 | 24 | 5784 | 12.7 | 12.7 | 14.8333 | 18.1137 | 15 | 88 | 88 | 0 | 0 | -27.8424 | 348.7059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 1 | 5785 | 12.3 | 12.3 | 14.8333 | 18.1137 | 15 | 89 | 89 | 0 | 0 | -28.3103 | 5.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 2 | 5786 | 12.1 | 12.1 | 14.8333 | 18.1137 | 15 | 91 | 91 | 0 | 0 | -26.4536 | 22.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 3 | 5787 | 11.9 | 11.9 | 14.8333 | 18.1137 | 15 | 92 | 92 | 0 | 0 | -21.8664 | 37.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 4 | 5788 | 10.6 | 10.6 | 14.8333 | 18.1137 | 15 | 95 | 95 | 0 | 0 | -15.3989 | 51.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 5 | 5789 | 10.9 | 10.9 | 14.8333 | 18.1137 | 15 | 95 | 95 | 0 | 0 | -7.5876 | 64.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 6 | 5790 | 10.7 | 10.7 | 14.8333 | 18.1137 | 15 | 94 | 94 | 0 | 0 | 1.0857 | 76.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 7 | 5791 | 12.3 | 12.3 | 14.8333 | 18.1137 | 15 | 93 | 93 | 4.2392 | 35.394 | 10.2032 | 88.2761 | 0.98696 | 3.6126 | 4.122 | 2.2168 | 0 | 0 | 0 | 0 | 0.60599 | 63.1206 | 202.0178 | 228.9664 | 128.1803 | 10.9096 | 10.9096 | 10.9096 | 10.9096 | 35.394 | 64.1076 | 205.6304 | 233.0884 | 130.397 | 10.9096 | 10.9096 | 10.9096 | 10.9096 | 36 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 30 | 8 | 5792 | 14.4 | 14.4 | 14.8333 | 18.1137 | 15 | 86 | 86 | 42.3459 | 126.3502 | 19.3753 | 100.3203 | 1.2537 | 30.3427 | 41.6574 | 28.5697 | 0 | 0 | 0 | 0 | 12.6498 | 59.6039 | 184.3256 | 232.8381 | 176.7234 | 54.2284 | 54.2284 | 54.2284 | 54.2284 | 126.3502 | 60.8577 | 214.6683 | 274.4954 | 205.2931 | 54.2284 | 54.2284 | 54.2284 | 54.2284 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 9 | 5793 | 17.1 | 17.1 | 14.8333 | 18.1137 | 15 | 72 | 72 | 185.2676 | 200.9893 | 28.1808 | 113.3586 | 0 | 99.445 | 171.9475 | 143.7255 | 31.311 | 0 | 0 | 0 | 82.0107 | 94.584 | 186.7161 | 253.8869 | 227.7402 | 123.5925 | 94.584 | 94.584 | 94.584 | 200.9893 | 94.584 | 286.1611 | 425.8344 | 371.4658 | 154.9036 | 94.584 | 94.584 | 94.584 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 10 | 5794 | 18.2 | 18.2 | 14.8333 | 18.1137 | 15 | 70 | 70 | 272.1811 | 243.2307 | 36.0909 | 128.183 | 0 | 88.4806 | 220.2539 | 223.0055 | 95.1235 | 0 | 0 | 0 | 153.7693 | 121.008 | 171.4663 | 246.6133 | 248.1825 | 175.2545 | 121.008 | 121.008 | 121.008 | 243.2307 | 121.008 | 259.9469 | 466.8673 | 471.188 | 270.378 | 121.008 | 121.008 | 121.008 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 11 | 5795 | 19.5 | 19.5 | 14.8333 | 18.1137 | 15 | 66 | 66 | 188.6478 | 298.0106 | 42.3944 | 145.541 | 0 | 18.0947 | 119.8264 | 151.3655 | 94.2367 | 0 | 0 | 0 | 123.9894 | 138.9561 | 155.1895 | 246.4568 | 274.7517 | 223.4993 | 138.9561 | 138.9561 | 138.9561 | 298.0106 | 138.9561 | 173.2842 | 366.2833 | 426.1172 | 317.736 | 138.9561 | 138.9561 | 138.9561 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 12 | 5796 | 19.9 | 19.9 | 14.8333 | 18.1137 | 15 | 67 | 67 | 52.8221 | 309.3256 | 46.2149 | 165.601 | 0 | 0 | 22.0726 | 38.3519 | 32.1652 | 7.1365 | 0 | 0 | 37.6744 | 137.5997 | 137.5997 | 188.0495 | 225.2579 | 211.1174 | 153.9112 | 137.5997 | 137.5997 | 309.3256 | 137.5997 | 137.5997 | 210.1221 | 263.6098 | 243.2825 | 161.0477 | 137.5997 | 137.5997 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 13 | 5797 | 20.1 | 20.1 | 14.8333 | 18.1137 | 15 | 66 | 66 | 8.7311 | 237.6349 | 46.798 | 187.1706 | 0 | 0 | 1.5024 | 5.2001 | 5.8517 | 3.0755 | 0 | 0 | 6.3651 | 115.4908 | 115.4908 | 119.1314 | 128.092 | 129.671 | 122.9434 | 115.4908 | 115.4908 | 237.6349 | 115.4908 | 115.4908 | 120.6338 | 133.2921 | 135.5227 | 126.0189 | 115.4908 | 115.4908 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 14 | 5798 | 19.9 | 19.9 | 14.8333 | 18.1137 | 15 | 72 | 72 | 9.754 | 235.1378 | 44.0088 | 207.9541 | 0 | 0 | 0 | 4.0953 | 6.6251 | 5.274 | 0.8335 | 0 | 6.8622 | 114.7877 | 114.7877 | 114.7877 | 122.7841 | 127.7238 | 125.0857 | 116.4152 | 114.7877 | 235.1378 | 114.7877 | 114.7877 | 114.7877 | 126.8794 | 134.349 | 130.3598 | 117.2487 | 114.7877 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 15 | 5799 | 19.3 | 19.3 | 14.8333 | 18.1137 | 15 | 80 | 80 | 2.6861 | 126.2849 | 38.4432 | 226.2606 | 0 | 0 | 0 | 0.56631 | 1.7065 | 1.847 | 0.9056 | 0 | 1.7151 | 62.6867 | 62.6867 | 62.6867 | 62.6867 | 62.6867 | 62.6867 | 62.6867 | 62.6867 | 126.2849 | 62.6867 | 62.6867 | 62.6867 | 63.253 | 64.3932 | 64.5337 | 63.5923 | 62.6867 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 16 | 5800 | 20.5 | 20.5 | 14.8333 | 18.1137 | 15 | 71 | 71 | 9.2801 | 178.003 | 30.9863 | 241.8708 | 0 | 0 | 0 | 0 | 5.0252 | 7.2666 | 5.2514 | 0.1599 | 4.997 | 88.2029 | 88.2029 | 88.2029 | 88.2029 | 92.6779 | 94.6739 | 92.8793 | 88.3453 | 178.003 | 88.2029 | 88.2029 | 88.2029 | 88.2029 | 97.7031 | 101.9405 | 98.1306 | 88.5052 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 17 | 5801 | 19.4 | 19.4 | 14.8333 | 18.1137 | 15 | 74 | 74 | 158.8516 | 187.8322 | 22.4166 | 255.4209 | 0 | 0 | 0 | 0 | 64.2045 | 130.3209 | 120.097 | 39.5219 | 65.1678 | 92.7369 | 92.7369 | 92.7369 | 92.7369 | 133.7569 | 175.9983 | 169.4664 | 117.9873 | 187.8322 | 92.7369 | 92.7369 | 92.7369 | 92.7369 | 197.9614 | 306.3192 | 289.5634 | 157.5092 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 30 | 18 | 5802 | 18.4 | 18.4 | 14.8333 | 18.1137 | 15 | 78 | 78 | 5.4528 | 73.5682 | 13.3176 | 267.7183 | 0 | 0 | 0 | 0 | 1.2689 | 4.3468 | 4.8785 | 2.5524 | 1.4318 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 73.5682 | 36.1383 | 36.1383 | 36.1383 | 36.1383 | 37.4072 | 40.4852 | 41.0168 | 38.6907 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 19 | 5803 | 17.7 | 17.7 | 14.8333 | 18.1137 | 15 | 80 | 80 | 9.4212 | 35.0057 | 4.1378 | 279.4911 | 0 | 0 | 0 | 0 | 0.365 | 6.7356 | 9.1606 | 6.2194 | 0.99429 | 18.0886 | 18.0886 | 18.0886 | 18.0886 | 18.4004 | 23.8426 | 25.9142 | 23.4017 | 35.0057 | 18.0886 | 18.0886 | 18.0886 | 18.0886 | 18.7654 | 30.5783 | 35.0748 | 29.6211 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 20 | 5804 | 17 | 17 | 14.8333 | 18.1137 | 15 | 85 | 85 | 0 | 3 | -4.7299 | 291.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 3 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 1.3875 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 21 | 5805 | 16.6 | 16.6 | 14.8333 | 18.1137 | 15 | 88 | 88 | 0 | 0 | -12.8829 | 303.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 22 | 5806 | 16.1 | 16.1 | 14.8333 | 18.1137 | 15 | 92 | 92 | 0 | 0 | -19.863 | 317.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 23 | 5807 | 16.3 | 16.3 | 14.8333 | 18.1137 | 15 | 89 | 89 | 0 | 0 | -25.1465 | 332.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 30 | 24 | 5808 | 16.2 | 16.2 | 16.1417 | 17.3606 | 15 | 82 | 82 | 0 | 0 | -28.2061 | 348.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 1 | 5809 | 15.6 | 15.6 | 16.1417 | 17.3606 | 15 | 84 | 84 | 0 | 0 | -28.6625 | 5.5886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 2 | 5810 | 14.3 | 14.3 | 16.1417 | 17.3606 | 15 | 88 | 88 | 0 | 0 | -26.7853 | 22.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 3 | 5811 | 14 | 14 | 16.1417 | 17.3606 | 15 | 91 | 91 | 0 | 0 | -22.1701 | 37.7942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 4 | 5812 | 14 | 14 | 16.1417 | 17.3606 | 15 | 92 | 92 | 0 | 0 | -15.6756 | 51.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 5 | 5813 | 14.2 | 14.2 | 16.1417 | 17.3606 | 15 | 93 | 93 | 0 | 0 | -7.8424 | 64.7658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 6 | 5814 | 14.3 | 14.3 | 16.1417 | 17.3606 | 15 | 94 | 94 | 0 | 0 | 0.84533 | 76.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 7 | 5815 | 14.6 | 14.6 | 16.1417 | 17.3606 | 15 | 95 | 95 | 1.0125 | 16.8602 | 9.9687 | 88.5637 | 0.23097 | 0.86033 | 0.98573 | 0.5337 | 0 | 0 | 0 | 0 | 0.13982 | 15.3437 | 37.3876 | 41.7796 | 25.9471 | 7.2541 | 7.2541 | 7.2541 | 7.2541 | 16.8602 | 15.5747 | 38.2479 | 42.7654 | 26.4808 | 7.2541 | 7.2541 | 7.2541 | 7.2541 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2001 | 8 | 31 | 8 | 5816 | 15.4 | 15.4 | 16.1417 | 17.3606 | 15 | 93 | 93 | 3.6793 | 67.9182 | 19.1372 | 100.617 | 0.09083 | 2.6258 | 3.6226 | 2.4974 | 0 | 0 | 0 | 0 | 1.0818 | 32.2613 | 60.5006 | 71.605 | 59.0697 | 31.2495 | 31.2495 | 31.2495 | 31.2495 | 67.9182 | 32.3521 | 63.1265 | 75.2277 | 61.5671 | 31.2495 | 31.2495 | 31.2495 | 31.2495 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 9 | 5817 | 15.9 | 15.9 | 16.1417 | 17.3606 | 15 | 92 | 92 | 2.7572 | 87.7921 | 27.9287 | 113.6618 | 0 | 1.471 | 2.5602 | 2.1497 | 0.47992 | 0 | 0 | 0 | 1.2079 | 43.3722 | 44.922 | 46.0695 | 45.637 | 43.8778 | 43.3722 | 43.3722 | 43.3722 | 87.7921 | 43.3722 | 46.393 | 48.6298 | 47.7867 | 44.3577 | 43.3722 | 43.3722 | 43.3722 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 10 | 5818 | 17.1 | 17.1 | 16.1417 | 17.3606 | 15 | 91 | 91 | 7.6374 | 176.7192 | 35.814 | 128.4818 | 0 | 2.4554 | 6.1806 | 6.2853 | 2.7082 | 0 | 0 | 0 | 4.2808 | 82.694 | 94.871 | 113.3457 | 113.865 | 96.1248 | 82.694 | 82.694 | 82.694 | 176.7192 | 82.694 | 97.3264 | 119.5263 | 120.1503 | 98.833 | 82.694 | 82.694 | 82.694 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 11 | 5819 | 18.4 | 18.4 | 16.1417 | 17.3606 | 15 | 82 | 82 | 39.6852 | 274.0899 | 42.0842 | 145.8076 | 0 | 3.6532 | 25.1919 | 31.9735 | 20.0255 | 0 | 0 | 0 | 25.9101 | 122.3694 | 132.977 | 195.5176 | 215.2089 | 180.5162 | 122.3694 | 122.3694 | 122.3694 | 274.0899 | 122.3694 | 136.6302 | 220.7094 | 247.1824 | 200.5417 | 122.3694 | 122.3694 | 122.3694 | 300 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 12 | 5820 | 19.1 | 19.1 | 16.1417 | 17.3606 | 15 | 74 | 74 | 189.7875 | 321.4554 | 45.8711 | 165.7889 | 0 | 0 | 79.1555 | 138.3544 | 116.5072 | 26.4116 | 0 | 0 | 134.5446 | 148.8484 | 148.8484 | 219.8522 | 272.9546 | 253.3572 | 172.5401 | 148.8484 | 148.8484 | 321.4554 | 148.8484 | 148.8484 | 299.0076 | 411.3089 | 369.8644 | 198.9517 | 148.8484 | 148.8484 | 456 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 13 | 5821 | 18.5 | 18.5 | 16.1417 | 17.3606 | 15 | 78 | 78 | 48.7187 | 311.6923 | 46.4335 | 187.2402 | 0 | 0 | 8.3276 | 29.1406 | 32.8835 | 17.3637 | 0 | 0 | 35.3077 | 138.7705 | 138.7705 | 158.409 | 207.4915 | 216.3181 | 179.7184 | 138.7705 | 138.7705 | 311.6923 | 138.7705 | 138.7705 | 166.7366 | 236.6321 | 249.2016 | 197.0821 | 138.7705 | 138.7705 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 14 | 5822 | 17.6 | 17.6 | 16.1417 | 17.3606 | 15 | 83 | 83 | 11.521 | 241.9445 | 43.6425 | 207.9098 | 0 | 0 | 0 | 4.8622 | 7.8769 | 6.2774 | 1.0007 | 0 | 8.0555 | 117.4594 | 117.4594 | 117.4594 | 127.0407 | 132.9813 | 129.8294 | 119.4313 | 117.4594 | 241.9445 | 117.4594 | 117.4594 | 117.4594 | 131.9029 | 140.8582 | 136.1068 | 120.432 | 117.4594 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 15 | 5823 | 17.4 | 17.4 | 16.1417 | 17.3606 | 15 | 88 | 88 | 5.2638 | 174.6621 | 38.0876 | 226.1416 | 0 | 0 | 0 | 1.1194 | 3.3661 | 3.641 | 1.783 | 0 | 3.3379 | 88.2049 | 88.2049 | 88.2049 | 88.3479 | 88.6349 | 88.67 | 88.4327 | 88.2049 | 174.6621 | 88.2049 | 88.2049 | 88.2049 | 89.4674 | 92.001 | 92.311 | 90.2157 | 88.2049 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 16 | 5824 | 17.8 | 17.8 | 16.1417 | 17.3606 | 15 | 88 | 88 | 65.9455 | 236.7857 | 30.6437 | 241.7154 | 0 | 0 | 0 | 0 | 35.9629 | 51.8933 | 37.4253 | 1.0341 | 35.2143 | 110.0609 | 110.0609 | 110.0609 | 110.0609 | 156.249 | 176.7088 | 158.1272 | 111.389 | 236.7857 | 110.0609 | 110.0609 | 110.0609 | 110.0609 | 192.2119 | 228.6021 | 195.5525 | 112.4231 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 17 | 5825 | 17.3 | 17.3 | 16.1417 | 17.3606 | 15 | 90 | 90 | 92.7011 | 184.3965 | 22.0834 | 255.2528 | 0 | 0 | 0 | 0 | 37.7923 | 76.3856 | 70.2332 | 22.9392 | 37.6035 | 88.6086 | 88.6086 | 88.6086 | 88.6086 | 129.2968 | 170.8473 | 164.2235 | 113.3055 | 184.3965 | 88.6086 | 88.6086 | 88.6086 | 88.6086 | 167.0891 | 247.2329 | 234.4567 | 136.2447 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2001 | 8 | 31 | 18 | 5826 | 16.3 | 16.3 | 16.1417 | 17.3606 | 15 | 94 | 94 | 3.3805 | 57.1284 | 12.9885 | 267.55 | 0 | 0 | 0 | 0 | 0.79739 | 2.7059 | 3.0293 | 1.5782 | 0.87162 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 57.1284 | 27.7201 | 27.7201 | 27.7201 | 27.7201 | 28.5174 | 30.4259 | 30.7493 | 29.2982 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 19 | 5827 | 15.5 | 15.5 | 16.1417 | 17.3606 | 15 | 94 | 94 | 1.9063 | 16.8082 | 3.8071 | 279.3301 | 0 | 0 | 0 | 0 | 0.079402 | 1.3684 | 1.8558 | 1.2561 | 0.19184 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 16.8082 | 7.9245 | 7.9245 | 7.9245 | 7.9245 | 8.0039 | 9.2929 | 9.7803 | 9.1806 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 20 | 5828 | 15 | 15 | 16.1417 | 17.3606 | 15 | 97 | 97 | 0 | 0 | -5.0672 | 291.2186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 21 | 5829 | 13.8 | 13.8 | 16.1417 | 17.3606 | 15 | 96 | 96 | 0 | 0 | -13.2302 | 303.7657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 22 | 5830 | 13.2 | 13.2 | 16.1417 | 17.3606 | 15 | 98 | 98 | 0 | 0 | -20.2213 | 317.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 23 | 5831 | 13 | 13 | 16.1417 | 17.3606 | 15 | 97 | 97 | 0 | 0 | -25.5129 | 332.4748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2001 | 8 | 31 | 24 | 5832 | 12.3 | 12.3 | 15.6083 | 16.5727 | 15 | 98 | 98 | 0 | 0 | -28.5723 | 348.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 1 | 5833 | 10.8 | 10.8 | 15.6083 | 16.5727 | 15 | 97 | 97 | 0 | 0 | -29.0169 | 5.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 2 | 5834 | 10.3 | 10.3 | 15.6083 | 16.5727 | 15 | 99 | 99 | 0 | 0 | -27.1187 | 22.4801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 3 | 5835 | 9.8 | 9.8 | 15.6083 | 16.5727 | 15 | 99 | 99 | 0 | 0 | -22.4751 | 38.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 4 | 5836 | 8.9 | 8.9 | 15.6083 | 16.5727 | 15 | 99 | 99 | 0 | 0 | -15.9532 | 52.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 5 | 5837 | 8 | 8 | 15.6083 | 16.5727 | 15 | 98 | 98 | 0 | 0 | -8.098 | 65.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 6 | 5838 | 8.2 | 8.2 | 15.6083 | 16.5727 | 15 | 97 | 97 | 0 | 0 | 0.60413 | 77.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 7 | 5839 | 9.9 | 9.9 | 15.6083 | 16.5727 | 15 | 95 | 95 | 3.6173 | 30.5182 | 9.7332 | 88.8537 | 0.80789 | 3.0643 | 3.5257 | 1.9218 | 0 | 0 | 0 | 0 | 0.48179 | 52.7344 | 173.8353 | 198.598 | 112.5168 | 9.3756 | 9.3756 | 9.3756 | 9.3756 | 30.5182 | 53.5423 | 176.8996 | 202.1237 | 114.4386 | 9.3756 | 9.3756 | 9.3756 | 9.3756 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 1 | 8 | 5840 | 12.2 | 12.2 | 15.6083 | 16.5727 | 15 | 79 | 79 | 58.8768 | 126.9688 | 18.8978 | 100.9158 | 1.1609 | 41.8456 | 58.0177 | 40.2039 | 0 | 0 | 0 | 0 | 17.0312 | 58.1416 | 196.4195 | 251.3848 | 190.8397 | 54.1961 | 54.1961 | 54.1961 | 54.1961 | 126.9688 | 59.3024 | 238.2651 | 309.4026 | 231.0436 | 54.1961 | 54.1961 | 54.1961 | 54.1961 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 9 | 5841 | 16.2 | 16.2 | 15.6083 | 16.5727 | 15 | 60 | 60 | 463.9542 | 151.8864 | 27.675 | 113.9667 | 0 | 245.9899 | 431.0039 | 363.5417 | 83.1217 | 0 | 0 | 0 | 201.1136 | 90.4893 | 152.9988 | 200.0135 | 182.8704 | 111.6117 | 90.4893 | 90.4893 | 90.4893 | 151.8864 | 90.4893 | 398.9887 | 631.0174 | 546.4121 | 194.7334 | 90.4893 | 90.4893 | 90.4893 | 353 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 10 | 5842 | 15.2 | 15.2 | 15.6083 | 16.5727 | 15 | 62 | 62 | 119.9258 | 255.3213 | 35.5351 | 128.7817 | 0 | 38.1184 | 97.049 | 99.1295 | 43.1414 | 0 | 0 | 0 | 66.6787 | 116.4862 | 160.4074 | 228.309 | 230.7064 | 166.1951 | 116.4862 | 116.4862 | 116.4862 | 255.3213 | 116.4862 | 198.5258 | 325.358 | 329.8359 | 209.3365 | 116.4862 | 116.4862 | 116.4862 | 322 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 11 | 5843 | 15.9 | 15.9 | 15.6083 | 16.5727 | 15 | 62 | 62 | 172.5477 | 296.1074 | 41.7719 | 146.0748 | 0 | 15.209 | 109.4567 | 139.5861 | 87.9479 | 0 | 0 | 0 | 111.8926 | 137.0001 | 151.9444 | 244.5523 | 274.1576 | 223.4178 | 137.0001 | 137.0001 | 137.0001 | 296.1074 | 137.0001 | 167.1534 | 354.009 | 413.7437 | 311.3658 | 137.0001 | 137.0001 | 137.0001 | 408 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 12 | 5844 | 17.5 | 17.5 | 15.6083 | 16.5727 | 15 | 55 | 55 | 588.6643 | 204.2532 | 45.5251 | 165.9774 | 0 | 0 | 245.0256 | 430.8518 | 364.291 | 84.3334 | 0 | 0 | 414.7468 | 129.6939 | 129.6939 | 194.2455 | 243.2011 | 225.6658 | 151.9114 | 129.6939 | 129.6939 | 204.2532 | 129.6939 | 129.6939 | 439.2711 | 674.053 | 589.9567 | 236.2448 | 129.6939 | 129.6939 | 619 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 13 | 5845 | 16.8 | 16.8 | 15.6083 | 16.5727 | 15 | 58 | 58 | 729.336 | 160.6051 | 46.0665 | 187.3111 | 0 | 0 | 123.8103 | 438.091 | 495.7439 | 262.9968 | 0 | 0 | 525.3949 | 122.849 | 122.849 | 143.5485 | 196.0924 | 205.7313 | 166.8188 | 122.849 | 122.849 | 160.6051 | 122.849 | 122.849 | 267.3588 | 634.1834 | 701.4752 | 429.8156 | 122.849 | 122.849 | 686 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 14 | 5846 | 17.1 | 17.1 | 15.6083 | 16.5727 | 15 | 57 | 57 | 131.8347 | 319.3972 | 43.2735 | 207.8673 | 0 | 0 | 0 | 55.9224 | 90.7263 | 72.384 | 11.6401 | 0 | 91.6028 | 144.0975 | 144.0975 | 144.0975 | 212.5864 | 255.2114 | 232.7473 | 158.3533 | 144.0975 | 319.3972 | 144.0975 | 144.0975 | 144.0975 | 268.5088 | 345.9377 | 305.1313 | 169.9934 | 144.0975 | 411 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 15 | 5847 | 17.7 | 17.7 | 15.6083 | 16.5727 | 15 | 59 | 59 | 698.23 | 149.3261 | 37.7291 | 226.0244 | 0 | 0 | 0 | 149.76 | 449.4194 | 485.815 | 237.6268 | 0 | 439.6739 | 110.5645 | 110.5645 | 110.5645 | 135.4826 | 185.342 | 191.3978 | 150.1025 | 110.5645 | 149.3261 | 110.5645 | 110.5645 | 110.5645 | 285.2426 | 634.7614 | 677.2128 | 387.7293 | 110.5645 | 589 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 16 | 5848 | 17.7 | 17.7 | 15.6083 | 16.5727 | 15 | 56 | 56 | 958.8558 | 100.32 | 30.2981 | 241.5613 | 0 | 0 | 0 | 0 | 526.5771 | 758.2502 | 545.7506 | 13.5577 | 507.68 | 102.0306 | 102.0306 | 102.0306 | 102.0306 | 130.8395 | 143.5142 | 131.8884 | 102.7723 | 100.32 | 102.0306 | 102.0306 | 102.0306 | 102.0306 | 657.4165 | 901.7644 | 677.639 | 116.33 | 608 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 17 | 5849 | 17.6 | 17.6 | 15.6083 | 16.5727 | 15 | 57 | 57 | 660.0176 | 102.3356 | 21.7473 | 255.0854 | 0 | 0 | 0 | 0 | 271.3812 | 546.2265 | 501.0998 | 162.4356 | 264.6644 | 76.0944 | 76.0944 | 76.0944 | 76.0944 | 114.8939 | 154.1886 | 147.7369 | 99.3179 | 102.3356 | 76.0944 | 76.0944 | 76.0944 | 76.0944 | 386.2751 | 700.4152 | 648.8366 | 261.7535 | 367 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 18 | 5850 | 17 | 17 | 15.6083 | 16.5727 | 15 | 58 | 58 | 715.0856 | 58.0449 | 12.6564 | 267.3821 | 0 | 0 | 0 | 0 | 170.9488 | 574.7106 | 641.8147 | 332.9525 | 180.9551 | 49.9555 | 49.9555 | 49.9555 | 49.9555 | 63.4829 | 95.4332 | 100.7433 | 76.3025 | 58.0449 | 49.9555 | 49.9555 | 49.9555 | 49.9555 | 234.4317 | 670.1438 | 742.558 | 409.255 | 239 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 19 | 5851 | 15.7 | 15.7 | 15.6083 | 16.5727 | 15 | 66 | 66 | 251.2997 | 23.1516 | 3.4735 | 279.1692 | 0 | 0 | 0 | 0 | 11.1993 | 181.1162 | 244.9377 | 165.278 | 65.8484 | 19.6006 | 19.6006 | 19.6006 | 19.6006 | 21.6221 | 52.2921 | 63.8119 | 49.4333 | 23.1516 | 19.6006 | 19.6006 | 19.6006 | 19.6006 | 32.8213 | 233.4082 | 308.7495 | 214.7113 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 20 | 5852 | 13.6 | 13.6 | 15.6083 | 16.5727 | 15 | 76 | 76 | 0 | 6 | -5.4073 | 291.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 6 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 2.812 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 21 | 5853 | 11.5 | 11.5 | 15.6083 | 16.5727 | 15 | 87 | 87 | 0 | 0 | -13.5803 | 303.6418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 22 | 5854 | 11.1 | 11.1 | 15.6083 | 16.5727 | 15 | 90 | 90 | 0 | 0 | -20.5825 | 317.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 23 | 5855 | 10.1 | 10.1 | 15.6083 | 16.5727 | 15 | 95 | 95 | 0 | 0 | -25.882 | 332.442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 1 | 24 | 5856 | 9.4 | 9.4 | 13.2583 | 15.3202 | 15 | 98 | 98 | 0 | 0 | -28.9411 | 348.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 1 | 5857 | 8.6 | 8.6 | 13.2583 | 15.3202 | 15 | 99 | 99 | 0 | 0 | -29.3733 | 5.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 2 | 5858 | 8.6 | 8.6 | 13.2583 | 15.3202 | 15 | 97 | 97 | 0 | 0 | -27.4536 | 22.6643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 3 | 5859 | 7.9 | 7.9 | 13.2583 | 15.3202 | 15 | 97 | 97 | 0 | 0 | -22.7812 | 38.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 4 | 5860 | 7.7 | 7.7 | 13.2583 | 15.3202 | 15 | 97 | 97 | 0 | 0 | -16.2317 | 52.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 5 | 5861 | 7.7 | 7.7 | 13.2583 | 15.3202 | 15 | 97 | 97 | 0 | 0 | -8.3543 | 65.3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 6 | 5862 | 7.7 | 7.7 | 13.2583 | 15.3202 | 15 | 97 | 97 | 0 | 0 | 0.36213 | 77.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 7 | 5863 | 9.9 | 9.9 | 13.2583 | 15.3202 | 15 | 92 | 92 | 9.6 | 42.7687 | 9.4967 | 89.146 | 2.0978 | 8.1074 | 9.3678 | 5.1407 | 0 | 0 | 0 | 0 | 1.2313 | 109.0395 | 399.6028 | 460.5425 | 256.1608 | 7.6106 | 7.6106 | 7.6106 | 7.6106 | 42.7687 | 111.1373 | 407.7103 | 469.9103 | 261.3014 | 7.6106 | 7.6106 | 7.6106 | 7.6106 | 44 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 2 | 8 | 5864 | 13.4 | 13.4 | 13.2583 | 15.3202 | 15 | 79 | 79 | 98.8966 | 129.8662 | 18.6572 | 101.2165 | 1.4538 | 69.9924 | 97.5304 | 67.9365 | 0 | 0 | 0 | 0 | 28.1338 | 58.9735 | 211.0528 | 272.1565 | 206.4909 | 55.7477 | 55.7477 | 55.7477 | 55.7477 | 129.8662 | 60.4272 | 281.0452 | 369.687 | 274.4274 | 55.7477 | 55.7477 | 55.7477 | 55.7477 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 9 | 5865 | 16.1 | 16.1 | 13.2583 | 15.3202 | 15 | 73 | 73 | 317.4656 | 177.8656 | 27.4197 | 114.2731 | 0 | 167.2519 | 295.0374 | 249.994 | 58.5075 | 0 | 0 | 0 | 136.1344 | 94.6072 | 165.761 | 220.1245 | 200.9618 | 119.498 | 94.6072 | 94.6072 | 94.6072 | 177.8656 | 94.6072 | 333.0129 | 515.1619 | 450.9558 | 178.0055 | 94.6072 | 94.6072 | 94.6072 | 314 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 10 | 5866 | 18.6 | 18.6 | 13.2583 | 15.3202 | 15 | 68 | 68 | 456.3122 | 195.3675 | 35.2544 | 129.0826 | 0 | 143.3527 | 369.2412 | 378.8332 | 166.5099 | 0 | 0 | 0 | 251.6325 | 112.8171 | 157.8093 | 228.7059 | 231.7164 | 165.0773 | 112.8171 | 112.8171 | 112.8171 | 195.3675 | 112.8171 | 301.162 | 597.9472 | 610.5497 | 331.5872 | 112.8171 | 112.8171 | 112.8171 | 447 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 11 | 5867 | 20.6 | 20.6 | 13.2583 | 15.3202 | 15 | 65 | 65 | 591.7442 | 185.9149 | 41.4573 | 146.3425 | 0 | 49.8172 | 375.0913 | 480.6419 | 304.6391 | 0 | 0 | 0 | 381.0851 | 121.107 | 133.2917 | 212.8501 | 238.6666 | 195.6183 | 121.107 | 121.107 | 121.107 | 185.9149 | 121.107 | 183.109 | 587.9414 | 719.3085 | 500.2574 | 121.107 | 121.107 | 121.107 | 567 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 12 | 5868 | 21.6 | 21.6 | 13.2583 | 15.3202 | 15 | 64 | 64 | 654.5764 | 180.7087 | 45.1767 | 166.1664 | 0 | 0 | 271.8881 | 480.9903 | 408.3349 | 96.4825 | 0 | 0 | 458.2913 | 124.1811 | 124.1811 | 178.8326 | 220.8636 | 206.2594 | 143.5748 | 124.1811 | 124.1811 | 180.7087 | 124.1811 | 124.1811 | 450.7207 | 701.8539 | 614.5943 | 240.0572 | 124.1811 | 124.1811 | 639 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 13 | 5869 | 22.3 | 22.3 | 13.2583 | 15.3202 | 15 | 63 | 63 | 598.9779 | 204.1521 | 45.6971 | 187.383 | 0 | 0 | 100.9574 | 361.2913 | 409.9856 | 218.5159 | 0 | 0 | 428.8479 | 128.4465 | 128.4465 | 152.405 | 214.1857 | 225.7415 | 180.3032 | 128.4465 | 128.4465 | 204.1521 | 128.4465 | 128.4465 | 253.3625 | 575.4771 | 635.7272 | 398.8192 | 128.4465 | 128.4465 | 633 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 14 | 5870 | 23.3 | 23.3 | 13.2583 | 15.3202 | 15 | 63 | 63 | 482.1094 | 236.1513 | 42.9019 | 207.8265 | 0 | 0 | 0 | 205.5334 | 333.9385 | 266.727 | 43.2704 | 0 | 332.8487 | 131.8179 | 131.8179 | 131.8179 | 205.3519 | 251.2916 | 227.2452 | 147.2989 | 131.8179 | 236.1513 | 131.8179 | 131.8179 | 131.8179 | 410.8853 | 585.2301 | 493.9722 | 190.5693 | 131.8179 | 569 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 15 | 5871 | 23.5 | 23.5 | 13.2583 | 15.3202 | 15 | 64 | 64 | 412.36 | 234.1883 | 37.3677 | 225.9088 | 0 | 0 | 0 | 89.1886 | 267.1331 | 288.5946 | 141.0014 | 0 | 257.8117 | 124.6332 | 124.6332 | 124.6332 | 161.432 | 234.8511 | 243.7061 | 182.8098 | 124.6332 | 234.1883 | 124.6332 | 124.6332 | 124.6332 | 250.6206 | 501.9842 | 532.3007 | 323.8112 | 124.6332 | 492 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 16 | 5872 | 24.8 | 24.8 | 13.2583 | 15.3202 | 15 | 62 | 62 | 271.4339 | 226.5276 | 29.9495 | 241.4084 | 0 | 0 | 0 | 0 | 150.1011 | 215.6967 | 154.94 | 3.4216 | 142.4724 | 113.5739 | 113.5739 | 113.5739 | 113.5739 | 199.4731 | 237.0118 | 202.2423 | 115.532 | 226.5276 | 113.5739 | 113.5739 | 113.5739 | 113.5739 | 349.5742 | 452.7085 | 357.1823 | 118.9536 | 369 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 17 | 5873 | 24.6 | 24.6 | 13.2583 | 15.3202 | 15 | 60 | 60 | 229.0782 | 176.2153 | 21.4082 | 254.9188 | 0 | 0 | 0 | 0 | 94.9891 | 190.4043 | 174.2833 | 56.0695 | 90.7847 | 90.0754 | 90.0754 | 90.0754 | 90.0754 | 144.733 | 199.6359 | 190.3597 | 122.3384 | 176.2153 | 90.0754 | 90.0754 | 90.0754 | 90.0754 | 239.7221 | 390.0402 | 364.643 | 178.4079 | 267 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 18 | 5874 | 23.8 | 23.8 | 13.2583 | 15.3202 | 15 | 66 | 66 | 345.9228 | 100.1321 | 12.3214 | 267.2145 | 0 | 0 | 0 | 0 | 83.7949 | 279.1361 | 310.9631 | 160.6321 | 85.8679 | 57.8561 | 57.8561 | 57.8561 | 57.8561 | 82.577 | 140.206 | 149.5955 | 105.2453 | 100.1321 | 57.8561 | 57.8561 | 57.8561 | 57.8561 | 166.3719 | 419.342 | 460.5586 | 265.8774 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 19 | 5875 | 22 | 22 | 13.2583 | 15.3202 | 15 | 75 | 75 | 95.3492 | 41.3483 | 3.137 | 279.0084 | 0 | 0 | 0 | 0 | 4.527 | 68.9923 | 93.0429 | 62.5902 | 8.6517 | 22.6835 | 22.6835 | 22.6835 | 22.6835 | 25.4767 | 65.253 | 80.0927 | 61.3028 | 41.3483 | 22.6835 | 22.6835 | 22.6835 | 22.6835 | 30.0037 | 134.2453 | 173.1356 | 123.893 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 20 | 5876 | 19.9 | 19.9 | 13.2583 | 15.3202 | 15 | 84 | 84 | 0 | 6 | -5.7501 | 290.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 6 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 2.8166 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 21 | 5877 | 20.2 | 20.2 | 13.2583 | 15.3202 | 15 | 80 | 80 | 0 | 0 | -13.9331 | 303.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 22 | 5878 | 17.2 | 17.2 | 13.2583 | 15.3202 | 15 | 94 | 94 | 0 | 0 | -20.9463 | 317.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 23 | 5879 | 16 | 16 | 13.2583 | 15.3202 | 15 | 99 | 99 | 0 | 0 | -26.2537 | 332.4101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 2 | 24 | 5880 | 14.2 | 14.2 | 16.675 | 15.3589 | 15 | 99 | 99 | 0 | 0 | -29.3122 | 348.8547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 1 | 5881 | 13.5 | 13.5 | 16.675 | 15.3589 | 15 | 99 | 99 | 0 | 0 | -29.7318 | 5.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 2 | 5882 | 13.1 | 13.1 | 16.675 | 15.3589 | 15 | 99 | 99 | 0 | 0 | -27.7899 | 22.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 3 | 5883 | 12.2 | 12.2 | 16.675 | 15.3589 | 15 | 100 | 100 | 0 | 0 | -23.0883 | 38.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 4 | 5884 | 12 | 12 | 16.675 | 15.3589 | 15 | 100 | 100 | 0 | 0 | -16.5109 | 52.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 5 | 5885 | 12.3 | 12.3 | 16.675 | 15.3589 | 15 | 100 | 100 | 0 | 0 | -8.6114 | 65.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 6 | 5886 | 12.2 | 12.2 | 16.675 | 15.3589 | 15 | 100 | 100 | 0 | 0 | 0.11935 | 77.6636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 7 | 5887 | 14.1 | 14.1 | 16.675 | 15.3589 | 15 | 100 | 100 | 4.2172 | 30.4801 | 9.2593 | 89.4405 | 0.90101 | 3.5503 | 4.1198 | 2.2761 | 0 | 0 | 0 | 0 | 0.51994 | 59.0471 | 208.9554 | 241.1839 | 136.8536 | 8.0634 | 8.0634 | 8.0634 | 8.0634 | 30.4801 | 59.9481 | 212.5057 | 245.3038 | 139.1297 | 8.0634 | 8.0634 | 8.0634 | 8.0634 | 31 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 3 | 8 | 5888 | 16.2 | 16.2 | 16.675 | 15.3589 | 15 | 99 | 99 | 15.0526 | 101.7906 | 18.4153 | 101.5191 | 0.14508 | 10.6072 | 14.8558 | 10.402 | 0 | 0 | 0 | 0 | 4.2094 | 42.5021 | 170.4839 | 222.4561 | 167.974 | 40.7273 | 40.7273 | 40.7273 | 40.7273 | 101.7906 | 42.6472 | 181.0911 | 237.3119 | 178.376 | 40.7273 | 40.7273 | 40.7273 | 40.7273 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 9 | 5889 | 19.1 | 19.1 | 16.675 | 15.3589 | 15 | 90 | 90 | 204.3646 | 191.3269 | 27.1628 | 114.5808 | 0 | 106.9665 | 189.994 | 161.7256 | 38.7206 | 0 | 0 | 0 | 86.6731 | 91.2247 | 179.547 | 248.1028 | 224.7616 | 123.1963 | 91.2247 | 91.2247 | 91.2247 | 191.3269 | 91.2247 | 286.5135 | 438.0968 | 386.4872 | 161.9168 | 91.2247 | 91.2247 | 91.2247 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 10 | 5890 | 22.4 | 22.4 | 16.675 | 15.3589 | 15 | 75 | 75 | 358.7418 | 217.8231 | 34.9718 | 129.3843 | 0 | 111.3565 | 290.252 | 299.1218 | 132.7701 | 0 | 0 | 0 | 196.1769 | 116.9707 | 164.4147 | 240.6339 | 244.4129 | 173.538 | 116.9707 | 116.9707 | 116.9707 | 217.8231 | 116.9707 | 275.7712 | 530.886 | 543.5348 | 306.3081 | 116.9707 | 116.9707 | 116.9707 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 11 | 5891 | 24.2 | 24.2 | 16.675 | 15.3589 | 15 | 69 | 69 | 475.4727 | 220.9446 | 41.1407 | 146.6105 | 0 | 38.1267 | 301.1395 | 387.7488 | 247.2202 | 0 | 0 | 0 | 304.0554 | 126.66 | 139.4564 | 227.731 | 256.7996 | 209.6342 | 126.66 | 126.66 | 126.66 | 220.9446 | 126.66 | 177.5831 | 528.8705 | 644.5484 | 456.8543 | 126.66 | 126.66 | 126.66 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 12 | 5892 | 25.4 | 25.4 | 16.675 | 15.3589 | 15 | 65 | 65 | 603.9053 | 196.8884 | 44.8262 | 166.3556 | 0 | 0 | 250.2887 | 445.493 | 379.7335 | 91.5313 | 0 | 0 | 420.1116 | 125.9324 | 125.9324 | 183.1108 | 227.7053 | 212.6825 | 146.8427 | 125.9324 | 125.9324 | 196.8884 | 125.9324 | 125.9324 | 433.3995 | 673.1983 | 592.4161 | 238.374 | 125.9324 | 125.9324 | 617 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 13 | 5893 | 26.4 | 26.4 | 16.675 | 15.3589 | 15 | 60 | 60 | 345.1252 | 287.4424 | 45.3254 | 187.456 | 0 | 0 | 57.7425 | 209.0306 | 237.8715 | 127.3704 | 0 | 0 | 245.5576 | 143.8487 | 143.8487 | 174.9064 | 256.2788 | 271.7913 | 212.3567 | 143.8487 | 143.8487 | 287.4424 | 143.8487 | 143.8487 | 232.6488 | 465.3095 | 509.6628 | 339.7272 | 143.8487 | 143.8487 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 14 | 5894 | 26.9 | 26.9 | 16.675 | 15.3589 | 15 | 59 | 59 | 690.0869 | 165.6582 | 42.5278 | 207.7874 | 0 | 0 | 0 | 295.6585 | 481.084 | 384.697 | 62.9597 | 0 | 473.3418 | 119.547 | 119.547 | 119.547 | 172.9387 | 206.4238 | 189.0177 | 130.9166 | 119.547 | 165.6582 | 119.547 | 119.547 | 119.547 | 468.5972 | 687.5078 | 573.7147 | 193.8763 | 119.547 | 639 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 15 | 5895 | 27.3 | 27.3 | 16.675 | 15.3589 | 15 | 57 | 57 | 542.3345 | 194.3886 | 37.0037 | 225.7949 | 0 | 0 | 0 | 118.2703 | 353.5841 | 381.7731 | 186.3246 | 0 | 336.6114 | 117.916 | 117.916 | 117.916 | 150.6276 | 215.7116 | 223.5082 | 169.4503 | 117.916 | 194.3886 | 117.916 | 117.916 | 117.916 | 268.898 | 569.2957 | 605.2813 | 355.7749 | 117.916 | 531 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 16 | 5896 | 27.7 | 27.7 | 16.675 | 15.3589 | 15 | 54 | 54 | 684.0006 | 127.1395 | 29.5982 | 241.2568 | 0 | 0 | 0 | 0 | 380.8548 | 546.1882 | 391.5719 | 7.5781 | 355.8605 | 94.664 | 94.664 | 94.664 | 94.664 | 153.4812 | 179.0145 | 155.1363 | 95.8343 | 127.1395 | 94.664 | 94.664 | 94.664 | 94.664 | 534.3361 | 725.2026 | 546.7082 | 103.4124 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 17 | 5897 | 27.4 | 27.4 | 16.675 | 15.3589 | 15 | 59 | 59 | 657.0715 | 100.7111 | 21.0664 | 254.7529 | 0 | 0 | 0 | 0 | 274.7443 | 548.4869 | 500.9333 | 159.9398 | 257.2889 | 74.7288 | 74.7288 | 74.7288 | 74.7288 | 113.9752 | 153.0784 | 146.2856 | 97.5757 | 100.7111 | 74.7288 | 74.7288 | 74.7288 | 74.7288 | 388.7195 | 701.5653 | 647.2189 | 257.5155 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 3 | 18 | 5898 | 26.2 | 26.2 | 16.675 | 15.3589 | 15 | 63 | 63 | 477.061 | 83.9001 | 11.9837 | 267.0472 | 0 | 0 | 0 | 0 | 117.0737 | 386.4906 | 429.5065 | 220.9234 | 116.0999 | 53.5599 | 53.5599 | 53.5599 | 53.5599 | 75.734 | 126.7623 | 134.9096 | 95.4034 | 83.9001 | 53.5599 | 53.5599 | 53.5599 | 53.5599 | 192.8077 | 513.2528 | 564.4161 | 316.3268 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 19 | 5899 | 23.9 | 23.9 | 16.675 | 15.3589 | 15 | 78 | 78 | 159.5852 | 36.6517 | 2.798 | 278.8475 | 0 | 0 | 0 | 0 | 8.0416 | 115.9242 | 155.9 | 104.5517 | 24.3483 | 22.051 | 22.051 | 22.051 | 22.051 | 25.2026 | 67.484 | 83.1513 | 63.0269 | 36.6517 | 22.051 | 22.051 | 22.051 | 22.051 | 33.2443 | 183.4083 | 239.0513 | 167.5786 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 20 | 5900 | 20.6 | 20.6 | 16.675 | 15.3589 | 15 | 91 | 91 | 0 | 3 | -6.0955 | 290.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 3 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 1.3911 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 21 | 5901 | 21.2 | 21.2 | 16.675 | 15.3589 | 15 | 84 | 84 | 0 | 0 | -14.2884 | 303.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 22 | 5902 | 22.1 | 22.1 | 16.675 | 15.3589 | 15 | 79 | 79 | 0 | 0 | -21.3126 | 317.1688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 23 | 5903 | 22 | 22 | 16.675 | 15.3589 | 15 | 76 | 76 | 0 | 0 | -26.6278 | 332.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 3 | 24 | 5904 | 22.3 | 22.3 | 20.4458 | 16.655 | 15 | 72 | 72 | 0 | 0 | -29.6857 | 348.8963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 1 | 5905 | 22 | 22 | 20.4458 | 16.655 | 15 | 78 | 78 | 0 | 0 | -30.0923 | 6.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 2 | 5906 | 18.9 | 18.9 | 20.4458 | 16.655 | 15 | 96 | 96 | 0 | 0 | -28.1277 | 23.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 3 | 5907 | 18.5 | 18.5 | 20.4458 | 16.655 | 15 | 98 | 98 | 0 | 0 | -23.3964 | 38.7232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 4 | 5908 | 18.5 | 18.5 | 20.4458 | 16.655 | 15 | 97 | 97 | 0 | 0 | -16.7909 | 52.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 5 | 5909 | 18.2 | 18.2 | 20.4458 | 16.655 | 15 | 97 | 97 | 0 | 0 | -8.8692 | 65.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 6 | 5910 | 17.7 | 17.7 | 20.4458 | 16.655 | 15 | 98 | 98 | 0 | 0 | -0.12419 | 77.9521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 7 | 5911 | 18 | 18 | 20.4458 | 16.655 | 15 | 99 | 99 | 0.57654 | 10.9318 | 9.0209 | 89.737 | 0.12034 | 0.48379 | 0.56384 | 0.3136 | 0 | 0 | 0 | 0 | 0.068198 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 10.9318 | 5.456 | 5.8194 | 5.8994 | 5.6492 | 5.3356 | 5.3356 | 5.3356 | 5.3356 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 4 | 8 | 5912 | 18.3 | 18.3 | 20.4458 | 16.655 | 15 | 97 | 97 | 0.8486 | 30.7668 | 18.1722 | 101.8233 | 0.0038477 | 0.59534 | 0.83809 | 0.5899 | 0 | 0 | 0 | 0 | 0.23317 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 30.7668 | 14.9374 | 15.5289 | 15.7717 | 15.5235 | 14.9336 | 14.9336 | 14.9336 | 14.9336 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 9 | 5913 | 18.2 | 18.2 | 20.4458 | 16.655 | 15 | 98 | 98 | 0.13686 | 18.9426 | 26.9044 | 114.8898 | 0 | 0.071157 | 0.12727 | 0.10884 | 0.026643 | 0 | 0 | 0 | 0.057393 | 8.9131 | 8.9131 | 8.9131 | 8.9131 | 8.9131 | 8.9131 | 8.9131 | 8.9131 | 18.9426 | 8.9131 | 8.9843 | 9.0404 | 9.0219 | 8.9397 | 8.9131 | 8.9131 | 8.9131 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 10 | 5914 | 18.6 | 18.6 | 20.4458 | 16.655 | 15 | 95 | 95 | 1.1757 | 71.3626 | 34.6873 | 129.6866 | 0 | 0.36048 | 0.95105 | 0.98451 | 0.44125 | 0 | 0 | 0 | 0.63745 | 34.7496 | 34.7496 | 34.7496 | 34.7496 | 34.7496 | 34.7496 | 34.7496 | 34.7496 | 71.3626 | 34.7496 | 35.1101 | 35.7006 | 35.7341 | 35.1909 | 34.7496 | 34.7496 | 34.7496 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 11 | 5915 | 19.6 | 19.6 | 20.4458 | 16.655 | 15 | 88 | 88 | 8.4348 | 205.6447 | 40.822 | 146.8786 | 0 | 0.64227 | 5.3374 | 6.9059 | 4.4291 | 0 | 0 | 0 | 5.3553 | 97.5546 | 99.9758 | 117.6749 | 123.5878 | 114.2508 | 97.5546 | 97.5546 | 97.5546 | 205.6447 | 97.5546 | 100.6181 | 123.0122 | 130.4937 | 118.6799 | 97.5546 | 97.5546 | 97.5546 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 12 | 5916 | 20.3 | 20.3 | 20.4458 | 16.655 | 15 | 83 | 83 | 46.2548 | 296.032 | 44.4735 | 166.5449 | 0 | 0 | 19.1262 | 34.2535 | 29.3156 | 7.205 | 0 | 0 | 31.968 | 132.0753 | 132.0753 | 179.9122 | 217.7473 | 205.3969 | 150.0958 | 132.0753 | 132.0753 | 296.032 | 132.0753 | 132.0753 | 199.0384 | 252.0008 | 234.7125 | 157.3007 | 132.0753 | 132.0753 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 13 | 5917 | 20.7 | 20.7 | 20.4458 | 16.655 | 15 | 75 | 75 | 76.457 | 317.946 | 44.9514 | 187.5298 | 0 | 0 | 12.6947 | 46.4958 | 53.0603 | 28.5428 | 0 | 0 | 54.054 | 142.7096 | 142.7096 | 162.8557 | 216.497 | 226.9147 | 188.0062 | 142.7096 | 142.7096 | 317.946 | 142.7096 | 142.7096 | 175.5503 | 262.9928 | 279.975 | 216.549 | 142.7096 | 142.7096 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 14 | 5918 | 20.5 | 20.5 | 20.4458 | 16.655 | 15 | 73 | 73 | 131.0787 | 313.6858 | 42.1513 | 207.7499 | 0 | 0 | 0 | 56.4336 | 91.9652 | 73.6249 | 12.156 | 0 | 89.3142 | 141.9671 | 141.9671 | 141.9671 | 210.5966 | 253.8069 | 231.503 | 156.7502 | 141.9671 | 313.6858 | 141.9671 | 141.9671 | 141.9671 | 267.0302 | 345.7721 | 305.1279 | 168.9062 | 141.9671 | 403 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 15 | 5919 | 20.6 | 20.6 | 20.4458 | 16.655 | 15 | 74 | 74 | 7.3494 | 192.4722 | 36.637 | 225.6826 | 0 | 0 | 0 | 1.6158 | 4.822 | 5.2036 | 2.537 | 0 | 4.5278 | 95.4921 | 95.4921 | 95.4921 | 97.329 | 100.9741 | 101.4079 | 98.3763 | 95.4921 | 192.4722 | 95.4921 | 95.4921 | 95.4921 | 98.9448 | 105.7961 | 106.6114 | 100.9133 | 95.4921 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 16 | 5920 | 20.9 | 20.9 | 20.4458 | 16.655 | 15 | 73 | 73 | 57.7912 | 226.2034 | 29.2441 | 241.1063 | 0 | 0 | 0 | 0 | 32.398 | 46.3702 | 33.1793 | 0.55244 | 29.7966 | 105.281 | 105.281 | 105.281 | 105.281 | 150.7418 | 170.3475 | 151.8381 | 106.0562 | 226.2034 | 105.281 | 105.281 | 105.281 | 105.281 | 183.1398 | 216.7177 | 185.0174 | 106.6087 | 256 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 17 | 5921 | 20.8 | 20.8 | 20.4458 | 16.655 | 15 | 74 | 74 | 45.5504 | 165.3815 | 20.7218 | 254.5877 | 0 | 0 | 0 | 0 | 19.2041 | 38.1848 | 34.7973 | 11.026 | 17.6185 | 78.8636 | 78.8636 | 78.8636 | 78.8636 | 103.8416 | 128.529 | 124.1231 | 93.2047 | 165.3815 | 78.8636 | 78.8636 | 78.8636 | 78.8636 | 123.0458 | 166.7138 | 158.9204 | 104.2307 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 4 | 18 | 5922 | 20.3 | 20.3 | 20.4458 | 16.655 | 15 | 78 | 78 | 122.8112 | 109.714 | 11.6434 | 266.8802 | 0 | 0 | 0 | 0 | 30.5273 | 99.888 | 110.7357 | 56.7159 | 29.286 | 56.0794 | 56.0794 | 56.0794 | 56.0794 | 72.9631 | 111.3246 | 117.3241 | 87.4473 | 109.714 | 56.0794 | 56.0794 | 56.0794 | 56.0794 | 103.4904 | 211.2126 | 228.0598 | 144.1632 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 19 | 5923 | 17.9 | 17.9 | 20.4458 | 16.655 | 15 | 94 | 94 | 6.6559 | 24.4628 | 2.4564 | 278.6866 | 0 | 0 | 0 | 0 | 0.35479 | 4.8537 | 6.5093 | 4.3519 | 0.53716 | 12.7977 | 12.7977 | 12.7977 | 12.7977 | 13.0283 | 15.9527 | 17.0289 | 15.6266 | 24.4628 | 12.7977 | 12.7977 | 12.7977 | 12.7977 | 13.3831 | 20.8064 | 23.5383 | 19.9785 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 20 | 5924 | 17 | 17 | 20.4458 | 16.655 | 15 | 98 | 98 | 0 | 6 | -6.4434 | 290.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 6 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 2.8283 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 21 | 5925 | 16.3 | 16.3 | 20.4458 | 16.655 | 15 | 98 | 98 | 0 | 0 | -14.6462 | 303.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 22 | 5926 | 16.2 | 16.2 | 20.4458 | 16.655 | 15 | 99 | 99 | 0 | 0 | -21.6813 | 317.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 23 | 5927 | 16.3 | 16.3 | 20.4458 | 16.655 | 15 | 97 | 97 | 0 | 0 | -27.0044 | 332.3483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 4 | 24 | 5928 | 16.4 | 16.4 | 18.7792 | 17.3217 | 15 | 98 | 98 | 0 | 0 | -30.0613 | 348.9397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 1 | 5929 | 14.7 | 14.7 | 18.7792 | 17.3217 | 15 | 96 | 96 | 0 | 0 | -30.4545 | 6.1759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 2 | 5930 | 14.1 | 14.1 | 18.7792 | 17.3217 | 15 | 94 | 94 | 0 | 0 | -28.4667 | 23.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 3 | 5931 | 13.4 | 13.4 | 18.7792 | 17.3217 | 15 | 94 | 94 | 0 | 0 | -23.7055 | 38.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 4 | 5932 | 12.8 | 12.8 | 18.7792 | 17.3217 | 15 | 94 | 94 | 0 | 0 | -17.0715 | 53.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 5 | 5933 | 12.4 | 12.4 | 18.7792 | 17.3217 | 15 | 94 | 94 | 0 | 0 | -9.1275 | 66.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 6 | 5934 | 12.2 | 12.2 | 18.7792 | 17.3217 | 15 | 94 | 94 | 0 | 0 | -0.36844 | 78.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 7 | 5935 | 12.8 | 12.8 | 18.7792 | 17.3217 | 15 | 91 | 91 | 9.703 | 37.9011 | 8.7815 | 90.0354 | 1.9771 | 8.115 | 9.4992 | 5.3189 | 0 | 0 | 0 | 0 | 1.0989 | 20.2766 | 31.3774 | 33.8809 | 26.3206 | 16.7009 | 16.7009 | 16.7009 | 16.7009 | 37.9011 | 22.2537 | 39.4923 | 43.3801 | 31.6395 | 16.7009 | 16.7009 | 16.7009 | 16.7009 | 39 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 5 | 8 | 5936 | 13.8 | 13.8 | 18.7792 | 17.3217 | 15 | 90 | 90 | 108.0946 | 123.8286 | 17.9279 | 102.129 | 0 | 75.4918 | 106.8275 | 75.5851 | 0.065954 | 0 | 0 | 0 | 29.1714 | 53.0528 | 213.85 | 280.5949 | 214.0487 | 53.1933 | 53.0528 | 53.0528 | 53.0528 | 123.8286 | 53.0528 | 289.3418 | 387.4223 | 289.6337 | 53.2592 | 53.0528 | 53.0528 | 53.0528 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 9 | 5937 | 14.4 | 14.4 | 18.7792 | 17.3217 | 15 | 88 | 88 | 2.5439 | 79.9454 | 26.6444 | 115.1998 | 0 | 1.3136 | 2.3663 | 2.0328 | 0.50855 | 0 | 0 | 0 | 1.0546 | 39.6558 | 40.1308 | 40.5114 | 40.3908 | 39.8397 | 39.6558 | 39.6558 | 39.6558 | 79.9454 | 39.6558 | 41.4444 | 42.8777 | 42.4237 | 40.3482 | 39.6558 | 39.6558 | 39.6558 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 10 | 5938 | 15.7 | 15.7 | 18.7792 | 17.3217 | 15 | 82 | 82 | 26.24 | 213.896 | 34.401 | 129.9895 | 0 | 7.9447 | 21.2214 | 22.0669 | 9.986 | 0 | 0 | 0 | 14.104 | 95.2696 | 121.1424 | 164.3798 | 167.1334 | 127.7901 | 95.2696 | 95.2696 | 95.2696 | 213.896 | 95.2696 | 129.087 | 185.6012 | 189.2003 | 137.776 | 95.2696 | 95.2696 | 95.2696 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 11 | 5939 | 16.7 | 16.7 | 18.7792 | 17.3217 | 15 | 73 | 73 | 205.4596 | 284.5028 | 40.5013 | 147.1467 | 0 | 14.8062 | 129.8841 | 168.8777 | 108.945 | 0 | 0 | 0 | 129.4972 | 134.6711 | 146.5037 | 238.47 | 269.6323 | 221.7362 | 134.6711 | 134.6711 | 134.6711 | 284.5028 | 134.6711 | 161.3099 | 368.3541 | 438.51 | 330.6812 | 134.6711 | 134.6711 | 134.6711 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 12 | 5940 | 16 | 16 | 18.7792 | 17.3217 | 15 | 69 | 69 | 241.1352 | 303.4497 | 44.1188 | 166.7343 | 0 | 0 | 99.4694 | 179.252 | 154.0313 | 38.5811 | 0 | 0 | 165.5503 | 145.8422 | 145.8422 | 212.2693 | 265.5493 | 248.7065 | 171.6072 | 145.8422 | 145.8422 | 303.4497 | 145.8422 | 145.8422 | 311.7387 | 444.8013 | 402.7377 | 210.1883 | 145.8422 | 145.8422 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 13 | 5941 | 17.9 | 17.9 | 18.7792 | 17.3217 | 15 | 63 | 63 | 647.1453 | 184.4356 | 44.5754 | 187.6043 | 0 | 0 | 106.6069 | 395.1274 | 452.1876 | 244.3624 | 0 | 0 | 454.5644 | 124.6141 | 124.6141 | 146.6296 | 206.2123 | 217.9959 | 175.0777 | 124.6141 | 124.6141 | 184.4356 | 124.6141 | 124.6141 | 253.2365 | 601.3397 | 670.1835 | 419.4401 | 124.6141 | 124.6141 | 639 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 14 | 5942 | 13.2 | 13.2 | 18.7792 | 17.3217 | 15 | 91 | 91 | 13.2611 | 241.0251 | 41.7725 | 207.7138 | 0 | 0 | 0 | 5.7368 | 9.3631 | 7.5046 | 1.25 | 0 | 8.9749 | 116.4269 | 116.4269 | 116.4269 | 127.5253 | 134.5407 | 130.9453 | 118.8452 | 116.4269 | 241.0251 | 116.4269 | 116.4269 | 116.4269 | 133.2622 | 143.9039 | 138.4499 | 120.0952 | 116.4269 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 15 | 5943 | 17.5 | 17.5 | 18.7792 | 17.3217 | 15 | 67 | 67 | 383.8106 | 237.3226 | 36.2679 | 225.5718 | 0 | 0 | 0 | 85.0561 | 253.4069 | 273.3153 | 133.1193 | 0 | 234.6774 | 123.8488 | 123.8488 | 123.8488 | 161.7457 | 236.7548 | 245.625 | 183.1604 | 123.8488 | 237.3226 | 123.8488 | 123.8488 | 123.8488 | 246.8019 | 490.1616 | 518.9403 | 316.2797 | 123.8488 | 472 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 16 | 5944 | 18.1 | 18.1 | 18.7792 | 17.3217 | 15 | 64 | 64 | 707.5524 | 119.5306 | 28.8875 | 240.957 | 0 | 0 | 0 | 0 | 399.3385 | 570.4428 | 407.3894 | 5.6928 | 361.4694 | 92.2723 | 92.2723 | 92.2723 | 92.2723 | 149.5702 | 174.1205 | 150.7253 | 93.0892 | 119.5306 | 92.2723 | 92.2723 | 92.2723 | 92.2723 | 548.9087 | 744.5633 | 558.1147 | 98.782 | 481 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 17 | 5945 | 18.2 | 18.2 | 18.7792 | 17.3217 | 15 | 62 | 62 | 588.4532 | 111.2276 | 20.3747 | 254.4232 | 0 | 0 | 0 | 0 | 250.1275 | 495.379 | 450.4442 | 141.6453 | 224.7724 | 75.8972 | 75.8972 | 75.8972 | 75.8972 | 118.6612 | 160.5917 | 152.9092 | 100.1141 | 111.2276 | 75.8972 | 75.8972 | 75.8972 | 75.8972 | 368.7887 | 655.9707 | 603.3534 | 241.7595 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 5 | 18 | 5946 | 17.4 | 17.4 | 18.7792 | 17.3217 | 15 | 68 | 68 | 31.9631 | 95.5358 | 11.3006 | 266.7135 | 0 | 0 | 0 | 0 | 8.0461 | 26.0986 | 28.8629 | 14.7197 | 7.4642 | 47.1549 | 47.1549 | 47.1549 | 47.1549 | 55.5953 | 74.5325 | 77.4322 | 62.596 | 95.5358 | 47.1549 | 47.1549 | 47.1549 | 47.1549 | 63.6413 | 100.631 | 106.2951 | 77.3157 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 19 | 5947 | 16.8 | 16.8 | 18.7792 | 17.3217 | 15 | 67 | 67 | 125.1446 | 13.3312 | 2.1123 | 278.5257 | 0 | 0 | 0 | 0 | 7.0354 | 91.607 | 122.5165 | 81.6575 | 67.6688 | 14.4658 | 14.4658 | 14.4658 | 14.4658 | 16.1808 | 36.7973 | 44.3322 | 34.3718 | 13.3312 | 14.4658 | 14.4658 | 14.4658 | 14.4658 | 23.2162 | 128.4043 | 166.8487 | 116.0293 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 20 | 5948 | 16.2 | 16.2 | 18.7792 | 17.3217 | 15 | 65 | 65 | 0 | 0 | -6.7936 | 290.4819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 21 | 5949 | 15.8 | 15.8 | 18.7792 | 17.3217 | 15 | 69 | 69 | 0 | 0 | -15.0063 | 303.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 22 | 5950 | 15.8 | 15.8 | 18.7792 | 17.3217 | 15 | 71 | 71 | 0 | 0 | -22.0524 | 316.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 23 | 5951 | 15.3 | 15.3 | 18.7792 | 17.3217 | 15 | 77 | 77 | 0 | 0 | -27.3832 | 332.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 5 | 24 | 5952 | 15.2 | 15.2 | 15.2667 | 16.8708 | 15 | 80 | 80 | 0 | 0 | -30.4391 | 348.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 1 | 5953 | 14.7 | 14.7 | 15.2667 | 16.8708 | 15 | 85 | 85 | 0 | 0 | -30.8186 | 6.3016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 2 | 5954 | 14.4 | 14.4 | 15.2667 | 16.8708 | 15 | 88 | 88 | 0 | 0 | -28.807 | 23.4346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 3 | 5955 | 14.8 | 14.8 | 15.2667 | 16.8708 | 15 | 82 | 82 | 0 | 0 | -24.0153 | 39.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 4 | 5956 | 14.4 | 14.4 | 15.2667 | 16.8708 | 15 | 81 | 81 | 0 | 0 | -17.3528 | 53.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 5 | 5957 | 14.2 | 14.2 | 15.2667 | 16.8708 | 15 | 81 | 81 | 0 | 0 | -9.3865 | 66.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 6 | 5958 | 14 | 14 | 15.2667 | 16.8708 | 15 | 78 | 78 | 0 | 0 | -0.6134 | 78.5358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 7 | 5959 | 13.9 | 13.9 | 15.2667 | 16.8708 | 15 | 80 | 80 | 2.0538 | 18.7778 | 8.5413 | 90.3356 | 0.40819 | 1.7119 | 2.0128 | 1.1346 | 0 | 0 | 0 | 0 | 0.22222 | 9.7117 | 12.6106 | 13.2797 | 11.327 | 8.8041 | 8.8041 | 8.8041 | 8.8041 | 18.7778 | 10.1199 | 14.3225 | 15.2924 | 12.4616 | 8.8041 | 8.8041 | 8.8041 | 8.8041 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 6 | 8 | 5960 | 14.4 | 14.4 | 15.2667 | 16.8708 | 15 | 82 | 82 | 16.9292 | 98.515 | 17.6824 | 102.4362 | 0 | 11.7684 | 16.7411 | 11.9071 | 0.09806 | 0 | 0 | 0 | 4.485 | 38.7486 | 182.589 | 243.3682 | 184.284 | 39.9471 | 38.7486 | 38.7486 | 38.7486 | 98.515 | 38.7486 | 194.3574 | 260.1093 | 196.1911 | 40.0452 | 38.7486 | 38.7486 | 38.7486 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 9 | 5961 | 15.1 | 15.1 | 15.2667 | 16.8708 | 15 | 80 | 80 | 27.1096 | 163.8923 | 26.383 | 115.5108 | 0 | 13.9021 | 25.2228 | 21.7683 | 5.5623 | 0 | 0 | 0 | 11.1077 | 69.9831 | 132.6178 | 183.6224 | 168.0586 | 95.0436 | 69.9831 | 69.9831 | 69.9831 | 163.8923 | 69.9831 | 146.5199 | 208.8452 | 189.827 | 100.6059 | 69.9831 | 69.9831 | 69.9831 | 175 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 10 | 5962 | 15.6 | 15.6 | 15.2667 | 16.8708 | 15 | 78 | 78 | 46.2096 | 228.3815 | 34.1129 | 130.2927 | 0 | 13.8111 | 37.3606 | 39.0248 | 17.8288 | 0 | 0 | 0 | 24.6185 | 102.4692 | 138.259 | 199.2848 | 203.5973 | 148.6703 | 102.4692 | 102.4692 | 102.4692 | 228.3815 | 102.4692 | 152.0701 | 236.6454 | 242.6221 | 166.4991 | 102.4692 | 102.4692 | 102.4692 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 11 | 5963 | 16.6 | 16.6 | 15.2667 | 16.8708 | 15 | 74 | 74 | 40.261 | 263.8125 | 40.1787 | 147.4146 | 0 | 2.7355 | 25.4251 | 33.221 | 21.5565 | 0 | 0 | 0 | 25.1875 | 118.1919 | 125.8894 | 189.7357 | 211.6726 | 178.8498 | 118.1919 | 118.1919 | 118.1919 | 263.8125 | 118.1919 | 128.625 | 215.1608 | 244.8936 | 200.4063 | 118.1919 | 118.1919 | 118.1919 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 12 | 5964 | 16.3 | 16.3 | 15.2667 | 16.8708 | 15 | 77 | 77 | 4.0908 | 166.2105 | 43.7621 | 166.9235 | 0 | 0 | 1.6832 | 3.0524 | 2.6335 | 0.67193 | 0 | 0 | 2.7895 | 83.5725 | 83.5725 | 84.1305 | 84.5844 | 84.4456 | 83.7953 | 83.5725 | 83.5725 | 166.2105 | 83.5725 | 83.5725 | 85.8138 | 87.6368 | 87.0791 | 84.4672 | 83.5725 | 83.5725 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 13 | 5965 | 15.1 | 15.1 | 15.2667 | 16.8708 | 15 | 90 | 90 | 1.287 | 96.1019 | 44.1974 | 187.6795 | 0 | 0 | 0.2103 | 0.78891 | 0.90539 | 0.4915 | 0 | 0 | 0.89806 | 47.0993 | 47.0993 | 47.0993 | 47.0993 | 47.0993 | 47.0993 | 47.0993 | 47.0993 | 96.1019 | 47.0993 | 47.0993 | 47.3096 | 47.8882 | 48.0047 | 47.5908 | 47.0993 | 47.0993 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 14 | 5966 | 15.6 | 15.6 | 15.2667 | 16.8708 | 15 | 88 | 88 | 2.3034 | 123.4517 | 41.3916 | 207.679 | 0 | 0 | 0 | 1.0012 | 1.6366 | 1.3133 | 0.22068 | 0 | 1.5483 | 61.1875 | 61.1875 | 61.1875 | 61.1875 | 61.1875 | 61.1875 | 61.1875 | 61.1875 | 123.4517 | 61.1875 | 61.1875 | 61.1875 | 62.1887 | 62.8242 | 62.5008 | 61.4082 | 61.1875 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 15 | 5967 | 15.3 | 15.3 | 15.2667 | 16.8708 | 15 | 93 | 93 | 0.74101 | 63.5504 | 35.8964 | 225.4624 | 0 | 0 | 0 | 0.16551 | 0.4923 | 0.5307 | 0.25823 | 0 | 0.44961 | 30.7191 | 30.7191 | 30.7191 | 30.7191 | 30.7191 | 30.7191 | 30.7191 | 30.7191 | 63.5504 | 30.7191 | 30.7191 | 30.7191 | 30.8846 | 31.2113 | 31.2498 | 30.9773 | 30.7191 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 16 | 5968 | 15.8 | 15.8 | 15.2667 | 16.8708 | 15 | 89 | 89 | 0.73038 | 52.6303 | 28.5285 | 240.8088 | 0 | 0 | 0 | 0 | 0.41498 | 0.59165 | 0.42173 | 0.0047752 | 0.36965 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 52.6303 | 25.2996 | 25.2996 | 25.2996 | 25.2996 | 25.7146 | 25.8912 | 25.7213 | 25.3044 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 17 | 5969 | 15.6 | 15.6 | 15.2667 | 16.8708 | 15 | 92 | 92 | 1.3155 | 52.5039 | 20.0252 | 254.2593 | 0 | 0 | 0 | 0 | 0.56371 | 1.1121 | 1.009 | 0.31487 | 0.4961 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 52.5039 | 25.2633 | 25.2633 | 25.2633 | 25.2633 | 25.8271 | 26.3754 | 26.2723 | 25.5782 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 6 | 18 | 5970 | 15.4 | 15.4 | 15.2667 | 16.8708 | 15 | 95 | 95 | 0.79687 | 24.8179 | 10.9555 | 266.547 | 0 | 0 | 0 | 0 | 0.20311 | 0.65317 | 0.72061 | 0.36593 | 0.18213 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 24.8179 | 11.7422 | 11.7422 | 11.7422 | 11.7422 | 11.9453 | 12.3953 | 12.4628 | 12.1081 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 19 | 5971 | 15.6 | 15.6 | 15.2667 | 16.8708 | 15 | 94 | 94 | 0.48174 | 5.966 | 1.766 | 278.3648 | 0 | 0 | 0 | 0 | 0.028486 | 0.35397 | 0.4721 | 0.31368 | 0.033986 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 2.771 | 5.966 | 2.771 | 2.771 | 2.771 | 2.771 | 2.7995 | 3.125 | 3.2431 | 3.0847 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 20 | 5972 | 15.9 | 15.9 | 15.2667 | 16.8708 | 15 | 93 | 93 | 0 | 0 | -7.1461 | 290.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 21 | 5973 | 15.8 | 15.8 | 15.2667 | 16.8708 | 15 | 93 | 93 | 0 | 0 | -15.3686 | 303.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 22 | 5974 | 15.7 | 15.7 | 15.2667 | 16.8708 | 15 | 94 | 94 | 0 | 0 | -22.4257 | 316.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 23 | 5975 | 15.7 | 15.7 | 15.2667 | 16.8708 | 15 | 94 | 94 | 0 | 0 | -27.7641 | 332.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 6 | 24 | 5976 | 15.2 | 15.2 | 15.2125 | 16.4962 | 15 | 96 | 96 | 0 | 0 | -30.8188 | 349.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 1 | 5977 | 14.8 | 14.8 | 15.2125 | 16.4962 | 15 | 84 | 84 | 0 | 0 | -31.1842 | 6.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 2 | 5978 | 14.5 | 14.5 | 15.2125 | 16.4962 | 15 | 79 | 79 | 0 | 0 | -29.1484 | 23.6352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 3 | 5979 | 14.5 | 14.5 | 15.2125 | 16.4962 | 15 | 76 | 76 | 0 | 0 | -24.326 | 39.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 4 | 5980 | 14.4 | 14.4 | 15.2125 | 16.4962 | 15 | 75 | 75 | 0 | 0 | -17.6347 | 53.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 5 | 5981 | 13.9 | 13.9 | 15.2125 | 16.4962 | 15 | 77 | 77 | 0 | 0 | -9.646 | 66.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 6 | 5982 | 14.2 | 14.2 | 15.2125 | 16.4962 | 15 | 79 | 79 | 0 | 0 | -0.85902 | 78.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 7 | 5983 | 14.2 | 14.2 | 15.2125 | 16.4962 | 15 | 79 | 79 | 0.40075 | 7.9587 | 8.3002 | 90.6375 | 0.07762 | 0.33286 | 0.39312 | 0.22309 | 0 | 0 | 0 | 0 | 0.04132 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 7.9587 | 3.9581 | 4.2133 | 4.2736 | 4.1036 | 3.8805 | 3.8805 | 3.8805 | 3.8805 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 7 | 8 | 5984 | 14.8 | 14.8 | 15.2125 | 16.4962 | 15 | 76 | 76 | 3.3139 | 57.1386 | 17.4357 | 102.7447 | 0 | 2.2928 | 3.279 | 2.3444 | 0.036486 | 0 | 0 | 0 | 0.86144 | 26.2838 | 54.4772 | 66.604 | 55.1117 | 26.7324 | 26.2838 | 26.2838 | 26.2838 | 57.1386 | 26.2838 | 56.77 | 69.883 | 57.4561 | 26.7689 | 26.2838 | 26.2838 | 26.2838 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 9 | 5985 | 15.3 | 15.3 | 15.2125 | 16.4962 | 15 | 76 | 76 | 7.0588 | 125.1422 | 26.12 | 115.8226 | 0 | 3.5941 | 6.5686 | 5.6952 | 1.4857 | 0 | 0 | 0 | 2.8578 | 56.936 | 84.3547 | 107.0456 | 100.383 | 68.2698 | 56.936 | 56.936 | 56.936 | 125.1422 | 56.936 | 87.9488 | 113.6142 | 106.0782 | 69.7554 | 56.936 | 56.936 | 56.936 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 10 | 5986 | 16.6 | 16.6 | 15.2125 | 16.4962 | 15 | 69 | 69 | 76.2614 | 237.7363 | 33.8231 | 130.5962 | 0 | 22.493 | 61.6359 | 64.6733 | 29.826 | 0 | 0 | 0 | 40.2637 | 107.1057 | 145.653 | 212.7341 | 217.9396 | 158.22 | 107.1057 | 107.1057 | 107.1057 | 237.7363 | 107.1057 | 168.146 | 274.37 | 282.6129 | 188.046 | 107.1057 | 107.1057 | 107.1057 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 11 | 5987 | 16.7 | 16.7 | 15.2125 | 16.4962 | 15 | 68 | 68 | 74.147 | 278.9635 | 39.8542 | 147.6823 | 0 | 4.7299 | 46.7726 | 61.4166 | 40.0835 | 0 | 0 | 0 | 46.0365 | 125.4885 | 133.5326 | 205.0349 | 229.94 | 193.6588 | 125.4885 | 125.4885 | 125.4885 | 278.9635 | 125.4885 | 138.2625 | 251.8075 | 291.3565 | 233.7423 | 125.4885 | 125.4885 | 125.4885 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 12 | 5988 | 16.7 | 16.7 | 15.2125 | 16.4962 | 15 | 67 | 67 | 129.5835 | 312.2428 | 43.4035 | 167.1125 | 0 | 0 | 53.1825 | 97.0513 | 84.0689 | 21.84 | 0 | 0 | 87.7572 | 140.9338 | 140.9338 | 210.2035 | 267.3423 | 250.4327 | 169.3802 | 140.9338 | 140.9338 | 312.2428 | 140.9338 | 140.9338 | 263.3859 | 364.3936 | 334.5016 | 191.2201 | 140.9338 | 140.9338 | 400 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 13 | 5989 | 15.2 | 15.2 | 15.2125 | 16.4962 | 15 | 83 | 83 | 3.5917 | 158.5106 | 43.8174 | 187.7551 | 0 | 0 | 0.58201 | 2.2102 | 2.5437 | 1.3872 | 0 | 0 | 2.4894 | 79.7007 | 79.7007 | 79.7007 | 79.7007 | 79.7007 | 79.7007 | 79.7007 | 79.7007 | 158.5106 | 79.7007 | 79.7007 | 80.2827 | 81.9109 | 82.2444 | 81.0878 | 79.7007 | 79.7007 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 14 | 5990 | 15.9 | 15.9 | 15.2125 | 16.4962 | 15 | 81 | 81 | 3.362 | 147.756 | 41.0085 | 207.6456 | 0 | 0 | 0 | 1.4682 | 2.4037 | 1.9311 | 0.32734 | 0 | 2.244 | 73.9663 | 73.9663 | 73.9663 | 73.9663 | 73.9663 | 73.9663 | 73.9663 | 73.9663 | 147.756 | 73.9663 | 73.9663 | 73.9663 | 75.4345 | 76.37 | 75.8974 | 74.2936 | 73.9663 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 15 | 5991 | 15.1 | 15.1 | 15.2125 | 16.4962 | 15 | 83 | 83 | 3.969 | 144.6106 | 35.5227 | 225.3545 | 0 | 0 | 0 | 0.89337 | 2.6531 | 2.8587 | 1.3897 | 0 | 2.3894 | 72.4099 | 72.4099 | 72.4099 | 72.4099 | 72.4099 | 72.4099 | 72.4099 | 72.4099 | 144.6106 | 72.4099 | 72.4099 | 72.4099 | 73.3032 | 75.063 | 75.2686 | 73.7996 | 72.4099 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 16 | 5992 | 15.2 | 15.2 | 15.2125 | 16.4962 | 15 | 83 | 83 | 4.5457 | 128.7212 | 28.1672 | 240.6616 | 0 | 0 | 0 | 0 | 2.5998 | 3.6996 | 2.6322 | 0.022889 | 2.2788 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 128.7212 | 64.2528 | 64.2528 | 64.2528 | 64.2528 | 66.8526 | 67.9524 | 66.885 | 64.2757 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 17 | 5993 | 15.4 | 15.4 | 15.2125 | 16.4962 | 15 | 81 | 81 | 16.4911 | 137.8618 | 19.6734 | 254.0961 | 0 | 0 | 0 | 0 | 7.1232 | 13.9984 | 12.6735 | 3.9247 | 6.1382 | 67.9895 | 67.9895 | 67.9895 | 67.9895 | 71.9173 | 75.7082 | 74.9777 | 70.1536 | 137.8618 | 67.9895 | 67.9895 | 67.9895 | 67.9895 | 79.0404 | 89.7066 | 87.6512 | 74.0782 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 7 | 18 | 5994 | 15.9 | 15.9 | 15.2125 | 16.4962 | 15 | 73 | 73 | 205.7191 | 101.0117 | 10.6081 | 266.3808 | 0 | 0 | 0 | 0 | 53.0815 | 169.2653 | 186.2959 | 94.1968 | 45.9883 | 54.407 | 54.407 | 54.407 | 54.407 | 79.3061 | 133.8049 | 141.7935 | 98.5922 | 101.0117 | 54.407 | 54.407 | 54.407 | 54.407 | 132.3876 | 303.0702 | 328.0894 | 192.789 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 19 | 5995 | 15.6 | 15.6 | 15.2125 | 16.4962 | 15 | 74 | 74 | 27.3212 | 26.2124 | 1.4176 | 278.2037 | 0 | 0 | 0 | 0 | 1.6952 | 20.1496 | 26.8007 | 17.7523 | 1.7876 | 14.1036 | 14.1036 | 14.1036 | 14.1036 | 15.2858 | 28.156 | 32.7944 | 26.484 | 26.2124 | 14.1036 | 14.1036 | 14.1036 | 14.1036 | 16.981 | 48.3056 | 59.5951 | 44.2363 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 20 | 5996 | 15.1 | 15.1 | 15.2125 | 16.4962 | 15 | 78 | 78 | 0 | 0 | -7.5006 | 290.1856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 21 | 5997 | 14.6 | 14.6 | 15.2125 | 16.4962 | 15 | 81 | 81 | 0 | 0 | -15.733 | 302.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 22 | 5998 | 13.8 | 13.8 | 15.2125 | 16.4962 | 15 | 88 | 88 | 0 | 0 | -22.801 | 316.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 23 | 5999 | 13.7 | 13.7 | 15.2125 | 16.4962 | 15 | 94 | 94 | 0 | 0 | -28.1472 | 332.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 7 | 24 | 6000 | 12.9 | 12.9 | 14.9583 | 16.187 | 15 | 94 | 94 | 0 | 0 | -31.2004 | 349.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 1 | 6001 | 12.9 | 12.9 | 14.9583 | 16.187 | 15 | 96 | 96 | 0 | 0 | -31.5514 | 6.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 2 | 6002 | 13 | 13 | 14.9583 | 16.187 | 15 | 93 | 93 | 0 | 0 | -29.4909 | 23.8388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 3 | 6003 | 12.9 | 12.9 | 14.9583 | 16.187 | 15 | 95 | 95 | 0 | 0 | -24.6373 | 39.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 4 | 6004 | 12.6 | 12.6 | 14.9583 | 16.187 | 15 | 95 | 95 | 0 | 0 | -17.9171 | 54.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 5 | 6005 | 12.9 | 12.9 | 14.9583 | 16.187 | 15 | 91 | 91 | 0 | 0 | -9.906 | 67.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 6 | 6006 | 13.1 | 13.1 | 14.9583 | 16.187 | 15 | 92 | 92 | 0 | 0 | -1.1053 | 79.1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 7 | 6007 | 13.4 | 13.4 | 14.9583 | 16.187 | 15 | 91 | 91 | 0.44348 | 7.9565 | 8.0582 | 90.941 | 0.083634 | 0.36704 | 0.43544 | 0.24876 | 0 | 0 | 0 | 0 | 0.043455 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 7.9565 | 3.9633 | 4.2467 | 4.3151 | 4.1284 | 3.8797 | 3.8797 | 3.8797 | 3.8797 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 8 | 8 | 6008 | 13.8 | 13.8 | 14.9583 | 16.187 | 15 | 88 | 88 | 1.1148 | 32.7158 | 17.1879 | 103.0543 | 0 | 0.76757 | 1.1036 | 0.79321 | 0.018127 | 0 | 0 | 0 | 0.2842 | 16.022 | 16.022 | 16.022 | 16.022 | 16.022 | 16.022 | 16.022 | 16.022 | 32.7158 | 16.022 | 16.7896 | 17.1256 | 16.8152 | 16.0401 | 16.022 | 16.022 | 16.022 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 9 | 6009 | 13.4 | 13.4 | 14.9583 | 16.187 | 15 | 96 | 96 | 0.39972 | 30.8401 | 25.8556 | 116.1351 | 0 | 0.20205 | 0.372 | 0.32403 | 0.086254 | 0 | 0 | 0 | 0.15986 | 14.6849 | 14.6849 | 14.6849 | 14.6849 | 14.6849 | 14.6849 | 14.6849 | 14.6849 | 30.8401 | 14.6849 | 14.8869 | 15.0569 | 15.0089 | 14.7711 | 14.6849 | 14.6849 | 14.6849 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 10 | 6010 | 14.5 | 14.5 | 14.9583 | 16.187 | 15 | 90 | 90 | 3.1594 | 112.3472 | 33.5315 | 130.8997 | 0 | 0.9193 | 2.5525 | 2.6904 | 1.2524 | 0 | 0 | 0 | 1.6528 | 56.0407 | 56.2751 | 56.6914 | 56.7266 | 56.36 | 56.0407 | 56.0407 | 56.0407 | 112.3472 | 56.0407 | 57.1944 | 59.2439 | 59.417 | 57.6124 | 56.0407 | 56.0407 | 56.0407 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 11 | 6011 | 15 | 15 | 14.9583 | 16.187 | 15 | 85 | 85 | 3.5342 | 139.8226 | 39.5278 | 147.9495 | 0 | 0.21065 | 2.2268 | 2.9385 | 1.9289 | 0 | 0 | 0 | 2.1774 | 70.2123 | 70.2216 | 70.3111 | 70.3427 | 70.2979 | 70.2123 | 70.2123 | 70.2123 | 139.8226 | 70.2123 | 70.4323 | 72.5379 | 73.2812 | 72.2268 | 70.2123 | 70.2123 | 70.2123 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 12 | 6012 | 14.6 | 14.6 | 14.9583 | 16.187 | 15 | 86 | 86 | 1.1653 | 88.2164 | 43.043 | 167.3011 | 0 | 0 | 0.47697 | 0.87595 | 0.76182 | 0.20142 | 0 | 0 | 0.78365 | 43.1005 | 43.1005 | 43.1005 | 43.1005 | 43.1005 | 43.1005 | 43.1005 | 43.1005 | 88.2164 | 43.1005 | 43.1005 | 43.5775 | 43.9765 | 43.8623 | 43.3019 | 43.1005 | 43.1005 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 13 | 6013 | 14.6 | 14.6 | 14.9583 | 16.187 | 15 | 93 | 93 | 1.6376 | 106.8727 | 43.4356 | 187.8312 | 0 | 0 | 0.26309 | 1.0116 | 1.1675 | 0.63954 | 0 | 0 | 1.1273 | 52.6138 | 52.6138 | 52.6138 | 52.6138 | 52.6138 | 52.6138 | 52.6138 | 52.6138 | 106.8727 | 52.6138 | 52.6138 | 52.8769 | 53.6254 | 53.7814 | 53.2534 | 52.6138 | 52.6138 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 14 | 6014 | 14.6 | 14.6 | 14.9583 | 16.187 | 15 | 96 | 96 | 1.5149 | 98.9961 | 40.6236 | 207.6132 | 0 | 0 | 0 | 0.6646 | 1.0898 | 0.87657 | 0.14988 | 0 | 1.0039 | 48.5793 | 48.5793 | 48.5793 | 48.5793 | 48.5793 | 48.5793 | 48.5793 | 48.5793 | 98.9961 | 48.5793 | 48.5793 | 48.5793 | 49.2439 | 49.669 | 49.4558 | 48.7292 | 48.5793 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 15 | 6015 | 15.1 | 15.1 | 14.9583 | 16.187 | 15 | 93 | 93 | 1.2238 | 80.2691 | 35.1469 | 225.2478 | 0 | 0 | 0 | 0.27757 | 0.82308 | 0.88644 | 0.43054 | 0 | 0.7309 | 39.0852 | 39.0852 | 39.0852 | 39.0852 | 39.0852 | 39.0852 | 39.0852 | 39.0852 | 80.2691 | 39.0852 | 39.0852 | 39.0852 | 39.3628 | 39.9083 | 39.9717 | 39.5158 | 39.0852 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 16 | 6016 | 15.9 | 15.9 | 14.9583 | 16.187 | 15 | 88 | 88 | 6.1969 | 146.9235 | 27.8036 | 240.5155 | 0 | 0 | 0 | 0 | 3.5675 | 5.0671 | 3.5984 | 0.021918 | 3.0765 | 73.8389 | 73.8389 | 73.8389 | 73.8389 | 74.2071 | 74.3619 | 74.2103 | 73.8412 | 146.9235 | 73.8389 | 73.8389 | 73.8389 | 73.8389 | 77.7746 | 79.4289 | 77.8088 | 73.8631 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 17 | 6017 | 16.5 | 16.5 | 14.9583 | 16.187 | 15 | 80 | 80 | 23.796 | 144.2603 | 19.3194 | 253.9335 | 0 | 0 | 0 | 0 | 10.36 | 20.2817 | 18.3228 | 5.6305 | 8.7397 | 69.0835 | 69.0835 | 69.0835 | 69.0835 | 90.4897 | 110.9904 | 106.9427 | 80.7176 | 144.2603 | 69.0835 | 69.0835 | 69.0835 | 69.0835 | 100.8496 | 131.2722 | 125.2654 | 86.3481 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 18 | 6018 | 16.1 | 16.1 | 14.9583 | 16.187 | 15 | 82 | 82 | 17.9068 | 82.0872 | 10.2586 | 266.2147 | 0 | 0 | 0 | 0 | 4.6767 | 14.7892 | 16.2384 | 8.1754 | 3.9128 | 40.734 | 40.734 | 40.734 | 40.734 | 47.7726 | 62.9922 | 65.1733 | 53.0382 | 82.0872 | 40.734 | 40.734 | 40.734 | 40.734 | 52.4493 | 77.7814 | 81.4117 | 61.2135 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 19 | 6019 | 15 | 15 | 14.9583 | 16.187 | 15 | 94 | 94 | 2.2152 | 10.8665 | 1.0671 | 278.0426 | 0 | 0 | 0 | 0 | 0.1439 | 1.6397 | 2.1751 | 1.4362 | 0.13354 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 10.8665 | 5.0935 | 5.0935 | 5.0935 | 5.0935 | 5.2374 | 6.7333 | 7.2686 | 6.5298 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 20 | 6020 | 15 | 15 | 14.9583 | 16.187 | 15 | 93 | 93 | 0 | 0 | -7.8572 | 290.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 21 | 6021 | 14.9 | 14.9 | 14.9583 | 16.187 | 15 | 91 | 91 | 0 | 0 | -16.0993 | 302.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 22 | 6022 | 14.5 | 14.5 | 14.9583 | 16.187 | 15 | 96 | 96 | 0 | 0 | -23.1783 | 316.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 23 | 6023 | 15.1 | 15.1 | 14.9583 | 16.187 | 15 | 96 | 96 | 0 | 0 | -28.5321 | 332.2319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 8 | 24 | 6024 | 15.5 | 15.5 | 14.3708 | 15.8102 | 15 | 96 | 96 | 0 | 0 | -31.5838 | 349.1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 1 | 6025 | 15.6 | 15.6 | 14.3708 | 15.8102 | 15 | 95 | 95 | 0 | 0 | -31.9202 | 6.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 2 | 6026 | 15.6 | 15.6 | 14.3708 | 15.8102 | 15 | 96 | 96 | 0 | 0 | -29.8343 | 24.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 3 | 6027 | 15.7 | 15.7 | 14.3708 | 15.8102 | 15 | 96 | 96 | 0 | 0 | -24.9493 | 39.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 4 | 6028 | 15.8 | 15.8 | 14.3708 | 15.8102 | 15 | 96 | 96 | 0 | 0 | -18.2 | 54.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 5 | 6029 | 16.1 | 16.1 | 14.3708 | 15.8102 | 15 | 95 | 95 | 0 | 0 | -10.1665 | 67.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 6 | 6030 | 16.2 | 16.2 | 14.3708 | 15.8102 | 15 | 95 | 95 | 0 | 0 | -1.3522 | 79.4265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 7 | 6031 | 16.4 | 16.4 | 14.3708 | 15.8102 | 15 | 94 | 94 | 2.2295 | 16.793 | 7.8154 | 91.2459 | 0.40899 | 1.8385 | 2.191 | 1.2601 | 0 | 0 | 0 | 0 | 0.20699 | 8.6272 | 11.2376 | 11.8814 | 10.1814 | 7.8803 | 7.8803 | 7.8803 | 7.8803 | 16.793 | 9.0362 | 13.0761 | 14.0724 | 11.4415 | 7.8803 | 7.8803 | 7.8803 | 7.8803 | 17 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 9 | 8 | 6032 | 16.6 | 16.6 | 14.3708 | 15.8102 | 15 | 92 | 92 | 2.0616 | 43.4848 | 16.9389 | 103.3649 | 0 | 1.4125 | 2.0419 | 1.4753 | 0.044411 | 0 | 0 | 0 | 0.51517 | 20.8587 | 30.1943 | 34.3548 | 30.6094 | 21.1522 | 20.8587 | 20.8587 | 20.8587 | 43.4848 | 20.8587 | 31.6068 | 36.3967 | 32.0847 | 21.1966 | 20.8587 | 20.8587 | 20.8587 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 9 | 6033 | 17.3 | 17.3 | 14.3708 | 15.8102 | 15 | 89 | 89 | 9.6347 | 132.1944 | 25.5898 | 116.4482 | 0 | 4.8342 | 8.9671 | 7.8472 | 2.1305 | 0 | 0 | 0 | 3.8056 | 58.9609 | 94.7174 | 125.2864 | 117.0027 | 74.719 | 58.9609 | 58.9609 | 58.9609 | 132.1944 | 58.9609 | 99.5517 | 134.2535 | 124.8499 | 76.8495 | 58.9609 | 58.9609 | 58.9609 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 10 | 6034 | 17.3 | 17.3 | 14.3708 | 15.8102 | 15 | 90 | 90 | 4.992 | 139.4128 | 33.2383 | 131.2032 | 0 | 1.4325 | 4.0311 | 4.2684 | 2.0053 | 0 | 0 | 0 | 2.5872 | 67.1683 | 72.2627 | 81.5044 | 82.3482 | 74.2999 | 67.1683 | 67.1683 | 67.1683 | 139.4128 | 67.1683 | 73.6952 | 85.5356 | 86.6166 | 76.3052 | 67.1683 | 67.1683 | 67.1683 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 11 | 6035 | 17.2 | 17.2 | 14.3708 | 15.8102 | 15 | 96 | 96 | 1.2259 | 82.2506 | 39.1997 | 148.2162 | 0 | 0.067897 | 0.77145 | 1.0231 | 0.67543 | 0 | 0 | 0 | 0.74938 | 40.1395 | 40.1395 | 40.1395 | 40.1395 | 40.1395 | 40.1395 | 40.1395 | 40.1395 | 82.2506 | 40.1395 | 40.2074 | 40.9109 | 41.1626 | 40.8149 | 40.1395 | 40.1395 | 40.1395 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 12 | 6036 | 18.1 | 18.1 | 14.3708 | 15.8102 | 15 | 90 | 90 | 1.7397 | 106.8384 | 42.6808 | 167.4891 | 0 | 0 | 0.71011 | 1.3125 | 1.146 | 0.30823 | 0 | 0 | 1.1616 | 52.6394 | 52.6394 | 52.6394 | 52.6394 | 52.6394 | 52.6394 | 52.6394 | 52.6394 | 106.8384 | 52.6394 | 52.6394 | 53.3495 | 53.9519 | 53.7854 | 52.9476 | 52.6394 | 52.6394 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 13 | 6037 | 18.7 | 18.7 | 14.3708 | 15.8102 | 15 | 88 | 88 | 3.6883 | 158.4786 | 43.0521 | 187.9075 | 0 | 0 | 0.58736 | 2.2871 | 2.647 | 1.4564 | 0 | 0 | 2.5214 | 79.7095 | 79.7095 | 79.7095 | 79.7095 | 79.7095 | 79.7095 | 79.7095 | 79.7095 | 158.4786 | 79.7095 | 79.7095 | 80.2969 | 81.9966 | 82.3566 | 81.166 | 79.7095 | 79.7095 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 14 | 6038 | 18.7 | 18.7 | 14.3708 | 15.8102 | 15 | 88 | 88 | 2.9681 | 137.0472 | 40.2368 | 207.582 | 0 | 0 | 0 | 1.3081 | 2.1483 | 1.73 | 0.29838 | 0 | 1.9528 | 68.323 | 68.323 | 68.323 | 68.323 | 68.323 | 68.323 | 68.323 | 68.323 | 137.0472 | 68.323 | 68.323 | 68.323 | 69.6311 | 70.4713 | 70.0531 | 68.6214 | 68.323 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 15 | 6039 | 19.5 | 19.5 | 14.3708 | 15.8102 | 15 | 83 | 83 | 26.9259 | 237.0492 | 34.7691 | 225.1424 | 0 | 0 | 0 | 6.1529 | 18.2187 | 19.6122 | 9.5172 | 0 | 15.9508 | 108.5711 | 108.5711 | 108.5711 | 127.0422 | 163.2639 | 167.4474 | 137.1419 | 108.5711 | 237.0492 | 108.5711 | 108.5711 | 108.5711 | 133.1951 | 181.4826 | 187.0596 | 146.6591 | 108.5711 | 253 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 16 | 6040 | 19.1 | 19.1 | 14.3708 | 15.8102 | 15 | 87 | 87 | 1.8959 | 82.0681 | 27.4381 | 240.3704 | 0 | 0 | 0 | 0 | 1.0985 | 1.5574 | 1.104 | 0.0038719 | 0.93192 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 82.0681 | 40.0438 | 40.0438 | 40.0438 | 40.0438 | 41.1422 | 41.6011 | 41.1477 | 40.0476 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 17 | 6041 | 18.9 | 18.9 | 14.3708 | 15.8102 | 15 | 89 | 89 | 0.98076 | 43.6447 | 18.9634 | 253.7714 | 0 | 0 | 0 | 0 | 0.43034 | 0.8393 | 0.75662 | 0.23072 | 0.35533 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 43.6447 | 20.8898 | 20.8898 | 20.8898 | 20.8898 | 21.3201 | 21.7291 | 21.6464 | 21.1205 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 18 | 6042 | 18.6 | 18.6 | 14.3708 | 15.8102 | 15 | 88 | 88 | 0.42182 | 16.91 | 9.9072 | 266.0489 | 0 | 0 | 0 | 0 | 0.11149 | 0.34968 | 0.38303 | 0.19201 | 0.090035 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 16.91 | 7.9453 | 7.9453 | 7.9453 | 7.9453 | 8.0567 | 8.2949 | 8.3283 | 8.1373 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 19 | 6043 | 18.2 | 18.2 | 14.3708 | 15.8102 | 15 | 92 | 92 | 0.78811 | 5.9566 | 0.71468 | 277.8813 | 0 | 0 | 0 | 0 | 0.053495 | 0.58549 | 0.77451 | 0.50983 | 0.043435 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 5.9566 | 2.7679 | 2.7679 | 2.7679 | 2.7679 | 2.8213 | 3.3533 | 3.5424 | 3.2777 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 20 | 6044 | 17.7 | 17.7 | 14.3708 | 15.8102 | 15 | 98 | 98 | 0 | 0 | -8.2155 | 289.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 21 | 6045 | 17.7 | 17.7 | 14.3708 | 15.8102 | 15 | 98 | 98 | 0 | 0 | -16.4675 | 302.6424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 22 | 6046 | 17.7 | 17.7 | 14.3708 | 15.8102 | 15 | 98 | 98 | 0 | 0 | -23.5574 | 316.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 23 | 6047 | 17.9 | 17.9 | 14.3708 | 15.8102 | 15 | 96 | 96 | 0 | 0 | -28.9189 | 332.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 9 | 24 | 6048 | 17.7 | 17.7 | 17.4292 | 16.1412 | 15 | 97 | 97 | 0 | 0 | -31.9689 | 349.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 1 | 6049 | 16.7 | 16.7 | 17.4292 | 16.1412 | 15 | 99 | 99 | 0 | 0 | -32.2902 | 6.8298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 2 | 6050 | 16.1 | 16.1 | 17.4292 | 16.1412 | 15 | 98 | 98 | 0 | 0 | -30.1786 | 24.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 3 | 6051 | 16 | 16 | 17.4292 | 16.1412 | 15 | 100 | 100 | 0 | 0 | -25.2619 | 40.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 4 | 6052 | 16.1 | 16.1 | 17.4292 | 16.1412 | 15 | 99 | 99 | 0 | 0 | -18.4833 | 54.5813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 5 | 6053 | 16.7 | 16.7 | 17.4292 | 16.1412 | 15 | 98 | 98 | 0 | 0 | -10.4275 | 67.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 6 | 6054 | 17.1 | 17.1 | 17.4292 | 16.1412 | 15 | 98 | 98 | 0 | 0 | -1.5997 | 79.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 7 | 6055 | 17.6 | 17.6 | 17.4292 | 16.1412 | 15 | 97 | 97 | 0.55337 | 7.9515 | 7.5717 | 91.5522 | 0.098649 | 0.45463 | 0.54429 | 0.31512 | 0 | 0 | 0 | 0 | 0.048515 | 4.0777 | 5.3004 | 5.6084 | 4.8212 | 3.7388 | 3.7388 | 3.7388 | 3.7388 | 7.9515 | 4.1763 | 5.755 | 6.1527 | 5.1363 | 3.7388 | 3.7388 | 3.7388 | 3.7388 | 8 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 10 | 8 | 6056 | 18.6 | 18.6 | 17.4292 | 16.1412 | 15 | 96 | 96 | 5.2794 | 67.7075 | 16.6888 | 103.6765 | 0 | 3.5989 | 5.2314 | 3.7994 | 0.14176 | 0 | 0 | 0 | 1.2925 | 29.1549 | 96.2373 | 126.6661 | 99.9741 | 31.7972 | 29.1549 | 29.1549 | 29.1549 | 67.7075 | 29.1549 | 99.8363 | 131.8975 | 103.7736 | 31.939 | 29.1549 | 29.1549 | 29.1549 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 9 | 6057 | 19.8 | 19.8 | 17.4292 | 16.1412 | 15 | 94 | 94 | 13.1057 | 138.8888 | 25.3226 | 116.7616 | 0 | 6.5262 | 12.1977 | 10.7239 | 2.9682 | 0 | 0 | 0 | 5.1112 | 60.9592 | 104.4348 | 142.216 | 132.398 | 80.7322 | 60.9592 | 60.9592 | 60.9592 | 138.8888 | 60.9592 | 110.9611 | 154.4136 | 143.1219 | 83.7004 | 60.9592 | 60.9592 | 60.9592 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 10 | 6058 | 21.5 | 21.5 | 17.4292 | 16.1412 | 15 | 87 | 87 | 134.2463 | 237.0858 | 32.9435 | 131.5064 | 0 | 37.9783 | 108.3494 | 115.2509 | 54.64 | 0 | 0 | 0 | 68.9142 | 109.3034 | 147.6615 | 218.7364 | 225.707 | 164.4899 | 109.3034 | 109.3034 | 109.3034 | 237.0858 | 109.3034 | 185.6398 | 327.0858 | 340.9579 | 219.1299 | 109.3034 | 109.3034 | 109.3034 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 11 | 6059 | 22.5 | 22.5 | 17.4292 | 16.1412 | 15 | 83 | 83 | 264.8736 | 264.3741 | 38.8698 | 148.4821 | 0 | 13.5452 | 166.4643 | 221.8709 | 147.3085 | 0 | 0 | 0 | 160.6259 | 130.6699 | 138.5042 | 226.9491 | 258.9949 | 215.8698 | 130.6699 | 130.6699 | 130.6699 | 264.3741 | 130.6699 | 152.0494 | 393.4134 | 480.8658 | 363.1782 | 130.6699 | 130.6699 | 130.6699 | 425 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 12 | 6060 | 23.3 | 23.3 | 17.4292 | 16.1412 | 15 | 80 | 80 | 250.3542 | 292.0476 | 42.317 | 167.6765 | 0 | 0 | 101.8969 | 189.5479 | 166.1643 | 45.4439 | 0 | 0 | 165.9524 | 141.8783 | 141.8783 | 205.6434 | 260.4937 | 245.8607 | 170.3162 | 141.8783 | 141.8783 | 292.0476 | 141.8783 | 141.8783 | 307.5403 | 450.0416 | 412.025 | 215.7601 | 141.8783 | 141.8783 | 458 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 13 | 6061 | 24 | 24 | 17.4292 | 16.1412 | 15 | 77 | 77 | 123.3125 | 313.2968 | 42.6669 | 187.9839 | 0 | 0 | 19.4609 | 76.7501 | 89.0802 | 49.2283 | 0 | 0 | 83.7032 | 141.2269 | 141.2269 | 167.0795 | 243.1845 | 259.5642 | 206.6235 | 141.2269 | 141.2269 | 313.2968 | 141.2269 | 141.2269 | 186.5404 | 319.9347 | 348.6444 | 255.8518 | 141.2269 | 141.2269 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 14 | 6062 | 24.7 | 24.7 | 17.4292 | 16.1412 | 15 | 74 | 74 | 201.8336 | 296.1864 | 39.8482 | 207.5516 | 0 | 0 | 0 | 89.3484 | 146.971 | 118.5001 | 20.6134 | 0 | 131.8136 | 140.2352 | 140.2352 | 140.2352 | 207.3395 | 250.6164 | 229.2336 | 155.7167 | 140.2352 | 296.1864 | 140.2352 | 140.2352 | 140.2352 | 296.6878 | 397.5875 | 347.7336 | 176.3301 | 140.2352 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 15 | 6063 | 24.9 | 24.9 | 17.4292 | 16.1412 | 15 | 74 | 74 | 203.9439 | 266.1788 | 34.3895 | 225.0382 | 0 | 0 | 0 | 46.9489 | 138.8201 | 149.3723 | 72.4243 | 0 | 119.8212 | 128.332 | 128.332 | 128.332 | 159.8113 | 221.4109 | 228.4861 | 176.8925 | 128.332 | 266.1788 | 128.332 | 128.332 | 128.332 | 206.7602 | 360.2309 | 377.8585 | 249.3168 | 128.332 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 16 | 6064 | 24.7 | 24.7 | 17.4292 | 16.1412 | 15 | 77 | 77 | 29.0085 | 196.8838 | 27.0705 | 240.2262 | 0 | 0 | 0 | 0 | 16.9156 | 23.9383 | 16.9382 | 0.015975 | 14.1162 | 91.9599 | 91.9599 | 91.9599 | 91.9599 | 131.5367 | 147.9673 | 131.5895 | 91.9973 | 196.8838 | 91.9599 | 91.9599 | 91.9599 | 91.9599 | 148.4523 | 171.9056 | 148.5277 | 92.0132 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 17 | 6065 | 24.5 | 24.5 | 17.4292 | 16.1412 | 15 | 78 | 78 | 35.2323 | 148.4119 | 18.6055 | 253.6099 | 0 | 0 | 0 | 0 | 15.5789 | 30.2712 | 27.2311 | 8.2394 | 12.5881 | 71.0992 | 71.0992 | 71.0992 | 71.0992 | 94.5989 | 116.7614 | 112.1756 | 83.5278 | 148.4119 | 71.0992 | 71.0992 | 71.0992 | 71.0992 | 110.1778 | 147.0327 | 139.4067 | 91.7672 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 10 | 18 | 6066 | 24 | 24 | 17.4292 | 16.1412 | 15 | 80 | 80 | 41.5119 | 88.3513 | 9.5538 | 265.8832 | 0 | 0 | 0 | 0 | 11.1014 | 34.5387 | 37.7436 | 18.8389 | 8.6487 | 43.9022 | 43.9022 | 43.9022 | 43.9022 | 52.5813 | 70.9047 | 73.4103 | 58.6305 | 88.3513 | 43.9022 | 43.9022 | 43.9022 | 43.9022 | 63.6828 | 105.4434 | 111.154 | 77.4694 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 19 | 6067 | 23.4 | 23.4 | 17.4292 | 16.1412 | 15 | 83 | 83 | 31.4927 | 20.4279 | 0.36051 | 277.7199 | 0 | 0 | 0 | 0 | 2.2295 | 23.4796 | 30.9757 | 20.3267 | 1.5721 | 11.1166 | 11.1166 | 11.1166 | 11.1166 | 12.201 | 22.5367 | 26.1826 | 21.0031 | 20.4279 | 11.1166 | 11.1166 | 11.1166 | 11.1166 | 14.4304 | 46.0163 | 57.1584 | 41.3298 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 20 | 6068 | 23.1 | 23.1 | 17.4292 | 16.1412 | 15 | 86 | 86 | 0 | 0 | -8.5756 | 289.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 21 | 6069 | 22.3 | 22.3 | 17.4292 | 16.1412 | 15 | 91 | 91 | 0 | 0 | -16.8373 | 302.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 22 | 6070 | 19 | 19 | 17.4292 | 16.1412 | 15 | 93 | 93 | 0 | 0 | -23.9383 | 316.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 23 | 6071 | 19 | 19 | 17.4292 | 16.1412 | 15 | 95 | 95 | 0 | 0 | -29.3073 | 332.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 10 | 24 | 6072 | 18.8 | 18.8 | 20.6 | 17.1226 | 15 | 95 | 95 | 0 | 0 | -32.3556 | 349.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 1 | 6073 | 18.3 | 18.3 | 20.6 | 17.1226 | 15 | 93 | 93 | 0 | 0 | -32.6616 | 6.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 2 | 6074 | 18 | 18 | 20.6 | 17.1226 | 15 | 94 | 94 | 0 | 0 | -30.5238 | 24.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 3 | 6075 | 17.7 | 17.7 | 20.6 | 17.1226 | 15 | 93 | 93 | 0 | 0 | -25.575 | 40.4735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 4 | 6076 | 17.3 | 17.3 | 20.6 | 17.1226 | 15 | 91 | 91 | 0 | 0 | -18.767 | 54.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 5 | 6077 | 16.8 | 16.8 | 20.6 | 17.1226 | 15 | 92 | 92 | 0 | 0 | -10.6889 | 67.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 6 | 6078 | 16.2 | 16.2 | 20.6 | 17.1226 | 15 | 95 | 95 | 0 | 0 | -1.8477 | 80.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 7 | 6079 | 16.7 | 16.7 | 20.6 | 17.1226 | 15 | 93 | 93 | 4.7259 | 21.6102 | 7.3272 | 91.8597 | 0.81785 | 3.8678 | 4.6521 | 2.7112 | 0 | 0 | 0 | 0 | 0.38979 | 11.0484 | 14.4553 | 15.3313 | 13.1633 | 10.1348 | 10.1348 | 10.1348 | 10.1348 | 21.6102 | 11.8662 | 18.3231 | 19.9834 | 15.8745 | 10.1348 | 10.1348 | 10.1348 | 10.1348 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 11 | 8 | 6080 | 17.7 | 17.7 | 20.6 | 17.1226 | 15 | 89 | 89 | 46.0532 | 102.9606 | 16.4376 | 103.9888 | 0 | 31.2334 | 45.653 | 33.3297 | 1.4823 | 0 | 0 | 0 | 11.0394 | 43.2078 | 192.885 | 261.9868 | 202.9309 | 50.3113 | 43.2078 | 43.2078 | 43.2078 | 102.9606 | 43.2078 | 224.1185 | 307.6399 | 236.2606 | 51.7936 | 43.2078 | 43.2078 | 43.2078 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 9 | 6081 | 18.1 | 18.1 | 20.6 | 17.1226 | 15 | 85 | 85 | 7.0786 | 119.2749 | 25.054 | 117.0752 | 0 | 3.4979 | 6.588 | 5.8189 | 1.6412 | 0 | 0 | 0 | 2.7251 | 54.1523 | 81.4106 | 105.4908 | 99.4977 | 66.9418 | 54.1523 | 54.1523 | 54.1523 | 119.2749 | 54.1523 | 84.9085 | 112.0788 | 105.3166 | 68.583 | 54.1523 | 54.1523 | 54.1523 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 10 | 6082 | 19.4 | 19.4 | 20.6 | 17.1226 | 15 | 79 | 79 | 181.5368 | 232.7099 | 32.647 | 131.8093 | 0 | 50.6143 | 146.4332 | 156.4735 | 74.8537 | 0 | 0 | 0 | 92.2901 | 109.9611 | 155.1192 | 240.6089 | 249.5669 | 176.7457 | 109.9611 | 109.9611 | 109.9611 | 232.7099 | 109.9611 | 205.7335 | 387.0421 | 406.0404 | 251.5994 | 109.9611 | 109.9611 | 109.9611 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 11 | 6083 | 19.3 | 19.3 | 20.6 | 17.1226 | 15 | 73 | 73 | 207.4821 | 272.1965 | 38.5382 | 148.7472 | 0 | 9.7238 | 130.2173 | 174.4313 | 116.4658 | 0 | 0 | 0 | 124.8035 | 129.6532 | 137.1751 | 230.3842 | 264.5865 | 219.7466 | 129.6532 | 129.6532 | 129.6532 | 272.1965 | 129.6532 | 146.8989 | 360.6015 | 439.0177 | 336.2124 | 129.6532 | 129.6532 | 129.6532 | 397 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 12 | 6084 | 19 | 19 | 20.6 | 17.1226 | 15 | 72 | 72 | 32.5454 | 270.5855 | 41.9515 | 167.8631 | 0 | 0 | 13.2074 | 24.7275 | 21.7627 | 6.0495 | 0 | 0 | 21.4145 | 121.4735 | 121.4735 | 163.8637 | 200.8388 | 191.3227 | 140.8899 | 121.4735 | 121.4735 | 270.5855 | 121.4735 | 121.4735 | 177.0711 | 225.5663 | 213.0854 | 146.9395 | 121.4735 | 121.4735 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 13 | 6085 | 18.9 | 18.9 | 20.6 | 17.1226 | 15 | 75 | 75 | 6.8193 | 206.4044 | 42.2802 | 188.0604 | 0 | 0 | 1.0663 | 4.26 | 4.9582 | 2.752 | 0 | 0 | 4.5956 | 101.2167 | 101.2167 | 103.4277 | 110.0501 | 111.498 | 106.9232 | 101.2167 | 101.2167 | 206.4044 | 101.2167 | 101.2167 | 104.494 | 114.3101 | 116.4563 | 109.6752 | 101.2167 | 101.2167 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 14 | 6086 | 18.7 | 18.7 | 20.6 | 17.1226 | 15 | 76 | 76 | 5.2944 | 179.5682 | 39.4581 | 207.5222 | 0 | 0 | 0 | 2.3541 | 3.8785 | 3.1309 | 0.54925 | 0 | 3.4318 | 90.0222 | 90.0222 | 90.0222 | 91.4922 | 92.4441 | 91.9773 | 90.3652 | 90.0222 | 179.5682 | 90.0222 | 90.0222 | 90.0222 | 93.8463 | 96.3225 | 95.1081 | 90.9145 | 90.0222 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 15 | 6087 | 18.9 | 18.9 | 20.6 | 17.1226 | 15 | 72 | 72 | 10.0934 | 197.1196 | 34.0081 | 224.9351 | 0 | 0 | 0 | 2.3405 | 6.9111 | 7.4332 | 3.6011 | 0 | 5.8804 | 96.6037 | 96.6037 | 96.6037 | 99.9574 | 106.5065 | 107.2547 | 101.7636 | 96.6037 | 197.1196 | 96.6037 | 96.6037 | 96.6037 | 102.2979 | 113.4176 | 114.6879 | 105.3647 | 96.6037 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 16 | 6088 | 19.2 | 19.2 | 20.6 | 17.1226 | 15 | 72 | 72 | 99.7456 | 220.9578 | 26.7012 | 240.0829 | 0 | 0 | 0 | 0.093623 | 58.5333 | 82.6849 | 58.4009 | 0 | 48.0422 | 104.6963 | 104.6963 | 104.6963 | 104.7746 | 153.6589 | 173.8616 | 153.5482 | 104.6963 | 220.9578 | 104.6963 | 104.6963 | 104.6963 | 104.8682 | 212.1922 | 256.5466 | 211.9491 | 104.6963 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 17 | 6089 | 17.1 | 17.1 | 20.6 | 17.1226 | 15 | 94 | 94 | 5.3535 | 98.1143 | 18.2458 | 253.4489 | 0 | 0 | 0 | 0 | 2.3853 | 4.6179 | 4.1453 | 1.2445 | 1.8857 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 98.1143 | 48.6511 | 48.6511 | 48.6511 | 48.6511 | 51.0364 | 53.269 | 52.7964 | 49.8956 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 11 | 18 | 6090 | 17.4 | 17.4 | 20.6 | 17.1226 | 15 | 83 | 83 | 13.0521 | 72.3476 | 9.1988 | 265.7177 | 0 | 0 | 0 | 0 | 3.5312 | 10.8989 | 11.8822 | 5.9051 | 2.6524 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 72.3476 | 35.9116 | 35.9116 | 35.9116 | 35.9116 | 39.4428 | 46.8106 | 47.7938 | 41.8167 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 19 | 6091 | 15.1 | 15.1 | 20.6 | 17.1226 | 15 | 94 | 94 | 15.0434 | 16.3275 | 0.004703 | 277.5583 | 0 | 0 | 0 | 0 | 1.1089 | 11.2553 | 14.8085 | 9.6871 | 0.67251 | 8.8995 | 8.8995 | 8.8995 | 8.8995 | 9.7876 | 17.9143 | 20.7602 | 16.6583 | 16.3275 | 8.8995 | 8.8995 | 8.8995 | 8.8995 | 10.8965 | 29.1696 | 35.5687 | 26.3454 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 20 | 6092 | 15.2 | 15.2 | 20.6 | 17.1226 | 15 | 95 | 95 | 0 | 0 | -8.9373 | 289.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 21 | 6093 | 15.3 | 15.3 | 20.6 | 17.1226 | 15 | 93 | 93 | 0 | 0 | -17.2088 | 302.3887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 22 | 6094 | 15 | 15 | 20.6 | 17.1226 | 15 | 93 | 93 | 0 | 0 | -24.3207 | 316.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 23 | 6095 | 15 | 15 | 20.6 | 17.1226 | 15 | 93 | 93 | 0 | 0 | -29.6974 | 332.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 11 | 24 | 6096 | 14.9 | 14.9 | 17.3 | 17.1114 | 15 | 91 | 91 | 0 | 0 | -32.7438 | 349.2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 1 | 6097 | 14.9 | 14.9 | 17.3 | 17.1114 | 15 | 88 | 88 | 0 | 0 | -33.0342 | 7.1083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 2 | 6098 | 14.4 | 14.4 | 17.3 | 17.1114 | 15 | 90 | 90 | 0 | 0 | -30.8697 | 24.6824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 3 | 6099 | 14.4 | 14.4 | 17.3 | 17.1114 | 15 | 89 | 89 | 0 | 0 | -25.8886 | 40.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 4 | 6100 | 14.3 | 14.3 | 17.3 | 17.1114 | 15 | 90 | 90 | 0 | 0 | -19.0511 | 55.1509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 5 | 6101 | 14.6 | 14.6 | 17.3 | 17.1114 | 15 | 87 | 87 | 0 | 0 | -10.9507 | 68.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 6 | 6102 | 14.8 | 14.8 | 17.3 | 17.1114 | 15 | 87 | 87 | 0 | 0 | -2.0964 | 80.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 7 | 6103 | 15.1 | 15.1 | 17.3 | 17.1114 | 15 | 87 | 87 | 0.10009 | 2.9923 | 7.0819 | 92.1682 | 0.016796 | 0.081597 | 0.098599 | 0.057844 | 0 | 0 | 0 | 0 | 0.0077331 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 2.9923 | 1.473 | 1.5378 | 1.5548 | 1.514 | 1.4562 | 1.4562 | 1.4562 | 1.4562 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 12 | 8 | 6104 | 15.6 | 15.6 | 17.3 | 17.1114 | 15 | 86 | 86 | 3.7836 | 55.1125 | 16.1853 | 104.3018 | 0 | 2.5526 | 3.752 | 2.7535 | 0.14205 | 0 | 0 | 0 | 0.88754 | 24.6949 | 66.255 | 85.7825 | 69.5258 | 27.0077 | 24.6949 | 24.6949 | 24.6949 | 55.1125 | 24.6949 | 68.8076 | 89.5345 | 72.2793 | 27.1498 | 24.6949 | 24.6949 | 24.6949 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 9 | 6105 | 16.3 | 16.3 | 17.3 | 17.1114 | 15 | 81 | 81 | 5.365 | 105.9618 | 24.784 | 117.389 | 0 | 2.6304 | 4.9927 | 4.4304 | 1.2728 | 0 | 0 | 0 | 2.0382 | 49.2329 | 67.4528 | 83.816 | 79.9209 | 58.0492 | 49.2329 | 49.2329 | 49.2329 | 105.9618 | 49.2329 | 70.0832 | 88.8087 | 84.3513 | 59.322 | 49.2329 | 49.2329 | 49.2329 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 10 | 6106 | 16.5 | 16.5 | 17.3 | 17.1114 | 15 | 82 | 82 | 2.9438 | 104.5181 | 32.3489 | 132.1117 | 0 | 0.80862 | 2.3731 | 2.5474 | 1.2295 | 0 | 0 | 0 | 1.4819 | 52.1327 | 52.1327 | 52.1327 | 52.1327 | 52.1327 | 52.1327 | 52.1327 | 52.1327 | 104.5181 | 52.1327 | 52.9413 | 54.5058 | 54.6801 | 53.3622 | 52.1327 | 52.1327 | 52.1327 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 11 | 6107 | 17.3 | 17.3 | 17.3 | 17.1114 | 15 | 79 | 79 | 2.9148 | 123.2612 | 38.205 | 149.0113 | 0 | 0.12408 | 1.8267 | 2.4593 | 1.6512 | 0 | 0 | 0 | 1.7388 | 61.4863 | 61.4863 | 61.4863 | 61.4863 | 61.4863 | 61.4863 | 61.4863 | 61.4863 | 123.2612 | 61.4863 | 61.6103 | 63.313 | 63.9455 | 63.1375 | 61.4863 | 61.4863 | 61.4863 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 12 | 6108 | 17.8 | 17.8 | 17.3 | 17.1114 | 15 | 79 | 79 | 1.749 | 104.8578 | 41.5845 | 168.0487 | 0 | 0 | 0.70763 | 1.3335 | 1.1782 | 0.33275 | 0 | 0 | 1.1422 | 51.6321 | 51.6321 | 51.6321 | 51.6321 | 51.6321 | 51.6321 | 51.6321 | 51.6321 | 104.8578 | 51.6321 | 51.6321 | 52.3397 | 52.9656 | 52.8103 | 51.9649 | 51.6321 | 51.6321 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 13 | 6109 | 18.3 | 18.3 | 17.3 | 17.1114 | 15 | 80 | 80 | 1.9278 | 112.7103 | 41.892 | 188.1367 | 0 | 0 | 0.29859 | 1.2086 | 1.4107 | 0.78636 | 0 | 0 | 1.2897 | 55.6359 | 55.6359 | 55.6359 | 55.6359 | 55.6359 | 55.6359 | 55.6359 | 55.6359 | 112.7103 | 55.6359 | 55.6359 | 55.9345 | 56.8445 | 57.0466 | 56.4223 | 55.6359 | 55.6359 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 14 | 6110 | 18.7 | 18.7 | 17.3 | 17.1114 | 15 | 81 | 81 | 2.272 | 117.5385 | 39.0665 | 207.4935 | 0 | 0 | 0 | 1.0146 | 1.6743 | 1.3532 | 0.23938 | 0 | 1.4615 | 58.1398 | 58.1398 | 58.1398 | 58.1398 | 58.1398 | 58.1398 | 58.1398 | 58.1398 | 117.5385 | 58.1398 | 58.1398 | 58.1398 | 59.1544 | 59.814 | 59.4929 | 58.3791 | 58.1398 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 15 | 6111 | 17.8 | 17.8 | 17.3 | 17.1114 | 15 | 93 | 93 | 2.3208 | 106.6594 | 33.6251 | 224.833 | 0 | 0 | 0 | 0.54203 | 1.5984 | 1.7184 | 0.83183 | 0 | 1.3406 | 52.5635 | 52.5635 | 52.5635 | 52.5635 | 52.5635 | 52.5635 | 52.5635 | 52.5635 | 106.6594 | 52.5635 | 52.5635 | 52.5635 | 53.1055 | 54.1619 | 54.2819 | 53.3953 | 52.5635 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 16 | 6112 | 20.3 | 20.3 | 17.3 | 17.1114 | 15 | 80 | 80 | 69.9497 | 213.6596 | 26.3303 | 239.9404 | 0 | 0 | 0 | 0.16973 | 41.3057 | 58.2454 | 41.0657 | 0 | 33.3404 | 100.3572 | 100.3572 | 100.3572 | 100.5504 | 147.38 | 166.6643 | 147.1067 | 100.3572 | 213.6596 | 100.3572 | 100.3572 | 100.3572 | 100.7201 | 188.6857 | 224.9096 | 188.1724 | 100.3572 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 17 | 6113 | 20.8 | 20.8 | 17.3 | 17.1114 | 15 | 74 | 74 | 75.8913 | 156.6531 | 17.8844 | 253.2884 | 0 | 0 | 0 | 0 | 34.0701 | 65.7184 | 58.8697 | 17.5359 | 26.3469 | 75.723 | 75.723 | 75.723 | 75.723 | 102.8067 | 127.9651 | 122.5208 | 89.663 | 156.6531 | 75.723 | 75.723 | 75.723 | 75.723 | 136.8768 | 193.6835 | 181.3905 | 107.1989 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 12 | 18 | 6114 | 20.1 | 20.1 | 17.3 | 17.1114 | 15 | 75 | 75 | 446.2055 | 65.4149 | 8.8422 | 265.5522 | 0 | 0 | 0 | 0 | 122.1083 | 373.9302 | 406.7088 | 201.2429 | 101.5851 | 43.8594 | 43.8594 | 43.8594 | 43.8594 | 66.2182 | 112.3284 | 118.3304 | 80.7082 | 65.4149 | 43.8594 | 43.8594 | 43.8594 | 43.8594 | 188.3265 | 486.2585 | 525.0392 | 281.9512 | 167 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 19 | 6115 | 19.1 | 19.1 | 17.3 | 17.1114 | 15 | 70 | 70 | 24.5734 | 17.0691 | -0.35261 | 277.3964 | 0 | 0 | 0 | 0 | 1.883 | 18.4493 | 24.2082 | 15.7863 | 10.9309 | 10.3078 | 10.3078 | 10.3078 | 10.3078 | 11.3151 | 20.1765 | 23.257 | 18.752 | 17.0691 | 10.3078 | 10.3078 | 10.3078 | 10.3078 | 13.1981 | 38.6258 | 47.4652 | 34.5383 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 20 | 6116 | 17.1 | 17.1 | 17.3 | 17.1114 | 15 | 79 | 79 | 0 | 0 | -9.3005 | 289.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 21 | 6117 | 16.7 | 16.7 | 17.3 | 17.1114 | 15 | 77 | 77 | 0 | 0 | -17.5816 | 302.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 22 | 6118 | 16.3 | 16.3 | 17.3 | 17.1114 | 15 | 77 | 77 | 0 | 0 | -24.7046 | 316.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 23 | 6119 | 15.6 | 15.6 | 17.3 | 17.1114 | 15 | 81 | 81 | 0 | 0 | -30.0889 | 332.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 12 | 24 | 6120 | 15.8 | 15.8 | 16.775 | 17.0968 | 15 | 81 | 81 | 0 | 0 | -33.1334 | 349.3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 1 | 6121 | 15.7 | 15.7 | 16.775 | 17.0968 | 15 | 82 | 82 | 0 | 0 | -33.4079 | 7.2509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 2 | 6122 | 15.3 | 15.3 | 16.775 | 17.0968 | 15 | 83 | 83 | 0 | 0 | -31.2163 | 24.9001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 3 | 6123 | 15.1 | 15.1 | 16.775 | 17.0968 | 15 | 84 | 84 | 0 | 0 | -26.2026 | 40.9993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 4 | 6124 | 14.4 | 14.4 | 16.775 | 17.0968 | 15 | 88 | 88 | 0 | 0 | -19.3355 | 55.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 5 | 6125 | 14.4 | 14.4 | 16.775 | 17.0968 | 15 | 87 | 87 | 0 | 0 | -11.2129 | 68.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 6 | 6126 | 13.9 | 13.9 | 16.775 | 17.0968 | 15 | 90 | 90 | 0 | 0 | -2.3455 | 80.6376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 7 | 6127 | 14.1 | 14.1 | 16.775 | 17.0968 | 15 | 88 | 88 | 4.6169 | 18.6675 | 6.8358 | 92.4777 | 0.75044 | 3.7491 | 4.5516 | 2.6878 | 0 | 0 | 0 | 0 | 0.33255 | 9.6648 | 15.2229 | 16.7103 | 13.2558 | 8.2739 | 8.2739 | 8.2739 | 8.2739 | 18.6675 | 10.4152 | 18.9719 | 21.2618 | 15.9436 | 8.2739 | 8.2739 | 8.2739 | 8.2739 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 13 | 8 | 6128 | 15.3 | 15.3 | 16.775 | 17.0968 | 15 | 83 | 83 | 130.2573 | 106.1172 | 15.932 | 104.6153 | 0 | 87.4121 | 129.2105 | 95.3191 | 5.591 | 0 | 0 | 0 | 29.8828 | 45.539 | 216.3142 | 297.9747 | 231.7618 | 56.4621 | 45.539 | 45.539 | 45.539 | 106.1172 | 45.539 | 303.7263 | 427.1852 | 327.0809 | 62.0531 | 45.539 | 45.539 | 45.539 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 9 | 6129 | 16.2 | 16.2 | 16.775 | 17.0968 | 15 | 74 | 74 | 103.0472 | 172.376 | 24.5126 | 117.7027 | 0 | 50.1196 | 95.8827 | 85.479 | 25.0029 | 0 | 0 | 0 | 38.624 | 77.6865 | 151.4687 | 218.8375 | 203.5221 | 114.4938 | 77.6865 | 77.6865 | 77.6865 | 172.376 | 77.6865 | 201.5883 | 314.7202 | 289.0011 | 139.4967 | 77.6865 | 77.6865 | 77.6865 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 10 | 6130 | 16.7 | 16.7 | 16.775 | 17.0968 | 15 | 67 | 67 | 629.2756 | 136.4038 | 32.0494 | 132.4134 | 0 | 170.2386 | 506.9273 | 546.6649 | 266.1736 | 0 | 0 | 0 | 313.5962 | 94.3288 | 124.5472 | 184.3115 | 191.3651 | 141.5762 | 94.3288 | 94.3288 | 94.3288 | 136.4038 | 94.3288 | 294.7858 | 691.2388 | 738.03 | 407.7498 | 94.3288 | 94.3288 | 94.3288 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 11 | 6131 | 17.1 | 17.1 | 16.775 | 17.0968 | 15 | 65 | 65 | 247.3584 | 261.6716 | 37.8703 | 149.2742 | 0 | 9.4616 | 154.7905 | 209.4452 | 141.4097 | 0 | 0 | 0 | 146.3284 | 128.0974 | 133.9934 | 224.5548 | 258.6127 | 216.2166 | 128.0974 | 128.0974 | 128.0974 | 261.6716 | 128.0974 | 143.455 | 379.3453 | 468.0579 | 357.6263 | 128.0974 | 128.0974 | 128.0974 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 12 | 6132 | 17.2 | 17.2 | 16.775 | 17.0968 | 15 | 64 | 64 | 69.9524 | 290.6645 | 41.216 | 168.2334 | 0 | 0 | 28.2139 | 53.5158 | 47.4689 | 13.6153 | 0 | 0 | 45.3355 | 130.9135 | 130.9135 | 179.2693 | 222.6342 | 212.2703 | 154.2487 | 130.9135 | 130.9135 | 290.6645 | 130.9135 | 130.9135 | 207.4832 | 276.15 | 259.7392 | 167.864 | 130.9135 | 130.9135 | 336 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 13 | 6133 | 17.2 | 17.2 | 16.775 | 17.0968 | 15 | 64 | 64 | 82.0665 | 301.5052 | 41.5025 | 188.2128 | 0 | 0 | 12.589 | 51.6363 | 60.4357 | 33.8328 | 0 | 0 | 54.4948 | 136.467 | 136.467 | 154.5549 | 210.658 | 223.3011 | 185.078 | 136.467 | 136.467 | 301.5052 | 136.467 | 136.467 | 167.1438 | 262.2943 | 283.7368 | 218.9107 | 136.467 | 136.467 | 356 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 14 | 6134 | 17.5 | 17.5 | 16.775 | 17.0968 | 15 | 64 | 64 | 220.7195 | 287.1179 | 38.6735 | 207.4654 | 0 | 0 | 0 | 98.9905 | 163.6073 | 132.3852 | 23.6136 | 0 | 140.8821 | 137.9729 | 137.9729 | 137.9729 | 204.1625 | 247.3683 | 226.4918 | 153.7621 | 137.9729 | 287.1179 | 137.9729 | 137.9729 | 137.9729 | 303.153 | 410.9756 | 358.877 | 177.3757 | 137.9729 | 428 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 15 | 6135 | 18.4 | 18.4 | 16.775 | 17.0968 | 15 | 56 | 56 | 811.3391 | 110.4021 | 33.2406 | 224.7319 | 0 | 0 | 0 | 190.8403 | 562.0346 | 603.9966 | 292.1456 | 0 | 464.5979 | 100.1546 | 100.1546 | 100.1546 | 117.5166 | 151.2867 | 155.1042 | 126.7331 | 100.1546 | 110.4021 | 100.1546 | 100.1546 | 100.1546 | 308.357 | 713.3213 | 759.1009 | 418.8787 | 100.1546 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 16 | 6136 | 18.5 | 18.5 | 16.775 | 17.0968 | 15 | 54 | 54 | 825.6589 | 88.6334 | 25.9578 | 239.7987 | 0 | 0 | 0 | 3.2313 | 490.58 | 690.5535 | 486.0102 | 0 | 389.3666 | 84.1611 | 84.1611 | 84.1611 | 84.4177 | 123.1227 | 139.0044 | 122.7597 | 84.1611 | 88.6334 | 84.1611 | 84.1611 | 84.1611 | 87.6491 | 613.7026 | 829.558 | 608.7699 | 84.1611 | 478 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 17 | 6137 | 18.2 | 18.2 | 16.775 | 17.0968 | 15 | 60 | 60 | 702.7736 | 81.6119 | 17.5216 | 253.1283 | 0 | 0 | 0 | 0 | 317.8586 | 610.9157 | 546.1067 | 161.3958 | 240.3881 | 66.7123 | 66.7123 | 66.7123 | 66.7123 | 96.993 | 124.9109 | 118.7369 | 82.0876 | 81.6119 | 66.7123 | 66.7123 | 66.7123 | 66.7123 | 414.8515 | 735.8266 | 664.8436 | 243.4835 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 13 | 18 | 6138 | 17.2 | 17.2 | 16.775 | 17.0968 | 15 | 64 | 64 | 269.9721 | 83.9269 | 8.4842 | 265.3868 | 0 | 0 | 0 | 0 | 74.7187 | 227.0405 | 246.3651 | 121.3724 | 52.0731 | 47.3358 | 47.3358 | 47.3358 | 47.3358 | 73.7218 | 127.5125 | 134.3367 | 90.197 | 83.9269 | 47.3358 | 47.3358 | 47.3358 | 47.3358 | 148.4405 | 354.553 | 380.7019 | 211.5694 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 19 | 6139 | 16.3 | 16.3 | 16.775 | 17.0968 | 15 | 65 | 65 | 23.4694 | 7.5091 | -0.71129 | 277.2343 | 0 | 0 | 0 | 0 | 1.8669 | 17.6807 | 23.1373 | 15.0404 | 25.4909 | 6.749 | 6.749 | 6.749 | 6.749 | 8.039 | 18.9655 | 22.7357 | 17.1412 | 7.5091 | 6.749 | 6.749 | 6.749 | 6.749 | 9.9059 | 36.6462 | 45.8731 | 32.1816 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 20 | 6140 | 14 | 14 | 16.775 | 17.0968 | 15 | 95 | 95 | 0 | 0 | -9.6649 | 289.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 21 | 6141 | 13.6 | 13.6 | 16.775 | 17.0968 | 15 | 93 | 93 | 0 | 0 | -17.9558 | 302.1328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 22 | 6142 | 14 | 14 | 16.775 | 17.0968 | 15 | 89 | 89 | 0 | 0 | -25.0899 | 316.2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 23 | 6143 | 12.2 | 12.2 | 16.775 | 17.0968 | 15 | 86 | 86 | 0 | 0 | -30.4819 | 332.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 13 | 24 | 6144 | 12.2 | 12.2 | 15.6125 | 16.8387 | 15 | 89 | 89 | 0 | 0 | -33.5242 | 349.3966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 1 | 6145 | 12.7 | 12.7 | 15.6125 | 16.8387 | 15 | 86 | 86 | 0 | 0 | -33.7826 | 7.3955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 2 | 6146 | 13.1 | 13.1 | 15.6125 | 16.8387 | 15 | 74 | 74 | 0 | 0 | -31.5635 | 25.1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 3 | 6147 | 12.8 | 12.8 | 15.6125 | 16.8387 | 15 | 73 | 73 | 0 | 0 | -26.5169 | 41.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 4 | 6148 | 12 | 12 | 15.6125 | 16.8387 | 15 | 75 | 75 | 0 | 0 | -19.6201 | 55.7294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 5 | 6149 | 11.6 | 11.6 | 15.6125 | 16.8387 | 15 | 78 | 78 | 0 | 0 | -11.4754 | 68.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 6 | 6150 | 11.7 | 11.7 | 15.6125 | 16.8387 | 15 | 80 | 80 | 0 | 0 | -2.5952 | 80.9438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 7 | 6151 | 12.2 | 12.2 | 15.6125 | 16.8387 | 15 | 79 | 79 | 8.0495 | 21.4625 | 6.5889 | 92.788 | 1.2657 | 6.5102 | 7.941 | 4.7201 | 0 | 0 | 0 | 0 | 0.5375 | 11.0661 | 17.4855 | 19.2369 | 15.2945 | 9.5168 | 9.5168 | 9.5168 | 9.5168 | 21.4625 | 12.3318 | 23.9957 | 27.178 | 20.0146 | 9.5168 | 9.5168 | 9.5168 | 9.5168 | 22 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 14 | 8 | 6152 | 13.8 | 13.8 | 15.6125 | 16.8387 | 15 | 76 | 76 | 173.4793 | 103.1014 | 15.6776 | 104.9291 | 0 | 115.7867 | 172.1295 | 127.6412 | 8.3824 | 0 | 0 | 0 | 38.8986 | 45.2014 | 216.1973 | 299.4054 | 233.7043 | 57.5806 | 45.2014 | 45.2014 | 45.2014 | 103.1014 | 45.2014 | 331.984 | 471.535 | 361.3455 | 65.963 | 45.2014 | 45.2014 | 45.2014 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 9 | 6153 | 15.3 | 15.3 | 15.6125 | 16.8387 | 15 | 69 | 69 | 358.3939 | 148.5047 | 24.24 | 118.0163 | 0 | 172.8999 | 333.4134 | 298.6178 | 88.896 | 0 | 0 | 0 | 132.4953 | 82.2088 | 142.2921 | 198.071 | 185.9794 | 113.1004 | 82.2088 | 82.2088 | 82.2088 | 148.5047 | 82.2088 | 315.192 | 531.4844 | 484.5972 | 201.9964 | 82.2088 | 82.2088 | 82.2088 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 10 | 6154 | 16.3 | 16.3 | 15.6125 | 16.8387 | 15 | 64 | 64 | 603.2193 | 141.4505 | 31.7483 | 132.7144 | 0 | 160.6654 | 485.5794 | 526.0476 | 258.3643 | 0 | 0 | 0 | 297.5495 | 96.532 | 129.3083 | 195.5918 | 203.8475 | 149.2392 | 96.532 | 96.532 | 96.532 | 141.4505 | 96.532 | 289.9736 | 681.1712 | 729.8951 | 407.6034 | 96.532 | 96.532 | 96.532 | 439 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 11 | 6155 | 15.6 | 15.6 | 15.6125 | 16.8387 | 15 | 64 | 64 | 87.6334 | 267.6007 | 37.534 | 149.5358 | 0 | 2.972 | 54.7536 | 74.4613 | 50.5506 | 0 | 0 | 0 | 51.3993 | 121.3526 | 125.6151 | 199.8827 | 228.1484 | 193.8546 | 121.3526 | 121.3526 | 121.3526 | 267.6007 | 121.3526 | 128.5871 | 254.6363 | 302.6097 | 244.4052 | 121.3526 | 121.3526 | 121.3526 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 12 | 6156 | 16.7 | 16.7 | 15.6125 | 16.8387 | 15 | 61 | 61 | 314.6831 | 269.6352 | 40.8462 | 168.4168 | 0 | 0 | 126.5174 | 241.5536 | 215.091 | 62.631 | 0 | 0 | 202.3648 | 135.5332 | 135.5332 | 206.4416 | 270.9153 | 256.0839 | 170.6356 | 135.5332 | 135.5332 | 269.6352 | 135.5332 | 135.5332 | 332.959 | 512.4689 | 471.1749 | 233.2666 | 135.5332 | 135.5332 | 472 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 13 | 6157 | 16.3 | 16.3 | 15.6125 | 16.8387 | 15 | 58 | 58 | 308.0565 | 277.984 | 41.1118 | 188.2886 | 0 | 0 | 46.7913 | 194.5111 | 228.289 | 128.3382 | 0 | 0 | 203.016 | 137.701 | 137.701 | 165.143 | 251.7772 | 271.5871 | 212.9684 | 137.701 | 137.701 | 277.984 | 137.701 | 137.701 | 211.9343 | 446.2884 | 499.8761 | 341.3066 | 137.701 | 137.701 | 481 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 14 | 6158 | 16.1 | 16.1 | 15.6125 | 16.8387 | 15 | 62 | 62 | 9.7282 | 212.8395 | 38.2792 | 207.4379 | 0 | 0 | 0 | 4.3815 | 7.253 | 5.8758 | 1.0566 | 0 | 6.1605 | 103.6471 | 103.6471 | 103.6471 | 111.9878 | 117.4541 | 114.8324 | 105.6585 | 103.6471 | 212.8395 | 103.6471 | 103.6471 | 103.6471 | 116.3693 | 124.707 | 120.7082 | 106.7152 | 103.6471 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 15 | 6159 | 16.2 | 16.2 | 15.6125 | 16.8387 | 15 | 65 | 65 | 21.8125 | 220.6195 | 32.8548 | 224.6316 | 0 | 0 | 0 | 5.1666 | 15.1967 | 16.3248 | 7.89 | 0 | 12.3805 | 105.958 | 105.958 | 105.958 | 112.9376 | 126.4871 | 128.0109 | 116.6165 | 105.958 | 220.6195 | 105.958 | 105.958 | 105.958 | 118.1042 | 141.6838 | 144.3357 | 124.5065 | 105.958 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 16 | 6160 | 15.8 | 15.8 | 15.6125 | 16.8387 | 15 | 67 | 67 | 18.854 | 177.2047 | 25.5839 | 239.6577 | 0 | 0 | 0 | 0.10183 | 11.2711 | 15.8379 | 11.1271 | 0 | 8.7953 | 86.1248 | 86.1248 | 86.1248 | 86.228 | 97.5471 | 102.1752 | 97.4011 | 86.1248 | 177.2047 | 86.1248 | 86.1248 | 86.1248 | 86.3298 | 108.8182 | 118.0131 | 108.5282 | 86.1248 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 17 | 6161 | 15.8 | 15.8 | 15.6125 | 16.8387 | 15 | 71 | 71 | 5.1622 | 92.2608 | 17.1573 | 252.9685 | 0 | 0 | 0 | 0 | 2.3521 | 4.5045 | 4.0183 | 1.1782 | 1.7392 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 92.2608 | 45.6485 | 45.6485 | 45.6485 | 45.6485 | 48.0005 | 50.153 | 49.6667 | 46.8266 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 14 | 18 | 6162 | 16 | 16 | 15.6125 | 16.8387 | 15 | 69 | 69 | 91.412 | 85.8439 | 8.1248 | 265.2214 | 0 | 0 | 0 | 0 | 25.5828 | 77.1427 | 83.5135 | 40.9632 | 17.1561 | 44.087 | 44.087 | 44.087 | 44.087 | 60.2235 | 92.7452 | 96.7637 | 69.9248 | 85.8439 | 44.087 | 44.087 | 44.087 | 44.087 | 85.8063 | 169.888 | 180.2771 | 110.888 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 19 | 6163 | 14.8 | 14.8 | 15.6125 | 16.8387 | 15 | 71 | 71 | 17.9043 | 5.94 | -1.0712 | 277.0718 | 0 | 0 | 0 | 0 | 1.4766 | 13.5337 | 17.663 | 11.4455 | 30.06 | 6.3416 | 6.3416 | 6.3416 | 6.3416 | 7.4463 | 16.4669 | 19.5562 | 14.9046 | 5.94 | 6.3416 | 6.3416 | 6.3416 | 6.3416 | 8.9228 | 30.0006 | 37.2192 | 26.3501 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 20 | 6164 | 13.3 | 13.3 | 15.6125 | 16.8387 | 15 | 80 | 80 | 0 | 0 | -10.0305 | 289.1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 21 | 6165 | 12.9 | 12.9 | 15.6125 | 16.8387 | 15 | 83 | 83 | 0 | 0 | -18.3312 | 302.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 22 | 6166 | 13.1 | 13.1 | 15.6125 | 16.8387 | 15 | 86 | 86 | 0 | 0 | -25.4764 | 316.2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 23 | 6167 | 13.2 | 13.2 | 15.6125 | 16.8387 | 15 | 89 | 89 | 0 | 0 | -30.876 | 332.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 14 | 24 | 6168 | 13.9 | 13.9 | 14.2167 | 16.2538 | 15 | 89 | 89 | 0 | 0 | -33.9163 | 349.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 1 | 6169 | 13.5 | 13.5 | 14.2167 | 16.2538 | 15 | 92 | 92 | 0 | 0 | -34.1582 | 7.5423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 2 | 6170 | 12.9 | 12.9 | 14.2167 | 16.2538 | 15 | 96 | 96 | 0 | 0 | -31.9113 | 25.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 3 | 6171 | 12.4 | 12.4 | 14.2167 | 16.2538 | 15 | 94 | 94 | 0 | 0 | -26.8316 | 41.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 4 | 6172 | 12.4 | 12.4 | 14.2167 | 16.2538 | 15 | 93 | 93 | 0 | 0 | -19.905 | 56.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 5 | 6173 | 11.5 | 11.5 | 14.2167 | 16.2538 | 15 | 97 | 97 | 0 | 0 | -11.7382 | 69.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 6 | 6174 | 10.9 | 10.9 | 14.2167 | 16.2538 | 15 | 97 | 97 | 0 | 0 | -2.8454 | 81.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 7 | 6175 | 10.6 | 10.6 | 14.2167 | 16.2538 | 15 | 98 | 98 | 20.7153 | 23.726 | 6.3413 | 93.099 | 3.147 | 16.6849 | 20.449 | 12.2344 | 0 | 0 | 0 | 0 | 1.274 | 11.9153 | 25.2398 | 28.9446 | 20.8594 | 8.8179 | 8.8179 | 8.8179 | 8.8179 | 23.726 | 15.0623 | 41.9247 | 49.3936 | 33.0938 | 8.8179 | 8.8179 | 8.8179 | 8.8179 | 25 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 15 | 8 | 6176 | 14.2 | 14.2 | 14.2167 | 16.2538 | 15 | 78 | 78 | 121.7402 | 101.3372 | 15.4221 | 105.2432 | 0 | 80.8062 | 120.8184 | 90.0568 | 6.5412 | 0 | 0 | 0 | 26.6628 | 43.0289 | 218.0726 | 304.7476 | 238.1113 | 57.1985 | 43.0289 | 43.0289 | 43.0289 | 101.3372 | 43.0289 | 298.8788 | 425.5659 | 328.1681 | 63.7396 | 43.0289 | 43.0289 | 43.0289 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 9 | 6177 | 15.6 | 15.6 | 14.2167 | 16.2538 | 15 | 73 | 73 | 362.2248 | 145.9565 | 23.966 | 118.3295 | 0 | 173.3059 | 336.8974 | 303.139 | 91.8058 | 0 | 0 | 0 | 132.0435 | 81.0972 | 140.2552 | 196.0972 | 184.5737 | 112.4351 | 81.0972 | 81.0972 | 81.0972 | 145.9565 | 81.0972 | 313.5612 | 532.9946 | 487.7127 | 204.241 | 81.0972 | 81.0972 | 81.0972 | 278 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 10 | 6178 | 16.7 | 16.7 | 14.2167 | 16.2538 | 15 | 69 | 69 | 465.5044 | 172.7606 | 31.4458 | 133.0144 | 0 | 122.025 | 374.4261 | 407.4935 | 201.8567 | 0 | 0 | 0 | 227.2394 | 101.8899 | 136.7978 | 209.0028 | 218.4624 | 159.6355 | 101.8899 | 101.8899 | 101.8899 | 172.7606 | 101.8899 | 258.8228 | 583.4289 | 625.956 | 361.4922 | 101.8899 | 101.8899 | 101.8899 | 400 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 11 | 6179 | 17.2 | 17.2 | 14.2167 | 16.2538 | 15 | 66 | 66 | 470.5847 | 204.3796 | 37.1963 | 149.796 | 0 | 13.9106 | 293.5493 | 401.2308 | 273.8768 | 0 | 0 | 0 | 273.6204 | 118.1779 | 122.6466 | 212.4801 | 247.0726 | 206.1604 | 118.1779 | 118.1779 | 118.1779 | 204.3796 | 118.1779 | 136.5572 | 506.0294 | 648.3035 | 480.0371 | 118.1779 | 118.1779 | 118.1779 | 478 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 12 | 6180 | 17.4 | 17.4 | 14.2167 | 16.2538 | 15 | 62 | 62 | 496.0555 | 216.5086 | 40.4751 | 168.5989 | 0 | 0 | 198.7884 | 382.04 | 341.4977 | 100.9107 | 0 | 0 | 316.4914 | 125.8617 | 125.8617 | 189.8838 | 248.902 | 235.8449 | 158.3611 | 125.8617 | 125.8617 | 216.5086 | 125.8617 | 125.8617 | 388.6722 | 630.942 | 577.3426 | 259.2718 | 125.8617 | 125.8617 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 13 | 6181 | 17.5 | 17.5 | 14.2167 | 16.2538 | 15 | 59 | 59 | 33.2723 | 270.241 | 40.7199 | 188.364 | 0 | 0 | 5.0032 | 21.0814 | 24.8104 | 14.0059 | 0 | 0 | 21.759 | 121.78 | 121.78 | 136.7666 | 184.9278 | 196.0979 | 163.7335 | 121.78 | 121.78 | 270.241 | 121.78 | 121.78 | 141.7697 | 206.0092 | 220.9083 | 177.7394 | 121.78 | 121.78 | 292 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 14 | 6182 | 18.4 | 18.4 | 14.2167 | 16.2538 | 15 | 56 | 56 | 496.6611 | 212.9959 | 37.8838 | 207.4108 | 0 | 0 | 0 | 224.6228 | 372.4196 | 302.0579 | 54.7549 | 0 | 312.0041 | 123.1117 | 123.1117 | 123.1117 | 195.2885 | 242.7791 | 220.1702 | 140.7058 | 123.1117 | 212.9959 | 123.1117 | 123.1117 | 123.1117 | 419.9113 | 615.1987 | 522.2282 | 195.4606 | 123.1117 | 525 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 15 | 6183 | 17.3 | 17.3 | 14.2167 | 16.2538 | 15 | 58 | 58 | 14.951 | 205.5901 | 32.4678 | 224.5321 | 0 | 0 | 0 | 3.5659 | 10.4754 | 11.2485 | 5.4324 | 0 | 8.4099 | 99.5833 | 99.5833 | 99.5833 | 104.8158 | 114.9545 | 116.0889 | 107.5547 | 99.5833 | 205.5901 | 99.5833 | 99.5833 | 99.5833 | 108.3817 | 125.4299 | 127.3375 | 112.9871 | 99.5833 | 214 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 16 | 6184 | 17.7 | 17.7 | 14.2167 | 16.2538 | 15 | 60 | 60 | 51.7053 | 201.1446 | 25.2087 | 239.5173 | 0 | 0 | 0 | 0.35622 | 31.0973 | 43.6219 | 30.5935 | 0 | 23.8554 | 94.3563 | 94.3563 | 94.3563 | 94.868 | 139.0283 | 157.0204 | 138.3046 | 94.3563 | 201.1446 | 94.3563 | 94.3563 | 94.3563 | 95.2242 | 170.1256 | 200.6423 | 168.8981 | 94.3563 | 225 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 17 | 6185 | 17.2 | 17.2 | 14.2167 | 16.2538 | 15 | 60 | 60 | 206.2488 | 150.578 | 16.7919 | 252.8091 | 0 | 0 | 0 | 0 | 94.6611 | 180.6481 | 160.814 | 46.7771 | 68.422 | 77.8342 | 77.8342 | 77.8342 | 77.8342 | 133.4983 | 184.0617 | 172.3985 | 105.3408 | 150.578 | 77.8342 | 77.8342 | 77.8342 | 77.8342 | 228.1594 | 364.7099 | 333.2125 | 152.1179 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 18 | 6186 | 16.4 | 16.4 | 14.2167 | 16.2538 | 15 | 62 | 62 | 306.1195 | 77.1478 | 7.7643 | 265.056 | 0 | 0 | 0 | 0 | 86.6175 | 259.2194 | 279.9741 | 136.7238 | 55.8522 | 44.6299 | 44.6299 | 44.6299 | 44.6299 | 70.5412 | 122.1744 | 128.3831 | 85.5303 | 77.1478 | 44.6299 | 44.6299 | 44.6299 | 44.6299 | 157.1588 | 381.3939 | 408.3573 | 222.2541 | 133 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 19 | 6187 | 14.3 | 14.3 | 14.2167 | 16.2538 | 15 | 76 | 76 | 18.2788 | 5.445 | -1.4322 | 276.9091 | 0 | 0 | 0 | 0 | 1.5609 | 13.8626 | 18.0439 | 11.6553 | 27.555 | 5.8194 | 5.8194 | 5.8194 | 5.8194 | 6.9099 | 15.5047 | 18.4259 | 13.9625 | 5.445 | 5.8194 | 5.8194 | 5.8194 | 5.8194 | 8.4708 | 29.3673 | 36.4698 | 25.6177 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 20 | 6188 | 12.8 | 12.8 | 14.2167 | 16.2538 | 15 | 85 | 85 | 0 | 0 | -10.3972 | 288.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 21 | 6189 | 11.7 | 11.7 | 14.2167 | 16.2538 | 15 | 87 | 87 | 0 | 0 | -18.7076 | 301.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 22 | 6190 | 11.1 | 11.1 | 14.2167 | 16.2538 | 15 | 88 | 88 | 0 | 0 | -25.8639 | 316.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 23 | 6191 | 10.3 | 10.3 | 14.2167 | 16.2538 | 15 | 90 | 90 | 0 | 0 | -31.2713 | 332.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 15 | 24 | 6192 | 9.9 | 9.9 | 14.1625 | 15.757 | 15 | 92 | 92 | 0 | 0 | -34.3094 | 349.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 1 | 6193 | 9 | 9 | 14.1625 | 15.757 | 15 | 95 | 95 | 0 | 0 | -34.5347 | 7.6909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 2 | 6194 | 9.1 | 9.1 | 14.1625 | 15.757 | 15 | 90 | 90 | 0 | 0 | -32.2595 | 25.5683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 3 | 6195 | 7.9 | 7.9 | 14.1625 | 15.757 | 15 | 95 | 95 | 0 | 0 | -27.1464 | 41.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 4 | 6196 | 7.8 | 7.8 | 14.1625 | 15.757 | 15 | 95 | 95 | 0 | 0 | -20.19 | 56.3158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 5 | 6197 | 7.9 | 7.9 | 14.1625 | 15.757 | 15 | 95 | 95 | 0 | 0 | -12.0013 | 69.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 6 | 6198 | 8.4 | 8.4 | 14.1625 | 15.757 | 15 | 93 | 93 | 0 | 0 | -3.0961 | 81.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 7 | 6199 | 9.1 | 9.1 | 14.1625 | 15.757 | 15 | 90 | 90 | 8.8386 | 18.5031 | 6.0929 | 93.4105 | 1.2955 | 7.0892 | 8.7301 | 5.2571 | 0 | 0 | 0 | 0 | 0.49685 | 9.4616 | 15.021 | 16.5957 | 13.263 | 8.2184 | 8.2184 | 8.2184 | 8.2184 | 18.5031 | 10.757 | 22.1102 | 25.3258 | 18.5201 | 8.2184 | 8.2184 | 8.2184 | 8.2184 | 19 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 16 | 8 | 6200 | 11.3 | 11.3 | 14.1625 | 15.757 | 15 | 83 | 83 | 109.0603 | 98.6852 | 15.1656 | 105.5574 | 0 | 71.9841 | 108.2522 | 81.1077 | 6.4514 | 0 | 0 | 0 | 23.3148 | 41.5307 | 218.3387 | 307.421 | 240.7482 | 57.3766 | 41.5307 | 41.5307 | 41.5307 | 98.6852 | 41.5307 | 290.3228 | 415.6732 | 321.8559 | 63.8279 | 41.5307 | 41.5307 | 41.5307 | 122 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 9 | 6201 | 12.4 | 12.4 | 14.1625 | 15.757 | 15 | 80 | 80 | 231.1135 | 160.9499 | 23.6908 | 118.6423 | 0 | 109.6478 | 214.8921 | 194.2555 | 59.8266 | 0 | 0 | 0 | 83.0501 | 78.3964 | 155.729 | 229.9557 | 215.4011 | 120.591 | 78.3964 | 78.3964 | 78.3964 | 160.9499 | 78.3964 | 265.3768 | 444.8478 | 409.6566 | 180.4176 | 78.3964 | 78.3964 | 78.3964 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 10 | 6202 | 14.3 | 14.3 | 14.1625 | 15.757 | 15 | 76 | 76 | 289.0066 | 207.4068 | 31.1418 | 133.3133 | 0 | 74.5344 | 232.2656 | 253.9388 | 126.858 | 0 | 0 | 0 | 139.5932 | 107.2591 | 145.5684 | 226.6392 | 237.7788 | 172.4617 | 107.2591 | 107.2591 | 107.2591 | 207.4068 | 107.2591 | 220.1028 | 458.9049 | 491.7176 | 299.3197 | 107.2591 | 107.2591 | 107.2591 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 11 | 6203 | 15.6 | 15.6 | 14.1625 | 15.757 | 15 | 69 | 69 | 342.3778 | 235.6773 | 36.8572 | 150.0546 | 0 | 8.6255 | 213.2183 | 292.9107 | 201.02 | 0 | 0 | 0 | 197.3227 | 123.697 | 127.7522 | 223.9396 | 261.4063 | 218.2047 | 123.697 | 123.697 | 123.697 | 235.6773 | 123.697 | 136.3776 | 437.1579 | 554.317 | 419.2248 | 123.697 | 123.697 | 123.697 | 433 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 12 | 6204 | 16.8 | 16.8 | 14.1625 | 15.757 | 15 | 65 | 65 | 493.1947 | 215.8494 | 40.1027 | 168.7796 | 0 | 0 | 196.9847 | 381.0773 | 341.94 | 102.4989 | 0 | 0 | 312.1506 | 125.2758 | 125.2758 | 188.9159 | 248.391 | 235.7468 | 158.3903 | 125.2758 | 125.2758 | 215.8494 | 125.2758 | 125.2758 | 385.9006 | 629.4682 | 577.6868 | 260.8891 | 125.2758 | 125.2758 | 528 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 13 | 6205 | 17.5 | 17.5 | 14.1625 | 15.757 | 15 | 63 | 63 | 211.2094 | 293.952 | 40.327 | 188.4387 | 0 | 0 | 31.4354 | 134.2792 | 158.4642 | 89.8229 | 0 | 0 | 137.048 | 139.8784 | 139.8784 | 162.9465 | 238.4162 | 256.1638 | 205.7929 | 139.8784 | 139.8784 | 293.952 | 139.8784 | 139.8784 | 194.3819 | 372.6955 | 414.6279 | 295.6159 | 139.8784 | 139.8784 | 431 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 14 | 6206 | 18.5 | 18.5 | 14.1625 | 15.757 | 15 | 59 | 59 | 534.2044 | 200.1374 | 37.4873 | 207.3841 | 0 | 0 | 0 | 242.5962 | 402.8487 | 327.1179 | 59.7659 | 0 | 332.8626 | 120.4899 | 120.4899 | 120.4899 | 190.0065 | 235.9273 | 214.2265 | 137.6159 | 120.4899 | 200.1374 | 120.4899 | 120.4899 | 120.4899 | 432.6027 | 638.776 | 541.3444 | 197.3818 | 120.4899 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 15 | 6207 | 18.9 | 18.9 | 14.1625 | 15.757 | 15 | 62 | 62 | 643.7973 | 149.1634 | 32.0797 | 224.4334 | 0 | 0 | 0 | 154.5996 | 453.6019 | 486.8903 | 234.965 | 0 | 358.8366 | 103.507 | 103.507 | 103.507 | 131.7317 | 186.3192 | 192.3966 | 146.4036 | 103.507 | 149.1634 | 103.507 | 103.507 | 103.507 | 286.3313 | 639.9211 | 679.2869 | 381.3686 | 103.507 | 508 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 16 | 6208 | 18.2 | 18.2 | 14.1625 | 15.757 | 15 | 64 | 64 | 68.7764 | 204.623 | 24.8325 | 239.3776 | 0 | 0 | 0 | 0.57632 | 41.6122 | 58.2722 | 40.7971 | 0 | 31.377 | 96.3979 | 96.3979 | 96.3979 | 97.0467 | 143.2445 | 162.0002 | 142.3269 | 96.3979 | 204.623 | 96.3979 | 96.3979 | 96.3979 | 97.623 | 184.8566 | 220.2723 | 183.124 | 96.3979 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 17 | 6209 | 18.6 | 18.6 | 14.1625 | 15.757 | 15 | 66 | 66 | 108.1156 | 150.6953 | 16.4253 | 252.65 | 0 | 0 | 0 | 0 | 49.9797 | 95.0461 | 84.4358 | 24.3641 | 35.3047 | 74.3035 | 74.3035 | 74.3035 | 74.3035 | 115.52 | 152.6846 | 143.9347 | 94.3958 | 150.6953 | 74.3035 | 74.3035 | 74.3035 | 74.3035 | 165.4997 | 247.7308 | 228.3705 | 118.7599 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 18 | 6210 | 16.9 | 16.9 | 14.1625 | 15.757 | 15 | 76 | 76 | 69.9856 | 79.5983 | 7.4027 | 264.8906 | 0 | 0 | 0 | 0 | 20.0185 | 59.4631 | 64.0751 | 31.1527 | 12.4017 | 40.7623 | 40.7623 | 40.7623 | 40.7623 | 56.2649 | 86.8113 | 90.3829 | 64.8874 | 79.5983 | 40.7623 | 40.7623 | 40.7623 | 40.7623 | 76.2834 | 146.2745 | 154.458 | 96.0401 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 19 | 6211 | 16.3 | 16.3 | 14.1625 | 15.757 | 15 | 81 | 81 | 14.8152 | 8.5041 | -1.7942 | 276.7459 | 0 | 0 | 0 | 0 | 1.3084 | 11.2725 | 14.6334 | 9.4222 | 2.4959 | 4.9304 | 4.9304 | 4.9304 | 4.9304 | 5.5214 | 10.0221 | 11.5402 | 9.1863 | 8.5041 | 4.9304 | 4.9304 | 4.9304 | 4.9304 | 6.8298 | 21.2946 | 26.1735 | 18.6085 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 20 | 6212 | 15.5 | 15.5 | 14.1625 | 15.757 | 15 | 85 | 85 | 0 | 0 | -10.7648 | 288.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 21 | 6213 | 15.7 | 15.7 | 14.1625 | 15.757 | 15 | 86 | 86 | 0 | 0 | -19.0849 | 301.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 22 | 6214 | 16.1 | 16.1 | 14.1625 | 15.757 | 15 | 85 | 85 | 0 | 0 | -26.2524 | 316.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 23 | 6215 | 15.1 | 15.1 | 14.1625 | 15.757 | 15 | 90 | 90 | 0 | 0 | -31.6677 | 332.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 16 | 24 | 6216 | 15.3 | 15.3 | 13.8417 | 15.1389 | 15 | 89 | 89 | 0 | 0 | -34.7034 | 349.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 1 | 6217 | 15.7 | 15.7 | 13.8417 | 15.1389 | 15 | 85 | 85 | 0 | 0 | -34.912 | 7.8414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 2 | 6218 | 15.6 | 15.6 | 13.8417 | 15.1389 | 15 | 86 | 86 | 0 | 0 | -32.608 | 25.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 3 | 6219 | 15.4 | 15.4 | 13.8417 | 15.1389 | 15 | 87 | 87 | 0 | 0 | -27.4615 | 42.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 4 | 6220 | 15.2 | 15.2 | 13.8417 | 15.1389 | 15 | 88 | 88 | 0 | 0 | -20.4752 | 56.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 5 | 6221 | 14.5 | 14.5 | 13.8417 | 15.1389 | 15 | 91 | 91 | 0 | 0 | -12.2646 | 69.6963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 6 | 6222 | 14.6 | 14.6 | 13.8417 | 15.1389 | 15 | 90 | 90 | 0 | 0 | -3.3473 | 81.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 7 | 6223 | 14.7 | 14.7 | 13.8417 | 15.1389 | 15 | 91 | 91 | 0.91955 | 5.9532 | 5.8438 | 93.7225 | 0.12985 | 0.7344 | 0.90876 | 0.55077 | 0 | 0 | 0 | 0 | 0.046815 | 3.0027 | 3.9353 | 4.2042 | 3.652 | 2.8024 | 2.8024 | 2.8024 | 2.8024 | 5.9532 | 3.1325 | 4.6697 | 5.113 | 4.2028 | 2.8024 | 2.8024 | 2.8024 | 2.8024 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 17 | 8 | 6224 | 14.5 | 14.5 | 13.8417 | 15.1389 | 15 | 89 | 89 | 4.277 | 52.1081 | 14.9081 | 105.8715 | 0 | 2.8069 | 4.2458 | 3.1976 | 0.27624 | 0 | 0 | 0 | 0.89186 | 22.6166 | 82.7436 | 113.5665 | 91.1121 | 28.534 | 22.6166 | 22.6166 | 22.6166 | 52.1081 | 22.6166 | 85.5506 | 117.8123 | 94.3097 | 28.8102 | 22.6166 | 22.6166 | 22.6166 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 9 | 6225 | 14.5 | 14.5 | 13.8417 | 15.1389 | 15 | 90 | 90 | 2.1623 | 63.2342 | 23.4143 | 118.9545 | 0 | 1.0171 | 2.0099 | 1.8253 | 0.57145 | 0 | 0 | 0 | 0.76575 | 31.2719 | 31.2719 | 31.2719 | 31.2719 | 31.2719 | 31.2719 | 31.2719 | 31.2719 | 63.2342 | 31.2719 | 32.289 | 33.2817 | 33.0971 | 31.8433 | 31.2719 | 31.2719 | 31.2719 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 10 | 6226 | 15.7 | 15.7 | 13.8417 | 15.1389 | 15 | 83 | 83 | 5.8469 | 139.2062 | 30.8365 | 133.611 | 0 | 1.483 | 4.6948 | 5.1564 | 2.5975 | 0 | 0 | 0 | 2.7938 | 66.0489 | 72.7438 | 87.2432 | 89.3272 | 77.7751 | 66.0489 | 66.0489 | 66.0489 | 139.2062 | 66.0489 | 74.2268 | 91.9379 | 94.4836 | 80.3726 | 66.0489 | 66.0489 | 66.0489 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 11 | 6227 | 16.4 | 16.4 | 13.8417 | 15.1389 | 15 | 79 | 79 | 16.5159 | 212.5665 | 36.5168 | 150.3116 | 0 | 0.34376 | 10.2677 | 14.1769 | 9.7815 | 0 | 0 | 0 | 9.4335 | 98.1412 | 99.2447 | 131.1033 | 143.6532 | 129.5427 | 98.1412 | 98.1412 | 98.1412 | 212.5665 | 98.1412 | 99.5885 | 141.371 | 157.8301 | 139.3242 | 98.1412 | 98.1412 | 98.1412 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 12 | 6228 | 16.8 | 16.8 | 13.8417 | 15.1389 | 15 | 76 | 76 | 23.0958 | 246.501 | 39.7293 | 168.9588 | 0 | 0 | 9.1933 | 17.9029 | 16.1252 | 4.9016 | 0 | 0 | 14.499 | 114.5659 | 114.5659 | 135.7255 | 155.7716 | 151.68 | 125.8475 | 114.5659 | 114.5659 | 246.501 | 114.5659 | 114.5659 | 144.9188 | 173.6745 | 167.8052 | 130.749 | 114.5659 | 114.5659 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 13 | 6229 | 16.3 | 16.3 | 13.8417 | 15.1389 | 15 | 79 | 79 | 3.5947 | 147.686 | 39.9331 | 188.5128 | 0 | 0 | 0.52946 | 2.2931 | 2.7134 | 1.5443 | 0 | 0 | 2.314 | 74.059 | 74.059 | 74.059 | 74.059 | 74.059 | 74.059 | 74.059 | 74.059 | 147.686 | 74.059 | 74.059 | 74.5885 | 76.3521 | 76.7724 | 75.6033 | 74.059 | 74.059 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 14 | 6230 | 16.4 | 16.4 | 13.8417 | 15.1389 | 15 | 78 | 78 | 3.5951 | 141.7784 | 37.0899 | 207.3576 | 0 | 0 | 0 | 1.6392 | 2.7263 | 2.2163 | 0.40807 | 0 | 2.2216 | 70.9152 | 70.9152 | 70.9152 | 70.9152 | 70.9152 | 70.9152 | 70.9152 | 70.9152 | 141.7784 | 70.9152 | 70.9152 | 70.9152 | 72.5544 | 73.6415 | 73.1315 | 71.3233 | 70.9152 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 15 | 6231 | 16.9 | 16.9 | 13.8417 | 15.1389 | 15 | 73 | 73 | 9.2753 | 183.878 | 31.6905 | 224.3352 | 0 | 0 | 0 | 2.2424 | 6.5713 | 7.0509 | 3.4001 | 0 | 5.122 | 90.2676 | 90.2676 | 90.2676 | 93.3128 | 99.1916 | 99.8428 | 94.885 | 90.2676 | 183.878 | 90.2676 | 90.2676 | 90.2676 | 95.5552 | 105.7629 | 106.8937 | 98.2851 | 90.2676 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 16 | 6232 | 15.9 | 15.9 | 13.8417 | 15.1389 | 15 | 80 | 80 | 1.461 | 66.3411 | 24.4552 | 239.2384 | 0 | 0 | 0 | 0.014424 | 0.88916 | 1.243 | 0.86876 | 0 | 0.65893 | 32.1322 | 32.1322 | 32.1322 | 32.1322 | 32.1322 | 32.1322 | 32.1322 | 32.1322 | 66.3411 | 32.1322 | 32.1322 | 32.1322 | 32.1467 | 33.0214 | 33.3753 | 33.001 | 32.1322 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 17 | 6233 | 15.8 | 15.8 | 13.8417 | 15.1389 | 15 | 76 | 76 | 1.2414 | 43.6011 | 16.0577 | 252.4912 | 0 | 0 | 0 | 0 | 0.57799 | 1.0953 | 0.97106 | 0.27795 | 0.3989 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 43.6011 | 20.8884 | 20.8884 | 20.8884 | 20.8884 | 21.4664 | 21.9837 | 21.8594 | 21.1663 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 17 | 18 | 6234 | 15 | 15 | 13.8417 | 15.1389 | 15 | 83 | 83 | 0.80849 | 18.861 | 7.0403 | 264.725 | 0 | 0 | 0 | 0 | 0.23374 | 0.68921 | 0.74095 | 0.35865 | 0.13901 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 18.861 | 8.8867 | 8.8867 | 8.8867 | 8.8867 | 9.1205 | 9.576 | 9.6277 | 9.2454 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 19 | 6235 | 15 | 15 | 13.8417 | 15.1389 | 15 | 83 | 83 | 38.5654 | 5.4972 | -2.157 | 276.5823 | 0 | 0 | 0 | 0 | 3.5188 | 29.4378 | 38.1126 | 24.4615 | 0.50281 | 3.1963 | 3.1963 | 3.1963 | 3.1963 | 4.7789 | 16.4358 | 20.3372 | 14.1977 | 5.4972 | 3.1963 | 3.1963 | 3.1963 | 3.1963 | 8.2977 | 45.8737 | 58.4498 | 38.6592 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 20 | 6236 | 14.9 | 14.9 | 13.8417 | 15.1389 | 15 | 81 | 81 | 0 | 0 | -11.1332 | 288.6789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 21 | 6237 | 14.7 | 14.7 | 13.8417 | 15.1389 | 15 | 81 | 81 | 0 | 0 | -19.463 | 301.6121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 22 | 6238 | 14.2 | 14.2 | 13.8417 | 15.1389 | 15 | 83 | 83 | 0 | 0 | -26.6418 | 315.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 23 | 6239 | 13.8 | 13.8 | 13.8417 | 15.1389 | 15 | 88 | 88 | 0 | 0 | -32.0649 | 331.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 17 | 24 | 6240 | 13.6 | 13.6 | 15.2542 | 14.9134 | 15 | 87 | 87 | 0 | 0 | -35.0984 | 349.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 1 | 6241 | 12 | 12 | 15.2542 | 14.9134 | 15 | 89 | 89 | 0 | 0 | -35.2899 | 7.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 2 | 6242 | 11.5 | 11.5 | 15.2542 | 14.9134 | 15 | 94 | 94 | 0 | 0 | -32.9569 | 26.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 3 | 6243 | 11.4 | 11.4 | 15.2542 | 14.9134 | 15 | 94 | 94 | 0 | 0 | -27.7767 | 42.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 4 | 6244 | 11.3 | 11.3 | 15.2542 | 14.9134 | 15 | 96 | 96 | 0 | 0 | -20.7605 | 56.9094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 5 | 6245 | 11.7 | 11.7 | 15.2542 | 14.9134 | 15 | 95 | 95 | 0 | 0 | -12.5282 | 70.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 6 | 6246 | 11.9 | 11.9 | 15.2542 | 14.9134 | 15 | 94 | 94 | 0 | 0 | -3.5989 | 82.1783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 7 | 6247 | 11.9 | 11.9 | 15.2542 | 14.9134 | 15 | 94 | 94 | 0.28646 | 2.9869 | 5.5939 | 94.0348 | 0.038908 | 0.22779 | 0.28324 | 0.17277 | 0 | 0 | 0 | 0 | 0.013061 | 1.5028 | 1.9698 | 2.1069 | 1.8338 | 1.4066 | 1.4066 | 1.4066 | 1.4066 | 2.9869 | 1.5417 | 2.1976 | 2.3902 | 2.0065 | 1.4066 | 1.4066 | 1.4066 | 1.4066 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 18 | 8 | 6248 | 12.3 | 12.3 | 15.2542 | 14.9134 | 15 | 92 | 92 | 3.5384 | 46.2808 | 14.6496 | 106.1855 | 0 | 2.3087 | 3.5128 | 2.6592 | 0.24779 | 0 | 0 | 0 | 0.71917 | 20.5369 | 66.7634 | 90.8723 | 73.7797 | 25.4982 | 20.5369 | 20.5369 | 20.5369 | 46.2808 | 20.5369 | 69.0721 | 94.3851 | 76.4388 | 25.746 | 20.5369 | 20.5369 | 20.5369 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 9 | 6249 | 12.6 | 12.6 | 15.2542 | 14.9134 | 15 | 84 | 84 | 42.7909 | 149.0707 | 23.1366 | 119.266 | 0 | 19.9537 | 39.7589 | 36.2738 | 11.5401 | 0 | 0 | 0 | 14.9293 | 66.5832 | 127.582 | 188.1268 | 177.473 | 101.8614 | 66.5832 | 66.5832 | 66.5832 | 149.0707 | 66.5832 | 147.5357 | 227.8856 | 213.7468 | 113.4015 | 66.5832 | 66.5832 | 66.5832 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 10 | 6250 | 13.8 | 13.8 | 15.2542 | 14.9134 | 15 | 73 | 73 | 286.3376 | 203.672 | 30.5299 | 133.9073 | 0 | 71.4017 | 229.699 | 253.4418 | 128.7218 | 0 | 0 | 0 | 135.328 | 105.3787 | 142.0526 | 223.3585 | 235.5534 | 171.4938 | 105.3787 | 105.3787 | 105.3787 | 203.672 | 105.3787 | 213.4542 | 453.0575 | 488.9952 | 300.2156 | 105.3787 | 105.3787 | 105.3787 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 11 | 6251 | 13.8 | 13.8 | 15.2542 | 14.9134 | 15 | 72 | 72 | 116.4996 | 262.0632 | 36.1751 | 150.5667 | 0 | 1.9137 | 72.2975 | 100.3304 | 69.5911 | 0 | 0 | 0 | 65.9368 | 120.4109 | 122.4925 | 199.0501 | 229.5419 | 196.1063 | 120.4109 | 120.4109 | 120.4109 | 262.0632 | 120.4109 | 124.4061 | 271.3475 | 329.8723 | 265.6975 | 120.4109 | 120.4109 | 120.4109 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 12 | 6252 | 14.8 | 14.8 | 15.2542 | 14.9134 | 15 | 72 | 72 | 275.0797 | 270.7367 | 39.3548 | 169.1363 | 0 | 0 | 109.117 | 213.9039 | 193.3888 | 59.5891 | 0 | 0 | 171.2633 | 133.1476 | 133.1476 | 203.2685 | 270.6068 | 257.4233 | 171.4409 | 133.1476 | 133.1476 | 270.7367 | 133.1476 | 133.1476 | 312.3856 | 484.5107 | 450.8121 | 231.03 | 133.1476 | 133.1476 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 13 | 6253 | 16 | 16 | 15.2542 | 14.9134 | 15 | 67 | 67 | 728.4842 | 145.8196 | 39.5384 | 188.5861 | 0 | 0 | 106.1653 | 466.2372 | 553.1936 | 316.0968 | 0 | 0 | 465.1804 | 112.603 | 112.603 | 129.4293 | 186.4977 | 200.2795 | 162.7017 | 112.603 | 112.603 | 145.8196 | 112.603 | 112.603 | 235.5946 | 652.7348 | 753.4731 | 478.7984 | 112.603 | 112.603 | 611 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 14 | 6254 | 14.2 | 14.2 | 15.2542 | 14.9134 | 15 | 73 | 73 | 846.8738 | 112.0579 | 36.6918 | 207.3312 | 0 | 0 | 0 | 387.6936 | 645.7878 | 525.5882 | 97.5062 | 0 | 518.9421 | 106.1396 | 106.1396 | 106.1396 | 140.1546 | 162.799 | 152.2531 | 114.6945 | 106.1396 | 112.0579 | 106.1396 | 106.1396 | 106.1396 | 527.8482 | 808.5868 | 677.8413 | 212.2008 | 106.1396 | 631 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 15 | 6255 | 13.3 | 13.3 | 15.2542 | 14.9134 | 15 | 74 | 74 | 11.5081 | 190.7048 | 31.3006 | 224.2376 | 0 | 0 | 0 | 2.8008 | 8.1978 | 8.7926 | 4.2369 | 0 | 6.2952 | 92.9823 | 92.9823 | 92.9823 | 97.0586 | 104.9134 | 105.7791 | 99.1486 | 92.9823 | 190.7048 | 92.9823 | 92.9823 | 92.9823 | 99.8594 | 113.1112 | 114.5717 | 103.3855 | 92.9823 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 16 | 6256 | 14.1 | 14.1 | 15.2542 | 14.9134 | 15 | 75 | 75 | 41.2244 | 189.6218 | 24.077 | 239.0997 | 0 | 0 | 0 | 0.4687 | 25.2366 | 35.2212 | 24.5737 | 0 | 18.3782 | 89.0873 | 89.0873 | 89.0873 | 89.8782 | 131.6755 | 148.5252 | 130.5569 | 89.0873 | 189.6218 | 89.0873 | 89.0873 | 89.0873 | 90.3469 | 156.9121 | 183.7464 | 155.1307 | 89.0873 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 17 | 6257 | 14.9 | 14.9 | 15.2542 | 14.9134 | 15 | 71 | 71 | 376.9408 | 124.8602 | 15.6894 | 252.3325 | 0 | 0 | 0 | 0 | 176.7347 | 333.7781 | 295.2989 | 83.8375 | 119.1398 | 71.7984 | 71.7984 | 71.7984 | 71.7984 | 125.8145 | 173.8123 | 162.0517 | 97.422 | 124.8602 | 71.7984 | 71.7984 | 71.7984 | 71.7984 | 302.5492 | 507.5904 | 457.3506 | 181.2595 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 18 | 18 | 6258 | 14 | 14 | 15.2542 | 14.9134 | 15 | 77 | 77 | 93.205 | 76.4675 | 6.6771 | 264.5593 | 0 | 0 | 0 | 0 | 27.2331 | 79.7143 | 85.5001 | 41.201 | 15.5325 | 39.5905 | 39.5905 | 39.5905 | 39.5905 | 55.2412 | 85.402 | 88.727 | 63.2685 | 76.4675 | 39.5905 | 39.5905 | 39.5905 | 39.5905 | 82.4743 | 165.1163 | 174.227 | 104.4695 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 19 | 6259 | 12.8 | 12.8 | 15.2542 | 14.9134 | 15 | 85 | 85 | 5.7073 | 3.63 | -2.5205 | 276.4183 | 0 | 0 | 0 | 0 | 0.53747 | 4.3703 | 5.6431 | 3.6102 | 18.37 | 3.8621 | 3.8621 | 3.8621 | 3.8621 | 4.1272 | 6.0181 | 6.646 | 5.6431 | 3.63 | 3.8621 | 3.8621 | 3.8621 | 3.8621 | 4.6647 | 10.3884 | 12.289 | 9.2533 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 20 | 6260 | 12 | 12 | 15.2542 | 14.9134 | 15 | 85 | 85 | 0 | 0 | -11.5022 | 288.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 21 | 6261 | 10.4 | 10.4 | 15.2542 | 14.9134 | 15 | 92 | 92 | 0 | 0 | -19.8417 | 301.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 22 | 6262 | 8.7 | 8.7 | 15.2542 | 14.9134 | 15 | 98 | 98 | 0 | 0 | -27.0319 | 315.8378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 23 | 6263 | 8.9 | 8.9 | 15.2542 | 14.9134 | 15 | 97 | 97 | 0 | 0 | -32.4629 | 331.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 18 | 24 | 6264 | 9.2 | 9.2 | 12.3958 | 14.1344 | 15 | 97 | 97 | 0 | 0 | -35.4941 | 349.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 1 | 6265 | 7.6 | 7.6 | 12.3958 | 14.1344 | 15 | 98 | 98 | 0 | 0 | -35.6684 | 8.1476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 2 | 6266 | 7.7 | 7.7 | 12.3958 | 14.1344 | 15 | 98 | 98 | 0 | 0 | -33.3061 | 26.2569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 3 | 6267 | 7.7 | 7.7 | 12.3958 | 14.1344 | 15 | 98 | 98 | 0 | 0 | -28.092 | 42.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 4 | 6268 | 8 | 8 | 12.3958 | 14.1344 | 15 | 98 | 98 | 0 | 0 | -21.0459 | 57.2085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 5 | 6269 | 7.1 | 7.1 | 12.3958 | 14.1344 | 15 | 99 | 99 | 0 | 0 | -12.792 | 70.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 6 | 6270 | 8 | 8 | 12.3958 | 14.1344 | 15 | 100 | 100 | 0 | 0 | -3.851 | 82.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 7 | 6271 | 8.2 | 8.2 | 12.3958 | 14.1344 | 15 | 100 | 100 | 4.9352 | 10.8013 | 5.3434 | 94.3473 | 0.64367 | 3.9071 | 4.8818 | 2.9968 | 0 | 0 | 0 | 0 | 0.19872 | 5.4474 | 8.7083 | 9.6822 | 7.7987 | 4.8043 | 4.8043 | 4.8043 | 4.8043 | 10.8013 | 6.0911 | 12.6154 | 14.564 | 10.7955 | 4.8043 | 4.8043 | 4.8043 | 4.8043 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 19 | 8 | 6272 | 10.1 | 10.1 | 12.3958 | 14.1344 | 15 | 98 | 98 | 152.8798 | 91.7376 | 14.3901 | 106.4991 | 0 | 99.1642 | 151.7775 | 115.4816 | 11.5382 | 0 | 0 | 0 | 30.2624 | 38.9273 | 226.3983 | 325.8644 | 257.2466 | 60.7404 | 38.9273 | 38.9273 | 38.9273 | 91.7376 | 38.9273 | 325.5625 | 477.6419 | 372.7282 | 72.2785 | 38.9273 | 38.9273 | 38.9273 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 9 | 6273 | 13.5 | 13.5 | 12.3958 | 14.1344 | 15 | 79 | 79 | 187.1246 | 157.6997 | 22.8577 | 119.5766 | 0 | 86.4893 | 173.7905 | 159.2876 | 51.4762 | 0 | 0 | 0 | 64.3003 | 74.7578 | 152.656 | 231.2853 | 218.223 | 121.1208 | 74.7578 | 74.7578 | 74.7578 | 157.6997 | 74.7578 | 239.1452 | 405.0758 | 377.5106 | 172.5969 | 74.7578 | 74.7578 | 74.7578 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 10 | 6274 | 15.1 | 15.1 | 12.3958 | 14.1344 | 15 | 75 | 75 | 377.1349 | 184.7374 | 30.2219 | 134.2021 | 0 | 92.423 | 302.2366 | 335.0041 | 171.5308 | 0 | 0 | 0 | 176.2626 | 102.2969 | 136.5539 | 214.3224 | 226.4679 | 165.8757 | 102.2969 | 102.2969 | 102.2969 | 184.7374 | 102.2969 | 228.9769 | 516.559 | 561.472 | 337.4065 | 102.2969 | 102.2969 | 102.2969 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 11 | 6275 | 15.4 | 15.4 | 12.3958 | 14.1344 | 15 | 70 | 70 | 88.1039 | 256.5952 | 35.8322 | 150.8199 | 0 | 1.0601 | 54.5758 | 76.1217 | 53.0765 | 0 | 0 | 0 | 49.4048 | 116.7443 | 118.2301 | 193.2319 | 223.4284 | 191.1308 | 116.7443 | 116.7443 | 116.7443 | 256.5952 | 116.7443 | 119.2902 | 247.8077 | 299.5501 | 244.2073 | 116.7443 | 116.7443 | 116.7443 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 12 | 6276 | 16.5 | 16.5 | 12.3958 | 14.1344 | 15 | 65 | 65 | 29.1386 | 251.0105 | 38.9793 | 169.312 | 0 | 0 | 11.5179 | 22.7289 | 20.6257 | 6.4402 | 0 | 0 | 17.9895 | 116.0006 | 116.0006 | 139.6296 | 162.6291 | 158.3143 | 129.2126 | 116.0006 | 116.0006 | 251.0105 | 116.0006 | 116.0006 | 151.1475 | 185.358 | 178.9399 | 135.6528 | 116.0006 | 116.0006 | 269 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 13 | 6277 | 16.9 | 16.9 | 12.3958 | 14.1344 | 15 | 68 | 68 | 430.709 | 235.2129 | 39.1429 | 188.6585 | 0 | 0 | 62.0964 | 276.556 | 329.0128 | 188.7384 | 0 | 0 | 272.7871 | 127.8777 | 127.8777 | 152.2179 | 236.2805 | 256.8422 | 201.8583 | 127.8777 | 127.8777 | 235.2129 | 127.8777 | 127.8777 | 214.3144 | 512.8365 | 585.855 | 390.5966 | 127.8777 | 127.8777 | 508 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 14 | 6278 | 17 | 17 | 12.3958 | 14.1344 | 15 | 64 | 64 | 376.335 | 240.356 | 36.2929 | 207.3049 | 0 | 0 | 0 | 172.9644 | 288.549 | 235.1055 | 43.9404 | 0 | 228.644 | 127.0688 | 127.0688 | 127.0688 | 201.7316 | 251.6255 | 228.5558 | 146.0364 | 127.0688 | 240.356 | 127.0688 | 127.0688 | 127.0688 | 374.696 | 540.1745 | 463.6613 | 189.9768 | 127.0688 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 15 | 6279 | 16.5 | 16.5 | 12.3958 | 14.1344 | 15 | 65 | 65 | 163.2386 | 250.5596 | 30.91 | 224.1404 | 0 | 0 | 0 | 39.9911 | 116.9107 | 125.3456 | 60.3547 | 0 | 88.4404 | 119.3635 | 119.3635 | 119.3635 | 151.9982 | 214.7684 | 221.6517 | 168.6159 | 119.3635 | 250.5596 | 119.3635 | 119.3635 | 119.3635 | 191.9893 | 331.6791 | 346.9973 | 228.9707 | 119.3635 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 16 | 6280 | 16.4 | 16.4 | 12.3958 | 14.1344 | 15 | 61 | 61 | 99.9238 | 202.9777 | 23.6982 | 238.9614 | 0 | 0 | 0 | 1.2861 | 61.5244 | 85.7226 | 59.7056 | 0 | 44.0223 | 96.8023 | 96.8023 | 96.8023 | 97.8233 | 145.6469 | 164.8579 | 144.2029 | 96.8023 | 202.9777 | 96.8023 | 96.8023 | 96.8023 | 99.1094 | 207.1713 | 250.5805 | 203.9085 | 96.8023 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 17 | 6281 | 16.1 | 16.1 | 12.3958 | 14.1344 | 15 | 67 | 67 | 399.685 | 119.7797 | 15.3203 | 252.174 | 0 | 0 | 0 | 0 | 188.7056 | 355.17 | 313.5806 | 88.2999 | 124.2203 | 70.1684 | 70.1684 | 70.1684 | 70.1684 | 123.3408 | 170.2461 | 158.5273 | 95.0491 | 119.7797 | 70.1684 | 70.1684 | 70.1684 | 70.1684 | 312.0464 | 525.4161 | 472.1079 | 183.349 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 19 | 18 | 6282 | 15.7 | 15.7 | 12.3958 | 14.1344 | 15 | 70 | 70 | 66.5304 | 72.2657 | 6.3133 | 264.3935 | 0 | 0 | 0 | 0 | 19.643 | 57.0837 | 61.0856 | 29.3044 | 10.7343 | 37.1883 | 37.1883 | 37.1883 | 37.1883 | 52.1724 | 80.7331 | 83.7858 | 59.5423 | 72.2657 | 37.1883 | 37.1883 | 37.1883 | 37.1883 | 71.8154 | 137.8168 | 144.8714 | 88.8467 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 19 | 6283 | 13.8 | 13.8 | 12.3958 | 14.1344 | 15 | 81 | 81 | 3.611 | 3.63 | -2.8845 | 276.2537 | 0 | 0 | 0 | 0 | 0.35064 | 2.7737 | 3.5719 | 2.2778 | 18.37 | 3.8629 | 3.8629 | 3.8629 | 3.8629 | 4.1479 | 6.1178 | 6.7667 | 5.7146 | 3.63 | 3.8629 | 3.8629 | 3.8629 | 3.8629 | 4.4986 | 8.8914 | 10.3386 | 7.9924 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 20 | 6284 | 13 | 13 | 12.3958 | 14.1344 | 15 | 86 | 86 | 0 | 0 | -11.8717 | 288.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 21 | 6285 | 12.1 | 12.1 | 12.3958 | 14.1344 | 15 | 88 | 88 | 0 | 0 | -20.2209 | 301.3463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 22 | 6286 | 11.1 | 11.1 | 12.3958 | 14.1344 | 15 | 92 | 92 | 0 | 0 | -27.4225 | 315.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 23 | 6287 | 12.2 | 12.2 | 12.3958 | 14.1344 | 15 | 85 | 85 | 0 | 0 | -32.8616 | 331.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 19 | 24 | 6288 | 12 | 12 | 12.4042 | 13.5386 | 15 | 85 | 85 | 0 | 0 | -35.8905 | 349.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 1 | 6289 | 11.8 | 11.8 | 12.4042 | 13.5386 | 15 | 86 | 86 | 0 | 0 | -36.0475 | 8.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 2 | 6290 | 11.5 | 11.5 | 12.4042 | 13.5386 | 15 | 90 | 90 | 0 | 0 | -33.6554 | 26.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 3 | 6291 | 11.5 | 11.5 | 12.4042 | 13.5386 | 15 | 92 | 92 | 0 | 0 | -28.4073 | 42.9125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 4 | 6292 | 11.8 | 11.8 | 12.4042 | 13.5386 | 15 | 94 | 94 | 0 | 0 | -21.3314 | 57.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 5 | 6293 | 12.6 | 12.6 | 12.4042 | 13.5386 | 15 | 94 | 94 | 0 | 0 | -13.056 | 70.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 6 | 6294 | 13.3 | 13.3 | 12.4042 | 13.5386 | 15 | 94 | 94 | 0 | 0 | -4.1035 | 82.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 7 | 6295 | 13.9 | 13.9 | 12.4042 | 13.5386 | 15 | 94 | 94 | 1.9503 | 5.9319 | 5.0921 | 94.6598 | 0.24382 | 1.5371 | 1.93 | 1.1923 | 0 | 0 | 0 | 0 | 0.068122 | 2.9775 | 4.7689 | 5.313 | 4.2913 | 2.6398 | 2.6398 | 2.6398 | 2.6398 | 5.9319 | 3.2214 | 6.306 | 7.243 | 5.4836 | 2.6398 | 2.6398 | 2.6398 | 2.6398 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 20 | 8 | 6296 | 14.6 | 14.6 | 12.4042 | 13.5386 | 15 | 91 | 91 | 3.9345 | 46.2421 | 14.1297 | 106.8123 | 0 | 2.5369 | 3.906 | 2.9871 | 0.31837 | 0 | 0 | 0 | 0.75793 | 20.0654 | 80.001 | 112.3489 | 90.6385 | 27.5873 | 20.0654 | 20.0654 | 20.0654 | 46.2421 | 20.0654 | 82.5378 | 116.255 | 93.6256 | 27.9057 | 20.0654 | 20.0654 | 20.0654 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 9 | 6297 | 16.2 | 16.2 | 12.4042 | 13.5386 | 15 | 86 | 86 | 243.0313 | 150.7748 | 22.5776 | 119.8861 | 0 | 111.3254 | 225.605 | 207.7283 | 68.1671 | 0 | 0 | 0 | 82.2252 | 74.1021 | 147.7615 | 223.3756 | 211.5473 | 119.2055 | 74.1021 | 74.1021 | 74.1021 | 150.7748 | 74.1021 | 259.0869 | 448.9806 | 419.2756 | 187.3726 | 74.1021 | 74.1021 | 74.1021 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 10 | 6298 | 16.6 | 16.6 | 12.4042 | 13.5386 | 15 | 82 | 82 | 28.1046 | 187.0129 | 29.9127 | 134.4953 | 0 | 6.7663 | 22.4997 | 25.053 | 12.9306 | 0 | 0 | 0 | 12.9871 | 82.8729 | 104.3519 | 154.2959 | 162.4012 | 123.9199 | 82.8729 | 82.8729 | 82.8729 | 187.0129 | 82.8729 | 111.1182 | 176.7956 | 187.4542 | 136.8506 | 82.8729 | 82.8729 | 82.8729 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 11 | 6299 | 17.6 | 17.6 | 12.4042 | 13.5386 | 15 | 79 | 79 | 38.5796 | 234.5693 | 35.4882 | 151.071 | 0 | 0.29456 | 23.8532 | 33.4389 | 23.4366 | 0 | 0 | 0 | 21.4307 | 106.0505 | 106.8627 | 171.8197 | 198.2501 | 170.6711 | 106.0505 | 106.0505 | 106.0505 | 234.5693 | 106.0505 | 107.1573 | 195.6729 | 231.689 | 194.1077 | 106.0505 | 106.0505 | 106.0505 | 256 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 12 | 6300 | 17.5 | 17.5 | 12.4042 | 13.5386 | 15 | 76 | 76 | 29.2322 | 249.1063 | 38.603 | 169.4858 | 0 | 0 | 11.5136 | 22.8717 | 20.8319 | 6.5891 | 0 | 0 | 17.8937 | 115.0964 | 115.0964 | 138.6614 | 161.9083 | 157.7333 | 128.5823 | 115.0964 | 115.0964 | 249.1063 | 115.0964 | 115.0964 | 150.175 | 184.78 | 178.5653 | 135.1713 | 115.0964 | 115.0964 | 267 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 13 | 6301 | 17.7 | 17.7 | 12.4042 | 13.5386 | 15 | 73 | 73 | 5.3084 | 174.6659 | 38.7468 | 188.7299 | 0 | 0 | 0.757 | 3.4194 | 4.0788 | 2.3488 | 0 | 0 | 3.3341 | 86.8457 | 86.8457 | 87.6938 | 90.6767 | 91.4154 | 89.4773 | 86.8457 | 86.8457 | 174.6659 | 86.8457 | 86.8457 | 88.4508 | 94.0961 | 95.4942 | 91.8261 | 86.8457 | 86.8457 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 14 | 6302 | 18.1 | 18.1 | 12.4042 | 13.5386 | 15 | 70 | 70 | 18.1697 | 228.0564 | 35.8935 | 207.2785 | 0 | 0 | 0 | 8.3834 | 14.0067 | 11.4251 | 2.1508 | 0 | 10.9436 | 108.9466 | 108.9466 | 108.9466 | 123.8091 | 133.7785 | 129.2016 | 112.7596 | 108.9466 | 228.0564 | 108.9466 | 108.9466 | 108.9466 | 132.1925 | 147.7852 | 140.6267 | 114.9104 | 108.9466 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 15 | 6303 | 18.3 | 18.3 | 12.4042 | 13.5386 | 15 | 71 | 71 | 28.5911 | 217.6603 | 30.5187 | 224.0437 | 0 | 0 | 0 | 7.0503 | 20.586 | 22.0628 | 10.6154 | 0 | 15.3397 | 100.5456 | 100.5456 | 100.5456 | 119.5272 | 155.9698 | 159.9457 | 129.1259 | 100.5456 | 217.6603 | 100.5456 | 100.5456 | 100.5456 | 126.5774 | 176.5558 | 182.0085 | 139.7413 | 100.5456 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 16 | 6304 | 18.3 | 18.3 | 12.4042 | 13.5386 | 15 | 72 | 72 | 38.004 | 183.4576 | 23.3187 | 238.8235 | 0 | 0 | 0 | 0.54642 | 23.5332 | 32.7345 | 22.7604 | 0 | 16.5424 | 86.3322 | 86.3322 | 86.3322 | 87.3012 | 128.0664 | 144.3842 | 126.696 | 86.3322 | 183.4576 | 86.3322 | 86.3322 | 86.3322 | 87.8477 | 151.5995 | 177.1187 | 149.4564 | 86.3322 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 17 | 6305 | 18 | 18 | 12.4042 | 13.5386 | 15 | 72 | 72 | 18.7523 | 116.2712 | 14.9507 | 252.0157 | 0 | 0 | 0 | 0 | 8.9147 | 16.7218 | 14.7335 | 4.1145 | 5.7288 | 57.2646 | 57.2646 | 57.2646 | 57.2646 | 61.4508 | 65.1169 | 64.1833 | 59.1967 | 116.2712 | 57.2646 | 57.2646 | 57.2646 | 57.2646 | 70.3655 | 81.8388 | 78.9168 | 63.3113 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 20 | 18 | 6306 | 17.6 | 17.6 | 12.4042 | 13.5386 | 15 | 76 | 76 | 13.2554 | 55.9318 | 5.949 | 264.2274 | 0 | 0 | 0 | 0 | 3.9541 | 11.4092 | 12.1809 | 5.8172 | 2.0682 | 28.2482 | 28.2482 | 28.2482 | 28.2482 | 33.5553 | 43.5612 | 44.597 | 36.0558 | 55.9318 | 28.2482 | 28.2482 | 28.2482 | 28.2482 | 37.5094 | 54.9704 | 56.7779 | 41.873 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 19 | 6307 | 17.1 | 17.1 | 12.4042 | 13.5386 | 15 | 77 | 77 | 0 | 6 | -3.2489 | 276.0886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 6 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 2.792 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 20 | 6308 | 16.8 | 16.8 | 12.4042 | 13.5386 | 15 | 77 | 77 | 0 | 0 | -12.2415 | 288.2142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 21 | 6309 | 16.4 | 16.4 | 12.4042 | 13.5386 | 15 | 80 | 80 | 0 | 0 | -20.6005 | 301.2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 22 | 6310 | 16.1 | 16.1 | 12.4042 | 13.5386 | 15 | 80 | 80 | 0 | 0 | -27.8136 | 315.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 23 | 6311 | 15.7 | 15.7 | 12.4042 | 13.5386 | 15 | 81 | 81 | 0 | 0 | -33.2608 | 331.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 20 | 24 | 6312 | 15.5 | 15.5 | 15.6042 | 14.0055 | 15 | 81 | 81 | 0 | 0 | -36.2875 | 349.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 1 | 6313 | 15.5 | 15.5 | 15.6042 | 14.0055 | 15 | 82 | 82 | 0 | 0 | -36.4269 | 8.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 2 | 6314 | 15.3 | 15.3 | 15.6042 | 14.0055 | 15 | 83 | 83 | 0 | 0 | -34.0048 | 26.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 3 | 6315 | 14.9 | 14.9 | 15.6042 | 14.0055 | 15 | 83 | 83 | 0 | 0 | -28.7226 | 43.1936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 4 | 6316 | 14.5 | 14.5 | 15.6042 | 14.0055 | 15 | 83 | 83 | 0 | 0 | -21.6168 | 57.8107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 5 | 6317 | 14.5 | 14.5 | 15.6042 | 14.0055 | 15 | 82 | 82 | 0 | 0 | -13.3202 | 70.9273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 6 | 6318 | 14.2 | 14.2 | 15.6042 | 14.0055 | 15 | 83 | 83 | 0 | 0 | -4.3564 | 83.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 7 | 6319 | 14.4 | 14.4 | 15.6042 | 14.0055 | 15 | 81 | 81 | 2.7176 | 5.9196 | 4.8402 | 94.9722 | 0.32502 | 2.132 | 2.6902 | 1.6724 | 0 | 0 | 0 | 0 | 0.08039 | 2.958 | 4.7506 | 5.3042 | 4.2946 | 2.6356 | 2.6356 | 2.6356 | 2.6356 | 5.9196 | 3.283 | 6.8826 | 7.9943 | 5.967 | 2.6356 | 2.6356 | 2.6356 | 2.6356 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 21 | 8 | 6320 | 14.8 | 14.8 | 15.6042 | 14.0055 | 15 | 80 | 80 | 3.6452 | 43.3172 | 13.8683 | 107.125 | 0 | 2.3361 | 3.6186 | 2.7813 | 0.31481 | 0 | 0 | 0 | 0.68277 | 18.9154 | 73.0838 | 102.8207 | 83.4071 | 26.2151 | 18.9154 | 18.9154 | 18.9154 | 43.3172 | 18.9154 | 75.4199 | 106.4393 | 86.1884 | 26.5299 | 18.9154 | 18.9154 | 18.9154 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 9 | 6321 | 15.3 | 15.3 | 15.6042 | 14.0055 | 15 | 80 | 80 | 5.2631 | 92.2473 | 22.2964 | 120.1945 | 0 | 2.389 | 4.8832 | 4.5168 | 1.5046 | 0 | 0 | 0 | 1.7527 | 42.7598 | 60.017 | 78.0335 | 75.3872 | 53.6282 | 42.7598 | 42.7598 | 42.7598 | 92.2473 | 42.7598 | 62.406 | 82.9167 | 79.9041 | 55.1328 | 42.7598 | 42.7598 | 42.7598 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 10 | 6322 | 15.7 | 15.7 | 15.6042 | 14.0055 | 15 | 78 | 78 | 3.3585 | 101.4658 | 29.6023 | 134.7867 | 0 | 0.79407 | 2.6858 | 3.0043 | 1.5628 | 0 | 0 | 0 | 1.5342 | 50.3108 | 50.8683 | 52.1966 | 52.4202 | 51.4081 | 50.3108 | 50.3108 | 50.3108 | 101.4658 | 50.3108 | 51.6624 | 54.8825 | 55.4245 | 52.971 | 50.3108 | 50.3108 | 50.3108 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 11 | 6323 | 16.7 | 16.7 | 15.6042 | 14.0055 | 15 | 74 | 74 | 5.8691 | 160.7708 | 35.1431 | 151.3199 | 0 | 0.018997 | 3.6218 | 5.103 | 3.5949 | 0 | 0 | 0 | 3.2292 | 77.6284 | 77.6875 | 88.8899 | 93.4955 | 88.8064 | 77.6284 | 77.6284 | 77.6284 | 160.7708 | 77.6284 | 77.7065 | 92.5117 | 98.5985 | 92.4013 | 77.6284 | 77.6284 | 77.6284 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 12 | 6324 | 17.1 | 17.1 | 15.6042 | 14.0055 | 15 | 74 | 74 | 7.1914 | 189.636 | 38.2259 | 169.6576 | 0 | 0 | 2.8222 | 5.6436 | 5.1591 | 1.6524 | 0 | 0 | 4.364 | 91.702 | 91.702 | 99.461 | 107.2179 | 105.8858 | 96.245 | 91.702 | 91.702 | 189.636 | 91.702 | 91.702 | 102.2832 | 112.8614 | 111.0448 | 97.8975 | 91.702 | 91.702 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 13 | 6325 | 17.8 | 17.8 | 15.6042 | 14.0055 | 15 | 68 | 68 | 11.6034 | 217.7733 | 38.3502 | 188.8002 | 0 | 0 | 1.6365 | 7.498 | 8.9673 | 5.1837 | 0 | 0 | 7.2267 | 104.4113 | 104.4113 | 108.2976 | 122.2177 | 125.7069 | 116.7215 | 104.4113 | 104.4113 | 217.7733 | 104.4113 | 104.4113 | 109.9341 | 129.7157 | 134.6742 | 121.9052 | 104.4113 | 104.4113 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 14 | 6326 | 17.8 | 17.8 | 15.6042 | 14.0055 | 15 | 68 | 68 | 3.5809 | 136.8622 | 35.4937 | 207.2519 | 0 | 0 | 0 | 1.6586 | 2.7752 | 2.2662 | 0.42963 | 0 | 2.1378 | 68.3688 | 68.3688 | 68.3688 | 68.3688 | 68.3688 | 68.3688 | 68.3688 | 68.3688 | 136.8622 | 68.3688 | 68.3688 | 68.3688 | 70.0274 | 71.144 | 70.635 | 68.7984 | 68.3688 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 15 | 6327 | 18.3 | 18.3 | 15.6042 | 14.0055 | 15 | 67 | 67 | 28.7139 | 215.7464 | 30.1271 | 223.9472 | 0 | 0 | 0 | 7.1264 | 20.7833 | 22.2656 | 10.705 | 0 | 15.2536 | 99.7409 | 99.7409 | 99.7409 | 118.7501 | 155.1787 | 159.1326 | 128.2956 | 99.7409 | 215.7464 | 99.7409 | 99.7409 | 99.7409 | 125.8765 | 175.962 | 181.3982 | 139.0006 | 99.7409 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 16 | 6328 | 18.4 | 18.4 | 15.6042 | 14.0055 | 15 | 68 | 68 | 16.3155 | 159.9847 | 22.9388 | 238.6859 | 0 | 0 | 0 | 0.25927 | 10.16 | 14.1092 | 9.7933 | 0 | 7.0153 | 77.9361 | 77.9361 | 77.9361 | 78.1935 | 88.0228 | 91.9435 | 87.6588 | 77.9361 | 159.9847 | 77.9361 | 77.9361 | 77.9361 | 78.4528 | 98.1828 | 106.0526 | 97.4521 | 77.9361 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 17 | 6329 | 17.5 | 17.5 | 15.6042 | 14.0055 | 15 | 73 | 73 | 3.8003 | 70.8592 | 14.5807 | 251.8573 | 0 | 0 | 0 | 0 | 1.819 | 3.4005 | 2.99 | 0.82805 | 1.1408 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 70.8592 | 34.6713 | 34.6713 | 34.6713 | 34.6713 | 36.4903 | 38.0718 | 37.6613 | 35.4994 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 21 | 18 | 6330 | 17.1 | 17.1 | 15.6042 | 14.0055 | 15 | 77 | 77 | 1.8182 | 24.726 | 5.5843 | 264.061 | 0 | 0 | 0 | 0 | 0.54792 | 1.5698 | 1.6721 | 0.79494 | 0.27398 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 24.726 | 11.7434 | 11.7434 | 11.7434 | 11.7434 | 12.2914 | 13.3132 | 13.4156 | 12.5384 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 19 | 6331 | 17 | 17 | 15.6042 | 14.0055 | 15 | 79 | 79 | 0 | 6 | -3.6135 | 275.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 6 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 2.7938 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 20 | 6332 | 16.8 | 16.8 | 15.6042 | 14.0055 | 15 | 82 | 82 | 0 | 0 | -12.6116 | 288.0576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 21 | 6333 | 16.5 | 16.5 | 15.6042 | 14.0055 | 15 | 87 | 87 | 0 | 0 | -20.9803 | 301.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 22 | 6334 | 16.1 | 16.1 | 15.6042 | 14.0055 | 15 | 84 | 84 | 0 | 0 | -28.205 | 315.5537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 23 | 6335 | 14.7 | 14.7 | 15.6042 | 14.0055 | 15 | 83 | 83 | 0 | 0 | -33.6605 | 331.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 21 | 24 | 6336 | 14.8 | 14.8 | 16.0708 | 14.5477 | 15 | 83 | 83 | 0 | 0 | -36.6849 | 349.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 1 | 6337 | 14.1 | 14.1 | 16.0708 | 14.5477 | 15 | 88 | 88 | 0 | 0 | -36.8066 | 8.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 2 | 6338 | 13.8 | 13.8 | 16.0708 | 14.5477 | 15 | 90 | 90 | 0 | 0 | -34.3543 | 26.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 3 | 6339 | 13.3 | 13.3 | 16.0708 | 14.5477 | 15 | 92 | 92 | 0 | 0 | -29.0378 | 43.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 4 | 6340 | 13.1 | 13.1 | 16.0708 | 14.5477 | 15 | 91 | 91 | 0 | 0 | -21.9023 | 58.1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 5 | 6341 | 13.2 | 13.2 | 16.0708 | 14.5477 | 15 | 90 | 90 | 0 | 0 | -13.5846 | 71.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 6 | 6342 | 13.4 | 13.4 | 16.0708 | 14.5477 | 15 | 90 | 90 | 0 | 0 | -4.6097 | 83.4226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 7 | 6343 | 13.4 | 13.4 | 16.0708 | 14.5477 | 15 | 92 | 92 | 4.0491 | 5.9019 | 4.5875 | 95.2844 | 0.46231 | 3.162 | 4.0094 | 2.5082 | 0 | 0 | 0 | 0 | 0.0981 | 2.7705 | 6.1718 | 7.2394 | 5.3481 | 2.1881 | 2.1881 | 2.1881 | 2.1881 | 5.9019 | 3.2328 | 9.3338 | 11.2489 | 7.8563 | 2.1881 | 2.1881 | 2.1881 | 2.1881 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 22 | 8 | 6344 | 14.1 | 14.1 | 16.0708 | 14.5477 | 15 | 89 | 89 | 3.8603 | 43.2976 | 13.606 | 107.4369 | 0 | 2.4587 | 3.8316 | 2.9599 | 0.35439 | 0 | 0 | 0 | 0.70243 | 18.6628 | 77.7926 | 110.8076 | 89.8454 | 27.1854 | 18.6628 | 18.6628 | 18.6628 | 43.2976 | 18.6628 | 80.2513 | 114.6391 | 92.8053 | 27.5398 | 18.6628 | 18.6628 | 18.6628 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 9 | 6345 | 15.1 | 15.1 | 16.0708 | 14.5477 | 15 | 84 | 84 | 22.6379 | 128.5819 | 22.0141 | 120.5017 | 0 | 10.1812 | 20.9916 | 19.5054 | 6.5932 | 0 | 0 | 0 | 7.4181 | 54.6459 | 110.091 | 168.9625 | 160.8689 | 90.5514 | 54.6459 | 54.6459 | 54.6459 | 128.5819 | 54.6459 | 120.2721 | 189.954 | 180.3743 | 97.1446 | 54.6459 | 54.6459 | 54.6459 | 136 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 10 | 6346 | 16.3 | 16.3 | 16.0708 | 14.5477 | 15 | 69 | 69 | 242.4751 | 201.5302 | 29.2908 | 135.0762 | 0 | 56.2783 | 193.6881 | 217.6381 | 114.0986 | 0 | 0 | 0 | 109.4698 | 99.6576 | 134.285 | 218.8318 | 233.5679 | 169.8612 | 99.6576 | 99.6576 | 99.6576 | 201.5302 | 99.6576 | 190.5633 | 412.5199 | 451.206 | 283.9598 | 99.6576 | 99.6576 | 99.6576 | 311 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 11 | 6347 | 17 | 17 | 16.0708 | 14.5477 | 15 | 58 | 58 | 473.5078 | 191.9971 | 34.797 | 151.5665 | 0 | 0 | 291.6244 | 412.9685 | 292.4012 | 0.54928 | 0 | 0 | 258.0029 | 112.2468 | 112.2468 | 201.7676 | 239.0169 | 202.006 | 112.4154 | 112.2468 | 112.2468 | 191.9971 | 112.2468 | 112.2468 | 493.392 | 651.9854 | 494.4073 | 112.9647 | 112.2468 | 112.2468 | 450 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 12 | 6348 | 17.3 | 17.3 | 16.0708 | 14.5477 | 15 | 54 | 54 | 439.8142 | 221.4469 | 37.8481 | 169.8273 | 0 | 0 | 171.9651 | 346.174 | 317.5989 | 102.9786 | 0 | 0 | 264.5531 | 123.0902 | 123.0902 | 185.8214 | 249.3711 | 238.9472 | 160.6558 | 123.0902 | 123.0902 | 221.4469 | 123.0902 | 123.0902 | 357.7865 | 595.5451 | 556.5461 | 263.6344 | 123.0902 | 123.0902 | 486 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 13 | 6349 | 16.7 | 16.7 | 16.0708 | 14.5477 | 15 | 55 | 55 | 228.1384 | 278.1288 | 37.9531 | 188.8692 | 0 | 0 | 31.8169 | 147.8788 | 177.3154 | 102.8829 | 0 | 0 | 140.8712 | 134.6067 | 134.6067 | 155.3747 | 231.1321 | 250.3463 | 201.7618 | 134.6067 | 134.6067 | 278.1288 | 134.6067 | 134.6067 | 187.1916 | 379.011 | 427.6617 | 304.6448 | 134.6067 | 134.6067 | 419 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 14 | 6350 | 16.5 | 16.5 | 16.0708 | 14.5477 | 15 | 57 | 57 | 160.0228 | 274.3169 | 35.0935 | 207.2251 | 0 | 0 | 0 | 74.3997 | 124.6715 | 101.9124 | 19.4544 | 0 | 94.6831 | 128.6724 | 128.6724 | 128.6724 | 196.5403 | 242.3985 | 221.6375 | 146.4188 | 128.6724 | 274.3169 | 128.6724 | 128.6724 | 128.6724 | 270.94 | 367.07 | 323.5499 | 165.8732 | 128.6724 | 369 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 15 | 6351 | 16.6 | 16.6 | 16.0708 | 14.5477 | 15 | 62 | 62 | 203.3041 | 240.0823 | 29.7351 | 223.851 | 0 | 0 | 0 | 50.7818 | 147.9178 | 158.4056 | 76.1015 | 0 | 106.9177 | 117.2939 | 117.2939 | 117.2939 | 149.4034 | 210.8228 | 217.4542 | 165.4131 | 117.2939 | 240.0823 | 117.2939 | 117.2939 | 117.2939 | 200.1852 | 358.7406 | 375.8598 | 241.5146 | 117.2939 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 16 | 6352 | 16.6 | 16.6 | 16.0708 | 14.5477 | 15 | 58 | 58 | 598.4557 | 123.869 | 22.5586 | 238.5485 | 0 | 0 | 0 | 10.4204 | 374.7467 | 519.5514 | 360.01 | 0 | 254.131 | 83.9632 | 83.9632 | 83.9632 | 85.8314 | 151.1474 | 177.1079 | 148.5055 | 83.9632 | 123.869 | 83.9632 | 83.9632 | 83.9632 | 96.2518 | 525.8941 | 696.6593 | 508.5154 | 83.9632 | 378 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 17 | 6353 | 16.6 | 16.6 | 16.0708 | 14.5477 | 15 | 53 | 53 | 241.9656 | 131.6583 | 14.2105 | 251.699 | 0 | 0 | 0 | 0 | 116.5922 | 217.234 | 190.6231 | 52.3477 | 71.3417 | 70.2962 | 70.2962 | 70.2962 | 70.2962 | 124.713 | 171.6854 | 159.2653 | 94.7283 | 131.6583 | 70.2962 | 70.2962 | 70.2962 | 70.2962 | 241.3052 | 388.9194 | 349.8884 | 147.0761 | 203 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 18 | 6354 | 14.9 | 14.9 | 16.0708 | 14.5477 | 15 | 62 | 62 | 96.5961 | 66.9604 | 5.2195 | 263.8944 | 0 | 0 | 0 | 0 | 29.4039 | 83.6563 | 88.904 | 42.0729 | 14.0396 | 34.9938 | 34.9938 | 34.9938 | 34.9938 | 49.9587 | 77.5701 | 80.2409 | 56.4065 | 66.9604 | 34.9938 | 34.9938 | 34.9938 | 34.9938 | 79.3626 | 161.2264 | 169.1449 | 98.4794 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 19 | 6355 | 13.9 | 13.9 | 16.0708 | 14.5477 | 15 | 67 | 67 | 0 | 6 | -3.9783 | 275.7565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 6 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 2.7958 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 20 | 6356 | 13.7 | 13.7 | 16.0708 | 14.5477 | 15 | 72 | 72 | 0 | 0 | -12.9817 | 287.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 21 | 6357 | 13.6 | 13.6 | 16.0708 | 14.5477 | 15 | 75 | 75 | 0 | 0 | -21.3602 | 300.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 22 | 6358 | 13.4 | 13.4 | 16.0708 | 14.5477 | 15 | 79 | 79 | 0 | 0 | -28.5965 | 315.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 23 | 6359 | 13.6 | 13.6 | 16.0708 | 14.5477 | 15 | 82 | 82 | 0 | 0 | -34.0604 | 331.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 22 | 24 | 6360 | 11.9 | 11.9 | 14.6708 | 14.5776 | 15 | 91 | 91 | 0 | 0 | -37.0826 | 349.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 1 | 6361 | 9.3 | 9.3 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -37.1866 | 8.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 2 | 6362 | 8.6 | 8.6 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -34.7037 | 27.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 3 | 6363 | 10.9 | 10.9 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -29.3529 | 43.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 4 | 6364 | 12 | 12 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -22.1877 | 58.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 5 | 6365 | 11.8 | 11.8 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -13.8491 | 71.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 6 | 6366 | 11.3 | 11.3 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -4.8634 | 83.7341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 7 | 6367 | 11.6 | 11.6 | 14.6708 | 14.5776 | 15 | 98 | 98 | 7.0542 | 5.8669 | 4.3343 | 95.5962 | 0.76714 | 5.4829 | 6.9868 | 4.398 | 0 | 0 | 0 | 0 | 0.1331 | 2.7718 | 6.7838 | 8.0633 | 5.8608 | 2.1192 | 2.1192 | 2.1192 | 2.1192 | 5.8669 | 3.539 | 12.2667 | 15.0501 | 10.2588 | 2.1192 | 2.1192 | 2.1192 | 2.1192 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 23 | 8 | 6368 | 13.1 | 13.1 | 14.6708 | 14.5776 | 15 | 93 | 93 | 14.5022 | 64.4388 | 13.3427 | 107.7479 | 0 | 9.1794 | 14.3918 | 11.1737 | 1.4102 | 0 | 0 | 0 | 2.5612 | 23.216 | 213.1935 | 321.0695 | 254.4669 | 52.4007 | 23.216 | 23.216 | 23.216 | 64.4388 | 23.216 | 222.3729 | 335.4613 | 265.6406 | 53.8108 | 23.216 | 23.216 | 23.216 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 9 | 6369 | 15.2 | 15.2 | 14.6708 | 14.5776 | 15 | 81 | 81 | 184.8609 | 148.4142 | 21.7307 | 120.8074 | 0 | 82.364 | 171.3103 | 159.9054 | 54.83 | 0 | 0 | 0 | 59.5858 | 70.3177 | 145.4857 | 226.6608 | 216.2523 | 120.3573 | 70.3177 | 70.3177 | 70.3177 | 148.4142 | 70.3177 | 227.8497 | 397.9712 | 376.1577 | 175.1874 | 70.3177 | 70.3177 | 70.3177 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 10 | 6370 | 16.4 | 16.4 | 14.6708 | 14.5776 | 15 | 76 | 76 | 353.2901 | 181.3923 | 28.9782 | 135.3637 | 0 | 80.4649 | 281.8748 | 318.1662 | 168.0802 | 0 | 0 | 0 | 157.6077 | 99.0256 | 130.5957 | 209.6181 | 223.8569 | 164.9712 | 99.0256 | 99.0256 | 99.0256 | 181.3923 | 99.0256 | 211.0606 | 491.4929 | 542.0231 | 333.0514 | 99.0256 | 99.0256 | 99.0256 | 339 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 11 | 6371 | 16.8 | 16.8 | 14.6708 | 14.5776 | 15 | 73 | 73 | 148.7209 | 250.7619 | 34.45 | 151.8106 | 0 | 0 | 91.4101 | 130.0991 | 92.5779 | 0.82577 | 0 | 0 | 80.2381 | 116.8362 | 116.8362 | 213.5344 | 254.4616 | 214.7697 | 117.7097 | 116.8362 | 116.8362 | 250.7619 | 116.8362 | 116.8362 | 304.9444 | 384.5607 | 307.3476 | 118.5355 | 116.8362 | 116.8362 | 331 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 12 | 6372 | 17.3 | 17.3 | 14.6708 | 14.5776 | 15 | 71 | 71 | 314.1801 | 251.6997 | 37.4696 | 169.9948 | 0 | 0 | 122.3857 | 248.0078 | 228.3502 | 74.9282 | 0 | 0 | 187.3003 | 128.2348 | 128.2348 | 193.8068 | 261.1129 | 250.5807 | 168.38 | 128.2348 | 128.2348 | 251.6997 | 128.2348 | 128.2348 | 316.1926 | 509.1206 | 478.931 | 243.3082 | 128.2348 | 128.2348 | 439 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 13 | 6373 | 17.1 | 17.1 | 14.6708 | 14.5776 | 15 | 71 | 71 | 129.5381 | 284.7064 | 37.5557 | 188.9369 | 0 | 0 | 17.8623 | 84.2234 | 101.2477 | 58.9624 | 0 | 0 | 79.2936 | 130.6745 | 130.6745 | 151.985 | 231.1571 | 251.4679 | 201.0195 | 130.6745 | 130.6745 | 284.7064 | 130.6745 | 130.6745 | 169.8473 | 315.3806 | 352.7155 | 259.9819 | 130.6745 | 130.6745 | 364 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 14 | 6374 | 17.6 | 17.6 | 14.6708 | 14.5776 | 15 | 67 | 67 | 126.8006 | 272.653 | 34.6931 | 207.198 | 0 | 0 | 0 | 59.1752 | 99.3022 | 81.2594 | 15.6159 | 0 | 74.347 | 126.0175 | 126.0175 | 126.0175 | 194.0169 | 240.1277 | 219.3943 | 143.9621 | 126.0175 | 272.653 | 126.0175 | 126.0175 | 126.0175 | 253.1921 | 339.4299 | 300.6537 | 159.578 | 126.0175 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 15 | 6375 | 17.9 | 17.9 | 14.6708 | 14.5776 | 15 | 67 | 67 | 11.0067 | 180.2705 | 29.3429 | 223.7549 | 0 | 0 | 0 | 2.7668 | 8.0493 | 8.6166 | 4.1364 | 0 | 5.7295 | 87.9354 | 87.9354 | 87.9354 | 91.8807 | 99.4132 | 100.2222 | 93.8337 | 87.9354 | 180.2705 | 87.9354 | 87.9354 | 87.9354 | 94.6475 | 107.4625 | 108.8388 | 97.9701 | 87.9354 | 186 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 16 | 6376 | 18.4 | 18.4 | 14.6708 | 14.5776 | 15 | 65 | 65 | 100.9256 | 193.6829 | 22.1782 | 238.4113 | 0 | 0 | 0 | 1.9117 | 63.5463 | 87.9564 | 60.8428 | 0 | 42.3171 | 92.6555 | 92.6555 | 92.6555 | 94.7282 | 161.5529 | 188.0185 | 158.6218 | 92.6555 | 193.6829 | 92.6555 | 92.6555 | 92.6555 | 96.6398 | 225.0992 | 275.9749 | 219.4645 | 92.6555 | 236 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 17 | 6377 | 18 | 18 | 14.6708 | 14.5776 | 15 | 67 | 67 | 275.3604 | 126.2869 | 13.8401 | 251.5406 | 0 | 0 | 0 | 0 | 133.5672 | 248.0341 | 217.2061 | 59.1416 | 79.7131 | 68.8468 | 68.8468 | 68.8468 | 68.8468 | 122.2434 | 168.0041 | 155.6799 | 92.4901 | 126.2869 | 68.8468 | 68.8468 | 68.8468 | 68.8468 | 255.8105 | 416.0383 | 372.886 | 151.6317 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 18 | 6378 | 16.8 | 16.8 | 14.6708 | 14.5776 | 15 | 70 | 70 | 199.6211 | 64.0561 | 4.8547 | 263.7274 | 0 | 0 | 0 | 0 | 61.3713 | 173.3997 | 183.8529 | 86.6076 | 27.9439 | 35.6458 | 35.6458 | 35.6458 | 35.6458 | 59.8152 | 103.9344 | 108.0511 | 69.7538 | 64.0561 | 35.6458 | 35.6458 | 35.6458 | 35.6458 | 121.1865 | 277.3342 | 291.9041 | 156.3613 | 92 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 19 | 6379 | 12.6 | 12.6 | 14.6708 | 14.5776 | 15 | 94 | 94 | 0 | 8 | -4.343 | 275.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 8 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 3.7537 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 20 | 6380 | 11.1 | 11.1 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -13.3517 | 287.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 21 | 6381 | 10.2 | 10.2 | 14.6708 | 14.5776 | 15 | 98 | 98 | 0 | 0 | -21.7401 | 300.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 22 | 6382 | 9.4 | 9.4 | 14.6708 | 14.5776 | 15 | 99 | 99 | 0 | 0 | -28.9881 | 315.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 23 | 6383 | 8.7 | 8.7 | 14.6708 | 14.5776 | 15 | 99 | 99 | 0 | 0 | -34.4605 | 331.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 23 | 24 | 6384 | 8.5 | 8.5 | 13.3583 | 14.2818 | 15 | 100 | 100 | 0 | 0 | -37.4806 | 349.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 1 | 6385 | 7.8 | 7.8 | 13.3583 | 14.2818 | 15 | 99 | 99 | 0 | 0 | -37.5667 | 8.9383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 2 | 6386 | 7.2 | 7.2 | 13.3583 | 14.2818 | 15 | 98 | 98 | 0 | 0 | -35.0531 | 27.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 3 | 6387 | 7.2 | 7.2 | 13.3583 | 14.2818 | 15 | 99 | 99 | 0 | 0 | -29.6678 | 44.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 4 | 6388 | 7 | 7 | 13.3583 | 14.2818 | 15 | 100 | 100 | 0 | 0 | -22.473 | 58.7223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 5 | 6389 | 6.8 | 6.8 | 13.3583 | 14.2818 | 15 | 100 | 100 | 0 | 0 | -14.1136 | 71.8579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 6 | 6390 | 6.4 | 6.4 | 13.3583 | 14.2818 | 15 | 98 | 98 | 0 | 0 | -5.1175 | 84.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 7 | 6391 | 7.3 | 7.3 | 13.3583 | 14.2818 | 15 | 100 | 100 | 12.8414 | 4.9107 | 4.0803 | 95.9075 | 1.3268 | 9.9334 | 12.7212 | 8.0571 | 0 | 0 | 0 | 0 | 6.0893 | 3.016 | 6.2232 | 7.262 | 5.5239 | 2.5216 | 2.5216 | 2.5216 | 2.5216 | 4.9107 | 4.3428 | 16.1566 | 19.9832 | 13.581 | 2.5216 | 2.5216 | 2.5216 | 2.5216 | 11 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 24 | 8 | 6392 | 10.3 | 10.3 | 13.3583 | 14.2818 | 15 | 98 | 98 | 58.5676 | 75.971 | 13.0786 | 108.058 | 0 | 36.8376 | 58.1089 | 45.3408 | 6.0126 | 0 | 0 | 0 | 10.029 | 30.0377 | 209.9266 | 313.8005 | 251.4501 | 59.3993 | 30.0377 | 30.0377 | 30.0377 | 75.971 | 30.0377 | 246.7642 | 371.9094 | 296.7908 | 65.4119 | 30.0377 | 30.0377 | 30.0377 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 9 | 6393 | 12.7 | 12.7 | 13.3583 | 14.2818 | 15 | 88 | 88 | 146.924 | 147.4318 | 21.4462 | 121.1115 | 0 | 64.8427 | 136.0635 | 127.5802 | 44.3621 | 0 | 0 | 0 | 46.5682 | 68.4326 | 144.0413 | 227.087 | 217.1951 | 120.1602 | 68.4326 | 68.4326 | 68.4326 | 147.4318 | 68.4326 | 208.884 | 363.1506 | 344.7753 | 164.5222 | 68.4326 | 68.4326 | 68.4326 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 10 | 6394 | 14.4 | 14.4 | 13.3583 | 14.2818 | 15 | 82 | 82 | 286.5974 | 190.6862 | 28.6645 | 135.6489 | 0 | 64.0298 | 228.3847 | 258.955 | 137.833 | 0 | 0 | 0 | 126.3138 | 99.3695 | 131.1058 | 212.5682 | 227.7204 | 167.6863 | 99.3695 | 99.3695 | 99.3695 | 190.6862 | 99.3695 | 195.1356 | 440.953 | 486.6754 | 305.5193 | 99.3695 | 99.3695 | 99.3695 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 11 | 6395 | 16.5 | 16.5 | 13.3583 | 14.2818 | 15 | 71 | 71 | 525.8193 | 175.1395 | 34.1021 | 152.0522 | 0 | 0 | 322.5268 | 461.3474 | 329.9169 | 5.2256 | 0 | 0 | 280.8605 | 108.1113 | 108.1113 | 193.2566 | 229.9044 | 195.2075 | 109.4908 | 108.1113 | 108.1113 | 175.1395 | 108.1113 | 108.1113 | 515.7834 | 691.2518 | 525.1244 | 114.7164 | 108.1113 | 108.1113 | 456 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 12 | 6396 | 17.7 | 17.7 | 13.3583 | 14.2818 | 15 | 67 | 67 | 584.2784 | 176.8258 | 37.0907 | 170.1599 | 0 | 0 | 226.7437 | 462.5368 | 427.3821 | 141.8728 | 0 | 0 | 345.1742 | 114.3389 | 114.3389 | 168.9667 | 225.7747 | 217.3051 | 148.5193 | 114.3389 | 114.3389 | 176.8258 | 114.3389 | 114.3389 | 395.7104 | 688.3115 | 644.6872 | 290.3921 | 114.3389 | 114.3389 | 522 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 13 | 6397 | 19 | 19 | 13.3583 | 14.2818 | 15 | 65 | 65 | 558.065 | 189.4004 | 37.1581 | 189.0032 | 0 | 0 | 76.0772 | 363.9385 | 438.6095 | 256.349 | 0 | 0 | 338.5996 | 117.8982 | 117.8982 | 137.9859 | 213.9938 | 233.7102 | 185.5855 | 117.8982 | 117.8982 | 189.4004 | 117.8982 | 117.8982 | 214.0631 | 577.9323 | 672.3197 | 441.9345 | 117.8982 | 117.8982 | 528 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 14 | 6398 | 19.9 | 19.9 | 13.3583 | 14.2818 | 15 | 60 | 60 | 650.4844 | 155.1048 | 34.2927 | 207.1704 | 0 | 0 | 0 | 304.6945 | 512.0304 | 419.4259 | 81.1274 | 0 | 377.8952 | 107.7347 | 107.7347 | 107.7347 | 164.2562 | 202.7175 | 185.5391 | 122.784 | 107.7347 | 155.1048 | 107.7347 | 107.7347 | 107.7347 | 468.9507 | 714.7479 | 604.965 | 203.9113 | 107.7347 | 533 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 15 | 6399 | 20.1 | 20.1 | 13.3583 | 14.2818 | 15 | 57 | 57 | 670.5168 | 132.5742 | 28.9507 | 223.6589 | 0 | 0 | 0 | 169.616 | 492.8328 | 527.3549 | 252.9596 | 0 | 345.4258 | 96.2111 | 96.2111 | 96.2111 | 124.0651 | 177.1431 | 182.8123 | 137.7516 | 96.2111 | 132.5742 | 96.2111 | 96.2111 | 96.2111 | 293.6811 | 669.9759 | 710.1671 | 390.7113 | 96.2111 | 478 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 16 | 6400 | 20.3 | 20.3 | 13.3583 | 14.2818 | 15 | 55 | 55 | 642.2673 | 112.1576 | 21.7978 | 238.2742 | 0 | 0 | 0 | 13.1537 | 406.5916 | 561.8536 | 387.9894 | 0 | 265.8424 | 80.4657 | 80.4657 | 80.4657 | 82.5444 | 144.7194 | 169.2555 | 141.7797 | 80.4657 | 112.1576 | 80.4657 | 80.4657 | 80.4657 | 95.6981 | 551.311 | 731.1091 | 529.7691 | 80.4657 | 378 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 17 | 6401 | 20.3 | 20.3 | 13.3583 | 14.2818 | 15 | 56 | 56 | 461.3206 | 101.9323 | 13.4697 | 251.3822 | 0 | 0 | 0 | 0 | 225.2428 | 416.8921 | 364.3316 | 98.3507 | 131.0677 | 63.2134 | 63.2134 | 63.2134 | 63.2134 | 113.678 | 156.616 | 144.8401 | 85.2484 | 101.9323 | 63.2134 | 63.2134 | 63.2134 | 63.2134 | 338.9207 | 573.5081 | 509.1717 | 183.5991 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 24 | 18 | 6402 | 17.6 | 17.6 | 13.3583 | 14.2818 | 15 | 74 | 74 | 204.2616 | 61.5029 | 4.4899 | 263.56 | 0 | 0 | 0 | 0 | 63.4175 | 177.9543 | 188.2479 | 88.2684 | 27.4971 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 60.8005 | 108.3381 | 112.6103 | 71.1146 | 61.5029 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 124.218 | 286.2924 | 300.8582 | 159.383 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 19 | 6403 | 13.2 | 13.2 | 13.3583 | 14.2818 | 15 | 95 | 95 | 0 | 3 | -4.7076 | 275.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 3 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 1.3867 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 20 | 6404 | 14.4 | 14.4 | 13.3583 | 14.2818 | 15 | 85 | 85 | 0 | 0 | -13.7215 | 287.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 21 | 6405 | 11.5 | 11.5 | 13.3583 | 14.2818 | 15 | 98 | 98 | 0 | 0 | -22.1197 | 300.6616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 22 | 6406 | 10 | 10 | 13.3583 | 14.2818 | 15 | 99 | 99 | 0 | 0 | -29.3796 | 315.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 23 | 6407 | 9.3 | 9.3 | 13.3583 | 14.2818 | 15 | 99 | 99 | 0 | 0 | -34.8607 | 331.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 24 | 24 | 6408 | 8.7 | 8.7 | 12.7333 | 13.8684 | 15 | 99 | 99 | 0 | 0 | -37.8788 | 350.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 1 | 6409 | 8.1 | 8.1 | 12.7333 | 13.8684 | 15 | 99 | 99 | 0 | 0 | -37.9469 | 9.0999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 2 | 6410 | 8 | 8 | 12.7333 | 13.8684 | 15 | 99 | 99 | 0 | 0 | -35.4023 | 27.6835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 3 | 6411 | 7.5 | 7.5 | 12.7333 | 13.8684 | 15 | 99 | 99 | 0 | 0 | -29.9826 | 44.3323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 4 | 6412 | 7.5 | 7.5 | 12.7333 | 13.8684 | 15 | 100 | 100 | 0 | 0 | -22.7581 | 59.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 5 | 6413 | 7.4 | 7.4 | 12.7333 | 13.8684 | 15 | 100 | 100 | 0 | 0 | -14.3783 | 72.1688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 6 | 6414 | 7.7 | 7.7 | 12.7333 | 13.8684 | 15 | 98 | 98 | 0 | 0 | -5.372 | 84.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 7 | 6415 | 9.1 | 9.1 | 12.7333 | 13.8684 | 15 | 98 | 98 | 6.2583 | 3.4394 | 3.8258 | 96.2182 | 0.61267 | 4.8177 | 6.2006 | 3.9513 | 0 | 0 | 0 | 0 | 2.5606 | 1.9257 | 4.18 | 4.9214 | 3.7155 | 1.5972 | 1.5972 | 1.5972 | 1.5972 | 3.4394 | 2.5383 | 8.9977 | 11.122 | 7.6668 | 1.5972 | 1.5972 | 1.5972 | 1.5972 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 25 | 8 | 6416 | 11.5 | 11.5 | 12.7333 | 13.8684 | 15 | 95 | 95 | 42.2182 | 70.9977 | 12.8137 | 108.367 | 0 | 26.3847 | 41.8763 | 32.8373 | 4.5627 | 0 | 0 | 0 | 7.0023 | 28.0546 | 191.5132 | 287.4867 | 231.4884 | 56.3213 | 28.0546 | 28.0546 | 28.0546 | 70.9977 | 28.0546 | 217.8979 | 329.363 | 264.3257 | 60.884 | 28.0546 | 28.0546 | 28.0546 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 9 | 6417 | 14.5 | 14.5 | 12.7333 | 13.8684 | 15 | 84 | 84 | 225.133 | 140.8564 | 21.1608 | 121.4139 | 0 | 98.4081 | 208.3432 | 196.2337 | 69.1731 | 0 | 0 | 0 | 70.1436 | 68.4497 | 140.018 | 219.9695 | 211.1627 | 118.7566 | 68.4497 | 68.4497 | 68.4497 | 140.8564 | 68.4497 | 238.4261 | 428.3127 | 407.3964 | 187.9298 | 68.4497 | 68.4497 | 68.4497 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 10 | 6418 | 17 | 17 | 12.7333 | 13.8684 | 15 | 76 | 76 | 417.9753 | 165.0404 | 28.3498 | 135.9319 | 0 | 91.5644 | 332.6576 | 378.8845 | 203.166 | 0 | 0 | 0 | 181.9596 | 95.0365 | 123.9291 | 200.0046 | 214.5912 | 159.1443 | 95.0365 | 95.0365 | 95.0365 | 165.0404 | 95.0365 | 215.4934 | 532.6622 | 593.4757 | 362.3103 | 95.0365 | 95.0365 | 95.0365 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 11 | 6419 | 19 | 19 | 12.7333 | 13.8684 | 15 | 68 | 68 | 531.1302 | 172.1758 | 33.7534 | 152.2911 | 0 | 0 | 325.1029 | 467.3675 | 335.8545 | 7.6025 | 0 | 0 | 280.8242 | 106.9828 | 106.9828 | 191.1603 | 227.9962 | 193.9441 | 108.9513 | 106.9828 | 106.9828 | 172.1758 | 106.9828 | 106.9828 | 516.2632 | 695.3637 | 529.7986 | 116.5538 | 106.9828 | 106.9828 | 453 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 12 | 6420 | 20.6 | 20.6 | 12.7333 | 13.8684 | 15 | 64 | 64 | 609.7112 | 168.1025 | 36.7113 | 170.3226 | 0 | 0 | 235.7149 | 484.0263 | 448.8016 | 150.675 | 0 | 0 | 356.8975 | 110.6433 | 110.6433 | 159.3347 | 210.628 | 203.3517 | 141.7681 | 110.6433 | 110.6433 | 168.1025 | 110.6433 | 110.6433 | 395.0496 | 694.6543 | 652.1533 | 292.4431 | 110.6433 | 110.6433 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 13 | 6421 | 21.6 | 21.6 | 12.7333 | 13.8684 | 15 | 61 | 61 | 670.07 | 155.0723 | 36.7604 | 189.068 | 0 | 0 | 90.2981 | 438.2797 | 529.523 | 310.5789 | 0 | 0 | 402.9277 | 110.2878 | 110.2878 | 126.5573 | 189.2548 | 205.6945 | 166.2463 | 110.2878 | 110.2878 | 155.0723 | 110.2878 | 110.2878 | 216.8553 | 627.5344 | 735.2175 | 476.8252 | 110.2878 | 110.2878 | 558 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 14 | 6422 | 21.9 | 21.9 | 12.7333 | 13.8684 | 15 | 60 | 60 | 676.5064 | 146.6502 | 33.8923 | 207.1422 | 0 | 0 | 0 | 318.047 | 535.2062 | 438.8489 | 85.4199 | 0 | 389.3498 | 105.76 | 105.76 | 105.76 | 160.603 | 198.0492 | 181.4337 | 120.4895 | 105.76 | 146.6502 | 105.76 | 105.76 | 105.76 | 478.6499 | 733.2554 | 620.2826 | 205.9094 | 105.76 | 536 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 15 | 6423 | 22.2 | 22.2 | 12.7333 | 13.8684 | 15 | 56 | 56 | 582.0236 | 153.3101 | 28.5585 | 223.5628 | 0 | 0 | 0 | 148.1544 | 429.9266 | 459.8536 | 220.4046 | 0 | 296.6899 | 99.2772 | 99.2772 | 99.2772 | 129.863 | 188.0338 | 194.2121 | 144.7788 | 99.2772 | 153.3101 | 99.2772 | 99.2772 | 99.2772 | 278.0174 | 617.9603 | 654.0657 | 365.1834 | 99.2772 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 16 | 6424 | 22.3 | 22.3 | 12.7333 | 13.8684 | 15 | 56 | 56 | 502.6493 | 138.6608 | 21.4175 | 238.1371 | 0 | 0 | 0 | 11.0729 | 319.9132 | 441.3527 | 304.2538 | 0 | 205.3392 | 85.8101 | 85.8101 | 85.8101 | 88.4842 | 163.0682 | 192.3955 | 159.2865 | 85.8101 | 138.6608 | 85.8101 | 85.8101 | 85.8101 | 99.5571 | 482.9815 | 633.7483 | 463.5403 | 85.8101 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 17 | 6425 | 21.5 | 21.5 | 12.7333 | 13.8684 | 15 | 62 | 62 | 329.3093 | 116.2128 | 13.0995 | 251.2236 | 0 | 0 | 0 | 0 | 161.834 | 298.5454 | 260.373 | 69.6776 | 91.7872 | 65.5131 | 65.5131 | 65.5131 | 65.5131 | 120.4287 | 166.8194 | 153.8662 | 89.157 | 116.2128 | 65.5131 | 65.5131 | 65.5131 | 65.5131 | 282.2627 | 465.3648 | 414.2392 | 158.8346 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 25 | 18 | 6426 | 20 | 20 | 12.7333 | 13.8684 | 15 | 69 | 69 | 78.4666 | 58.8589 | 4.1254 | 263.3921 | 0 | 0 | 0 | 0 | 24.5992 | 68.5588 | 72.3575 | 33.7702 | 10.1411 | 30.7877 | 30.7877 | 30.7877 | 30.7877 | 44.793 | 69.8209 | 71.9837 | 50.0144 | 58.8589 | 30.7877 | 30.7877 | 30.7877 | 30.7877 | 69.3923 | 138.3797 | 144.3412 | 83.7846 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 19 | 6427 | 17.6 | 17.6 | 12.7333 | 13.8684 | 15 | 79 | 79 | 0 | 6 | -5.0718 | 275.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 6 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 2.804 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 20 | 6428 | 18 | 18 | 12.7333 | 13.8684 | 15 | 78 | 78 | 0 | 0 | -14.091 | 287.4207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 21 | 6429 | 17 | 17 | 12.7333 | 13.8684 | 15 | 82 | 82 | 0 | 0 | -22.499 | 300.5206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 22 | 6430 | 16.8 | 16.8 | 12.7333 | 13.8684 | 15 | 85 | 85 | 0 | 0 | -29.7709 | 315.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 23 | 6431 | 14.1 | 14.1 | 12.7333 | 13.8684 | 15 | 96 | 96 | 0 | 0 | -35.2609 | 331.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 25 | 24 | 6432 | 13.6 | 13.6 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -38.277 | 350.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 1 | 6433 | 13.5 | 13.5 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -38.3271 | 9.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 2 | 6434 | 12.8 | 12.8 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -35.7513 | 27.9262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 3 | 6435 | 11.9 | 11.9 | 15.1875 | 14.2934 | 15 | 100 | 100 | 0 | 0 | -30.2971 | 44.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 4 | 6436 | 12 | 12 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -23.0432 | 59.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 5 | 6437 | 12.9 | 12.9 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -14.6431 | 72.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 6 | 6438 | 14.3 | 14.3 | 15.1875 | 14.2934 | 15 | 95 | 95 | 0 | 0 | -5.6267 | 84.6681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 7 | 6439 | 14.2 | 14.2 | 15.1875 | 14.2934 | 15 | 95 | 95 | 1.1801 | 0.99 | 3.5706 | 96.5281 | 0.10914 | 0.90405 | 1.1694 | 0.7497 | 0 | 0 | 0 | 0 | 5.01 | 0.95111 | 1.6349 | 1.8632 | 1.5022 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 0.99 | 1.0602 | 2.539 | 3.0326 | 2.2519 | 0.85722 | 0.85722 | 0.85722 | 0.85722 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 26 | 8 | 6440 | 14.7 | 14.7 | 15.1875 | 14.2934 | 15 | 94 | 94 | 23.1147 | 63.2907 | 12.5479 | 108.6747 | 0 | 14.3525 | 22.9203 | 18.0617 | 2.6228 | 0 | 0 | 0 | 3.7093 | 25.3973 | 160.1153 | 240.5364 | 194.9319 | 50.0163 | 25.3973 | 25.3973 | 25.3973 | 63.2907 | 25.3973 | 174.4678 | 263.4567 | 212.9936 | 52.6391 | 25.3973 | 25.3973 | 25.3973 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 9 | 6441 | 17.1 | 17.1 | 15.1875 | 14.2934 | 15 | 86 | 86 | 116.3455 | 142.3796 | 20.8744 | 121.7145 | 0 | 50.3631 | 107.5875 | 101.7886 | 36.3633 | 0 | 0 | 0 | 35.6204 | 64.501 | 132.0691 | 208.8426 | 201.0627 | 113.2868 | 64.501 | 64.501 | 64.501 | 142.3796 | 64.501 | 182.4322 | 316.43 | 302.8513 | 149.6501 | 64.501 | 64.501 | 64.501 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 10 | 6442 | 19.2 | 19.2 | 15.1875 | 14.2934 | 15 | 77 | 77 | 218.0216 | 195.2693 | 28.0341 | 136.2125 | 0 | 46.8135 | 173.2929 | 198.2596 | 107.0886 | 0 | 0 | 0 | 93.7307 | 95.3189 | 127.6176 | 214.8813 | 232.107 | 169.204 | 95.3189 | 95.3189 | 95.3189 | 195.2693 | 95.3189 | 174.4312 | 388.1742 | 430.3666 | 276.2926 | 95.3189 | 95.3189 | 95.3189 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 11 | 6443 | 21.3 | 21.3 | 15.1875 | 14.2934 | 15 | 67 | 67 | 506.9729 | 176.7035 | 33.404 | 152.5272 | 0 | 0 | 309.6559 | 447.3885 | 323.047 | 9.4689 | 0 | 0 | 265.2965 | 107.2347 | 107.2347 | 192.2263 | 230.0299 | 195.9017 | 109.8337 | 107.2347 | 107.2347 | 176.7035 | 107.2347 | 107.2347 | 501.8822 | 677.4184 | 518.9487 | 119.3026 | 107.2347 | 107.2347 | 442 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 12 | 6444 | 22.3 | 22.3 | 15.1875 | 14.2934 | 15 | 63 | 63 | 645.6821 | 156.5611 | 36.3315 | 170.4828 | 0 | 0 | 248.6653 | 513.9969 | 478.2361 | 162.331 | 0 | 0 | 374.4389 | 108.2818 | 108.2818 | 155.0883 | 205.0318 | 198.3005 | 138.8375 | 108.2818 | 108.2818 | 156.5611 | 108.2818 | 108.2818 | 403.7536 | 719.0287 | 676.5366 | 301.1685 | 108.2818 | 108.2818 | 531 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 13 | 6445 | 22.3 | 22.3 | 15.1875 | 14.2934 | 15 | 55 | 55 | 640.4063 | 162.397 | 36.3627 | 189.1312 | 0 | 0 | 85.3031 | 420.1026 | 508.8117 | 299.4658 | 0 | 0 | 381.603 | 110.8958 | 110.8958 | 127.4209 | 192.279 | 209.464 | 168.909 | 110.8958 | 110.8958 | 162.397 | 110.8958 | 110.8958 | 212.724 | 612.3817 | 718.2756 | 468.3747 | 110.8958 | 110.8958 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 14 | 6446 | 22 | 22 | 15.1875 | 14.2934 | 15 | 60 | 60 | 94.8088 | 262.9506 | 33.492 | 207.1135 | 0 | 0 | 0 | 44.7345 | 75.3801 | 61.8692 | 12.1161 | 0 | 54.0494 | 121.6388 | 121.6388 | 121.6388 | 170.9716 | 204.7675 | 189.8676 | 135.0003 | 121.6388 | 262.9506 | 121.6388 | 121.6388 | 121.6388 | 215.7061 | 280.1476 | 251.7368 | 147.1163 | 121.6388 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 15 | 6447 | 21.5 | 21.5 | 15.1875 | 14.2934 | 15 | 59 | 59 | 46.5746 | 218.5113 | 28.1666 | 223.4667 | 0 | 0 | 0 | 11.9295 | 34.573 | 36.9642 | 17.7022 | 0 | 23.4887 | 101.3308 | 101.3308 | 101.3308 | 122.4936 | 162.6631 | 166.905 | 132.7343 | 101.3308 | 218.5113 | 101.3308 | 101.3308 | 101.3308 | 134.4231 | 197.2362 | 203.8691 | 150.4365 | 101.3308 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 16 | 6448 | 20.8 | 20.8 | 15.1875 | 14.2934 | 15 | 64 | 64 | 33.3857 | 167.5424 | 21.0375 | 238.0001 | 0 | 0 | 0 | 0.78754 | 21.3611 | 29.4216 | 20.2473 | 0 | 13.4576 | 79.2617 | 79.2617 | 79.2617 | 80.7373 | 119.2859 | 134.3888 | 117.199 | 79.2617 | 167.5424 | 79.2617 | 79.2617 | 79.2617 | 81.5249 | 140.6469 | 163.8104 | 137.4464 | 79.2617 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 17 | 6449 | 19.1 | 19.1 | 15.1875 | 14.2934 | 15 | 80 | 80 | 4.5709 | 70.7507 | 12.7296 | 251.0648 | 0 | 0 | 0 | 0 | 2.2607 | 4.1569 | 3.6179 | 0.95969 | 1.2493 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 70.7507 | 34.7202 | 34.7202 | 34.7202 | 34.7202 | 36.9809 | 38.877 | 38.3381 | 35.6799 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 26 | 18 | 6450 | 18.1 | 18.1 | 15.1875 | 14.2934 | 15 | 86 | 86 | 3.3663 | 27.583 | 3.7613 | 263.2238 | 0 | 0 | 0 | 0 | 1.0655 | 2.9496 | 3.1059 | 1.4428 | 0.41695 | 13.189 | 13.189 | 13.189 | 13.189 | 13.189 | 13.189 | 13.189 | 13.189 | 27.583 | 13.189 | 13.189 | 13.189 | 13.189 | 14.2546 | 16.1387 | 16.295 | 14.6318 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 19 | 6451 | 17.1 | 17.1 | 15.1875 | 14.2934 | 15 | 97 | 97 | 0 | 3 | -5.4355 | 275.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 3 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 1.388 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 20 | 6452 | 16.8 | 16.8 | 15.1875 | 14.2934 | 15 | 97 | 97 | 0 | 0 | -14.4599 | 287.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 21 | 6453 | 15.7 | 15.7 | 15.1875 | 14.2934 | 15 | 98 | 98 | 0 | 0 | -22.8778 | 300.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 22 | 6454 | 14.2 | 14.2 | 15.1875 | 14.2934 | 15 | 100 | 100 | 0 | 0 | -30.1618 | 315.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 23 | 6455 | 12.9 | 12.9 | 15.1875 | 14.2934 | 15 | 99 | 99 | 0 | 0 | -35.6608 | 331.7054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 26 | 24 | 6456 | 12.4 | 12.4 | 16.6292 | 14.976 | 15 | 99 | 99 | 0 | 0 | -38.6751 | 350.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 1 | 6457 | 13.6 | 13.6 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -38.7072 | 9.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 2 | 6458 | 14.6 | 14.6 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -36.1 | 28.1701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 3 | 6459 | 14.8 | 14.8 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -30.6113 | 44.9084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 4 | 6460 | 14.7 | 14.7 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -23.3281 | 59.6405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 5 | 6461 | 14.9 | 14.9 | 16.6292 | 14.976 | 15 | 98 | 98 | 0 | 0 | -14.9079 | 72.7909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 6 | 6462 | 15.1 | 15.1 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -5.8818 | 84.9787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 7 | 6463 | 15.2 | 15.2 | 16.6292 | 14.976 | 15 | 98 | 98 | 0 | 3 | 3.3149 | 96.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 27 | 8 | 6464 | 15.7 | 15.7 | 16.6292 | 14.976 | 15 | 98 | 98 | 2.981 | 32.5377 | 12.2812 | 108.981 | 0 | 1.8389 | 2.9548 | 2.3399 | 0.35429 | 0 | 0 | 0 | 0.46229 | 14.1463 | 54.1893 | 78.4906 | 65.0998 | 21.8612 | 14.1463 | 14.1463 | 14.1463 | 32.5377 | 14.1463 | 56.0281 | 81.4454 | 67.4398 | 22.2155 | 14.1463 | 14.1463 | 14.1463 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 9 | 6465 | 16.2 | 16.2 | 16.6292 | 14.976 | 15 | 98 | 98 | 6.292 | 90.1077 | 20.587 | 122.0132 | 0 | 2.6969 | 5.8137 | 5.5249 | 1.9997 | 0 | 0 | 0 | 1.8923 | 40.8948 | 63.9387 | 90.5698 | 88.1019 | 57.9808 | 40.8948 | 40.8948 | 40.8948 | 90.1077 | 40.8948 | 66.6356 | 96.3834 | 93.6268 | 59.9805 | 40.8948 | 40.8948 | 40.8948 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 10 | 6466 | 17.6 | 17.6 | 16.6292 | 14.976 | 15 | 87 | 87 | 45.6984 | 183.6022 | 27.7176 | 136.4905 | 0 | 9.6139 | 36.2744 | 41.6858 | 22.6783 | 0 | 0 | 0 | 19.3978 | 83.2706 | 106.9079 | 172.4572 | 185.7623 | 139.0291 | 83.2706 | 83.2706 | 83.2706 | 183.6022 | 83.2706 | 116.5217 | 208.7316 | 227.4481 | 161.7074 | 83.2706 | 83.2706 | 83.2706 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 11 | 6467 | 18.3 | 18.3 | 16.6292 | 14.976 | 15 | 83 | 83 | 76.1804 | 235.551 | 33.054 | 152.7604 | 0 | 0 | 46.4299 | 67.4159 | 48.9106 | 1.7541 | 0 | 0 | 39.449 | 107.358 | 107.358 | 179.0021 | 211.3848 | 182.83 | 110.0647 | 107.358 | 107.358 | 235.551 | 107.358 | 107.358 | 225.432 | 278.8007 | 231.7406 | 111.8188 | 107.358 | 107.358 | 275 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 12 | 6468 | 18.7 | 18.7 | 16.6292 | 14.976 | 15 | 80 | 80 | 26.7553 | 231.6306 | 35.9516 | 170.6403 | 0 | 0 | 10.2643 | 21.3564 | 19.9382 | 6.8405 | 0 | 0 | 15.3694 | 107.1208 | 107.1208 | 128.9885 | 152.6199 | 149.5985 | 121.6943 | 107.1208 | 107.1208 | 231.6306 | 107.1208 | 107.1208 | 139.2528 | 173.9763 | 169.5367 | 128.5348 | 107.1208 | 107.1208 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 13 | 6469 | 19 | 19 | 16.6292 | 14.976 | 15 | 78 | 78 | 21.0214 | 229.5889 | 35.965 | 189.1927 | 0 | 0 | 2.7675 | 13.8296 | 16.7906 | 9.9158 | 0 | 0 | 12.4111 | 108.1131 | 108.1131 | 113.6738 | 135.9009 | 141.8503 | 128.0368 | 108.1131 | 108.1131 | 229.5889 | 108.1131 | 108.1131 | 116.4414 | 149.7306 | 158.6408 | 137.9526 | 108.1131 | 108.1131 | 242 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 14 | 6470 | 19.4 | 19.4 | 16.6292 | 14.976 | 15 | 73 | 73 | 101.8565 | 261.4897 | 33.0921 | 207.084 | 0 | 0 | 0 | 48.2326 | 81.3814 | 66.8581 | 13.1702 | 0 | 57.5103 | 121.3661 | 121.3661 | 121.3661 | 170.9252 | 204.9857 | 190.0629 | 134.8985 | 121.3661 | 261.4897 | 121.3661 | 121.3661 | 121.3661 | 219.1577 | 286.367 | 256.921 | 148.0688 | 121.3661 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 15 | 6471 | 20.2 | 20.2 | 16.6292 | 14.976 | 15 | 68 | 68 | 478.0048 | 175.5381 | 27.775 | 223.3704 | 0 | 0 | 0 | 123.1935 | 356.5542 | 381.0503 | 182.3323 | 0 | 238.4619 | 103.3816 | 103.3816 | 103.3816 | 139.5041 | 207.9296 | 215.1123 | 156.8447 | 103.3816 | 175.5381 | 103.3816 | 103.3816 | 103.3816 | 262.6976 | 564.4839 | 596.1626 | 339.1769 | 103.3816 | 414 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 16 | 6472 | 20 | 20 | 16.6292 | 14.976 | 15 | 71 | 71 | 354.6681 | 161.9627 | 20.6578 | 237.8629 | 0 | 0 | 0 | 8.924 | 228.114 | 313.6779 | 215.4936 | 0 | 141.0373 | 89.6636 | 89.6636 | 89.6636 | 92.8303 | 170.612 | 200.9752 | 166.1336 | 89.6636 | 161.9627 | 89.6636 | 89.6636 | 89.6636 | 101.7543 | 398.726 | 514.6532 | 381.6272 | 89.6636 | 303 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 17 | 6473 | 20.5 | 20.5 | 16.6292 | 14.976 | 15 | 68 | 68 | 248.057 | 119.5425 | 12.3602 | 250.9058 | 0 | 0 | 0 | 0 | 123.4691 | 226.2834 | 196.5439 | 51.6717 | 66.4575 | 64.6484 | 64.6484 | 64.6484 | 64.6484 | 118.3137 | 163.0014 | 150.0753 | 87.1073 | 119.5425 | 64.6484 | 64.6484 | 64.6484 | 64.6484 | 241.7828 | 389.2848 | 346.6192 | 138.779 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 27 | 18 | 6474 | 18 | 18 | 16.6292 | 14.976 | 15 | 84 | 84 | 295.5531 | 50.9855 | 3.3977 | 263.055 | 0 | 0 | 0 | 0 | 94.4408 | 259.6918 | 272.8188 | 126.1323 | 35.0145 | 30.1992 | 30.1992 | 30.1992 | 30.1992 | 55.0589 | 98.558 | 102.0134 | 63.4011 | 50.9855 | 30.1992 | 30.1992 | 30.1992 | 30.1992 | 149.4998 | 358.2498 | 374.8322 | 189.5334 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 19 | 6475 | 14.9 | 14.9 | 16.6292 | 14.976 | 15 | 96 | 96 | 0 | 3 | -5.7987 | 274.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 3 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 1.3889 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 20 | 6476 | 13.4 | 13.4 | 16.6292 | 14.976 | 15 | 99 | 99 | 0 | 0 | -14.8281 | 287.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 21 | 6477 | 12.3 | 12.3 | 16.6292 | 14.976 | 15 | 100 | 100 | 0 | 0 | -23.256 | 300.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 22 | 6478 | 11.7 | 11.7 | 16.6292 | 14.976 | 15 | 99 | 99 | 0 | 0 | -30.5523 | 314.9495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 23 | 6479 | 11.2 | 11.2 | 16.6292 | 14.976 | 15 | 99 | 99 | 0 | 0 | -36.0605 | 331.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 27 | 24 | 6480 | 10.4 | 10.4 | 15.85 | 15.1556 | 15 | 100 | 100 | 0 | 0 | -39.0731 | 350.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 1 | 6481 | 10.3 | 10.3 | 15.85 | 15.1556 | 15 | 100 | 100 | 0 | 0 | -39.0871 | 9.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 2 | 6482 | 9.8 | 9.8 | 15.85 | 15.1556 | 15 | 99 | 99 | 0 | 0 | -36.4483 | 28.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 3 | 6483 | 9.5 | 9.5 | 15.85 | 15.1556 | 15 | 100 | 100 | 0 | 0 | -30.9251 | 45.1977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 4 | 6484 | 9.2 | 9.2 | 15.85 | 15.1556 | 15 | 99 | 99 | 0 | 0 | -23.6127 | 59.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 5 | 6485 | 9.1 | 9.1 | 15.85 | 15.1556 | 15 | 99 | 99 | 0 | 0 | -15.1728 | 73.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 6 | 6486 | 9.2 | 9.2 | 15.85 | 15.1556 | 15 | 98 | 98 | 0 | 0 | -6.1373 | 85.2887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 7 | 6487 | 9 | 9 | 15.85 | 15.1556 | 15 | 99 | 99 | 0 | 6 | 3.0585 | 97.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 2.9207 | 6 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 28 | 8 | 6488 | 13.5 | 13.5 | 15.85 | 15.1556 | 15 | 98 | 98 | 109.7965 | 69.5654 | 12.0138 | 109.2858 | 0 | 67.282 | 108.7887 | 86.5684 | 13.6375 | 0 | 0 | 0 | 16.4346 | 26.9787 | 184.2518 | 281.2744 | 229.334 | 58.8566 | 26.9787 | 26.9787 | 26.9787 | 69.5654 | 26.9787 | 251.5338 | 390.0631 | 315.9024 | 72.4941 | 26.9787 | 26.9787 | 26.9787 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 9 | 6489 | 16.4 | 16.4 | 15.85 | 15.1556 | 15 | 90 | 90 | 320.1252 | 124.4631 | 20.2988 | 122.3097 | 0 | 135.8546 | 295.5427 | 282.1058 | 103.4152 | 0 | 0 | 0 | 94.5369 | 67.5808 | 116.1865 | 173.3193 | 168.5119 | 104.5804 | 67.5808 | 67.5808 | 67.5808 | 124.4631 | 67.5808 | 252.0412 | 468.862 | 450.6177 | 207.9956 | 67.5808 | 67.5808 | 67.5808 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 10 | 6490 | 19.1 | 19.1 | 15.85 | 15.1556 | 15 | 79 | 79 | 501.4568 | 142.8813 | 27.4002 | 136.7658 | 0 | 103.3192 | 397.4963 | 458.8255 | 251.3809 | 0 | 0 | 0 | 210.1187 | 88.3185 | 113.3326 | 184.5543 | 199.4024 | 149.1791 | 88.3185 | 88.3185 | 88.3185 | 142.8813 | 88.3185 | 216.6518 | 582.0507 | 658.2279 | 400.56 | 88.3185 | 88.3185 | 88.3185 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 11 | 6491 | 20.4 | 20.4 | 15.85 | 15.1556 | 15 | 69 | 69 | 643.8509 | 139.1181 | 32.7034 | 152.9906 | 0 | 0 | 391.5493 | 571.3481 | 416.459 | 17.6139 | 0 | 0 | 329.8819 | 97.3941 | 97.3941 | 166.9325 | 198.8644 | 171.3564 | 100.5223 | 97.3941 | 97.3941 | 139.1181 | 97.3941 | 97.3941 | 558.4817 | 770.2125 | 587.8154 | 118.1361 | 97.3941 | 97.3941 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 12 | 6492 | 21.7 | 21.7 | 15.85 | 15.1556 | 15 | 64 | 64 | 721.3937 | 133.5632 | 35.5714 | 170.7951 | 0 | 0 | 275.6781 | 577.358 | 540.8294 | 187.4902 | 0 | 0 | 410.4368 | 103.2661 | 103.2661 | 145.7867 | 192.3179 | 186.6837 | 132.1846 | 103.2661 | 103.2661 | 133.5632 | 103.2661 | 103.2661 | 421.4649 | 769.6759 | 727.5131 | 319.6749 | 103.2661 | 103.2661 | 544 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 13 | 6493 | 22.7 | 22.7 | 15.85 | 15.1556 | 15 | 60 | 60 | 769.6112 | 124.8491 | 35.5676 | 189.2524 | 0 | 0 | 100.1372 | 507.7529 | 617.9338 | 366.1375 | 0 | 0 | 450.1509 | 103.4845 | 103.4845 | 117.1963 | 173.0113 | 188.0984 | 153.6199 | 103.4845 | 103.4845 | 124.8491 | 103.4845 | 103.4845 | 217.3335 | 680.7642 | 806.0323 | 519.7574 | 103.4845 | 103.4845 | 575 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 14 | 6494 | 22.9 | 22.9 | 15.85 | 15.1556 | 15 | 62 | 62 | 761.3257 | 121.3199 | 32.6925 | 207.0537 | 0 | 0 | 0 | 361.7965 | 611.2281 | 502.6105 | 99.5706 | 0 | 425.6801 | 99.6119 | 99.6119 | 99.6119 | 148.71 | 182.5595 | 167.8194 | 113.1242 | 99.6119 | 121.3199 | 99.6119 | 99.6119 | 99.6119 | 510.5065 | 793.7876 | 670.4299 | 212.6948 | 99.6119 | 547 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 15 | 6495 | 23.4 | 23.4 | 15.85 | 15.1556 | 15 | 59 | 59 | 703.4422 | 119.9261 | 27.3839 | 223.2739 | 0 | 0 | 0 | 182.4115 | 527.2272 | 563.2003 | 269.2584 | 0 | 347.0739 | 91.5101 | 91.5101 | 91.5101 | 118.4642 | 169.416 | 174.7316 | 131.2971 | 91.5101 | 119.9261 | 91.5101 | 91.5101 | 91.5101 | 300.8756 | 696.6432 | 737.9319 | 400.5555 | 91.5101 | 467 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 16 | 6496 | 23.7 | 23.7 | 15.85 | 15.1556 | 15 | 64 | 64 | 638.8056 | 107.4556 | 20.2786 | 237.7257 | 0 | 0 | 0 | 17.086 | 412.9876 | 566.9668 | 388.8244 | 0 | 250.5444 | 77.0773 | 77.0773 | 77.0773 | 79.7488 | 141.6511 | 165.7269 | 137.873 | 77.0773 | 107.4556 | 77.0773 | 77.0773 | 77.0773 | 96.8348 | 554.6387 | 732.6937 | 526.6974 | 77.0773 | 358 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 17 | 6497 | 22.9 | 22.9 | 15.85 | 15.1556 | 15 | 65 | 65 | 552.2931 | 83.0292 | 11.9913 | 250.7466 | 0 | 0 | 0 | 0 | 276.631 | 505.3354 | 438.0212 | 114.1201 | 144.9708 | 56.1126 | 56.1126 | 56.1126 | 56.1126 | 101.7444 | 139.4705 | 128.3666 | 74.9374 | 83.0292 | 56.1126 | 56.1126 | 56.1126 | 56.1126 | 378.3754 | 644.8058 | 566.3878 | 189.0575 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2011 | 9 | 28 | 18 | 6498 | 20.4 | 20.4 | 15.85 | 15.1556 | 15 | 76 | 76 | 280.2177 | 49.313 | 3.0349 | 262.8856 | 0 | 0 | 0 | 0 | 90.3848 | 246.8913 | 258.7723 | 119.068 | 31.687 | 29.0494 | 29.0494 | 29.0494 | 29.0494 | 53.892 | 96.9084 | 100.174 | 61.7757 | 49.313 | 29.0494 | 29.0494 | 29.0494 | 29.0494 | 144.2767 | 343.7998 | 358.9463 | 180.8436 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 19 | 6499 | 16.8 | 16.8 | 15.85 | 15.1556 | 15 | 93 | 93 | 0 | 3 | -6.161 | 274.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 3 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 20 | 6500 | 15.3 | 15.3 | 15.85 | 15.1556 | 15 | 96 | 96 | 0 | 0 | -15.1956 | 286.9307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 21 | 6501 | 15 | 15 | 15.85 | 15.1556 | 15 | 95 | 95 | 0 | 0 | -23.6334 | 300.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 22 | 6502 | 14.4 | 14.4 | 15.85 | 15.1556 | 15 | 95 | 95 | 0 | 0 | -30.942 | 314.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 23 | 6503 | 14 | 14 | 15.85 | 15.1556 | 15 | 97 | 97 | 0 | 0 | -36.4597 | 331.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 28 | 24 | 6504 | 13.7 | 13.7 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -39.4708 | 350.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 1 | 6505 | 13.7 | 13.7 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -39.4667 | 9.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 2 | 6506 | 13.8 | 13.8 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -36.7963 | 28.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 3 | 6507 | 15.1 | 15.1 | 15.9333 | 15.3209 | 15 | 95 | 95 | 0 | 0 | -31.2386 | 45.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 4 | 6508 | 15.3 | 15.3 | 15.9333 | 15.3209 | 15 | 94 | 94 | 0 | 0 | -23.8972 | 60.2545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 5 | 6509 | 13.5 | 13.5 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -15.4377 | 73.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 6 | 6510 | 13.2 | 13.2 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -6.393 | 85.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 7 | 6511 | 13.3 | 13.3 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 3 | 2.8016 | 97.4521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 29 | 8 | 6512 | 15.7 | 15.7 | 15.9333 | 15.3209 | 15 | 94 | 94 | 68.4649 | 65.1218 | 11.7457 | 109.5889 | 0 | 41.6744 | 67.8055 | 54.2171 | 8.8691 | 0 | 0 | 0 | 9.8782 | 24.5488 | 193.2182 | 298.9793 | 243.9828 | 60.4448 | 24.5488 | 24.5488 | 24.5488 | 65.1218 | 24.5488 | 234.8926 | 366.7849 | 298.1999 | 69.3138 | 24.5488 | 24.5488 | 24.5488 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 9 | 6513 | 17.7 | 17.7 | 15.9333 | 15.3209 | 15 | 86 | 86 | 297.7197 | 124.6994 | 20.0097 | 122.604 | 0 | 125.0794 | 274.6152 | 263.2851 | 97.7262 | 0 | 0 | 0 | 86.3006 | 66.6844 | 114.5507 | 171.7762 | 167.4403 | 104.083 | 66.6844 | 66.6844 | 66.6844 | 124.6994 | 66.6844 | 239.6302 | 446.3914 | 430.7254 | 201.8092 | 66.6844 | 66.6844 | 66.6844 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 10 | 6514 | 19.8 | 19.8 | 15.9333 | 15.3209 | 15 | 80 | 80 | 480.4845 | 145.2991 | 27.0821 | 137.0383 | 0 | 96.9178 | 380.3333 | 440.9547 | 243.2709 | 0 | 0 | 0 | 198.7009 | 88.1027 | 112.6144 | 184.2938 | 199.6258 | 149.629 | 88.1027 | 88.1027 | 88.1027 | 145.2991 | 88.1027 | 209.5322 | 564.6271 | 640.5805 | 392.8998 | 88.1027 | 88.1027 | 88.1027 | 344 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 11 | 6515 | 21.9 | 21.9 | 15.9333 | 15.3209 | 15 | 74 | 74 | 620.2494 | 143.6218 | 32.3523 | 153.2177 | 0 | 0 | 376.3582 | 551.8928 | 404.1361 | 19.642 | 0 | 0 | 314.3782 | 97.4761 | 97.4761 | 167.7263 | 200.4912 | 172.9113 | 101.1424 | 97.4761 | 97.4761 | 143.6218 | 97.4761 | 97.4761 | 544.0845 | 752.3841 | 577.0474 | 120.7844 | 97.4761 | 97.4761 | 458 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 12 | 6516 | 23.4 | 23.4 | 15.9333 | 15.3209 | 15 | 66 | 66 | 695.1619 | 139.3224 | 35.1912 | 170.9472 | 0 | 0 | 264.6183 | 557.819 | 524.2569 | 183.5922 | 0 | 0 | 391.6776 | 103.6448 | 103.6448 | 147.1138 | 195.2781 | 189.7648 | 133.8036 | 103.6448 | 103.6448 | 139.3224 | 103.6448 | 103.6448 | 411.7322 | 753.0971 | 714.0217 | 317.3958 | 103.6448 | 103.6448 | 531 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 13 | 6517 | 24.8 | 24.8 | 15.9333 | 15.3209 | 15 | 61 | 61 | 733.5386 | 132.9981 | 35.1705 | 189.3101 | 0 | 0 | 94.3241 | 485.308 | 592.005 | 351.9135 | 0 | 0 | 425.0019 | 104.263 | 104.263 | 118.423 | 177.1178 | 193.1352 | 157.0925 | 104.263 | 104.263 | 132.9981 | 104.263 | 104.263 | 212.7472 | 662.4257 | 785.1402 | 509.006 | 104.263 | 104.263 | 558 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 14 | 6518 | 24.9 | 24.9 | 15.9333 | 15.3209 | 15 | 60 | 60 | 732.9397 | 127.2324 | 32.2935 | 207.0225 | 0 | 0 | 0 | 349.5342 | 591.2432 | 486.61 | 96.9273 | 0 | 405.7676 | 100.0565 | 100.0565 | 100.0565 | 151.0571 | 186.325 | 171.0579 | 114.1992 | 100.0565 | 127.2324 | 100.0565 | 100.0565 | 100.0565 | 500.5913 | 777.5682 | 657.6679 | 211.1265 | 100.0565 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 15 | 6519 | 25.1 | 25.1 | 15.9333 | 15.3209 | 15 | 59 | 59 | 699.7513 | 119.5923 | 26.9934 | 223.177 | 0 | 0 | 0 | 182.5671 | 526.9386 | 562.6366 | 268.7497 | 0 | 341.4077 | 90.8494 | 90.8494 | 90.8494 | 117.9778 | 169.1495 | 174.454 | 130.7841 | 90.8494 | 119.5923 | 90.8494 | 90.8494 | 90.8494 | 300.5449 | 696.0881 | 737.0906 | 399.5338 | 90.8494 | 461 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 16 | 6520 | 24.8 | 24.8 | 15.9333 | 15.3209 | 15 | 54 | 54 | 638.109 | 106.2174 | 19.9001 | 237.5882 | 0 | 0 | 0 | 18.0879 | 414.6424 | 568.3051 | 389.0623 | 0 | 246.7826 | 76.2031 | 76.2031 | 76.2031 | 79.0222 | 140.8268 | 164.7757 | 136.84 | 76.2031 | 106.2174 | 76.2031 | 76.2031 | 76.2031 | 97.1101 | 555.4692 | 733.0808 | 525.9024 | 76.2031 | 353 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 17 | 6521 | 24 | 24 | 15.9333 | 15.3209 | 15 | 60 | 60 | 481.7505 | 90.1627 | 11.6232 | 250.5869 | 0 | 0 | 0 | 0 | 242.7995 | 442.0949 | 382.4171 | 98.7245 | 123.8373 | 56.9696 | 56.9696 | 56.9696 | 56.9696 | 105.0258 | 144.4714 | 132.6596 | 76.5097 | 90.1627 | 56.9696 | 56.9696 | 56.9696 | 56.9696 | 347.8253 | 586.5663 | 515.0767 | 175.2342 | 214 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 18 | 6522 | 21.5 | 21.5 | 15.9333 | 15.3209 | 15 | 72 | 72 | 226.0199 | 46.5441 | 2.6728 | 262.7156 | 0 | 0 | 0 | 0 | 73.5831 | 199.6741 | 208.7987 | 95.6119 | 31.4559 | 27.6738 | 27.6738 | 27.6738 | 27.6738 | 52.1309 | 94.0401 | 97.0729 | 59.4526 | 46.5441 | 27.6738 | 27.6738 | 27.6738 | 27.6738 | 125.714 | 293.7142 | 305.8716 | 155.0645 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 19 | 6523 | 16.8 | 16.8 | 15.9333 | 15.3209 | 15 | 93 | 93 | 0 | 3 | -6.5225 | 274.5701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 3 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 20 | 6524 | 15.6 | 15.6 | 15.9333 | 15.3209 | 15 | 98 | 98 | 0 | 0 | -15.5621 | 286.7648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 21 | 6525 | 14.5 | 14.5 | 15.9333 | 15.3209 | 15 | 97 | 97 | 0 | 0 | -24.0099 | 299.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 22 | 6526 | 13.7 | 13.7 | 15.9333 | 15.3209 | 15 | 97 | 97 | 0 | 0 | -31.331 | 314.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 23 | 6527 | 12.8 | 12.8 | 15.9333 | 15.3209 | 15 | 99 | 99 | 0 | 0 | -36.8583 | 331.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 29 | 24 | 6528 | 12.7 | 12.7 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -39.8681 | 350.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 1 | 6529 | 12.9 | 12.9 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -39.846 | 9.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 2 | 6530 | 12.9 | 12.9 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -37.1437 | 28.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 3 | 6531 | 12 | 12 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -31.5516 | 45.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 4 | 6532 | 12.1 | 12.1 | 17.8167 | 16.0407 | 15 | 97 | 97 | 0 | 0 | -24.1814 | 60.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 5 | 6533 | 12.6 | 12.6 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -15.7025 | 73.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 6 | 6534 | 11.8 | 11.8 | 17.8167 | 16.0407 | 15 | 97 | 97 | 0 | 0 | -6.649 | 85.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 7 | 6535 | 13.2 | 13.2 | 17.8167 | 16.0407 | 15 | 97 | 97 | 0 | 3 | 2.5442 | 97.7577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2011 | 9 | 30 | 8 | 6536 | 15.2 | 15.2 | 17.8167 | 16.0407 | 15 | 89 | 89 | 81.9767 | 63.6153 | 11.4768 | 109.8903 | 0 | 49.5624 | 81.1463 | 65.1959 | 11.0546 | 0 | 0 | 0 | 11.3847 | 23.9084 | 168.6322 | 260.8585 | 214.2826 | 56.1882 | 23.9084 | 23.9084 | 23.9084 | 63.6153 | 23.9084 | 218.1946 | 342.0048 | 279.4785 | 67.2427 | 23.9084 | 23.9084 | 23.9084 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 9 | 6537 | 17.2 | 17.2 | 17.8167 | 16.0407 | 15 | 80 | 80 | 302.5999 | 121.9335 | 19.7198 | 122.896 | 0 | 125.8417 | 278.8591 | 268.5246 | 100.892 | 0 | 0 | 0 | 86.0665 | 65.4631 | 112.4548 | 169.5943 | 165.7352 | 103.1381 | 65.4631 | 65.4631 | 65.4631 | 121.9335 | 65.4631 | 238.2965 | 448.4535 | 434.2599 | 204.0301 | 65.4631 | 65.4631 | 65.4631 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 10 | 6538 | 18.8 | 18.8 | 17.8167 | 16.0407 | 15 | 74 | 74 | 529.7612 | 133.8285 | 26.7632 | 137.3079 | 0 | 104.5695 | 418.7314 | 487.6062 | 270.8479 | 0 | 0 | 0 | 216.1715 | 85.2446 | 108.6257 | 178.8704 | 194.2704 | 145.8045 | 85.2446 | 85.2446 | 85.2446 | 133.8285 | 85.2446 | 213.1952 | 597.6018 | 681.8765 | 416.6524 | 85.2446 | 85.2446 | 85.2446 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 11 | 6539 | 21.1 | 21.1 | 17.8167 | 16.0407 | 15 | 68 | 68 | 639.012 | 137.6382 | 32.0008 | 153.4415 | 0 | 0 | 386.8714 | 570.095 | 419.3647 | 22.9762 | 0 | 0 | 320.3618 | 95.8625 | 95.8625 | 164.7452 | 197.3683 | 170.5306 | 99.9534 | 95.8625 | 95.8625 | 137.6382 | 95.8625 | 95.8625 | 551.6166 | 767.4633 | 589.8953 | 122.9296 | 95.8625 | 95.8625 | 458 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 12 | 6540 | 22.2 | 22.2 | 17.8167 | 16.0407 | 15 | 59 | 59 | 718.7741 | 131.9986 | 34.811 | 171.0963 | 0 | 0 | 272.5365 | 578.2478 | 545.2293 | 192.8229 | 0 | 0 | 401.0014 | 101.7742 | 101.7742 | 143.7722 | 190.8825 | 185.7943 | 131.4883 | 101.7742 | 101.7742 | 131.9986 | 101.7742 | 101.7742 | 416.3088 | 769.1302 | 731.0236 | 324.3112 | 101.7742 | 101.7742 | 533 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 13 | 6541 | 23.9 | 23.9 | 17.8167 | 16.0407 | 15 | 51 | 51 | 768.1752 | 123.1879 | 34.7738 | 189.366 | 0 | 0 | 97.6168 | 509.6251 | 623.102 | 371.5741 | 0 | 0 | 440.8121 | 101.9852 | 101.9852 | 115.3046 | 171.5211 | 187.0045 | 152.6848 | 101.9852 | 101.9852 | 123.1879 | 101.9852 | 101.9852 | 212.9213 | 681.1463 | 810.1065 | 524.2589 | 101.9852 | 101.9852 | 564 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 14 | 6542 | 23.8 | 23.8 | 17.8167 | 16.0407 | 15 | 54 | 54 | 769.1847 | 117.4234 | 31.8951 | 206.9904 | 0 | 0 | 0 | 368.0997 | 623.3934 | 513.5116 | 102.8217 | 0 | 421.5766 | 97.7216 | 97.7216 | 97.7216 | 146.258 | 179.9202 | 165.4315 | 111.2793 | 97.7216 | 117.4234 | 97.7216 | 97.7216 | 97.7216 | 514.3577 | 803.3136 | 678.9431 | 214.101 | 97.7216 | 539 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 15 | 6543 | 23.8 | 23.8 | 17.8167 | 16.0407 | 15 | 55 | 55 | 730.7587 | 111.4922 | 26.6036 | 223.0798 | 0 | 0 | 0 | 191.8212 | 552.8512 | 590.0285 | 281.5751 | 0 | 352.5078 | 88.6805 | 88.6805 | 88.6805 | 114.7914 | 163.9351 | 168.9957 | 127.0088 | 88.6805 | 111.4922 | 88.6805 | 88.6805 | 88.6805 | 306.6126 | 716.7864 | 759.0242 | 408.5839 | 88.6805 | 464 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 16 | 6544 | 23.6 | 23.6 | 17.8167 | 16.0407 | 15 | 60 | 60 | 632.3586 | 105.9066 | 19.5224 | 237.4505 | 0 | 0 | 0 | 18.9455 | 412.9761 | 565.0908 | 386.183 | 0 | 241.0934 | 75.5167 | 75.5167 | 75.5167 | 78.4991 | 140.5286 | 164.475 | 136.3108 | 75.5167 | 105.9066 | 75.5167 | 75.5167 | 75.5167 | 97.4447 | 553.5047 | 729.5658 | 522.4938 | 75.5167 | 347 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 17 | 6545 | 23.1 | 23.1 | 17.8167 | 16.0407 | 15 | 59 | 59 | 455.0105 | 91.5113 | 11.256 | 250.427 | 0 | 0 | 0 | 0 | 230.7343 | 418.7667 | 361.4913 | 92.4592 | 114.4887 | 57.017 | 57.017 | 57.017 | 57.017 | 107.0916 | 147.899 | 135.4689 | 77.0827 | 91.5113 | 57.017 | 57.017 | 57.017 | 57.017 | 337.8259 | 566.6657 | 496.9602 | 169.5419 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 18 | 6546 | 20 | 20 | 17.8167 | 16.0407 | 15 | 77 | 77 | 219.544 | 46.5419 | 2.3117 | 262.545 | 0 | 0 | 0 | 0 | 72.1343 | 194.4637 | 202.8788 | 92.4503 | 22.4581 | 26.7603 | 26.7603 | 26.7603 | 26.7603 | 51.7408 | 94.1041 | 97.0184 | 58.7763 | 46.5419 | 26.7603 | 26.7603 | 26.7603 | 26.7603 | 123.8751 | 288.5678 | 299.8972 | 151.2267 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 19 | 6547 | 15.4 | 15.4 | 17.8167 | 16.0407 | 15 | 94 | 94 | 0 | 0 | -6.8829 | 274.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 20 | 6548 | 13.2 | 13.2 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -15.9275 | 286.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 21 | 6549 | 12.6 | 12.6 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -24.3853 | 299.7919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 22 | 6550 | 11.3 | 11.3 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -31.7191 | 314.6243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 23 | 6551 | 10.3 | 10.3 | 17.8167 | 16.0407 | 15 | 98 | 98 | 0 | 0 | -37.2563 | 331.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2011 | 9 | 30 | 24 | 6552 | 8.9 | 8.9 | 16.3292 | 16.269 | 15 | 98 | 98 | 0 | 0 | -40.2649 | 350.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 1 | 6553 | 8.7 | 8.7 | 16.3292 | 16.269 | 15 | 98 | 98 | 0 | 0 | -40.2248 | 10.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 2 | 6554 | 8.4 | 8.4 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 0 | -37.4906 | 29.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 3 | 6555 | 8.6 | 8.6 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 0 | -31.8641 | 46.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 4 | 6556 | 8.8 | 8.8 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 0 | -24.4653 | 60.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 5 | 6557 | 8.4 | 8.4 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 0 | -15.9674 | 74.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 6 | 6558 | 7.7 | 7.7 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 0 | -6.9052 | 86.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 7 | 6559 | 6.9 | 6.9 | 16.3292 | 16.269 | 15 | 99 | 99 | 0 | 3 | 2.2862 | 98.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 1 | 8 | 6560 | 9.3 | 9.3 | 16.3292 | 16.269 | 15 | 99 | 99 | 155.3598 | 62.2636 | 11.2071 | 110.1897 | 0 | 93.2897 | 153.702 | 124.0778 | 21.7705 | 0 | 0 | 0 | 20.7364 | 25.9449 | 25.9449 | 25.9449 | 25.9449 | 25.9449 | 25.9449 | 25.9449 | 25.9449 | 62.2636 | 25.9449 | 119.2346 | 179.6469 | 150.0227 | 47.7154 | 25.9449 | 25.9449 | 25.9449 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 9 | 6561 | 10.9 | 10.9 | 16.3292 | 16.269 | 15 | 94 | 94 | 325.1747 | 117.2868 | 19.4291 | 123.1855 | 0 | 133.8463 | 299.3746 | 289.5334 | 110.0874 | 0 | 0 | 0 | 90.7132 | 64.02 | 110.0751 | 167.0317 | 163.6455 | 101.9 | 64.02 | 64.02 | 64.02 | 117.2868 | 64.02 | 243.9214 | 466.4063 | 453.1788 | 211.9874 | 64.02 | 64.02 | 64.02 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 10 | 6562 | 13 | 13 | 16.3292 | 16.269 | 15 | 88 | 88 | 566.5751 | 124.923 | 26.4437 | 137.5745 | 0 | 109.3971 | 447.1664 | 522.9917 | 292.4556 | 0 | 0 | 0 | 228.077 | 82.775 | 105.0739 | 173.9229 | 189.3787 | 142.3875 | 82.775 | 82.775 | 82.775 | 124.923 | 82.775 | 214.471 | 621.0893 | 712.3704 | 434.8431 | 82.775 | 82.775 | 82.775 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 11 | 6563 | 14.6 | 14.6 | 16.3292 | 16.269 | 15 | 75 | 75 | 626.7849 | 139.2375 | 31.6489 | 153.662 | 0 | 0 | 378.607 | 560.6393 | 414.2568 | 25.2082 | 0 | 0 | 310.7625 | 95.47 | 95.47 | 164.4811 | 197.6613 | 170.9793 | 100.0649 | 95.47 | 95.47 | 139.2375 | 95.47 | 95.47 | 543.0881 | 758.3007 | 585.236 | 125.2731 | 95.47 | 95.47 | 450 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 12 | 6564 | 15.8 | 15.8 | 16.3292 | 16.269 | 15 | 74 | 74 | 709.1034 | 133.3341 | 34.431 | 171.2424 | 0 | 0 | 267.8161 | 571.9067 | 540.9822 | 193.1576 | 0 | 0 | 391.6659 | 101.3888 | 101.3888 | 143.5239 | 191.3661 | 186.5008 | 131.778 | 101.3888 | 101.3888 | 133.3341 | 101.3888 | 101.3888 | 411.34 | 763.2728 | 727.4829 | 324.9356 | 101.3888 | 101.3888 | 525 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 13 | 6565 | 16.6 | 16.6 | 16.3292 | 16.269 | 15 | 65 | 65 | 759.8409 | 124.1974 | 34.3776 | 189.4197 | 0 | 0 | 95.4215 | 505.4664 | 619.4159 | 370.52 | 0 | 0 | 431.8026 | 101.5405 | 101.5405 | 114.801 | 171.784 | 187.6193 | 153.0308 | 101.5405 | 101.5405 | 124.1974 | 101.5405 | 101.5405 | 210.2225 | 677.2504 | 807.0352 | 523.5508 | 101.5405 | 101.5405 | 556 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 14 | 6566 | 16.8 | 16.8 | 16.3292 | 16.269 | 15 | 65 | 65 | 409.6175 | 208.7705 | 31.4975 | 206.9572 | 0 | 0 | 0 | 196.7042 | 333.5126 | 274.9537 | 55.3307 | 0 | 222.2295 | 114.3208 | 114.3208 | 114.3208 | 189.048 | 241.021 | 218.7747 | 135.3408 | 114.3208 | 208.7705 | 114.3208 | 114.3208 | 114.3208 | 385.7523 | 574.5335 | 493.7284 | 190.6715 | 114.3208 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 15 | 6567 | 16.8 | 16.8 | 16.3292 | 16.269 | 15 | 65 | 65 | 365.673 | 192.626 | 26.2147 | 222.9821 | 0 | 0 | 0 | 96.5716 | 277.9178 | 296.4635 | 141.3449 | 0 | 174.374 | 104.956 | 104.956 | 104.956 | 142.0314 | 211.6532 | 218.7732 | 159.2206 | 104.956 | 192.626 | 104.956 | 104.956 | 104.956 | 238.6031 | 489.571 | 515.2367 | 300.5655 | 104.956 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 16 | 6568 | 15.9 | 15.9 | 16.3292 | 16.269 | 15 | 69 | 69 | 153.4246 | 175.3478 | 19.1457 | 237.3126 | 0 | 0 | 0 | 4.8467 | 100.6959 | 137.5588 | 93.8416 | 0 | 57.6522 | 86.6109 | 86.6109 | 86.6109 | 89.9068 | 155.089 | 180.1576 | 150.4278 | 86.6109 | 175.3478 | 86.6109 | 86.6109 | 86.6109 | 94.7535 | 255.7849 | 317.7164 | 244.2694 | 86.6109 | 233 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 17 | 6569 | 15.2 | 15.2 | 16.3292 | 16.269 | 15 | 70 | 70 | 26.7003 | 99.4271 | 10.8897 | 250.2666 | 0 | 0 | 0 | 0 | 13.6221 | 24.6433 | 21.2288 | 5.3788 | 6.5729 | 48.643 | 48.643 | 48.643 | 48.643 | 68.3738 | 84.3374 | 79.3917 | 56.4338 | 99.4271 | 48.643 | 48.643 | 48.643 | 48.643 | 81.9959 | 108.9807 | 100.6205 | 61.8126 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 1 | 18 | 6570 | 14.4 | 14.4 | 16.3292 | 16.269 | 15 | 74 | 74 | 8.8811 | 32.1394 | 1.9517 | 262.3737 | 0 | 0 | 0 | 0 | 2.9446 | 7.8868 | 8.209 | 3.7225 | 0.8606 | 16.5931 | 16.5931 | 16.5931 | 16.5931 | 19.4542 | 24.2562 | 24.5692 | 20.21 | 32.1394 | 16.5931 | 16.5931 | 16.5931 | 16.5931 | 22.3989 | 32.143 | 32.7782 | 23.9324 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 19 | 6571 | 13.9 | 13.9 | 16.3292 | 16.269 | 15 | 73 | 73 | 0 | 0 | -7.2421 | 274.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 20 | 6572 | 13.5 | 13.5 | 16.3292 | 16.269 | 15 | 75 | 75 | 0 | 0 | -16.2917 | 286.4288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 21 | 6573 | 13.3 | 13.3 | 16.3292 | 16.269 | 15 | 77 | 77 | 0 | 0 | -24.7595 | 299.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 22 | 6574 | 12.6 | 12.6 | 16.3292 | 16.269 | 15 | 85 | 85 | 0 | 0 | -32.1061 | 314.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 23 | 6575 | 12.1 | 12.1 | 16.3292 | 16.269 | 15 | 91 | 91 | 0 | 0 | -37.6534 | 331.5077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 1 | 24 | 6576 | 12.1 | 12.1 | 12.2625 | 15.3549 | 15 | 94 | 94 | 0 | 0 | -40.6611 | 350.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 1 | 6577 | 12.2 | 12.2 | 12.2625 | 15.3549 | 15 | 95 | 95 | 0 | 0 | -40.6031 | 10.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 2 | 6578 | 12.3 | 12.3 | 12.2625 | 15.3549 | 15 | 95 | 95 | 0 | 0 | -37.8369 | 29.4009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 3 | 6579 | 12.3 | 12.3 | 12.2625 | 15.3549 | 15 | 96 | 96 | 0 | 0 | -32.1761 | 46.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 4 | 6580 | 12.4 | 12.4 | 12.2625 | 15.3549 | 15 | 97 | 97 | 0 | 0 | -24.7489 | 61.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 5 | 6581 | 12.5 | 12.5 | 12.2625 | 15.3549 | 15 | 97 | 97 | 0 | 0 | -16.2322 | 74.3412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 6 | 6582 | 12.9 | 12.9 | 12.2625 | 15.3549 | 15 | 98 | 98 | 0 | 0 | -7.1618 | 86.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 7 | 6583 | 13.5 | 13.5 | 12.2625 | 15.3549 | 15 | 97 | 97 | 0 | 0 | 2.0278 | 98.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 2 | 8 | 6584 | 14 | 14 | 12.2625 | 15.3549 | 15 | 97 | 97 | 0.48428 | 10.938 | 10.9369 | 110.4871 | 0 | 0.2888 | 0.47883 | 0.38837 | 0.070404 | 0 | 0 | 0 | 0.062023 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 5.3197 | 10.938 | 5.3197 | 5.6085 | 5.7986 | 5.7081 | 5.3901 | 5.3197 | 5.3197 | 5.3197 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 9 | 6585 | 14.6 | 14.6 | 12.2625 | 15.3549 | 15 | 96 | 96 | 1.1373 | 35.6889 | 19.1377 | 123.4724 | 0 | 0.4633 | 1.046 | 1.016 | 0.39083 | 0 | 0 | 0 | 0.31106 | 17.3056 | 17.3056 | 17.3056 | 17.3056 | 17.3056 | 17.3056 | 17.3056 | 17.3056 | 35.6889 | 17.3056 | 17.7689 | 18.3516 | 18.3216 | 17.6964 | 17.3056 | 17.3056 | 17.3056 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 10 | 6586 | 15.6 | 15.6 | 12.2625 | 15.3549 | 15 | 92 | 92 | 11.5544 | 139.4124 | 26.1236 | 137.8379 | 0 | 2.1814 | 9.1054 | 10.6956 | 6.0204 | 0 | 0 | 0 | 4.5876 | 63.5537 | 74.0601 | 107.4084 | 115.0672 | 92.5501 | 63.5537 | 63.5537 | 63.5537 | 139.4124 | 63.5537 | 76.2415 | 116.5139 | 125.7629 | 98.5705 | 63.5537 | 63.5537 | 63.5537 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 11 | 6587 | 16.7 | 16.7 | 12.2625 | 15.3549 | 15 | 88 | 88 | 107.7184 | 228.1906 | 31.2969 | 153.8792 | 0 | 0 | 64.9178 | 96.5959 | 71.6895 | 4.7884 | 0 | 0 | 52.8094 | 105.3886 | 105.3886 | 177.5193 | 212.7172 | 185.0435 | 110.709 | 105.3886 | 105.3886 | 228.1906 | 105.3886 | 105.3886 | 242.4371 | 309.3132 | 256.733 | 115.4973 | 105.3886 | 105.3886 | 281 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 12 | 6588 | 17 | 17 | 12.2625 | 15.3549 | 15 | 85 | 85 | 15.4383 | 202.5589 | 34.0512 | 171.3854 | 0 | 0 | 5.8079 | 12.4822 | 11.8445 | 4.2685 | 0 | 0 | 8.4411 | 95.0022 | 95.0022 | 110.4895 | 128.287 | 126.5866 | 106.3846 | 95.0022 | 95.0022 | 202.5589 | 95.0022 | 95.0022 | 116.2974 | 140.7691 | 138.4312 | 110.6531 | 95.0022 | 95.0022 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 13 | 6589 | 17.9 | 17.9 | 12.2625 | 15.3549 | 15 | 81 | 81 | 201.3024 | 258.7273 | 33.9822 | 189.4714 | 0 | 0 | 24.9824 | 134.2707 | 164.905 | 98.9402 | 0 | 0 | 113.2727 | 124.5449 | 124.5449 | 142.4947 | 221.0179 | 243.0285 | 195.6331 | 124.5449 | 124.5449 | 258.7273 | 124.5449 | 124.5449 | 167.4771 | 355.2886 | 407.9336 | 294.5733 | 124.5449 | 124.5449 | 372 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 14 | 6590 | 17.7 | 17.7 | 12.2625 | 15.3549 | 15 | 81 | 81 | 12.1709 | 190.4647 | 31.1008 | 206.9229 | 0 | 0 | 0 | 5.8647 | 9.9546 | 8.2133 | 1.6607 | 0 | 6.5353 | 91.7945 | 91.7945 | 91.7945 | 102.8208 | 110.5103 | 107.2364 | 94.9169 | 91.7945 | 190.4647 | 91.7945 | 91.7945 | 91.7945 | 108.6855 | 120.465 | 115.4498 | 96.5776 | 91.7945 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 15 | 6591 | 16.9 | 16.9 | 12.2625 | 15.3549 | 15 | 86 | 86 | 2.6112 | 92.7693 | 25.8268 | 222.8839 | 0 | 0 | 0 | 0.69379 | 1.9936 | 2.1255 | 1.0124 | 0 | 1.2307 | 45.5802 | 45.5802 | 45.5802 | 45.5802 | 45.5802 | 45.5802 | 45.5802 | 45.5802 | 92.7693 | 45.5802 | 45.5802 | 45.5802 | 46.274 | 47.5738 | 47.7058 | 46.5926 | 45.5802 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 16 | 6592 | 16.2 | 16.2 | 12.2625 | 15.3549 | 15 | 91 | 91 | 1.0577 | 46.6084 | 18.77 | 237.1742 | 0 | 0 | 0 | 0.035155 | 0.69762 | 0.95143 | 0.64791 | 0 | 0.39165 | 22.3517 | 22.3517 | 22.3517 | 22.3517 | 22.3517 | 22.3517 | 22.3517 | 22.3517 | 46.6084 | 22.3517 | 22.3517 | 22.3517 | 22.3868 | 23.0493 | 23.3031 | 22.9996 | 22.3517 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 17 | 6593 | 15.9 | 15.9 | 12.2625 | 15.3549 | 15 | 96 | 96 | 0.40896 | 18.9016 | 10.5247 | 250.1057 | 0 | 0 | 0 | 0 | 0.2099 | 0.3785 | 0.32538 | 0.081657 | 0.098446 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 18.9016 | 8.8944 | 8.8944 | 8.8944 | 8.8944 | 9.1043 | 9.2729 | 9.2198 | 8.9761 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 2 | 18 | 6594 | 16 | 16 | 12.2625 | 15.3549 | 15 | 96 | 96 | 0.50167 | 7.9541 | 1.593 | 262.2016 | 0 | 0 | 0 | 0 | 0.16784 | 0.44663 | 0.4638 | 0.20927 | 0.04591 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 7.9541 | 3.7052 | 3.7052 | 3.7052 | 3.7052 | 3.8731 | 4.1519 | 4.169 | 3.9145 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 19 | 6595 | 16 | 16 | 12.2625 | 15.3549 | 15 | 97 | 97 | 0 | 0 | -7.6 | 274.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 20 | 6596 | 16.1 | 16.1 | 12.2625 | 15.3549 | 15 | 96 | 96 | 0 | 0 | -16.6544 | 286.2585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 21 | 6597 | 16.2 | 16.2 | 12.2625 | 15.3549 | 15 | 96 | 96 | 0 | 0 | -25.1324 | 299.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 22 | 6598 | 16.1 | 16.1 | 12.2625 | 15.3549 | 15 | 95 | 95 | 0 | 0 | -32.4919 | 314.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 23 | 6599 | 16.2 | 16.2 | 12.2625 | 15.3549 | 15 | 95 | 95 | 0 | 0 | -38.0496 | 331.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 2 | 24 | 6600 | 16.1 | 16.1 | 15.1375 | 15.2914 | 15 | 95 | 95 | 0 | 0 | -41.0566 | 350.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 1 | 6601 | 16.3 | 16.3 | 15.1375 | 15.2914 | 15 | 93 | 93 | 0 | 0 | -40.9808 | 10.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 2 | 6602 | 16.2 | 16.2 | 15.1375 | 15.2914 | 15 | 91 | 91 | 0 | 0 | -38.1826 | 29.6484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 3 | 6603 | 16.1 | 16.1 | 15.1375 | 15.2914 | 15 | 90 | 90 | 0 | 0 | -32.4876 | 46.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 4 | 6604 | 15.7 | 15.7 | 15.1375 | 15.2914 | 15 | 90 | 90 | 0 | 0 | -25.0321 | 61.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 5 | 6605 | 15.5 | 15.5 | 15.1375 | 15.2914 | 15 | 88 | 88 | 0 | 0 | -16.497 | 74.6493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 6 | 6606 | 15.2 | 15.2 | 15.1375 | 15.2914 | 15 | 87 | 87 | 0 | 0 | -7.4185 | 86.8254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 7 | 6607 | 14.8 | 14.8 | 15.1375 | 15.2914 | 15 | 88 | 88 | 0 | 0 | 1.7689 | 98.6653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 3 | 8 | 6608 | 15.5 | 15.5 | 15.1375 | 15.2914 | 15 | 84 | 84 | 6.9661 | 38.1455 | 10.6659 | 110.7824 | 0 | 4.1254 | 6.8833 | 5.609 | 1.049 | 0 | 0 | 0 | 0.85454 | 13.1005 | 129.4426 | 207.2169 | 171.2805 | 42.6843 | 13.1005 | 13.1005 | 13.1005 | 38.1455 | 13.1005 | 133.568 | 214.1002 | 176.8895 | 43.7334 | 13.1005 | 13.1005 | 13.1005 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 9 | 6609 | 16.6 | 16.6 | 15.1375 | 15.2914 | 15 | 80 | 80 | 219.3739 | 122.1986 | 18.8456 | 123.7565 | 0 | 88.4333 | 201.5568 | 196.6111 | 76.4933 | 0 | 0 | 0 | 58.8014 | 59.1356 | 126.3288 | 212.2821 | 208.5243 | 117.2565 | 59.1356 | 59.1356 | 59.1356 | 122.1986 | 59.1356 | 214.7621 | 413.839 | 405.1354 | 193.7498 | 59.1356 | 59.1356 | 59.1356 | 181 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 10 | 6610 | 18.1 | 18.1 | 15.1375 | 15.2914 | 15 | 74 | 74 | 503.9896 | 133.6771 | 25.803 | 138.0981 | 0 | 92.9994 | 396.5575 | 467.8176 | 265.0365 | 0 | 0 | 0 | 197.3229 | 83.2083 | 104.8763 | 175.6025 | 192.2054 | 144.9593 | 83.2083 | 83.2083 | 83.2083 | 133.6771 | 83.2083 | 197.8757 | 572.1599 | 660.023 | 409.9958 | 83.2083 | 83.2083 | 83.2083 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 11 | 6611 | 19.5 | 19.5 | 15.1375 | 15.2914 | 15 | 71 | 71 | 508.8999 | 164.3413 | 30.9446 | 154.0928 | 0 | 0 | 305.986 | 457.4908 | 341.0037 | 24.7613 | 0 | 0 | 246.6587 | 100.7011 | 100.7011 | 180.9692 | 220.7128 | 190.1552 | 107.1966 | 100.7011 | 100.7011 | 164.3413 | 100.7011 | 100.7011 | 486.9552 | 678.2037 | 531.159 | 131.9579 | 100.7011 | 100.7011 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 12 | 6612 | 20.5 | 20.5 | 15.1375 | 15.2914 | 15 | 69 | 69 | 498.5838 | 186.1788 | 33.6717 | 171.5253 | 0 | 0 | 186.8328 | 404.0945 | 384.6431 | 139.8731 | 0 | 0 | 269.8212 | 111.0853 | 111.0853 | 165.3044 | 228.3541 | 222.7093 | 151.6766 | 111.0853 | 111.0853 | 186.1788 | 111.0853 | 111.0853 | 352.1372 | 632.4485 | 607.3524 | 291.5497 | 111.0853 | 111.0853 | 456 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 13 | 6613 | 21.2 | 21.2 | 15.1375 | 15.2914 | 15 | 68 | 68 | 702.7466 | 136.4989 | 33.5874 | 189.5208 | 0 | 0 | 86.19 | 469.9782 | 578.4596 | 348.0872 | 0 | 0 | 391.5011 | 102.4627 | 102.4627 | 116.2689 | 177.745 | 195.1219 | 158.2202 | 102.4627 | 102.4627 | 136.4989 | 102.4627 | 102.4627 | 202.4588 | 647.7233 | 773.5815 | 506.3074 | 102.4627 | 102.4627 | 528 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 14 | 6614 | 21.8 | 21.8 | 15.1375 | 15.2914 | 15 | 66 | 66 | 700.5644 | 130.7388 | 30.7051 | 206.8874 | 0 | 0 | 0 | 338.7254 | 575.5613 | 475.2411 | 96.5312 | 0 | 372.2612 | 98.2924 | 98.2924 | 98.2924 | 151.2884 | 188.3431 | 172.6473 | 113.3954 | 98.2924 | 130.7388 | 98.2924 | 98.2924 | 98.2924 | 490.0139 | 763.9044 | 647.8884 | 209.9265 | 98.2924 | 503 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 15 | 6615 | 21.6 | 21.6 | 15.1375 | 15.2914 | 15 | 70 | 70 | 250.5633 | 208.2977 | 25.4401 | 222.7851 | 0 | 0 | 0 | 66.9759 | 192.1467 | 204.7607 | 97.4286 | 0 | 116.7023 | 105.4595 | 105.4595 | 105.4595 | 145.242 | 219.5912 | 227.0836 | 163.3303 | 105.4595 | 208.2977 | 105.4595 | 105.4595 | 105.4595 | 212.2178 | 411.7379 | 431.8443 | 260.7589 | 105.4595 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 16 | 6616 | 22 | 22 | 15.1375 | 15.2914 | 15 | 71 | 71 | 324.3046 | 153.7069 | 18.3956 | 237.0355 | 0 | 0 | 0 | 11.3182 | 214.9306 | 292.6396 | 198.9243 | 0 | 118.2931 | 84.1947 | 84.1947 | 84.1947 | 88.4953 | 165.862 | 195.3892 | 159.7801 | 84.1947 | 153.7069 | 84.1947 | 84.1947 | 84.1947 | 99.8135 | 380.7927 | 488.0288 | 358.7044 | 84.1947 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 17 | 6617 | 21.4 | 21.4 | 15.1375 | 15.2914 | 15 | 73 | 73 | 21.3507 | 91.9767 | 10.161 | 249.9444 | 0 | 0 | 0 | 0 | 11.0237 | 19.8143 | 16.998 | 4.2245 | 5.0233 | 45.1497 | 45.1497 | 45.1497 | 45.1497 | 63.3018 | 77.7769 | 73.1394 | 52.1059 | 91.9767 | 45.1497 | 45.1497 | 45.1497 | 45.1497 | 74.3255 | 97.5912 | 90.1374 | 56.3304 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 3 | 18 | 6618 | 20.2 | 20.2 | 15.1375 | 15.2914 | 15 | 78 | 78 | 14.881 | 31.7183 | 1.2357 | 262.0289 | 0 | 0 | 0 | 0 | 5.0231 | 13.2812 | 13.7594 | 6.1774 | 1.2817 | 16.3911 | 16.3911 | 16.3911 | 16.3911 | 19.5331 | 24.6986 | 24.9977 | 20.2551 | 31.7183 | 16.3911 | 16.3911 | 16.3911 | 16.3911 | 24.5562 | 37.9799 | 38.7571 | 26.4326 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 19 | 6619 | 19.3 | 19.3 | 15.1375 | 15.2914 | 15 | 80 | 80 | 0 | 0 | -7.9563 | 273.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 20 | 6620 | 18.8 | 18.8 | 15.1375 | 15.2914 | 15 | 81 | 81 | 0 | 0 | -17.0156 | 286.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 21 | 6621 | 18.1 | 18.1 | 15.1375 | 15.2914 | 15 | 81 | 81 | 0 | 0 | -25.5037 | 299.3332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 22 | 6622 | 17.6 | 17.6 | 15.1375 | 15.2914 | 15 | 80 | 80 | 0 | 0 | -32.8764 | 314.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 23 | 6623 | 17.5 | 17.5 | 15.1375 | 15.2914 | 15 | 78 | 78 | 0 | 0 | -38.4448 | 331.4157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 3 | 24 | 6624 | 17 | 17 | 18.1875 | 16.0253 | 15 | 79 | 79 | 0 | 0 | -41.4513 | 350.5821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 1 | 6625 | 15.9 | 15.9 | 18.1875 | 16.0253 | 15 | 86 | 86 | 0 | 0 | -41.3578 | 10.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 2 | 6626 | 13.8 | 13.8 | 18.1875 | 16.0253 | 15 | 96 | 96 | 0 | 0 | -38.5275 | 29.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 3 | 6627 | 13.8 | 13.8 | 18.1875 | 16.0253 | 15 | 96 | 96 | 0 | 0 | -32.7985 | 46.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 4 | 6628 | 13.9 | 13.9 | 18.1875 | 16.0253 | 15 | 96 | 96 | 0 | 0 | -25.315 | 61.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 5 | 6629 | 13.3 | 13.3 | 18.1875 | 16.0253 | 15 | 99 | 99 | 0 | 0 | -16.7616 | 74.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 6 | 6630 | 13.2 | 13.2 | 18.1875 | 16.0253 | 15 | 99 | 99 | 0 | 0 | -7.6754 | 87.1291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 7 | 6631 | 14.9 | 14.9 | 18.1875 | 16.0253 | 15 | 90 | 90 | 0 | 0 | 1.5095 | 98.9645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 4 | 8 | 6632 | 15.9 | 15.9 | 18.1875 | 16.0253 | 15 | 87 | 87 | 6.3086 | 35.2602 | 10.3944 | 111.0753 | 0 | 3.71 | 6.2294 | 5.0997 | 0.98267 | 0 | 0 | 0 | 0.73985 | 12.1349 | 118.2543 | 190.3187 | 158.0054 | 40.2432 | 12.1349 | 12.1349 | 12.1349 | 35.2602 | 12.1349 | 121.9643 | 196.5481 | 163.1051 | 41.2258 | 12.1349 | 12.1349 | 12.1349 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 9 | 6633 | 16.8 | 16.8 | 18.1875 | 16.0253 | 15 | 83 | 83 | 12.5098 | 93.7152 | 18.5529 | 124.0378 | 0 | 4.9899 | 11.4814 | 11.2473 | 4.4246 | 0 | 0 | 0 | 3.2848 | 40.3949 | 81.3413 | 134.6096 | 132.6882 | 76.7027 | 40.3949 | 40.3949 | 40.3949 | 93.7152 | 40.3949 | 86.3312 | 146.091 | 143.9355 | 81.1273 | 40.3949 | 40.3949 | 40.3949 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 10 | 6634 | 18.5 | 18.5 | 18.1875 | 16.0253 | 15 | 76 | 76 | 165.8592 | 179.9794 | 25.482 | 138.3549 | 0 | 29.9008 | 130.2994 | 154.3704 | 88.0133 | 0 | 0 | 0 | 64.0206 | 85.729 | 113.0062 | 204.5955 | 226.5544 | 166.0197 | 85.729 | 85.729 | 85.729 | 179.9794 | 85.729 | 142.907 | 334.8949 | 380.9248 | 254.033 | 85.729 | 85.729 | 85.729 | 244 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 11 | 6635 | 18.7 | 18.7 | 18.1875 | 16.0253 | 15 | 77 | 77 | 231.6132 | 217.0307 | 30.5923 | 154.3028 | 0 | 0 | 138.9382 | 208.7237 | 156.2417 | 12.2354 | 0 | 0 | 110.9693 | 107.0373 | 107.0373 | 193.1207 | 236.3584 | 203.8416 | 114.6182 | 107.0373 | 107.0373 | 217.0307 | 107.0373 | 107.0373 | 332.0589 | 445.0821 | 360.0833 | 126.8536 | 107.0373 | 107.0373 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 12 | 6636 | 20.2 | 20.2 | 18.1875 | 16.0253 | 15 | 73 | 73 | 232.5135 | 242.4725 | 33.2926 | 171.662 | 0 | 0 | 86.7882 | 188.8986 | 180.3547 | 66.1615 | 0 | 0 | 124.5275 | 119.1294 | 119.1294 | 172.623 | 235.5607 | 230.2945 | 159.9094 | 119.1294 | 119.1294 | 242.4725 | 119.1294 | 119.1294 | 259.4112 | 424.4592 | 410.6492 | 226.0709 | 119.1294 | 119.1294 | 367 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 13 | 6637 | 21.2 | 21.2 | 18.1875 | 16.0253 | 15 | 69 | 69 | 523.5552 | 183.2651 | 33.1936 | 189.568 | 0 | 0 | 63.4616 | 351.053 | 433.0024 | 261.3048 | 0 | 0 | 288.7349 | 111.4484 | 111.4484 | 128.9192 | 208.0925 | 230.653 | 183.385 | 111.4484 | 111.4484 | 183.2651 | 111.4484 | 111.4484 | 192.3808 | 559.1455 | 663.6554 | 444.6899 | 111.4484 | 111.4484 | 472 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 14 | 6638 | 21 | 21 | 18.1875 | 16.0253 | 15 | 67 | 67 | 123.7781 | 245.9207 | 30.3105 | 206.8507 | 0 | 0 | 0 | 60.0495 | 102.1398 | 84.398 | 17.217 | 0 | 65.0793 | 115.0434 | 115.0434 | 115.0434 | 181.7404 | 228.4902 | 208.7843 | 134.1663 | 115.0434 | 245.9207 | 115.0434 | 115.0434 | 115.0434 | 241.7899 | 330.6299 | 293.1823 | 151.3833 | 115.0434 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 15 | 6639 | 20.4 | 20.4 | 18.1875 | 16.0253 | 15 | 72 | 72 | 4.8379 | 122.7736 | 25.0546 | 222.6857 | 0 | 0 | 0 | 1.301 | 3.7263 | 3.9688 | 1.8864 | 0 | 2.2264 | 61.3692 | 61.3692 | 61.3692 | 61.3692 | 61.3692 | 61.3692 | 61.3692 | 61.3692 | 122.7736 | 61.3692 | 61.3692 | 61.3692 | 62.6702 | 65.0955 | 65.338 | 63.2557 | 61.3692 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 16 | 6640 | 20.5 | 20.5 | 18.1875 | 16.0253 | 15 | 77 | 77 | 66.436 | 162.1332 | 18.0225 | 236.8963 | 0 | 0 | 0 | 2.4303 | 44.2408 | 60.1356 | 40.8038 | 0 | 23.8668 | 77.5112 | 77.5112 | 77.5112 | 79.9801 | 122.4523 | 138.5987 | 118.9609 | 77.5112 | 162.1332 | 77.5112 | 77.5112 | 77.5112 | 82.4104 | 166.6931 | 198.7343 | 159.7646 | 77.5112 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 17 | 6641 | 19.7 | 19.7 | 18.1875 | 16.0253 | 15 | 77 | 77 | 8.7217 | 75.9955 | 9.7987 | 249.7825 | 0 | 0 | 0 | 0 | 4.5297 | 8.1157 | 6.9476 | 1.7097 | 2.0045 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 75.9955 | 37.7523 | 37.7523 | 37.7523 | 37.7523 | 42.282 | 45.8679 | 44.6999 | 39.462 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 4 | 18 | 6642 | 18.8 | 18.8 | 18.1875 | 16.0253 | 15 | 82 | 82 | 1.9709 | 13.8408 | 0.87994 | 261.8553 | 0 | 0 | 0 | 0 | 0.67118 | 1.7633 | 1.8225 | 0.8141 | 0.15916 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 13.8408 | 6.5187 | 6.5187 | 6.5187 | 6.5187 | 7.1899 | 8.282 | 8.3412 | 7.3328 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 19 | 6643 | 18.4 | 18.4 | 18.1875 | 16.0253 | 15 | 82 | 82 | 0 | 0 | -8.311 | 273.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 20 | 6644 | 18.1 | 18.1 | 18.1875 | 16.0253 | 15 | 81 | 81 | 0 | 0 | -17.3752 | 285.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 21 | 6645 | 17.7 | 17.7 | 18.1875 | 16.0253 | 15 | 82 | 82 | 0 | 0 | -25.8734 | 299.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 22 | 6646 | 16.4 | 16.4 | 18.1875 | 16.0253 | 15 | 89 | 89 | 0 | 0 | -33.2594 | 314.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 23 | 6647 | 16.7 | 16.7 | 18.1875 | 16.0253 | 15 | 85 | 85 | 0 | 0 | -38.8387 | 331.3664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 4 | 24 | 6648 | 15.2 | 15.2 | 17.2083 | 16.3251 | 15 | 91 | 91 | 0 | 0 | -41.8451 | 350.6356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 1 | 6649 | 14.8 | 14.8 | 17.2083 | 16.3251 | 15 | 90 | 90 | 0 | 0 | -41.734 | 10.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 2 | 6650 | 14.3 | 14.3 | 17.2083 | 16.3251 | 15 | 92 | 92 | 0 | 0 | -38.8716 | 30.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 3 | 6651 | 14.9 | 14.9 | 17.2083 | 16.3251 | 15 | 90 | 90 | 0 | 0 | -33.1087 | 47.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 4 | 6652 | 14.2 | 14.2 | 17.2083 | 16.3251 | 15 | 94 | 94 | 0 | 0 | -25.5975 | 62.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 5 | 6653 | 15.1 | 15.1 | 17.2083 | 16.3251 | 15 | 93 | 93 | 0 | 0 | -17.0262 | 75.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 6 | 6654 | 15.1 | 15.1 | 17.2083 | 16.3251 | 15 | 94 | 94 | 0 | 0 | -7.9326 | 87.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 7 | 6655 | 15.2 | 15.2 | 17.2083 | 16.3251 | 15 | 96 | 96 | 0 | 0 | 1.2497 | 99.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 5 | 8 | 6656 | 15.8 | 15.8 | 17.2083 | 16.3251 | 15 | 93 | 93 | 5.7008 | 32.3621 | 10.1223 | 111.3658 | 0 | 3.329 | 5.6252 | 4.6262 | 0.91729 | 0 | 0 | 0 | 0.63785 | 11.1918 | 106.6772 | 172.5394 | 143.8863 | 37.5026 | 11.1918 | 11.1918 | 11.1918 | 32.3621 | 11.1918 | 110.0062 | 178.1645 | 148.5125 | 38.4199 | 11.1918 | 11.1918 | 11.1918 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 9 | 6657 | 16 | 16 | 17.2083 | 16.3251 | 15 | 93 | 93 | 2.19 | 46.4369 | 18.2597 | 124.3162 | 0 | 0.86428 | 2.0077 | 1.975 | 0.78543 | 0 | 0 | 0 | 0.56306 | 22.9687 | 22.9687 | 22.9687 | 22.9687 | 22.9687 | 22.9687 | 22.9687 | 22.9687 | 46.4369 | 22.9687 | 23.833 | 24.9764 | 24.9437 | 23.7541 | 22.9687 | 22.9687 | 22.9687 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 10 | 6658 | 16.6 | 16.6 | 17.2083 | 16.3251 | 15 | 91 | 91 | 6.3322 | 114.5908 | 25.1605 | 138.6082 | 0 | 1.1148 | 4.9667 | 5.9091 | 3.3901 | 0 | 0 | 0 | 2.4092 | 53.8901 | 59.2546 | 77.79 | 82.3252 | 70.2034 | 53.8901 | 53.8901 | 53.8901 | 114.5908 | 53.8901 | 60.3694 | 82.7567 | 88.2343 | 73.5935 | 53.8901 | 53.8901 | 53.8901 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 11 | 6659 | 17.3 | 17.3 | 17.2083 | 16.3251 | 15 | 86 | 86 | 10.1697 | 162.1843 | 30.2401 | 154.5091 | 0 | 0 | 6.0863 | 9.1866 | 6.9055 | 0.57929 | 0 | 0 | 4.8157 | 76.0043 | 76.0043 | 98.2306 | 109.5525 | 101.2224 | 78.1198 | 76.0043 | 76.0043 | 162.1843 | 76.0043 | 76.0043 | 104.3169 | 118.7391 | 108.1279 | 78.6991 | 76.0043 | 76.0043 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 12 | 6660 | 17.7 | 17.7 | 17.2083 | 16.3251 | 15 | 83 | 83 | 54.9249 | 234.8923 | 32.9141 | 171.7954 | 0 | 0 | 20.4213 | 44.7266 | 42.8317 | 15.8465 | 0 | 0 | 29.1077 | 107.2186 | 107.2186 | 146.0896 | 192.3534 | 188.7464 | 137.3816 | 107.2186 | 107.2186 | 234.8923 | 107.2186 | 107.2186 | 166.5109 | 237.08 | 231.5781 | 153.2281 | 107.2186 | 107.2186 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 13 | 6661 | 17.6 | 17.6 | 17.2083 | 16.3251 | 15 | 83 | 83 | 2.5654 | 106.5996 | 32.8007 | 189.6128 | 0 | 0 | 0.30734 | 1.7246 | 2.1316 | 1.2899 | 0 | 0 | 1.4004 | 52.6659 | 52.6659 | 52.6659 | 52.6659 | 52.6659 | 52.6659 | 52.6659 | 52.6659 | 106.5996 | 52.6659 | 52.6659 | 52.9732 | 54.3904 | 54.7974 | 53.9558 | 52.6659 | 52.6659 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 14 | 6662 | 17.6 | 17.6 | 17.2083 | 16.3251 | 15 | 83 | 83 | 4.2845 | 130.7714 | 29.9172 | 206.8126 | 0 | 0 | 0 | 2.0856 | 3.5508 | 2.936 | 0.60139 | 0 | 2.2286 | 65.4279 | 65.4279 | 65.4279 | 65.4279 | 65.4279 | 65.4279 | 65.4279 | 65.4279 | 130.7714 | 65.4279 | 65.4279 | 65.4279 | 67.5134 | 68.9787 | 68.3639 | 66.0293 | 65.4279 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 15 | 6663 | 19.4 | 19.4 | 17.2083 | 16.3251 | 15 | 73 | 73 | 604.278 | 133.2836 | 24.6705 | 222.5855 | 0 | 0 | 0 | 163.4782 | 467.4454 | 497.5894 | 236.2523 | 0 | 274.7164 | 89.7687 | 89.7687 | 89.7687 | 120.0984 | 176.4926 | 182.0851 | 133.5999 | 89.7687 | 133.2836 | 89.7687 | 89.7687 | 89.7687 | 283.5766 | 643.9379 | 679.6745 | 369.8522 | 89.7687 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 16 | 6664 | 18.9 | 18.9 | 17.2083 | 16.3251 | 15 | 74 | 74 | 115.1369 | 165.2732 | 17.6509 | 236.7566 | 0 | 0 | 0 | 4.4077 | 77.0339 | 104.5347 | 70.8004 | 0 | 40.7268 | 80.7006 | 80.7006 | 80.7006 | 84.5734 | 148.3851 | 172.5482 | 142.9082 | 80.7006 | 165.2732 | 80.7006 | 80.7006 | 80.7006 | 88.9811 | 225.419 | 277.0828 | 213.7086 | 80.7006 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 17 | 6665 | 18.5 | 18.5 | 17.2083 | 16.3251 | 15 | 76 | 76 | 60.4917 | 100.4272 | 9.438 | 249.62 | 0 | 0 | 0 | 0 | 31.6002 | 56.4346 | 48.2104 | 11.7452 | 13.5728 | 49.4919 | 49.4919 | 49.4919 | 49.4919 | 72.5061 | 90.5928 | 84.6032 | 58.0459 | 100.4272 | 49.4919 | 49.4919 | 49.4919 | 49.4919 | 104.1062 | 147.0274 | 132.8136 | 69.7911 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 5 | 18 | 6666 | 17.8 | 17.8 | 17.2083 | 16.3251 | 15 | 81 | 81 | 7.9921 | 24.3975 | 0.52588 | 261.6809 | 0 | 0 | 0 | 0 | 2.7455 | 7.1672 | 7.3904 | 3.2844 | 0.60247 | 12.7177 | 12.7177 | 12.7177 | 12.7177 | 14.6481 | 17.757 | 17.9139 | 15.027 | 24.3975 | 12.7177 | 12.7177 | 12.7177 | 12.7177 | 17.3936 | 24.9242 | 25.3043 | 18.3114 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 19 | 6667 | 17.5 | 17.5 | 17.2083 | 16.3251 | 15 | 82 | 82 | 0 | 0 | -8.6639 | 273.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 20 | 6668 | 17.7 | 17.7 | 17.2083 | 16.3251 | 15 | 77 | 77 | 0 | 0 | -17.7329 | 285.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 21 | 6669 | 17.3 | 17.3 | 17.2083 | 16.3251 | 15 | 81 | 81 | 0 | 0 | -26.2413 | 299.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 22 | 6670 | 17 | 17 | 17.2083 | 16.3251 | 15 | 84 | 84 | 0 | 0 | -33.6408 | 314.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 23 | 6671 | 16.8 | 16.8 | 17.2083 | 16.3251 | 15 | 85 | 85 | 0 | 0 | -39.2313 | 331.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 5 | 24 | 6672 | 16.5 | 16.5 | 16.65 | 16.3855 | 15 | 87 | 87 | 0 | 0 | -42.2379 | 350.6877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 1 | 6673 | 16.2 | 16.2 | 16.65 | 16.3855 | 15 | 88 | 88 | 0 | 0 | -42.1093 | 10.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 2 | 6674 | 16.1 | 16.1 | 16.65 | 16.3855 | 15 | 89 | 89 | 0 | 0 | -39.2149 | 30.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 3 | 6675 | 16.1 | 16.1 | 16.65 | 16.3855 | 15 | 89 | 89 | 0 | 0 | -33.4182 | 47.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 4 | 6676 | 16.1 | 16.1 | 16.65 | 16.3855 | 15 | 89 | 89 | 0 | 0 | -25.8795 | 62.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 5 | 6677 | 15.9 | 15.9 | 16.65 | 16.3855 | 15 | 90 | 90 | 0 | 0 | -17.2906 | 75.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 6 | 6678 | 15.8 | 15.8 | 16.65 | 16.3855 | 15 | 90 | 90 | 0 | 0 | -8.1898 | 87.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 7 | 6679 | 16.2 | 16.2 | 16.65 | 16.3855 | 15 | 87 | 87 | 0 | 0 | 0.98951 | 99.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 6 | 8 | 6680 | 16.5 | 16.5 | 16.65 | 16.3855 | 15 | 87 | 87 | 1.1317 | 13.8795 | 9.8497 | 111.6538 | 0 | 0.65616 | 1.1158 | 0.92184 | 0.18786 | 0 | 0 | 0 | 0.12053 | 6.3846 | 15.0945 | 21.1959 | 18.6211 | 8.8782 | 6.3846 | 6.3846 | 6.3846 | 13.8795 | 6.3846 | 15.7507 | 22.3117 | 19.5429 | 9.0661 | 6.3846 | 6.3846 | 6.3846 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 9 | 6681 | 16.6 | 16.6 | 16.65 | 16.3855 | 15 | 89 | 89 | 7.2141 | 79.1846 | 17.9659 | 124.5915 | 0 | 2.8167 | 6.6062 | 6.5258 | 2.6227 | 0 | 0 | 0 | 1.8154 | 35.2127 | 62.7938 | 99.9 | 99.1133 | 60.8945 | 35.2127 | 35.2127 | 35.2127 | 79.1846 | 35.2127 | 65.6105 | 106.5062 | 105.6391 | 63.5172 | 35.2127 | 35.2127 | 35.2127 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 10 | 6682 | 17.5 | 17.5 | 16.65 | 16.3855 | 15 | 85 | 85 | 91.8723 | 173.555 | 24.8388 | 138.8579 | 0 | 15.7888 | 71.9434 | 85.9545 | 49.6146 | 0 | 0 | 0 | 34.445 | 79.6275 | 100.9793 | 176.919 | 195.8667 | 146.723 | 79.6275 | 79.6275 | 79.6275 | 173.555 | 79.6275 | 116.7681 | 248.8625 | 281.8212 | 196.3377 | 79.6275 | 79.6275 | 79.6275 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 11 | 6683 | 17.7 | 17.7 | 16.65 | 16.3855 | 15 | 82 | 82 | 33.3269 | 195.4051 | 29.8879 | 154.7116 | 0 | 0 | 19.8984 | 30.1754 | 22.7761 | 2.0349 | 0 | 0 | 15.5949 | 89.3601 | 89.3601 | 146.6891 | 176.2982 | 154.9802 | 95.2228 | 89.3601 | 89.3601 | 195.4051 | 89.3601 | 89.3601 | 166.5874 | 206.4737 | 177.7563 | 97.2577 | 89.3601 | 89.3601 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 12 | 6684 | 18.1 | 18.1 | 16.65 | 16.3855 | 15 | 81 | 81 | 5.1482 | 144.3006 | 32.5362 | 171.9254 | 0 | 0 | 1.9067 | 4.202 | 4.0358 | 1.5055 | 0 | 0 | 2.6994 | 71.1341 | 71.1341 | 73.8866 | 77.1999 | 76.96 | 73.3074 | 71.1341 | 71.1341 | 144.3006 | 71.1341 | 71.1341 | 75.7933 | 81.4019 | 80.9958 | 74.8129 | 71.1341 | 71.1341 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 13 | 6685 | 19.1 | 19.1 | 16.65 | 16.3855 | 15 | 75 | 75 | 25.4809 | 217.2345 | 32.4089 | 189.6552 | 0 | 0 | 3.0174 | 17.1729 | 21.2687 | 12.9056 | 0 | 0 | 13.7655 | 101.6804 | 101.6804 | 107.2316 | 133.2743 | 140.8097 | 125.4236 | 101.6804 | 101.6804 | 217.2345 | 101.6804 | 101.6804 | 110.249 | 150.4472 | 162.0784 | 138.3293 | 101.6804 | 101.6804 | 231 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 14 | 6686 | 18.5 | 18.5 | 16.65 | 16.3855 | 15 | 79 | 79 | 3.2151 | 112.3457 | 29.5253 | 206.7731 | 0 | 0 | 0 | 1.5702 | 2.6759 | 2.2141 | 0.45525 | 0 | 1.6543 | 55.6993 | 55.6993 | 55.6993 | 55.6993 | 55.6993 | 55.6993 | 55.6993 | 55.6993 | 112.3457 | 55.6993 | 55.6993 | 55.6993 | 57.2696 | 58.3752 | 57.9134 | 56.1546 | 55.6993 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 15 | 6687 | 18.1 | 18.1 | 16.65 | 16.3855 | 15 | 71 | 71 | 1.3305 | 63.4025 | 24.288 | 222.4846 | 0 | 0 | 0 | 0.36212 | 1.0336 | 1.0997 | 0.52151 | 0 | 0.59746 | 30.6681 | 30.6681 | 30.6681 | 30.6681 | 30.6681 | 30.6681 | 30.6681 | 30.6681 | 63.4025 | 30.6681 | 30.6681 | 30.6681 | 31.0302 | 31.7017 | 31.7677 | 31.1896 | 30.6681 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 16 | 6688 | 17.3 | 17.3 | 16.65 | 16.3855 | 15 | 80 | 80 | 0.42353 | 27.8525 | 17.281 | 236.6164 | 0 | 0 | 0 | 0.016942 | 0.28469 | 0.38567 | 0.26073 | 0 | 0.14747 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 27.8525 | 13.1903 | 13.1903 | 13.1903 | 13.2073 | 13.475 | 13.576 | 13.4511 | 13.1903 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 17 | 6689 | 15.4 | 15.4 | 16.65 | 16.3855 | 15 | 91 | 91 | 0.087459 | 7.9809 | 9.079 | 249.4569 | 0 | 0 | 0 | 0 | 0.045952 | 0.081801 | 0.069733 | 0.016816 | 0.019147 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 3.716 | 7.9809 | 3.716 | 3.716 | 3.716 | 3.716 | 3.762 | 3.7978 | 3.7858 | 3.7329 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 18 | 6690 | 15.3 | 15.3 | 16.65 | 16.3855 | 15 | 93 | 93 | 0.12022 | 2.9916 | 0.17367 | 261.5057 | 0 | 0 | 0 | 0 | 0.041659 | 0.10807 | 0.11117 | 0.04915 | 0.0084184 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 2.9916 | 1.3817 | 1.3817 | 1.3817 | 1.3817 | 1.4234 | 1.4898 | 1.4929 | 1.4309 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 19 | 6691 | 15.3 | 15.3 | 16.65 | 16.3855 | 15 | 93 | 93 | 0 | 0 | -9.0149 | 273.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 20 | 6692 | 14.9 | 14.9 | 16.65 | 16.3855 | 15 | 93 | 93 | 0 | 0 | -18.0886 | 285.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 21 | 6693 | 14.5 | 14.5 | 16.65 | 16.3855 | 15 | 95 | 95 | 0 | 0 | -26.6073 | 298.8561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 22 | 6694 | 14.2 | 14.2 | 16.65 | 16.3855 | 15 | 97 | 97 | 0 | 0 | -34.0204 | 313.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 23 | 6695 | 13.8 | 13.8 | 16.65 | 16.3855 | 15 | 99 | 99 | 0 | 0 | -39.6225 | 331.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 6 | 24 | 6696 | 12.6 | 12.6 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -42.6295 | 350.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 1 | 6697 | 12.3 | 12.3 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -42.4837 | 11.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 2 | 6698 | 12.5 | 12.5 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -39.5573 | 30.6381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 3 | 6699 | 11.1 | 11.1 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -33.727 | 47.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 4 | 6700 | 11.4 | 11.4 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -26.1611 | 62.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 5 | 6701 | 10.8 | 10.8 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -17.5549 | 75.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 6 | 6702 | 10.4 | 10.4 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | -8.4473 | 88.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 7 | 6703 | 10 | 10 | 16.1583 | 16.2886 | 15 | 99 | 99 | 0 | 0 | 0.72896 | 99.8497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 7 | 8 | 6704 | 9.7 | 9.7 | 16.1583 | 16.2886 | 15 | 99 | 99 | 2.3103 | 18.7663 | 9.5766 | 111.9391 | 0 | 1.33 | 2.2761 | 1.8889 | 0.39518 | 0 | 0 | 0 | 0.23366 | 7.7613 | 36.8263 | 57.5015 | 49.0395 | 16.3973 | 7.7613 | 7.7613 | 7.7613 | 18.7663 | 7.7613 | 38.1563 | 59.7775 | 50.9284 | 16.7925 | 7.7613 | 7.7613 | 7.7613 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 9 | 6705 | 10.2 | 10.2 | 16.1583 | 16.2886 | 15 | 99 | 99 | 6.1755 | 73.4797 | 17.6717 | 124.8635 | 0 | 2.3853 | 5.6485 | 5.6028 | 2.2751 | 0 | 0 | 0 | 1.5203 | 33.0708 | 56.2003 | 87.8424 | 87.4 | 55.1323 | 33.0708 | 33.0708 | 33.0708 | 73.4797 | 33.0708 | 58.5856 | 93.4908 | 93.0028 | 57.4074 | 33.0708 | 33.0708 | 33.0708 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 10 | 6706 | 12 | 12 | 16.1583 | 16.2886 | 15 | 100 | 100 | 8.5837 | 121.8293 | 24.5168 | 139.104 | 0 | 1.4394 | 6.7107 | 8.051 | 4.6751 | 0 | 0 | 0 | 3.1707 | 56.2195 | 63.6679 | 90.9457 | 97.8813 | 80.412 | 56.2195 | 56.2195 | 56.2195 | 121.8293 | 56.2195 | 65.1073 | 97.6564 | 105.9323 | 85.0871 | 56.2195 | 56.2195 | 56.2195 | 125 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 11 | 6707 | 13.9 | 13.9 | 16.1583 | 16.2886 | 15 | 98 | 98 | 24.9744 | 185.4533 | 29.5359 | 154.9103 | 0 | 0 | 14.8763 | 22.6644 | 17.1761 | 1.6262 | 0 | 0 | 11.5467 | 84.3193 | 84.3193 | 123.8031 | 144.4739 | 129.907 | 88.6354 | 84.3193 | 84.3193 | 185.4533 | 84.3193 | 84.3193 | 138.6793 | 167.1384 | 147.0831 | 90.2616 | 84.3193 | 84.3193 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 12 | 6708 | 15.6 | 15.6 | 16.1583 | 16.2886 | 15 | 90 | 90 | 81.983 | 238.4759 | 32.1591 | 172.0519 | 0 | 0 | 30.2462 | 67.0655 | 64.5988 | 24.291 | 0 | 0 | 42.5241 | 109.6092 | 109.6092 | 150.3467 | 199.9374 | 196.6151 | 142.3259 | 109.6092 | 109.6092 | 238.4759 | 109.6092 | 109.6092 | 180.5928 | 267.0029 | 261.2139 | 166.6169 | 109.6092 | 109.6092 | 281 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 13 | 6709 | 16.1 | 16.1 | 16.1583 | 16.2886 | 15 | 88 | 88 | 33.917 | 223.8686 | 32.0184 | 189.6952 | 0 | 0 | 3.9703 | 22.9157 | 28.4374 | 17.3008 | 0 | 0 | 18.1314 | 102.6346 | 102.6346 | 113.1103 | 163.0975 | 177.6663 | 148.2826 | 102.6346 | 102.6346 | 223.8686 | 102.6346 | 102.6346 | 117.0807 | 186.0132 | 206.1037 | 165.5834 | 102.6346 | 102.6346 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 14 | 6710 | 16.7 | 16.7 | 16.1583 | 16.2886 | 15 | 84 | 84 | 20.2565 | 197.6912 | 29.135 | 206.7321 | 0 | 0 | 0 | 9.9259 | 16.9298 | 14.0164 | 2.8924 | 0 | 10.3088 | 93.9085 | 93.9085 | 93.9085 | 110.604 | 122.3845 | 117.4842 | 98.7735 | 93.9085 | 197.6912 | 93.9085 | 93.9085 | 93.9085 | 120.5299 | 139.3142 | 131.5005 | 101.6659 | 93.9085 | 208 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 15 | 6711 | 16.5 | 16.5 | 16.1583 | 16.2886 | 15 | 86 | 86 | 27.0783 | 179.9921 | 23.9072 | 222.3829 | 0 | 0 | 0 | 7.414 | 21.1243 | 22.4602 | 10.6392 | 0 | 12.0079 | 84.3546 | 84.3546 | 84.3546 | 102.982 | 137.4281 | 140.7845 | 111.0851 | 84.3546 | 179.9921 | 84.3546 | 84.3546 | 84.3546 | 110.396 | 158.5524 | 163.2447 | 121.7243 | 84.3546 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 16 | 6712 | 16.6 | 16.6 | 16.1583 | 16.2886 | 15 | 87 | 87 | 4.4156 | 87.4869 | 16.9128 | 236.4756 | 0 | 0 | 0 | 0.18432 | 2.9818 | 4.0325 | 2.7211 | 0 | 1.5131 | 43.2163 | 43.2163 | 43.2163 | 43.2163 | 43.2163 | 43.2163 | 43.2163 | 43.2163 | 87.4869 | 43.2163 | 43.2163 | 43.2163 | 43.4006 | 46.198 | 47.2488 | 45.9374 | 43.2163 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 17 | 6713 | 16.4 | 16.4 | 16.1583 | 16.2886 | 15 | 89 | 89 | 11.8255 | 75.4754 | 8.7219 | 249.2932 | 0 | 0 | 0 | 0 | 6.2487 | 11.0879 | 9.432 | 2.2509 | 2.5246 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 75.4754 | 37.6486 | 37.6486 | 37.6486 | 37.6486 | 43.8972 | 48.7364 | 47.0805 | 39.8995 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 18 | 6714 | 16.2 | 16.2 | 16.1583 | 16.2886 | 15 | 91 | 91 | 5.6497 | 18.6346 | -0.17656 | 261.3296 | 0 | 0 | 0 | 0 | 1.9746 | 5.0899 | 5.2236 | 2.2974 | 0.36539 | 9.8004 | 9.8004 | 9.8004 | 9.8004 | 10.9056 | 12.6494 | 12.7242 | 11.0864 | 18.6346 | 9.8004 | 9.8004 | 9.8004 | 9.8004 | 12.8802 | 17.7392 | 17.9478 | 13.3838 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 19 | 6715 | 16 | 16 | 16.1583 | 16.2886 | 15 | 92 | 92 | 0 | 0 | -9.3638 | 273.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 20 | 6716 | 15.9 | 15.9 | 16.1583 | 16.2886 | 15 | 91 | 91 | 0 | 0 | -18.4421 | 285.3837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 21 | 6717 | 16.1 | 16.1 | 16.1583 | 16.2886 | 15 | 89 | 89 | 0 | 0 | -26.9712 | 298.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 22 | 6718 | 15.9 | 15.9 | 16.1583 | 16.2886 | 15 | 90 | 90 | 0 | 0 | -34.3982 | 313.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 23 | 6719 | 15.8 | 15.8 | 16.1583 | 16.2886 | 15 | 91 | 91 | 0 | 0 | -40.0121 | 331.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 7 | 24 | 6720 | 15.6 | 15.6 | 13.9042 | 15.7089 | 15 | 93 | 93 | 0 | 0 | -43.0199 | 350.7866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 1 | 6721 | 15.2 | 15.2 | 13.9042 | 15.7089 | 15 | 94 | 94 | 0 | 0 | -42.8571 | 11.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 2 | 6722 | 14.6 | 14.6 | 13.9042 | 15.7089 | 15 | 97 | 97 | 0 | 0 | -39.8986 | 30.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 3 | 6723 | 14.2 | 14.2 | 13.9042 | 15.7089 | 15 | 97 | 97 | 0 | 0 | -34.035 | 48.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 4 | 6724 | 14 | 14 | 13.9042 | 15.7089 | 15 | 98 | 98 | 0 | 0 | -26.4422 | 63.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 5 | 6725 | 13.4 | 13.4 | 13.9042 | 15.7089 | 15 | 99 | 99 | 0 | 0 | -17.819 | 76.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 6 | 6726 | 13.4 | 13.4 | 13.9042 | 15.7089 | 15 | 99 | 99 | 0 | 0 | -8.7048 | 88.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 7 | 6727 | 13.4 | 13.4 | 13.9042 | 15.7089 | 15 | 97 | 97 | 0 | 0 | 0.46808 | 100.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 8 | 8 | 6728 | 13.9 | 13.9 | 13.9042 | 15.7089 | 15 | 96 | 96 | 9.192 | 32.1196 | 9.3031 | 112.2216 | 0 | 5.2537 | 9.0482 | 7.5423 | 1.6183 | 0 | 0 | 0 | 0.88039 | 9.2739 | 138.4426 | 231.7336 | 194.7107 | 49.0614 | 9.2739 | 9.2739 | 9.2739 | 32.1196 | 9.2739 | 143.6963 | 240.7818 | 202.253 | 50.6797 | 9.2739 | 9.2739 | 9.2739 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 9 | 6729 | 14.5 | 14.5 | 13.9042 | 15.7089 | 15 | 91 | 91 | 74.8582 | 109.9796 | 17.377 | 125.1323 | 0 | 28.6014 | 68.3868 | 68.1121 | 27.9383 | 0 | 0 | 0 | 18.0204 | 48.9563 | 109.4532 | 193.6061 | 193.025 | 108.0505 | 48.9563 | 48.9563 | 48.9563 | 109.9796 | 48.9563 | 138.0547 | 261.9929 | 261.1372 | 135.9888 | 48.9563 | 48.9563 | 48.9563 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 10 | 6730 | 15 | 15 | 13.9042 | 15.7089 | 15 | 87 | 87 | 17.2317 | 137.7303 | 24.1947 | 139.3463 | 0 | 2.8183 | 13.4493 | 16.202 | 9.4637 | 0 | 0 | 0 | 6.2697 | 61.6731 | 73.5298 | 118.2557 | 129.8363 | 101.4877 | 61.6731 | 61.6731 | 61.6731 | 137.7303 | 61.6731 | 76.3481 | 131.7051 | 146.0382 | 110.9514 | 61.6731 | 61.6731 | 61.6731 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 11 | 6731 | 15.3 | 15.3 | 13.9042 | 15.7089 | 15 | 87 | 87 | 12.5014 | 163.2901 | 29.1842 | 155.105 | 0 | 0 | 7.4291 | 11.3705 | 8.6512 | 0.86419 | 0 | 0 | 5.7099 | 75.8713 | 75.8713 | 101.9086 | 115.7225 | 106.192 | 78.9001 | 75.8713 | 75.8713 | 163.2901 | 75.8713 | 75.8713 | 109.3377 | 127.093 | 114.8433 | 79.7643 | 75.8713 | 75.8713 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 12 | 6732 | 15.5 | 15.5 | 13.9042 | 15.7089 | 15 | 86 | 86 | 6.3386 | 154.748 | 31.7828 | 172.175 | 0 | 0 | 2.3296 | 5.1967 | 5.0197 | 1.9023 | 0 | 0 | 3.252 | 75.1761 | 75.1761 | 80.6737 | 87.4402 | 87.0225 | 79.6653 | 75.1761 | 75.1761 | 154.748 | 75.1761 | 75.1761 | 83.0033 | 92.6369 | 92.0422 | 81.5676 | 75.1761 | 75.1761 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 13 | 6733 | 16.2 | 16.2 | 13.9042 | 15.7089 | 15 | 83 | 83 | 6.1578 | 157.743 | 31.6292 | 189.7326 | 0 | 0 | 0.71266 | 4.1708 | 5.1857 | 3.1629 | 0 | 0 | 3.257 | 77.4742 | 77.4742 | 78.6342 | 84.2626 | 85.9145 | 82.6222 | 77.4742 | 77.4742 | 157.743 | 77.4742 | 77.4742 | 79.3468 | 88.4333 | 91.1002 | 85.7851 | 77.4742 | 77.4742 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 14 | 6734 | 16.1 | 16.1 | 13.9042 | 15.7089 | 15 | 81 | 81 | 4.232 | 125.8701 | 28.7462 | 206.6896 | 0 | 0 | 0 | 2.0806 | 3.5515 | 2.942 | 0.60915 | 0 | 2.1299 | 62.8951 | 62.8951 | 62.8951 | 62.8951 | 62.8951 | 62.8951 | 62.8951 | 62.8951 | 125.8701 | 62.8951 | 62.8951 | 62.8951 | 64.9757 | 66.4466 | 65.8371 | 63.5043 | 62.8951 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 15 | 6735 | 16.1 | 16.1 | 13.9042 | 15.7089 | 15 | 83 | 83 | 4.4348 | 112.0582 | 23.5281 | 222.2803 | 0 | 0 | 0 | 1.2216 | 3.474 | 3.6914 | 1.7464 | 0 | 1.9418 | 55.7866 | 55.7866 | 55.7866 | 55.7866 | 55.7866 | 55.7866 | 55.7866 | 55.7866 | 112.0582 | 55.7866 | 55.7866 | 55.7866 | 57.0082 | 59.2606 | 59.478 | 57.5331 | 55.7866 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 16 | 6736 | 15.7 | 15.7 | 13.9042 | 15.7089 | 15 | 84 | 84 | 2.5836 | 66.1289 | 16.5465 | 236.3341 | 0 | 0 | 0 | 0.1124 | 1.7526 | 2.3661 | 1.5936 | 0 | 0.87108 | 32.1961 | 32.1961 | 32.1961 | 32.1961 | 32.1961 | 32.1961 | 32.1961 | 32.1961 | 66.1289 | 32.1961 | 32.1961 | 32.1961 | 32.3085 | 33.9487 | 34.5623 | 33.7898 | 32.1961 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 17 | 6737 | 15.3 | 15.3 | 13.9042 | 15.7089 | 15 | 85 | 85 | 0.94466 | 24.8035 | 8.3669 | 249.1288 | 0 | 0 | 0 | 0 | 0.50199 | 0.88788 | 0.75367 | 0.17797 | 0.19654 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 24.8035 | 11.7504 | 11.7504 | 11.7504 | 11.7504 | 12.2524 | 12.6383 | 12.5041 | 11.9284 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 8 | 18 | 6738 | 15.1 | 15.1 | 13.9042 | 15.7089 | 15 | 84 | 84 | 1.1892 | 7.9294 | -0.52467 | 261.1526 | 0 | 0 | 0 | 0 | 0.41915 | 1.0737 | 1.0993 | 0.48094 | 0.070563 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 7.9294 | 3.7009 | 3.7009 | 3.7009 | 3.7009 | 4.1201 | 4.7746 | 4.8002 | 4.1819 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 19 | 6739 | 15.1 | 15.1 | 13.9042 | 15.7089 | 15 | 85 | 85 | 0 | 0 | -9.7105 | 272.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 20 | 6740 | 13.9 | 13.9 | 13.9042 | 15.7089 | 15 | 88 | 88 | 0 | 0 | -18.7934 | 285.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 21 | 6741 | 13 | 13 | 13.9042 | 15.7089 | 15 | 92 | 92 | 0 | 0 | -27.3328 | 298.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 22 | 6742 | 12.8 | 12.8 | 13.9042 | 15.7089 | 15 | 94 | 94 | 0 | 0 | -34.7738 | 313.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 23 | 6743 | 12.3 | 12.3 | 13.9042 | 15.7089 | 15 | 97 | 97 | 0 | 0 | -40.4 | 331.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 8 | 24 | 6744 | 11.8 | 11.8 | 14.4083 | 15.5049 | 15 | 97 | 97 | 0 | 0 | -43.4089 | 350.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 1 | 6745 | 11.1 | 11.1 | 14.4083 | 15.5049 | 15 | 99 | 99 | 0 | 0 | -43.2293 | 11.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 2 | 6746 | 10.9 | 10.9 | 14.4083 | 15.5049 | 15 | 99 | 99 | 0 | 0 | -40.239 | 31.1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 3 | 6747 | 10.5 | 10.5 | 14.4083 | 15.5049 | 15 | 98 | 98 | 0 | 0 | -34.3422 | 48.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 4 | 6748 | 10.3 | 10.3 | 14.4083 | 15.5049 | 15 | 98 | 98 | 0 | 0 | -26.7227 | 63.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 5 | 6749 | 9.7 | 9.7 | 14.4083 | 15.5049 | 15 | 98 | 98 | 0 | 0 | -18.0829 | 76.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 6 | 6750 | 9.6 | 9.6 | 14.4083 | 15.5049 | 15 | 97 | 97 | 0 | 0 | -8.9624 | 88.6224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 7 | 6751 | 9.6 | 9.6 | 14.4083 | 15.5049 | 15 | 96 | 96 | 0 | 0 | 0.20691 | 100.4285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 9 | 8 | 6752 | 10 | 10 | 14.4083 | 15.5049 | 15 | 95 | 95 | 26.4229 | 36.6105 | 9.0291 | 112.5013 | 0 | 14.9932 | 25.9863 | 21.757 | 4.7827 | 0 | 0 | 0 | 2.3895 | 12.2632 | 117.1937 | 194.1295 | 164.5304 | 45.7353 | 12.2632 | 12.2632 | 12.2632 | 36.6105 | 12.2632 | 132.1869 | 220.1158 | 186.2874 | 50.518 | 12.2632 | 12.2632 | 12.2632 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 9 | 6753 | 12.8 | 12.8 | 14.4083 | 15.5049 | 15 | 85 | 85 | 212.1833 | 108.0779 | 17.0821 | 125.3977 | 0 | 80.1886 | 193.6009 | 193.6045 | 80.1971 | 0 | 0 | 0 | 49.9221 | 51.9268 | 116.9887 | 209.0071 | 209.0099 | 116.9956 | 51.9268 | 51.9268 | 51.9268 | 108.0779 | 51.9268 | 197.1773 | 402.608 | 402.6144 | 197.1928 | 51.9268 | 51.9268 | 51.9268 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 10 | 6754 | 14.9 | 14.9 | 14.4083 | 15.5049 | 15 | 74 | 74 | 500.6101 | 123.6274 | 23.8724 | 139.5847 | 0 | 79.8222 | 390.0708 | 471.8212 | 277.1852 | 0 | 0 | 0 | 179.3726 | 77.1087 | 95.0969 | 165.0124 | 183.4351 | 139.5733 | 77.1087 | 77.1087 | 77.1087 | 123.6274 | 77.1087 | 174.9191 | 555.0831 | 655.2563 | 416.7585 | 77.1087 | 77.1087 | 77.1087 | 303 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 11 | 6755 | 16.3 | 16.3 | 14.4083 | 15.5049 | 15 | 69 | 69 | 615.2706 | 130.4313 | 28.8329 | 155.2958 | 0 | 0 | 364.768 | 560.8331 | 428.3698 | 44.9732 | 0 | 0 | 277.5687 | 88.6448 | 88.6448 | 154.3751 | 189.7056 | 165.836 | 96.7488 | 88.6448 | 88.6448 | 130.4313 | 88.6448 | 88.6448 | 519.1432 | 750.5387 | 594.2058 | 141.7221 | 88.6448 | 88.6448 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 12 | 6756 | 17.9 | 17.9 | 14.4083 | 15.5049 | 15 | 63 | 63 | 654.1137 | 137.098 | 31.4074 | 172.2944 | 0 | 0 | 239.4859 | 537.4468 | 520.5787 | 198.7626 | 0 | 0 | 331.902 | 96.9747 | 96.9747 | 138.7308 | 190.6824 | 187.7413 | 131.6304 | 96.9747 | 96.9747 | 137.098 | 96.9747 | 96.9747 | 378.2167 | 728.1292 | 708.32 | 330.393 | 96.9747 | 96.9747 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 13 | 6757 | 18.7 | 18.7 | 14.4083 | 15.5049 | 15 | 63 | 63 | 673.7932 | 136.4221 | 31.2414 | 189.7674 | 0 | 0 | 77.1068 | 457.4876 | 569.8783 | 348.4421 | 0 | 0 | 352.5779 | 98.7362 | 98.7362 | 111.7052 | 175.6834 | 194.587 | 157.3425 | 98.7362 | 98.7362 | 136.4221 | 98.7362 | 98.7362 | 188.812 | 633.171 | 764.4653 | 505.7846 | 98.7362 | 98.7362 | 489 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 14 | 6758 | 19 | 19 | 14.4083 | 15.5049 | 15 | 62 | 62 | 646.4163 | 136.3168 | 28.3593 | 206.6455 | 0 | 0 | 0 | 318.8393 | 544.668 | 451.4376 | 93.7611 | 0 | 321.6832 | 95.614 | 95.614 | 95.614 | 151.508 | 191.0968 | 174.7531 | 112.0508 | 95.614 | 136.3168 | 95.614 | 95.614 | 95.614 | 470.3473 | 735.7648 | 626.1907 | 205.8119 | 95.614 | 458 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 15 | 6759 | 19.1 | 19.1 | 14.4083 | 15.5049 | 15 | 61 | 61 | 592.8533 | 129.7269 | 23.151 | 222.1768 | 0 | 0 | 0 | 164.2814 | 466.297 | 495.1621 | 233.968 | 0 | 256.2731 | 86.5887 | 86.5887 | 86.5887 | 117.3367 | 173.864 | 179.2665 | 130.3797 | 86.5887 | 129.7269 | 86.5887 | 86.5887 | 86.5887 | 281.6182 | 640.161 | 674.4287 | 364.3477 | 86.5887 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 16 | 6760 | 18.9 | 18.9 | 14.4083 | 15.5049 | 15 | 61 | 61 | 486.4564 | 116.671 | 16.1823 | 236.192 | 0 | 0 | 0 | 22.0304 | 331.4708 | 446.7401 | 300.3151 | 0 | 161.329 | 72.6487 | 72.6487 | 72.6487 | 77.7055 | 148.7338 | 175.1925 | 141.5824 | 72.6487 | 116.671 | 72.6487 | 72.6487 | 72.6487 | 99.7359 | 480.2046 | 621.9326 | 441.8975 | 72.6487 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 17 | 6761 | 17.8 | 17.8 | 14.4083 | 15.5049 | 15 | 64 | 64 | 266.7594 | 89.9475 | 8.014 | 248.9637 | 0 | 0 | 0 | 0 | 142.5472 | 251.3181 | 212.8703 | 49.7259 | 54.0525 | 50.2911 | 50.2911 | 50.2911 | 50.2911 | 101.0413 | 139.7663 | 126.078 | 67.9947 | 89.9475 | 50.2911 | 50.2911 | 50.2911 | 50.2911 | 243.5885 | 391.0845 | 338.9483 | 117.7206 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 9 | 18 | 6762 | 15.6 | 15.6 | 14.4083 | 15.5049 | 15 | 71 | 71 | 106.8022 | 25.2307 | -0.8705 | 260.9747 | 0 | 0 | 0 | 0 | 37.9632 | 96.643 | 98.7106 | 42.9549 | 5.7693 | 14.3571 | 14.3571 | 14.3571 | 14.3571 | 35.3316 | 67.7519 | 68.8942 | 38.0895 | 25.2307 | 14.3571 | 14.3571 | 14.3571 | 14.3571 | 73.2948 | 164.3948 | 167.6049 | 81.0445 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 19 | 6763 | 14.8 | 14.8 | 14.4083 | 15.5049 | 15 | 71 | 71 | 0 | 0 | -10.0548 | 272.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 20 | 6764 | 14.1 | 14.1 | 14.4083 | 15.5049 | 15 | 73 | 73 | 0 | 0 | -19.1423 | 285.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 21 | 6765 | 12.7 | 12.7 | 14.4083 | 15.5049 | 15 | 76 | 76 | 0 | 0 | -27.6921 | 298.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 22 | 6766 | 11.2 | 11.2 | 14.4083 | 15.5049 | 15 | 81 | 81 | 0 | 0 | -35.1473 | 313.5267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 23 | 6767 | 11.2 | 11.2 | 14.4083 | 15.5049 | 15 | 81 | 81 | 0 | 0 | -40.786 | 331.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 9 | 24 | 6768 | 10.4 | 10.4 | 13.6292 | 15.0099 | 15 | 82 | 82 | 0 | 0 | -43.7965 | 350.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 1 | 6769 | 10.1 | 10.1 | 13.6292 | 15.0099 | 15 | 80 | 80 | 0 | 0 | -43.6003 | 11.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 2 | 6770 | 9.6 | 9.6 | 13.6292 | 15.0099 | 15 | 82 | 82 | 0 | 0 | -40.5782 | 31.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 3 | 6771 | 9.3 | 9.3 | 13.6292 | 15.0099 | 15 | 82 | 82 | 0 | 0 | -34.6486 | 48.6778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 4 | 6772 | 8.6 | 8.6 | 13.6292 | 15.0099 | 15 | 85 | 85 | 0 | 0 | -27.0027 | 63.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 5 | 6773 | 8.2 | 8.2 | 13.6292 | 15.0099 | 15 | 87 | 87 | 0 | 0 | -18.3466 | 76.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 6 | 6774 | 7.5 | 7.5 | 13.6292 | 15.0099 | 15 | 89 | 89 | 0 | 0 | -9.2201 | 88.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 7 | 6775 | 7.8 | 7.8 | 13.6292 | 15.0099 | 15 | 88 | 88 | 0 | 0 | -0.054526 | 100.7141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 10 | 8 | 6776 | 8.5 | 8.5 | 13.6292 | 15.0099 | 15 | 85 | 85 | 225.081 | 38.8453 | 8.7549 | 112.7779 | 0 | 126.7934 | 221.1572 | 185.9701 | 41.8443 | 0 | 0 | 0 | 19.1547 | 20.009 | 26.5004 | 31.3315 | 29.53 | 22.1512 | 20.009 | 20.009 | 20.009 | 38.8453 | 20.009 | 153.2937 | 252.4886 | 215.5001 | 63.9955 | 20.009 | 20.009 | 20.009 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 9 | 6777 | 10.3 | 10.3 | 13.6292 | 15.0099 | 15 | 79 | 79 | 369.1236 | 93.1612 | 16.7868 | 125.6595 | 0 | 137.9754 | 336.3713 | 337.7254 | 141.2446 | 0 | 0 | 0 | 84.8388 | 52.1823 | 78.4532 | 116.2283 | 116.4862 | 79.0757 | 52.1823 | 52.1823 | 52.1823 | 93.1612 | 52.1823 | 216.4286 | 452.5996 | 454.2116 | 220.3203 | 52.1823 | 52.1823 | 52.1823 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 10 | 6778 | 12 | 12 | 13.6292 | 15.0099 | 15 | 73 | 73 | 647.5764 | 96.5514 | 23.5502 | 139.8192 | 0 | 100.6233 | 503.7314 | 611.7604 | 361.4285 | 0 | 0 | 0 | 228.4486 | 69.4112 | 84.6445 | 145.6709 | 162.0253 | 124.1277 | 69.4112 | 69.4112 | 69.4112 | 96.5514 | 69.4112 | 185.2679 | 649.4023 | 773.7858 | 485.5562 | 69.4112 | 69.4112 | 69.4112 | 325 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 11 | 6779 | 13.6 | 13.6 | 13.6292 | 15.0099 | 15 | 67 | 67 | 735.0057 | 103.534 | 28.4821 | 155.4824 | 0 | 0 | 434.7285 | 671.4052 | 514.7819 | 56.6063 | 0 | 0 | 327.466 | 83.1696 | 83.1696 | 142.5206 | 174.8327 | 153.4498 | 90.8977 | 83.1696 | 83.1696 | 103.534 | 83.1696 | 83.1696 | 577.2491 | 846.2379 | 668.2317 | 147.504 | 83.1696 | 83.1696 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 12 | 6780 | 15.1 | 15.1 | 13.6292 | 15.0099 | 15 | 60 | 60 | 776.1654 | 107.5516 | 31.0331 | 172.4103 | 0 | 0 | 283.1037 | 639.0929 | 620.7102 | 238.7238 | 0 | 0 | 389.4484 | 91.0199 | 91.0199 | 127.3079 | 172.9382 | 170.5819 | 121.6193 | 91.0199 | 91.0199 | 107.5516 | 91.0199 | 91.0199 | 410.4116 | 812.0311 | 791.2921 | 360.3431 | 91.0199 | 91.0199 | 497 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 13 | 6781 | 16.3 | 16.3 | 13.6292 | 15.0099 | 15 | 53 | 53 | 780.4722 | 110.0173 | 30.8552 | 189.7995 | 0 | 0 | 88.3288 | 531.2016 | 662.9038 | 406.2858 | 0 | 0 | 403.9827 | 93.3321 | 93.3321 | 104.5701 | 160.9162 | 177.6725 | 145.0233 | 93.3321 | 93.3321 | 110.0173 | 93.3321 | 93.3321 | 192.8989 | 692.1178 | 840.5762 | 551.3092 | 93.3321 | 93.3321 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 14 | 6782 | 17.5 | 17.5 | 13.6292 | 15.0099 | 15 | 51 | 51 | 760.7709 | 108.7002 | 27.9742 | 206.5998 | 0 | 0 | 0 | 376.4701 | 643.567 | 533.6711 | 111.1578 | 0 | 374.2998 | 89.8298 | 89.8298 | 89.8298 | 138.6277 | 173.2487 | 159.004 | 104.238 | 89.8298 | 108.7002 | 89.8298 | 89.8298 | 89.8298 | 515.0978 | 816.8157 | 692.6751 | 215.3959 | 89.8298 | 483 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 15 | 6783 | 17.6 | 17.6 | 13.6292 | 15.0099 | 15 | 51 | 51 | 714.3545 | 103.1988 | 22.776 | 222.0723 | 0 | 0 | 0 | 199.141 | 564.1125 | 598.6346 | 282.4846 | 0 | 304.8012 | 80.7607 | 80.7607 | 80.7607 | 107.8684 | 157.5494 | 162.2487 | 119.2134 | 80.7607 | 103.1988 | 80.7607 | 80.7607 | 80.7607 | 307.0094 | 721.6619 | 760.8833 | 401.698 | 80.7607 | 408 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 16 | 6784 | 17 | 17 | 13.6292 | 15.0099 | 15 | 59 | 59 | 596.9056 | 97.3325 | 15.8203 | 236.0492 | 0 | 0 | 0 | 28.1098 | 408.5336 | 549.6439 | 368.7803 | 0 | 194.6675 | 67.2991 | 67.2991 | 67.2991 | 71.8938 | 134.0766 | 157.142 | 127.5787 | 67.2991 | 97.3325 | 67.2991 | 67.2991 | 67.2991 | 100.0036 | 542.6101 | 706.7859 | 496.359 | 67.2991 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 17 | 6785 | 15.6 | 15.6 | 13.6292 | 15.0099 | 15 | 63 | 63 | 371.4888 | 79.7384 | 7.6634 | 248.7979 | 0 | 0 | 0 | 0 | 199.6108 | 350.7919 | 296.4839 | 68.4996 | 73.2616 | 47.5855 | 47.5855 | 47.5855 | 47.5855 | 98.6272 | 137.2851 | 123.3982 | 65.1013 | 79.7384 | 47.5855 | 47.5855 | 47.5855 | 47.5855 | 298.238 | 488.0771 | 419.8821 | 133.6009 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 10 | 18 | 6786 | 13.3 | 13.3 | 13.6292 | 15.0099 | 15 | 69 | 69 | 91.5932 | 22.7774 | -1.2139 | 260.7959 | 0 | 0 | 0 | 0 | 32.8296 | 83.0569 | 84.6306 | 36.6288 | 8.2226 | 13.3263 | 13.3263 | 13.3263 | 13.3263 | 33.4579 | 64.258 | 65.223 | 35.7876 | 22.7774 | 13.3263 | 13.3263 | 13.3263 | 13.3263 | 66.2875 | 147.315 | 149.8537 | 72.4165 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 19 | 6787 | 12.2 | 12.2 | 13.6292 | 15.0099 | 15 | 72 | 72 | 0 | 0 | -10.3966 | 272.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 20 | 6788 | 11 | 11 | 13.6292 | 15.0099 | 15 | 76 | 76 | 0 | 0 | -19.4886 | 284.8385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 21 | 6789 | 9.9 | 9.9 | 13.6292 | 15.0099 | 15 | 80 | 80 | 0 | 0 | -28.0488 | 298.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 22 | 6790 | 8.7 | 8.7 | 13.6292 | 15.0099 | 15 | 84 | 84 | 0 | 0 | -35.5184 | 313.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 23 | 6791 | 7.9 | 7.9 | 13.6292 | 15.0099 | 15 | 87 | 87 | 0 | 0 | -41.17 | 331.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 10 | 24 | 6792 | 7.7 | 7.7 | 11.4708 | 13.9135 | 15 | 84 | 84 | 0 | 0 | -44.1825 | 350.9198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 1 | 6793 | 7.1 | 7.1 | 11.4708 | 13.9135 | 15 | 86 | 86 | 0 | 0 | -43.9701 | 11.7135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 2 | 6794 | 6.2 | 6.2 | 11.4708 | 13.9135 | 15 | 90 | 90 | 0 | 0 | -40.9163 | 31.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 3 | 6795 | 5.8 | 5.8 | 11.4708 | 13.9135 | 15 | 91 | 91 | 0 | 0 | -34.954 | 48.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 4 | 6796 | 5.5 | 5.5 | 11.4708 | 13.9135 | 15 | 89 | 89 | 0 | 0 | -27.2822 | 63.9027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 5 | 6797 | 5.5 | 5.5 | 11.4708 | 13.9135 | 15 | 89 | 89 | 0 | 0 | -18.61 | 77.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 6 | 6798 | 5 | 5 | 11.4708 | 13.9135 | 15 | 91 | 91 | 0 | 0 | -9.4778 | 89.2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 7 | 6799 | 4.9 | 4.9 | 11.4708 | 13.9135 | 15 | 89 | 89 | 0 | 0 | -0.31618 | 100.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 11 | 8 | 6800 | 5.4 | 5.4 | 11.4708 | 13.9135 | 15 | 87 | 87 | 88.414 | 36.9457 | 8.4803 | 113.0513 | 0 | 49.4436 | 86.7892 | 73.2948 | 16.8653 | 0 | 0 | 0 | 7.0543 | 14.7332 | 34.3935 | 49.2433 | 43.8775 | 21.4394 | 14.7332 | 14.7332 | 14.7332 | 36.9457 | 14.7332 | 83.8372 | 136.0325 | 117.1723 | 38.3047 | 14.7332 | 14.7332 | 14.7332 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 9 | 6801 | 7.5 | 7.5 | 11.4708 | 13.9135 | 15 | 78 | 78 | 354.8384 | 92.3709 | 16.4914 | 125.9178 | 0 | 131.1799 | 322.9363 | 325.5211 | 137.42 | 0 | 0 | 0 | 79.6291 | 51.152 | 75.7801 | 111.781 | 112.2663 | 76.9516 | 51.152 | 51.152 | 51.152 | 92.3709 | 51.152 | 206.96 | 434.7173 | 437.7874 | 214.3716 | 51.152 | 51.152 | 51.152 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 10 | 6802 | 10 | 10 | 11.4708 | 13.9135 | 15 | 66 | 66 | 658.6289 | 93.2928 | 23.2281 | 140.0496 | 0 | 99.6891 | 511.4546 | 623.6169 | 370.4729 | 0 | 0 | 0 | 228.7072 | 68.1066 | 82.8142 | 143.5636 | 160.1114 | 122.764 | 68.1066 | 68.1066 | 68.1066 | 93.2928 | 68.1066 | 182.5033 | 655.0182 | 783.7283 | 493.2369 | 68.1066 | 68.1066 | 68.1066 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 11 | 6803 | 11.6 | 11.6 | 11.4708 | 13.9135 | 15 | 63 | 63 | 756.6815 | 98.116 | 28.1318 | 155.665 | 0 | 0 | 446.4984 | 692.6477 | 533.0534 | 61.2037 | 0 | 0 | 332.884 | 81.471 | 81.471 | 139.1304 | 170.9174 | 150.3079 | 89.3746 | 81.471 | 81.471 | 98.116 | 81.471 | 81.471 | 585.6288 | 863.5651 | 683.3613 | 150.5783 | 81.471 | 81.471 | 431 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 12 | 6804 | 13.7 | 13.7 | 11.4708 | 13.9135 | 15 | 56 | 56 | 784.6123 | 104.7448 | 30.66 | 172.5225 | 0 | 0 | 285.1217 | 647.4042 | 630.4461 | 244.1812 | 0 | 0 | 389.2552 | 89.8509 | 89.8509 | 125.4927 | 170.7799 | 168.66 | 120.3749 | 89.8509 | 89.8509 | 104.7448 | 89.8509 | 89.8509 | 410.6144 | 818.1841 | 799.1061 | 364.5561 | 89.8509 | 89.8509 | 494 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 13 | 6805 | 14.8 | 14.8 | 11.4708 | 13.9135 | 15 | 55 | 55 | 798.4615 | 105.2258 | 30.4707 | 189.829 | 0 | 0 | 89.3836 | 544.7451 | 681.0023 | 418.3376 | 0 | 0 | 408.7742 | 93.5514 | 93.5514 | 102.0322 | 145.2369 | 158.165 | 133.2433 | 93.5514 | 93.5514 | 105.2258 | 93.5514 | 93.5514 | 191.4158 | 689.982 | 839.1673 | 551.581 | 93.5514 | 93.5514 | 514 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 14 | 6806 | 15.7 | 15.7 | 11.4708 | 13.9135 | 15 | 50 | 50 | 790.556 | 101.5047 | 27.5911 | 206.5525 | 0 | 0 | 0 | 392.4829 | 671.37 | 556.9777 | 116.3154 | 0 | 384.4953 | 89.5899 | 89.5899 | 89.5899 | 126.4036 | 152.5623 | 141.8327 | 100.4999 | 89.5899 | 101.5047 | 89.5899 | 89.5899 | 89.5899 | 518.8865 | 823.9324 | 698.8104 | 216.8153 | 89.5899 | 486 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 15 | 6807 | 15.9 | 15.9 | 11.4708 | 13.9135 | 15 | 46 | 46 | 750.1013 | 95.1373 | 22.4031 | 221.9668 | 0 | 0 | 0 | 210.3656 | 594.6773 | 630.635 | 297.1754 | 0 | 315.8627 | 78.4635 | 78.4635 | 78.4635 | 104.3963 | 151.7723 | 156.205 | 115.0978 | 78.4635 | 95.1373 | 78.4635 | 78.4635 | 78.4635 | 314.7619 | 746.4496 | 786.8401 | 412.2732 | 78.4635 | 411 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 16 | 6808 | 15.7 | 15.7 | 11.4708 | 13.9135 | 15 | 49 | 49 | 656.7567 | 86.4297 | 15.4606 | 235.9056 | 0 | 0 | 0 | 32.1286 | 451.4638 | 606.3375 | 406.027 | 0 | 210.5703 | 64.2706 | 64.2706 | 64.2706 | 68.7468 | 127.1686 | 148.7457 | 120.8384 | 64.2706 | 86.4297 | 64.2706 | 64.2706 | 64.2706 | 100.8754 | 578.6324 | 755.0832 | 526.8654 | 64.2706 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 17 | 6809 | 14.6 | 14.6 | 11.4708 | 13.9135 | 15 | 52 | 52 | 438.3042 | 71.93 | 7.3152 | 248.6313 | 0 | 0 | 0 | 0 | 236.8041 | 414.8145 | 349.8321 | 79.9229 | 84.07 | 44.7719 | 44.7719 | 44.7719 | 44.7719 | 93.0756 | 129.3865 | 116.1312 | 61.0747 | 71.93 | 44.7719 | 44.7719 | 44.7719 | 44.7719 | 329.8798 | 544.2009 | 465.9634 | 140.9976 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 11 | 18 | 6810 | 12.7 | 12.7 | 11.4708 | 13.9135 | 15 | 59 | 59 | 97.0468 | 19.2502 | -1.5548 | 260.6161 | 0 | 0 | 0 | 0 | 35.0729 | 88.1851 | 89.6397 | 38.5846 | 11.7498 | 11.8276 | 11.8276 | 11.8276 | 11.8276 | 30.2029 | 58.0294 | 58.7915 | 32.0428 | 19.2502 | 11.8276 | 11.8276 | 11.8276 | 11.8276 | 65.2758 | 146.2145 | 148.4312 | 70.6273 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 19 | 6811 | 11 | 11 | 11.4708 | 13.9135 | 15 | 71 | 71 | 0 | 0 | -10.7357 | 272.4176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 20 | 6812 | 9.2 | 9.2 | 11.4708 | 13.9135 | 15 | 80 | 80 | 0 | 0 | -19.8322 | 284.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 21 | 6813 | 9.6 | 9.6 | 11.4708 | 13.9135 | 15 | 78 | 78 | 0 | 0 | -28.4029 | 298.0164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 22 | 6814 | 8.7 | 8.7 | 11.4708 | 13.9135 | 15 | 87 | 87 | 0 | 0 | -35.8871 | 313.2534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 23 | 6815 | 7.8 | 7.8 | 11.4708 | 13.9135 | 15 | 92 | 92 | 0 | 0 | -41.552 | 330.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 11 | 24 | 6816 | 7 | 7 | 9.6208 | 12.6101 | 15 | 96 | 96 | 0 | 0 | -44.5668 | 350.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 1 | 6817 | 6.5 | 6.5 | 9.6208 | 12.6101 | 15 | 98 | 98 | 0 | 0 | -44.3384 | 11.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 2 | 6818 | 6.1 | 6.1 | 9.6208 | 12.6101 | 15 | 98 | 98 | 0 | 0 | -41.2532 | 31.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 3 | 6819 | 6.1 | 6.1 | 9.6208 | 12.6101 | 15 | 98 | 98 | 0 | 0 | -35.2585 | 49.2488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 4 | 6820 | 5.5 | 5.5 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -27.561 | 64.1992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 5 | 6821 | 6.2 | 6.2 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -18.8732 | 77.3626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 6 | 6822 | 6.6 | 6.6 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -9.7355 | 89.4934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 7 | 6823 | 6.6 | 6.6 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -0.57802 | 101.2771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 12 | 8 | 6824 | 6.5 | 6.5 | 9.6208 | 12.6101 | 15 | 99 | 99 | 4.2468 | 18.6836 | 8.2054 | 113.3216 | 0 | 2.3576 | 4.1646 | 3.5321 | 0.83044 | 0 | 0 | 0 | 0.31635 | 8.771 | 11.2918 | 13.2238 | 12.5475 | 9.6589 | 8.771 | 8.771 | 8.771 | 18.6836 | 8.771 | 13.6494 | 17.3885 | 16.0795 | 10.4894 | 8.771 | 8.771 | 8.771 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 9 | 6825 | 6.6 | 6.6 | 9.6208 | 12.6101 | 15 | 99 | 99 | 58.8863 | 98.1043 | 16.1958 | 126.1722 | 0 | 21.5297 | 53.5216 | 54.1612 | 23.0739 | 0 | 0 | 0 | 12.8957 | 43.4381 | 101.1277 | 186.8506 | 188.5645 | 105.2653 | 43.4381 | 43.4381 | 43.4381 | 98.1043 | 43.4381 | 122.6574 | 240.3722 | 242.7257 | 128.3392 | 43.4381 | 43.4381 | 43.4381 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 10 | 6826 | 8 | 8 | 9.6208 | 12.6101 | 15 | 93 | 93 | 138.4725 | 160.6801 | 22.9061 | 140.276 | 0 | 20.4073 | 107.3453 | 131.4019 | 78.485 | 0 | 0 | 0 | 47.3199 | 75.8915 | 97.8417 | 191.3529 | 217.2283 | 160.3106 | 75.8915 | 75.8915 | 75.8915 | 160.6801 | 75.8915 | 118.249 | 298.6982 | 348.6302 | 238.7956 | 75.8915 | 75.8915 | 75.8915 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 11 | 6827 | 10.5 | 10.5 | 9.6208 | 12.6101 | 15 | 79 | 79 | 471.1312 | 156.3745 | 27.7822 | 155.8432 | 0 | 0 | 277.3523 | 432.141 | 333.7873 | 39.9056 | 0 | 0 | 204.6255 | 93.403 | 93.403 | 169.2732 | 211.6158 | 184.711 | 104.3193 | 93.403 | 93.403 | 156.3745 | 93.403 | 93.403 | 446.6255 | 643.7568 | 518.4983 | 144.2248 | 93.403 | 93.403 | 361 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 12 | 6828 | 11.3 | 11.3 | 9.6208 | 12.6101 | 15 | 74 | 74 | 507.5267 | 168.0757 | 30.2882 | 172.631 | 0 | 0 | 183.7552 | 419.6368 | 409.7008 | 159.7676 | 0 | 0 | 248.9243 | 102.3339 | 102.3339 | 151.6744 | 215.0114 | 212.3435 | 145.2334 | 102.3339 | 102.3339 | 168.0757 | 102.3339 | 102.3339 | 335.4296 | 634.6482 | 622.0443 | 305.001 | 102.3339 | 102.3339 | 417 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 13 | 6829 | 12.4 | 12.4 | 9.6208 | 12.6101 | 15 | 70 | 70 | 347.4466 | 210.0904 | 30.0879 | 189.8557 | 0 | 0 | 38.4805 | 237.6038 | 297.542 | 183.1842 | 0 | 0 | 175.9096 | 112.1887 | 112.1887 | 128.8118 | 214.8304 | 240.7229 | 191.3218 | 112.1887 | 112.1887 | 210.0904 | 112.1887 | 112.1887 | 167.2923 | 452.4342 | 538.2649 | 374.506 | 112.1887 | 112.1887 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 14 | 6830 | 12.6 | 12.6 | 9.6208 | 12.6101 | 15 | 69 | 69 | 606.1554 | 141.6073 | 27.2102 | 206.5034 | 0 | 0 | 0 | 301.9107 | 516.7399 | 428.8699 | 89.7737 | 0 | 291.3927 | 94.65 | 94.65 | 94.65 | 152.3945 | 193.4835 | 176.6772 | 111.8205 | 94.65 | 141.6073 | 94.65 | 94.65 | 94.65 | 454.3053 | 710.2235 | 605.5471 | 201.5941 | 94.65 | 433 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 15 | 6831 | 12.5 | 12.5 | 9.6208 | 12.6101 | 15 | 71 | 71 | 271.5621 | 184.1629 | 22.0326 | 221.8603 | 0 | 0 | 0 | 76.6188 | 216.1291 | 229.0339 | 107.7738 | 0 | 112.8371 | 95.975 | 95.975 | 95.975 | 135.07 | 206.2556 | 212.8403 | 150.9669 | 95.975 | 184.1629 | 95.975 | 95.975 | 95.975 | 211.6888 | 422.3846 | 441.8742 | 258.7407 | 95.975 | 297 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 16 | 6832 | 12.5 | 12.5 | 9.6208 | 12.6101 | 15 | 68 | 68 | 233.9537 | 143.2756 | 15.1033 | 235.7613 | 0 | 0 | 0 | 11.878 | 161.5178 | 216.5427 | 144.7198 | 0 | 73.7244 | 75.5263 | 75.5263 | 75.5263 | 81.6551 | 158.8661 | 187.2578 | 150.1987 | 75.5263 | 143.2756 | 75.5263 | 75.5263 | 75.5263 | 93.5331 | 320.3839 | 403.8005 | 294.9184 | 75.5263 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 17 | 6833 | 12.1 | 12.1 | 9.6208 | 12.6101 | 15 | 73 | 73 | 77.4184 | 85.5678 | 6.9696 | 248.464 | 0 | 0 | 0 | 0 | 42.0542 | 73.4297 | 61.791 | 13.956 | 14.4322 | 43.4186 | 43.4186 | 43.4186 | 43.4186 | 78.4534 | 104.5918 | 94.8959 | 55.0452 | 85.5678 | 43.4186 | 43.4186 | 43.4186 | 43.4186 | 120.5076 | 178.0215 | 156.6869 | 69.0012 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 12 | 18 | 6834 | 11.6 | 11.6 | 9.6208 | 12.6101 | 15 | 74 | 74 | 11.9263 | 13.5449 | -1.893 | 260.4353 | 0 | 0 | 0 | 0 | 4.3456 | 10.8593 | 11.0117 | 4.7136 | 0.45515 | 7.1945 | 7.1945 | 7.1945 | 7.1945 | 7.8191 | 8.7552 | 8.7771 | 7.872 | 13.5449 | 7.1945 | 7.1945 | 7.1945 | 7.1945 | 12.1647 | 19.6145 | 19.7888 | 12.5856 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 19 | 6835 | 10.9 | 10.9 | 9.6208 | 12.6101 | 15 | 78 | 78 | 0 | 0 | -11.0721 | 272.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 20 | 6836 | 8.8 | 8.8 | 9.6208 | 12.6101 | 15 | 87 | 87 | 0 | 0 | -20.1729 | 284.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 21 | 6837 | 6.7 | 6.7 | 9.6208 | 12.6101 | 15 | 97 | 97 | 0 | 0 | -28.7541 | 297.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 22 | 6838 | 5.8 | 5.8 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -36.2532 | 313.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 23 | 6839 | 5.4 | 5.4 | 9.6208 | 12.6101 | 15 | 99 | 99 | 0 | 0 | -41.9317 | 330.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 12 | 24 | 6840 | 6 | 6 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -44.9493 | 350.9968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 1 | 6841 | 6.6 | 6.6 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -44.7053 | 12.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 2 | 6842 | 7.4 | 7.4 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -41.5888 | 32.1044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 3 | 6843 | 7.7 | 7.7 | 8.4917 | 11.3294 | 15 | 98 | 98 | 0 | 0 | -35.562 | 49.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 4 | 6844 | 8 | 8 | 8.4917 | 11.3294 | 15 | 96 | 96 | 0 | 0 | -27.8391 | 64.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 5 | 6845 | 8.4 | 8.4 | 8.4917 | 11.3294 | 15 | 95 | 95 | 0 | 0 | -19.136 | 77.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 6 | 6846 | 8.4 | 8.4 | 8.4917 | 11.3294 | 15 | 96 | 96 | 0 | 0 | -9.9931 | 89.7788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 7 | 6847 | 8.4 | 8.4 | 8.4917 | 11.3294 | 15 | 97 | 97 | 0 | 0 | -0.84 | 101.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 13 | 8 | 6848 | 8.9 | 8.9 | 8.4917 | 11.3294 | 15 | 90 | 90 | 0.87156 | 7.9397 | 7.9304 | 113.5884 | 0 | 0.48031 | 0.85381 | 0.72716 | 0.17455 | 0 | 0 | 0 | 0.060326 | 3.7347 | 4.7804 | 5.5935 | 5.3178 | 4.1147 | 3.7347 | 3.7347 | 3.7347 | 7.9397 | 3.7347 | 5.2607 | 6.4473 | 6.0449 | 4.2892 | 3.7347 | 3.7347 | 3.7347 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 9 | 6849 | 9.5 | 9.5 | 8.4917 | 11.3294 | 15 | 88 | 88 | 1.3743 | 30.7065 | 15.9001 | 126.4229 | 0 | 0.49692 | 1.2474 | 1.2672 | 0.54469 | 0 | 0 | 0 | 0.29354 | 14.9784 | 14.9784 | 14.9784 | 14.9784 | 14.9784 | 14.9784 | 14.9784 | 14.9784 | 30.7065 | 14.9784 | 15.4754 | 16.2259 | 16.2457 | 15.5231 | 14.9784 | 14.9784 | 14.9784 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 10 | 6850 | 10.2 | 10.2 | 8.4917 | 11.3294 | 15 | 80 | 80 | 3.976 | 81.6632 | 22.5844 | 140.498 | 0 | 0.57029 | 3.0769 | 3.7811 | 2.2704 | 0 | 0 | 0 | 1.3368 | 39.8022 | 41.0191 | 46.3679 | 47.8705 | 44.6469 | 39.8022 | 39.8022 | 39.8022 | 81.6632 | 39.8022 | 41.5894 | 49.4448 | 51.6517 | 46.9173 | 39.8022 | 39.8022 | 39.8022 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 11 | 6851 | 10.7 | 10.7 | 8.4917 | 11.3294 | 15 | 72 | 72 | 4.8587 | 114.9169 | 27.4334 | 156.0173 | 0 | 0 | 2.8537 | 4.4655 | 3.4615 | 0.42983 | 0 | 0 | 2.0831 | 56.1697 | 56.1697 | 61.6376 | 64.726 | 62.8023 | 56.9933 | 56.1697 | 56.1697 | 114.9169 | 56.1697 | 56.1697 | 64.4912 | 69.1916 | 66.2638 | 57.4231 | 56.1697 | 56.1697 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 12 | 6852 | 11 | 11 | 8.4917 | 11.3294 | 15 | 71 | 71 | 5.9979 | 144.0921 | 29.9177 | 172.7356 | 0 | 0 | 2.1638 | 4.9693 | 4.8638 | 1.9092 | 0 | 0 | 2.9079 | 70.1283 | 70.1283 | 74.9304 | 81.1567 | 80.9227 | 74.3655 | 70.1283 | 70.1283 | 144.0921 | 70.1283 | 70.1283 | 77.0942 | 86.126 | 85.7866 | 76.2748 | 70.1283 | 70.1283 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 13 | 6853 | 11.7 | 11.7 | 8.4917 | 11.3294 | 15 | 70 | 70 | 17.8475 | 191.0649 | 29.7071 | 189.8796 | 0 | 0 | 1.956 | 12.2337 | 15.3451 | 9.4675 | 0 | 0 | 8.9351 | 90.104 | 90.104 | 94.222 | 115.8595 | 122.4097 | 110.0357 | 90.104 | 90.104 | 191.0649 | 90.104 | 90.104 | 96.1781 | 128.0932 | 137.7547 | 119.5031 | 90.104 | 90.104 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 14 | 6854 | 12.8 | 12.8 | 8.4917 | 11.3294 | 15 | 67 | 67 | 91.2542 | 220.6461 | 26.8315 | 206.4525 | 0 | 0 | 0 | 45.5984 | 78.0853 | 64.8309 | 13.5994 | 0 | 43.3539 | 103.315 | 103.315 | 103.315 | 150.8649 | 184.7422 | 170.9205 | 117.4964 | 103.315 | 220.6461 | 103.315 | 103.315 | 103.315 | 196.4633 | 262.8275 | 235.7514 | 131.0958 | 103.315 | 264 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 15 | 6855 | 12.6 | 12.6 | 8.4917 | 11.3294 | 15 | 69 | 69 | 86.117 | 189.6976 | 21.6645 | 221.7527 | 0 | 0 | 0 | 24.4439 | 68.8001 | 72.8541 | 34.2312 | 0 | 35.3024 | 89.9503 | 89.9503 | 89.9503 | 113.2394 | 155.5002 | 159.3628 | 122.5644 | 89.9503 | 189.6976 | 89.9503 | 89.9503 | 89.9503 | 137.6833 | 224.3003 | 232.2169 | 156.7956 | 89.9503 | 225 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 16 | 6856 | 12.2 | 12.2 | 8.4917 | 11.3294 | 15 | 72 | 72 | 149.9972 | 145.5553 | 14.7487 | 235.6162 | 0 | 0 | 0 | 7.8966 | 103.9973 | 139.1777 | 92.8298 | 0 | 46.4447 | 72.8591 | 72.8591 | 72.8591 | 77.8657 | 138.7947 | 161.0996 | 131.7144 | 72.8591 | 145.5553 | 72.8591 | 72.8591 | 72.8591 | 85.7623 | 242.792 | 300.2773 | 224.5442 | 72.8591 | 192 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 17 | 6857 | 10.8 | 10.8 | 8.4917 | 11.3294 | 15 | 84 | 84 | 7.0491 | 56.7238 | 6.6267 | 248.2958 | 0 | 0 | 0 | 0 | 3.8497 | 6.7002 | 5.6257 | 1.2559 | 1.2762 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 56.7238 | 27.9125 | 27.9125 | 27.9125 | 27.9125 | 31.7622 | 34.6127 | 33.5383 | 29.1684 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 18 | 6858 | 7.9 | 7.9 | 8.4917 | 11.3294 | 15 | 96 | 96 | 3.8532 | 7.8732 | -2.2283 | 260.2536 | 0 | 0 | 0 | 0 | 1.4154 | 3.5154 | 3.5561 | 1.5137 | 0.12684 | 4.222 | 4.222 | 4.222 | 4.222 | 4.222 | 4.222 | 4.222 | 4.222 | 7.8732 | 4.222 | 4.222 | 4.222 | 4.222 | 5.6375 | 7.7374 | 7.7781 | 5.7357 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 19 | 6859 | 5.8 | 5.8 | 8.4917 | 11.3294 | 15 | 98 | 98 | 0 | 0 | -11.4055 | 272.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 20 | 6860 | 5 | 5 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -20.5107 | 284.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 21 | 6861 | 4.5 | 4.5 | 8.4917 | 11.3294 | 15 | 98 | 98 | 0 | 0 | -29.1024 | 297.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 22 | 6862 | 6.2 | 6.2 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -36.6164 | 312.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 23 | 6863 | 4.1 | 4.1 | 8.4917 | 11.3294 | 15 | 99 | 99 | 0 | 0 | -42.309 | 330.8028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 13 | 24 | 6864 | 3 | 3 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -45.3299 | 351.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 1 | 6865 | 2.8 | 2.8 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -45.0706 | 12.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 2 | 6866 | 2.5 | 2.5 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -41.923 | 32.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 3 | 6867 | 3.1 | 3.1 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -35.8644 | 49.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 4 | 6868 | 3.4 | 3.4 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -28.1166 | 64.7866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 5 | 6869 | 4.3 | 4.3 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -19.3984 | 77.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 6 | 6870 | 6.4 | 6.4 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -10.2507 | 90.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 7 | 6871 | 7.6 | 7.6 | 8.4083 | 10.3328 | 15 | 99 | 99 | 0 | 0 | -1.1021 | 101.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 14 | 8 | 6872 | 8.8 | 8.8 | 8.4083 | 10.3328 | 15 | 99 | 99 | 1.02 | 7.9348 | 7.6553 | 113.8518 | 0 | 0.55801 | 0.99819 | 0.85365 | 0.20905 | 0 | 0 | 0 | 0.065245 | 3.7329 | 4.7702 | 5.5885 | 5.3198 | 4.1215 | 3.7329 | 3.7329 | 3.7329 | 7.9348 | 3.7329 | 5.3282 | 6.5867 | 6.1735 | 4.3305 | 3.7329 | 3.7329 | 3.7329 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 9 | 6873 | 9.5 | 9.5 | 8.4083 | 10.3328 | 15 | 97 | 97 | 1.6381 | 32.6589 | 15.6045 | 126.6697 | 0 | 0.58572 | 1.4848 | 1.5141 | 0.65649 | 0 | 0 | 0 | 0.34106 | 16.0208 | 16.0208 | 16.0208 | 16.0208 | 16.0208 | 16.0208 | 16.0208 | 16.0208 | 32.6589 | 16.0208 | 16.6065 | 17.5056 | 17.535 | 16.6773 | 16.0208 | 16.0208 | 16.0208 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 10 | 6874 | 10.7 | 10.7 | 8.4083 | 10.3328 | 15 | 89 | 89 | 2.2184 | 60.2663 | 22.263 | 140.7158 | 0 | 0.30955 | 1.7137 | 2.1141 | 1.276 | 0 | 0 | 0 | 0.73366 | 29.6211 | 29.6211 | 29.6211 | 29.6211 | 29.6211 | 29.6211 | 29.6211 | 29.6211 | 60.2663 | 29.6211 | 29.9307 | 31.3349 | 31.7352 | 30.8971 | 29.6211 | 29.6211 | 29.6211 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 11 | 6875 | 11.2 | 11.2 | 8.4083 | 10.3328 | 15 | 85 | 85 | 3.6417 | 98.459 | 27.0855 | 156.187 | 0 | 0 | 2.1339 | 3.3534 | 2.6086 | 0.33565 | 0 | 0 | 1.541 | 49.1091 | 49.1091 | 49.1317 | 49.1446 | 49.1367 | 49.1127 | 49.1091 | 49.1091 | 98.459 | 49.1091 | 49.1091 | 51.2656 | 52.4981 | 51.7453 | 49.4483 | 49.1091 | 49.1091 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 12 | 6876 | 11.6 | 11.6 | 8.4083 | 10.3328 | 15 | 82 | 82 | 8.8657 | 159.7517 | 29.5487 | 172.8365 | 0 | 0 | 3.187 | 7.3598 | 7.2214 | 2.8528 | 0 | 0 | 4.2483 | 76.2529 | 76.2529 | 85.3604 | 97.2852 | 96.8896 | 84.4053 | 76.2529 | 76.2529 | 159.7517 | 76.2529 | 76.2529 | 88.5473 | 104.645 | 104.1109 | 87.258 | 76.2529 | 76.2529 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 13 | 6877 | 12.3 | 12.3 | 8.4083 | 10.3328 | 15 | 78 | 78 | 7.8641 | 160.1074 | 29.3283 | 189.9007 | 0 | 0 | 0.85311 | 5.403 | 6.7879 | 4.1965 | 0 | 0 | 3.8926 | 77.5869 | 77.5869 | 79.4208 | 89.2017 | 92.1788 | 86.6081 | 77.5869 | 77.5869 | 160.1074 | 77.5869 | 77.5869 | 80.2739 | 94.6047 | 98.9667 | 90.8046 | 77.5869 | 77.5869 | 164 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 14 | 6878 | 12.2 | 12.2 | 8.4083 | 10.3328 | 15 | 78 | 78 | 2.6143 | 92.7727 | 26.4552 | 206.3998 | 0 | 0 | 0 | 1.3105 | 2.2452 | 1.8647 | 0.39188 | 0 | 1.2273 | 45.63 | 45.63 | 45.63 | 45.63 | 45.63 | 45.63 | 45.63 | 45.63 | 92.7727 | 45.63 | 45.63 | 45.63 | 46.9406 | 47.8753 | 47.4948 | 46.0219 | 45.63 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 15 | 6879 | 12.1 | 12.1 | 8.4083 | 10.3328 | 15 | 78 | 78 | 5.6472 | 116.7165 | 21.2991 | 221.6439 | 0 | 0 | 0 | 1.6126 | 4.5286 | 4.7917 | 2.248 | 0 | 2.2835 | 58.3228 | 58.3228 | 58.3228 | 58.5107 | 58.8506 | 58.8812 | 58.5848 | 58.3228 | 116.7165 | 58.3228 | 58.3228 | 58.3228 | 60.1234 | 63.3791 | 63.673 | 60.8328 | 58.3228 | 119 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 16 | 6880 | 12.3 | 12.3 | 8.4083 | 10.3328 | 15 | 77 | 77 | 6.3627 | 92.0647 | 14.3967 | 235.4702 | 0 | 0 | 0 | 0.34704 | 4.43 | 5.9179 | 3.9392 | 0 | 1.9353 | 45.8685 | 45.8685 | 45.8685 | 45.8685 | 45.8685 | 45.8685 | 45.8685 | 45.8685 | 92.0647 | 45.8685 | 45.8685 | 45.8685 | 46.2155 | 50.2985 | 51.7864 | 49.8077 | 45.8685 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 17 | 6881 | 11.9 | 11.9 | 8.4083 | 10.3328 | 15 | 81 | 81 | 4.0899 | 43.2815 | 6.2866 | 248.1269 | 0 | 0 | 0 | 0 | 2.2455 | 3.8955 | 3.2636 | 0.71989 | 0.71855 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 43.2815 | 20.9937 | 20.9937 | 20.9937 | 20.9937 | 23.2392 | 24.8892 | 24.2573 | 21.7136 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 18 | 6882 | 10.9 | 10.9 | 8.4083 | 10.3328 | 15 | 91 | 91 | 3.0598 | 5.9152 | -2.5607 | 260.0708 | 0 | 0 | 0 | 0 | 1.1331 | 2.7969 | 2.8224 | 1.1946 | 0.08475 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 5.9152 | 3.1685 | 3.1685 | 3.1685 | 3.1685 | 4.3016 | 5.9655 | 5.9909 | 4.3631 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 19 | 6883 | 10.7 | 10.7 | 8.4083 | 10.3328 | 15 | 92 | 92 | 0 | 0 | -11.7358 | 271.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 20 | 6884 | 10.8 | 10.8 | 8.4083 | 10.3328 | 15 | 92 | 92 | 0 | 0 | -20.8453 | 284.0864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 21 | 6885 | 10.5 | 10.5 | 8.4083 | 10.3328 | 15 | 95 | 95 | 0 | 0 | -29.4476 | 297.4837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 22 | 6886 | 10.8 | 10.8 | 8.4083 | 10.3328 | 15 | 92 | 92 | 0 | 0 | -36.9768 | 312.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 23 | 6887 | 11.1 | 11.1 | 8.4083 | 10.3328 | 15 | 90 | 90 | 0 | 0 | -42.6838 | 330.7246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 14 | 24 | 6888 | 10.8 | 10.8 | 9.0958 | 9.8123 | 15 | 94 | 94 | 0 | 0 | -45.7085 | 351.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 1 | 6889 | 10.5 | 10.5 | 9.0958 | 9.8123 | 15 | 98 | 98 | 0 | 0 | -45.4343 | 12.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 2 | 6890 | 10.4 | 10.4 | 9.0958 | 9.8123 | 15 | 98 | 98 | 0 | 0 | -42.2558 | 32.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 3 | 6891 | 9.3 | 9.3 | 9.0958 | 9.8123 | 15 | 99 | 99 | 0 | 0 | -36.1658 | 50.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 4 | 6892 | 10 | 10 | 9.0958 | 9.8123 | 15 | 98 | 98 | 0 | 0 | -28.3933 | 65.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 5 | 6893 | 9.9 | 9.9 | 9.0958 | 9.8123 | 15 | 99 | 99 | 0 | 0 | -19.6605 | 78.2323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 6 | 6894 | 9.6 | 9.6 | 9.0958 | 9.8123 | 15 | 98 | 98 | 0 | 0 | -10.5081 | 90.3414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 7 | 6895 | 10 | 10 | 9.0958 | 9.8123 | 15 | 96 | 96 | 0 | 0 | -1.3642 | 102.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 15 | 8 | 6896 | 10.3 | 10.3 | 9.0958 | 9.8123 | 15 | 94 | 94 | 2.286 | 10.8657 | 7.3801 | 114.1117 | 0 | 1.2413 | 2.2345 | 1.9188 | 0.47902 | 0 | 0 | 0 | 0.13426 | 5.1107 | 6.5273 | 7.6607 | 7.3004 | 5.6574 | 5.1107 | 5.1107 | 5.1107 | 10.8657 | 5.1107 | 7.7687 | 9.8953 | 9.2192 | 6.1364 | 5.1107 | 5.1107 | 5.1107 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 9 | 6897 | 11.6 | 11.6 | 9.0958 | 9.8123 | 15 | 89 | 89 | 51.0504 | 89.645 | 15.3089 | 126.9124 | 0 | 18.0511 | 46.2103 | 47.3001 | 20.6822 | 0 | 0 | 0 | 10.355 | 39.5522 | 95.9448 | 183.9155 | 187.3202 | 104.1643 | 39.5522 | 39.5522 | 39.5522 | 89.645 | 39.5522 | 113.9959 | 230.1258 | 234.6203 | 124.8464 | 39.5522 | 39.5522 | 39.5522 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 10 | 6898 | 11.4 | 11.4 | 9.0958 | 9.8123 | 15 | 91 | 91 | 3.4656 | 73.8729 | 21.9421 | 140.9293 | 0 | 0.47027 | 2.6726 | 3.3094 | 2.0076 | 0 | 0 | 0 | 1.1271 | 36.3459 | 36.8684 | 39.3153 | 40.0228 | 38.5764 | 36.3459 | 36.3459 | 36.3459 | 73.8729 | 36.3459 | 37.3387 | 41.9879 | 43.3322 | 40.584 | 36.3459 | 36.3459 | 36.3459 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 11 | 6899 | 11.5 | 11.5 | 9.0958 | 9.8123 | 15 | 93 | 93 | 3.9651 | 101.3443 | 26.7385 | 156.3523 | 0 | 0 | 2.3181 | 3.6582 | 2.8554 | 0.37993 | 0 | 0 | 1.6557 | 50.2511 | 50.2511 | 51.6512 | 52.4606 | 51.9757 | 50.4806 | 50.2511 | 50.2511 | 101.3443 | 50.2511 | 50.2511 | 53.9693 | 56.1188 | 54.8311 | 50.8605 | 50.2511 | 50.2511 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 12 | 6900 | 12.3 | 12.3 | 9.0958 | 9.8123 | 15 | 86 | 86 | 13.2562 | 171.7224 | 29.1814 | 172.9335 | 0 | 0 | 4.7487 | 11.0261 | 10.8446 | 4.3105 | 0 | 0 | 6.2776 | 80.748 | 80.748 | 93.89 | 111.2631 | 110.7608 | 92.6774 | 80.748 | 80.748 | 171.7224 | 80.748 | 80.748 | 98.6387 | 122.2892 | 121.6054 | 96.9879 | 80.748 | 80.748 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 13 | 6901 | 12.8 | 12.8 | 9.0958 | 9.8123 | 15 | 86 | 86 | 21.4384 | 192.5093 | 28.9517 | 189.9189 | 0 | 0 | 2.3026 | 14.7629 | 18.5753 | 11.5065 | 0 | 0 | 10.4907 | 90.3269 | 90.3269 | 94.8575 | 119.3736 | 126.8745 | 112.9664 | 90.3269 | 90.3269 | 192.5093 | 90.3269 | 90.3269 | 97.1601 | 134.1365 | 145.4498 | 124.4729 | 90.3269 | 90.3269 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 14 | 6902 | 11.8 | 11.8 | 9.0958 | 9.8123 | 15 | 90 | 90 | 2.2403 | 84.9608 | 26.0814 | 206.3452 | 0 | 0 | 0 | 1.1267 | 1.931 | 1.6042 | 0.33767 | 0 | 1.0392 | 41.6139 | 41.6139 | 41.6139 | 41.6139 | 41.6139 | 41.6139 | 41.6139 | 41.6139 | 84.9608 | 41.6139 | 41.6139 | 41.6139 | 42.7406 | 43.545 | 43.2182 | 41.9516 | 41.6139 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 15 | 6903 | 11 | 11 | 9.0958 | 9.8123 | 15 | 95 | 95 | 1.285 | 55.4875 | 20.9363 | 221.534 | 0 | 0 | 0 | 0.36916 | 1.0342 | 1.0935 | 0.51217 | 0 | 0.51246 | 26.7521 | 26.7521 | 26.7521 | 26.7521 | 26.7521 | 26.7521 | 26.7521 | 26.7521 | 55.4875 | 26.7521 | 26.7521 | 26.7521 | 27.1213 | 27.7864 | 27.8456 | 27.2643 | 26.7521 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 16 | 6904 | 10.9 | 10.9 | 9.0958 | 9.8123 | 15 | 96 | 96 | 1.4141 | 43.5776 | 14.0476 | 235.3234 | 0 | 0 | 0 | 0.079847 | 0.98865 | 1.3183 | 0.87573 | 0 | 0.4224 | 20.9123 | 20.9123 | 20.9123 | 20.9123 | 20.9123 | 20.9123 | 20.9123 | 20.9123 | 43.5776 | 20.9123 | 20.9123 | 20.9123 | 20.9921 | 21.9009 | 22.2306 | 21.788 | 20.9123 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 17 | 6905 | 10.2 | 10.2 | 9.0958 | 9.8123 | 15 | 96 | 96 | 0.81071 | 18.8619 | 5.9496 | 247.9571 | 0 | 0 | 0 | 0 | 0.44745 | 0.77373 | 0.64677 | 0.14094 | 0.13811 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 18.8619 | 8.8945 | 8.8945 | 8.8945 | 8.8945 | 9.342 | 9.6683 | 9.5413 | 9.0355 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 15 | 18 | 6906 | 10.2 | 10.2 | 9.0958 | 9.8123 | 15 | 96 | 96 | 1.1583 | 2.9739 | -2.89 | 259.8871 | 0 | 0 | 0 | 0 | 0.43237 | 1.0608 | 1.0678 | 0.44935 | 0.026065 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 2.9739 | 1.5896 | 1.5896 | 1.5896 | 1.5896 | 2.022 | 2.6504 | 2.6575 | 2.039 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 19 | 6907 | 9.9 | 9.9 | 9.0958 | 9.8123 | 15 | 97 | 97 | 0 | 0 | -12.0629 | 271.6597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 20 | 6908 | 9.8 | 9.8 | 9.0958 | 9.8123 | 15 | 97 | 97 | 0 | 0 | -21.1766 | 283.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 21 | 6909 | 9.6 | 9.6 | 9.0958 | 9.8123 | 15 | 97 | 97 | 0 | 0 | -29.7895 | 297.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 22 | 6910 | 9.6 | 9.6 | 9.0958 | 9.8123 | 15 | 94 | 94 | 0 | 0 | -37.3342 | 312.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 23 | 6911 | 8.9 | 8.9 | 9.0958 | 9.8123 | 15 | 98 | 98 | 0 | 0 | -43.056 | 330.6428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 15 | 24 | 6912 | 8.8 | 8.8 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -46.0849 | 351.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 1 | 6913 | 7.6 | 7.6 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -45.7963 | 12.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 2 | 6914 | 6.1 | 6.1 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -42.5871 | 32.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 3 | 6915 | 6.1 | 6.1 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -36.466 | 50.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 4 | 6916 | 6.7 | 6.7 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -28.6693 | 65.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 5 | 6917 | 7.2 | 7.2 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -19.9222 | 78.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 6 | 6918 | 6.8 | 6.8 | 10.4292 | 9.74 | 15 | 99 | 99 | 0 | 0 | -10.7654 | 90.6184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 7 | 6919 | 8.6 | 8.6 | 10.4292 | 9.74 | 15 | 96 | 96 | 0 | 0 | -1.6263 | 102.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 16 | 8 | 6920 | 9.7 | 9.7 | 10.4292 | 9.74 | 15 | 89 | 89 | 4.4554 | 13.7615 | 7.1048 | 114.3678 | 0 | 2.4016 | 4.3503 | 3.7506 | 0.95384 | 0 | 0 | 0 | 0.2385 | 6.1123 | 9.5038 | 12.2555 | 11.4087 | 7.4593 | 6.1123 | 6.1123 | 6.1123 | 13.7615 | 6.1123 | 11.9054 | 16.6058 | 15.1592 | 8.4131 | 6.1123 | 6.1123 | 6.1123 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 9 | 6921 | 9.5 | 9.5 | 10.4292 | 9.74 | 15 | 86 | 86 | 212.0864 | 91.1145 | 15.0134 | 127.151 | 0 | 74.1585 | 191.7094 | 196.9595 | 86.8334 | 0 | 0 | 0 | 41.8855 | 46.2669 | 79.4453 | 132.0375 | 134.3864 | 85.1161 | 46.2669 | 46.2669 | 46.2669 | 91.1145 | 46.2669 | 153.6038 | 323.7469 | 331.3459 | 171.9495 | 46.2669 | 46.2669 | 46.2669 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 10 | 6922 | 9.1 | 9.1 | 10.4292 | 9.74 | 15 | 79 | 79 | 61.841 | 144.2253 | 21.6217 | 141.1383 | 0 | 8.1569 | 47.6076 | 59.1705 | 36.072 | 0 | 0 | 0 | 19.7747 | 65.9394 | 81.1792 | 154.8863 | 176.4895 | 133.334 | 65.9394 | 65.9394 | 65.9394 | 144.2253 | 65.9394 | 89.3361 | 202.4939 | 235.6599 | 169.406 | 65.9394 | 65.9394 | 65.9394 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 11 | 6923 | 8.3 | 8.3 | 10.4292 | 9.74 | 15 | 76 | 76 | 15.9161 | 154.4423 | 26.3926 | 156.5131 | 0 | 0 | 9.2838 | 14.7113 | 11.5212 | 1.5821 | 0 | 0 | 6.5577 | 71.0185 | 71.0185 | 101.3767 | 119.1252 | 108.6933 | 76.1921 | 71.0185 | 71.0185 | 154.4423 | 71.0185 | 71.0185 | 110.6605 | 133.8365 | 120.2146 | 77.7742 | 71.0185 | 71.0185 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 12 | 6924 | 8.5 | 8.5 | 10.4292 | 9.74 | 15 | 73 | 73 | 9.0218 | 156.7783 | 28.8157 | 173.0266 | 0 | 0 | 3.2208 | 7.5184 | 7.4119 | 2.9636 | 0 | 0 | 4.2217 | 74.7517 | 74.7517 | 83.9714 | 96.2739 | 95.9689 | 83.2352 | 74.7517 | 74.7517 | 156.7783 | 74.7517 | 74.7517 | 87.1922 | 103.7923 | 103.3808 | 86.1988 | 74.7517 | 74.7517 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 13 | 6925 | 8.8 | 8.8 | 10.4292 | 9.74 | 15 | 73 | 73 | 7.9701 | 157.1448 | 28.5773 | 189.9342 | 0 | 0 | 0.84782 | 5.5008 | 6.9316 | 4.3019 | 0 | 0 | 3.8552 | 76.0825 | 76.0825 | 77.9122 | 87.9543 | 91.042 | 85.3666 | 76.0825 | 76.0825 | 157.1448 | 76.0825 | 76.0825 | 78.76 | 93.4551 | 97.9735 | 89.6685 | 76.0825 | 76.0825 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 14 | 6926 | 9.7 | 9.7 | 10.4292 | 9.74 | 15 | 68 | 68 | 56.8459 | 204.9512 | 25.7103 | 206.2888 | 0 | 0 | 0 | 28.6802 | 49.172 | 40.8595 | 8.6121 | 0 | 26.0488 | 95.3782 | 95.3782 | 95.3782 | 139.3853 | 170.8282 | 158.0735 | 108.5927 | 95.3782 | 204.9512 | 95.3782 | 95.3782 | 95.3782 | 168.0655 | 220.0002 | 198.933 | 117.2048 | 95.3782 | 231 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 15 | 6927 | 9.4 | 9.4 | 10.4292 | 9.74 | 15 | 68 | 68 | 183.9497 | 183.6578 | 20.5764 | 221.4229 | 0 | 0 | 0 | 53.1687 | 148.5968 | 156.9788 | 73.4048 | 0 | 72.3422 | 91.2562 | 91.2562 | 91.2562 | 123.7954 | 182.1972 | 187.327 | 136.1798 | 91.2562 | 183.6578 | 91.2562 | 91.2562 | 91.2562 | 176.9641 | 330.7939 | 344.3058 | 209.5847 | 91.2562 | 256 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 16 | 6928 | 9.8 | 9.8 | 10.4292 | 9.74 | 15 | 64 | 64 | 251.7848 | 132.161 | 13.7016 | 235.1757 | 0 | 0 | 0 | 14.7072 | 176.7555 | 235.2627 | 155.9563 | 0 | 73.839 | 70.8576 | 70.8576 | 70.8576 | 77.6329 | 152.2847 | 179.2376 | 142.703 | 70.8576 | 132.161 | 70.8576 | 70.8576 | 70.8576 | 92.3401 | 329.0401 | 414.5003 | 298.6593 | 70.8576 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 17 | 6929 | 8.9 | 8.9 | 10.4292 | 9.74 | 15 | 65 | 65 | 367.8487 | 67.2911 | 5.6156 | 247.7865 | 0 | 0 | 0 | 0 | 204.0863 | 351.7593 | 293.3764 | 63.1377 | 60.7089 | 40.5456 | 40.5456 | 40.5456 | 40.5456 | 90.074 | 125.9118 | 111.7433 | 55.8681 | 67.2911 | 40.5456 | 40.5456 | 40.5456 | 40.5456 | 294.1603 | 477.6711 | 405.1197 | 119.0057 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 16 | 18 | 6930 | 7.7 | 7.7 | 10.4292 | 9.74 | 15 | 66 | 66 | 26.8937 | 3.9 | -3.216 | 259.7023 | 0 | 0 | 0 | 0 | 10.1186 | 24.6758 | 24.7782 | 10.3659 | 13.1 | 3.5611 | 3.5611 | 3.5611 | 3.5611 | 9.2502 | 17.4349 | 17.4925 | 9.3893 | 3.9 | 3.5611 | 3.5611 | 3.5611 | 3.5611 | 19.3688 | 42.1107 | 42.2707 | 19.7552 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 19 | 6931 | 6.7 | 6.7 | 10.4292 | 9.74 | 15 | 73 | 73 | 0 | 0 | -12.3867 | 271.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 20 | 6932 | 6.2 | 6.2 | 10.4292 | 9.74 | 15 | 73 | 73 | 0 | 0 | -21.5045 | 283.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 21 | 6933 | 5.6 | 5.6 | 10.4292 | 9.74 | 15 | 73 | 73 | 0 | 0 | -30.1281 | 297.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 22 | 6934 | 5.2 | 5.2 | 10.4292 | 9.74 | 15 | 75 | 75 | 0 | 0 | -37.6883 | 312.5159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 23 | 6935 | 4.7 | 4.7 | 10.4292 | 9.74 | 15 | 78 | 78 | 0 | 0 | -43.4254 | 330.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 16 | 24 | 6936 | 4.6 | 4.6 | 7.5625 | 8.9854 | 15 | 77 | 77 | 0 | 0 | -46.4591 | 351.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 1 | 6937 | 4.2 | 4.2 | 7.5625 | 8.9854 | 15 | 79 | 79 | 0 | 0 | -46.1565 | 12.6333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 2 | 6938 | 3.8 | 3.8 | 7.5625 | 8.9854 | 15 | 82 | 82 | 0 | 0 | -42.9169 | 33.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 3 | 6939 | 3.7 | 3.7 | 7.5625 | 8.9854 | 15 | 85 | 85 | 0 | 0 | -36.765 | 50.6479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 4 | 6940 | 3.6 | 3.6 | 7.5625 | 8.9854 | 15 | 87 | 87 | 0 | 0 | -28.9445 | 65.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 5 | 6941 | 3.2 | 3.2 | 7.5625 | 8.9854 | 15 | 90 | 90 | 0 | 0 | -20.1834 | 78.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 6 | 6942 | 3 | 3 | 7.5625 | 8.9854 | 15 | 91 | 91 | 0 | 0 | -11.0226 | 90.8924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 7 | 6943 | 2.9 | 2.9 | 7.5625 | 8.9854 | 15 | 92 | 92 | 0 | 0 | -1.8884 | 102.6314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 17 | 8 | 6944 | 3.5 | 3.5 | 7.5625 | 8.9854 | 15 | 90 | 90 | 172.0789 | 22.6794 | 6.8296 | 114.6202 | 0 | 92.0748 | 167.8229 | 145.2625 | 37.6094 | 0 | 0 | 0 | 8.3206 | 11.7489 | 15.4572 | 18.508 | 17.5993 | 13.2636 | 11.7489 | 11.7489 | 11.7489 | 22.6794 | 11.7489 | 107.532 | 186.3308 | 162.8619 | 50.873 | 11.7489 | 11.7489 | 11.7489 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 9 | 6945 | 5.4 | 5.4 | 7.5625 | 8.9854 | 15 | 84 | 84 | 258.9841 | 86.2314 | 14.7182 | 127.3854 | 0 | 89.5491 | 233.769 | 241.0503 | 107.1275 | 0 | 0 | 0 | 49.7686 | 45.0395 | 77.8323 | 130.6455 | 133.3119 | 84.2695 | 45.0395 | 45.0395 | 45.0395 | 86.2314 | 45.0395 | 167.3813 | 364.4145 | 374.3621 | 191.397 | 45.0395 | 45.0395 | 45.0395 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 10 | 6946 | 7.5 | 7.5 | 7.5625 | 8.9854 | 15 | 76 | 76 | 602.2631 | 93.6987 | 21.3019 | 141.3427 | 0 | 77.1861 | 462.8372 | 577.3645 | 353.6795 | 0 | 0 | 0 | 189.3013 | 63.7146 | 75.8975 | 136.7676 | 154.8442 | 119.5384 | 63.7146 | 63.7146 | 63.7146 | 93.6987 | 63.7146 | 153.0836 | 599.6048 | 732.2088 | 473.218 | 63.7146 | 63.7146 | 63.7146 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 11 | 6947 | 8.9 | 8.9 | 7.5625 | 8.9854 | 15 | 68 | 68 | 725.459 | 97.1214 | 26.0479 | 156.6695 | 0 | 0 | 422.2047 | 671.7578 | 527.8042 | 74.6701 | 0 | 0 | 294.8786 | 77.1575 | 77.1575 | 134.5027 | 168.3977 | 148.8455 | 87.2994 | 77.1575 | 77.1575 | 97.1214 | 77.1575 | 77.1575 | 556.7074 | 840.1555 | 676.6498 | 161.9696 | 77.1575 | 77.1575 | 392 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 12 | 6948 | 9.6 | 9.6 | 7.5625 | 8.9854 | 15 | 62 | 62 | 626.5357 | 132.329 | 28.4519 | 173.1158 | 0 | 0 | 222.9264 | 523.1162 | 516.8716 | 207.8506 | 0 | 0 | 289.671 | 90.8751 | 90.8751 | 130.8756 | 184.7399 | 183.6194 | 128.1705 | 90.8751 | 90.8751 | 132.329 | 90.8751 | 90.8751 | 353.8021 | 707.8561 | 700.491 | 336.0211 | 90.8751 | 90.8751 | 422 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 13 | 6949 | 10.1 | 10.1 | 7.5625 | 8.9854 | 15 | 56 | 56 | 755.697 | 107.7106 | 28.2054 | 189.9465 | 0 | 0 | 79.6395 | 522.7437 | 659.6317 | 410.1165 | 0 | 0 | 361.2894 | 88.3003 | 88.3003 | 98.8117 | 157.2961 | 175.3636 | 142.4306 | 88.3003 | 88.3003 | 107.7106 | 88.3003 | 88.3003 | 178.4512 | 680.0397 | 834.9953 | 552.5471 | 88.3003 | 88.3003 | 469 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 14 | 6950 | 9.6 | 9.6 | 7.5625 | 8.9854 | 15 | 60 | 60 | 254.6942 | 203.7148 | 25.3419 | 206.2304 | 0 | 0 | 0 | 128.9117 | 221.078 | 183.7398 | 38.7693 | 0 | 115.2852 | 103.8704 | 103.8704 | 103.8704 | 178.7137 | 232.2234 | 210.5457 | 126.379 | 103.8704 | 203.7148 | 103.8704 | 103.8704 | 103.8704 | 307.6254 | 453.3014 | 394.2855 | 165.1483 | 103.8704 | 319 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 15 | 6951 | 9.4 | 9.4 | 7.5625 | 8.9854 | 15 | 61 | 61 | 521.0327 | 130.9725 | 20.2195 | 221.3105 | 0 | 0 | 0 | 151.5163 | 422.4029 | 445.8516 | 208.1265 | 0 | 202.0275 | 82.6958 | 82.6958 | 82.6958 | 117.2565 | 179.0455 | 184.3941 | 130.1692 | 82.6958 | 130.9725 | 82.6958 | 82.6958 | 82.6958 | 268.7728 | 601.4484 | 630.2457 | 338.2957 | 82.6958 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 16 | 6952 | 9.6 | 9.6 | 7.5625 | 8.9854 | 15 | 59 | 59 | 270.7175 | 128.077 | 13.3586 | 235.0272 | 0 | 0 | 0 | 16.3468 | 190.8163 | 253.5082 | 167.6984 | 0 | 77.923 | 69.5275 | 69.5275 | 69.5275 | 76.4126 | 149.8975 | 176.3027 | 140.1604 | 69.5275 | 128.077 | 69.5275 | 69.5275 | 69.5275 | 92.7594 | 340.7138 | 429.8109 | 307.8588 | 69.5275 | 206 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 17 | 6953 | 9.1 | 9.1 | 7.5625 | 8.9854 | 15 | 66 | 66 | 135.7194 | 75.3193 | 5.2849 | 247.6151 | 0 | 0 | 0 | 0 | 75.6878 | 130.0303 | 108.2027 | 22.9915 | 21.6807 | 40.2624 | 40.2624 | 40.2624 | 40.2624 | 90.3748 | 126.3545 | 111.9026 | 55.4849 | 75.3193 | 40.2624 | 40.2624 | 40.2624 | 40.2624 | 166.0626 | 256.3847 | 220.1053 | 78.4763 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 17 | 18 | 6954 | 5.9 | 5.9 | 7.5625 | 8.9854 | 15 | 85 | 85 | 52.0532 | 2.805 | -3.5387 | 259.5166 | 0 | 0 | 0 | 0 | 19.739 | 47.8465 | 47.9262 | 19.9314 | 14.195 | 3.2639 | 3.2639 | 3.2639 | 3.2639 | 7.6566 | 13.9115 | 13.9293 | 7.6994 | 2.805 | 3.2639 | 3.2639 | 3.2639 | 3.2639 | 27.3956 | 61.7581 | 61.8555 | 27.6307 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 19 | 6955 | 3.2 | 3.2 | 7.5625 | 8.9854 | 15 | 97 | 97 | 0 | 0 | -12.707 | 271.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 20 | 6956 | 1.6 | 1.6 | 7.5625 | 8.9854 | 15 | 98 | 98 | 0 | 0 | -21.8288 | 283.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 21 | 6957 | 1 | 1 | 7.5625 | 8.9854 | 15 | 99 | 99 | 0 | 0 | -30.4631 | 296.9284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 22 | 6958 | 0.4 | 0.4 | 7.5625 | 8.9854 | 15 | 98 | 98 | 0 | 0 | -38.0391 | 312.3587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 23 | 6959 | -0.1 | -0.1 | 7.5625 | 8.9854 | 15 | 98 | 98 | 0 | 0 | -43.7919 | 330.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 17 | 24 | 6960 | -0.5 | -0.5 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -46.831 | 351.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 1 | 6961 | -1 | -1 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -46.5147 | 12.7792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 2 | 6962 | -1.1 | -1.1 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -43.245 | 33.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 3 | 6963 | -1.2 | -1.2 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -37.0629 | 50.9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 4 | 6964 | -1.3 | -1.3 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -29.2189 | 65.9347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 5 | 6965 | -1.6 | -1.6 | 4.9417 | 7.7979 | 15 | 99 | 99 | 0 | 0 | -20.4441 | 79.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 6 | 6966 | -1.1 | -1.1 | 4.9417 | 7.7979 | 15 | 98 | 98 | 0 | 0 | -11.2794 | 91.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 7 | 6967 | 0.1 | 0.1 | 4.9417 | 7.7979 | 15 | 99 | 99 | 0 | 0 | -2.1504 | 102.8922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 18 | 8 | 6968 | 1.9 | 1.9 | 4.9417 | 7.7979 | 15 | 98 | 98 | 211.747 | 18.0209 | 6.5545 | 114.8687 | 0 | 112.4671 | 206.2638 | 179.2339 | 47.2112 | 0 | 0 | 0 | 14.9791 | 10.2527 | 13.202 | 15.6618 | 14.953 | 11.4907 | 10.2527 | 10.2527 | 10.2527 | 18.0209 | 10.2527 | 125.6692 | 221.9256 | 194.1869 | 58.702 | 10.2527 | 10.2527 | 10.2527 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 9 | 6969 | 5.2 | 5.2 | 4.9417 | 7.7979 | 15 | 88 | 88 | 65.2892 | 84.7995 | 14.4233 | 127.6156 | 0 | 22.3239 | 58.848 | 60.8997 | 27.2773 | 0 | 0 | 0 | 12.2005 | 37.2037 | 97.9319 | 197.2892 | 202.8706 | 111.4066 | 37.2037 | 37.2037 | 37.2037 | 84.7995 | 37.2037 | 120.2557 | 256.1371 | 263.7703 | 138.6839 | 37.2037 | 37.2037 | 37.2037 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 10 | 6970 | 6.9 | 6.9 | 4.9417 | 7.7979 | 15 | 82 | 82 | 8.9028 | 103.2501 | 20.9828 | 141.5427 | 0 | 1.1082 | 6.8298 | 8.5507 | 5.2626 | 0 | 0 | 0 | 2.7499 | 47.311 | 53.3744 | 84.6806 | 94.0962 | 76.1057 | 47.311 | 47.311 | 47.311 | 103.2501 | 47.311 | 54.4826 | 91.5104 | 102.6469 | 81.3683 | 47.311 | 47.311 | 47.311 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 11 | 6971 | 8.9 | 8.9 | 4.9417 | 7.7979 | 15 | 69 | 69 | 217.8685 | 184.6473 | 25.7046 | 156.8213 | 0 | 0 | 126.5141 | 202.0964 | 159.2933 | 23.1784 | 0 | 0 | 87.3527 | 91.3231 | 91.3231 | 170.9476 | 218.5171 | 191.578 | 105.911 | 91.3231 | 91.3231 | 184.6473 | 91.3231 | 91.3231 | 297.4617 | 420.6134 | 350.8713 | 129.0894 | 91.3231 | 91.3231 | 272 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 12 | 6972 | 10.3 | 10.3 | 4.9417 | 7.7979 | 15 | 65 | 65 | 494.0147 | 160.3598 | 28.09 | 173.201 | 0 | 0 | 175.2024 | 413.2337 | 409.1983 | 165.4601 | 0 | 0 | 225.6402 | 97.1133 | 97.1133 | 144.1212 | 207.9865 | 206.9038 | 141.5073 | 97.1133 | 97.1133 | 160.3598 | 97.1133 | 97.1133 | 319.3236 | 621.2202 | 616.1022 | 306.9675 | 97.1133 | 97.1133 | 386 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 13 | 6973 | 11.4 | 11.4 | 4.9417 | 7.7979 | 15 | 65 | 65 | 714.3992 | 115.46 | 27.8359 | 189.9559 | 0 | 0 | 74.6127 | 495.2787 | 625.8171 | 389.7603 | 0 | 0 | 337.54 | 89.1218 | 89.1218 | 100.0181 | 161.4512 | 180.5147 | 146.0415 | 89.1218 | 89.1218 | 115.46 | 89.1218 | 89.1218 | 174.6308 | 656.7299 | 806.3318 | 535.8019 | 89.1218 | 89.1218 | 453 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 14 | 6974 | 11.8 | 11.8 | 4.9417 | 7.7979 | 15 | 65 | 65 | 217.0182 | 205.9793 | 24.9764 | 206.1701 | 0 | 0 | 0 | 110.1941 | 189.0169 | 157.1161 | 33.1789 | 0 | 97.0207 | 102.6402 | 102.6402 | 102.6402 | 165.2306 | 210.002 | 191.8823 | 121.4858 | 102.6402 | 205.9793 | 102.6402 | 102.6402 | 102.6402 | 275.4247 | 399.0189 | 348.9984 | 154.6647 | 102.6402 | 303 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 15 | 6975 | 12.1 | 12.1 | 4.9417 | 7.7979 | 15 | 61 | 61 | 449.3574 | 142.2399 | 19.8656 | 221.197 | 0 | 0 | 0 | 131.4711 | 365.578 | 385.5343 | 179.6498 | 0 | 171.7601 | 84.4083 | 84.4083 | 84.4083 | 120.8714 | 185.8002 | 191.335 | 134.2336 | 84.4083 | 142.2399 | 84.4083 | 84.4083 | 84.4083 | 252.3425 | 551.3782 | 576.8692 | 313.8834 | 84.4083 | 314 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 16 | 6976 | 11.1 | 11.1 | 4.9417 | 7.7979 | 15 | 68 | 68 | 5.3515 | 79.4885 | 13.0189 | 234.8778 | 0 | 0 | 0 | 0.33382 | 3.7871 | 5.022 | 3.315 | 0 | 1.5115 | 39.3403 | 39.3403 | 39.3403 | 39.3403 | 39.3403 | 39.3403 | 39.3403 | 39.3403 | 79.4885 | 39.3403 | 39.3403 | 39.3403 | 39.6742 | 43.1275 | 44.3623 | 42.6554 | 39.3403 | 81 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 17 | 6977 | 10.9 | 10.9 | 4.9417 | 7.7979 | 15 | 70 | 70 | 2.1375 | 27.6698 | 4.9576 | 247.4428 | 0 | 0 | 0 | 0 | 1.1982 | 2.0517 | 1.7034 | 0.35726 | 0.33021 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 27.6698 | 13.2107 | 13.2107 | 13.2107 | 13.2107 | 14.4089 | 15.2625 | 14.9141 | 13.568 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 18 | 18 | 6978 | 9.8 | 9.8 | 4.9417 | 7.7979 | 15 | 82 | 82 | 23.5989 | 2.8328 | -3.8578 | 259.3299 | 0 | 0 | 0 | 0 | 9.0188 | 21.73 | 21.712 | 8.9755 | 0.16721 | 1.7332 | 1.7332 | 1.7332 | 1.7332 | 7.171 | 14.8352 | 14.8244 | 7.1449 | 2.8328 | 1.7332 | 1.7332 | 1.7332 | 1.7332 | 16.1899 | 36.5652 | 36.5364 | 16.1204 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 19 | 6979 | 9.9 | 9.9 | 4.9417 | 7.7979 | 15 | 81 | 81 | 0 | 0 | -13.0236 | 271.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 20 | 6980 | 9.6 | 9.6 | 4.9417 | 7.7979 | 15 | 84 | 84 | 0 | 0 | -22.1495 | 283.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 21 | 6981 | 9.5 | 9.5 | 4.9417 | 7.7979 | 15 | 84 | 84 | 0 | 0 | -30.7944 | 296.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 22 | 6982 | 9.8 | 9.8 | 4.9417 | 7.7979 | 15 | 86 | 86 | 0 | 0 | -38.3865 | 312.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 23 | 6983 | 9.8 | 9.8 | 4.9417 | 7.7979 | 15 | 93 | 93 | 0 | 0 | -44.1553 | 330.3752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 18 | 24 | 6984 | 9.8 | 9.8 | 6.3125 | 7.3361 | 15 | 93 | 93 | 0 | 0 | -47.2003 | 351.1576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 1 | 6985 | 9.8 | 9.8 | 6.3125 | 7.3361 | 15 | 92 | 92 | 0 | 0 | -46.871 | 12.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 2 | 6986 | 10 | 10 | 6.3125 | 7.3361 | 15 | 92 | 92 | 0 | 0 | -43.5715 | 33.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 3 | 6987 | 9.9 | 9.9 | 6.3125 | 7.3361 | 15 | 95 | 95 | 0 | 0 | -37.3594 | 51.1929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 4 | 6988 | 9.6 | 9.6 | 6.3125 | 7.3361 | 15 | 97 | 97 | 0 | 0 | -29.4923 | 66.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 5 | 6989 | 8.4 | 8.4 | 6.3125 | 7.3361 | 15 | 99 | 99 | 0 | 0 | -20.7043 | 79.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 6 | 6990 | 8.1 | 8.1 | 6.3125 | 7.3361 | 15 | 98 | 98 | 0 | 0 | -11.536 | 91.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 7 | 6991 | 8.2 | 8.2 | 6.3125 | 7.3361 | 15 | 99 | 99 | 0 | 0 | -2.4122 | 103.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 19 | 8 | 6992 | 7.9 | 7.9 | 6.3125 | 7.3361 | 15 | 97 | 97 | 2.8687 | 7.8907 | 6.2797 | 115.1132 | 0 | 1.5125 | 2.791 | 2.4346 | 0.65202 | 0 | 0 | 0 | 0.10927 | 3.5107 | 5.4071 | 7.0101 | 6.5632 | 4.3282 | 3.5107 | 3.5107 | 3.5107 | 7.8907 | 3.5107 | 6.9195 | 9.8011 | 8.9978 | 4.9802 | 3.5107 | 3.5107 | 3.5107 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 9 | 6993 | 8.9 | 8.9 | 6.3125 | 7.3361 | 15 | 95 | 95 | 20.7865 | 71.2253 | 14.1288 | 127.8414 | 0 | 7.0283 | 18.7086 | 19.4296 | 8.769 | 0 | 0 | 0 | 3.7747 | 31.7309 | 76.7304 | 151.5142 | 156.1305 | 87.8752 | 31.7309 | 31.7309 | 31.7309 | 71.2253 | 31.7309 | 83.7588 | 170.2228 | 175.5601 | 96.6442 | 31.7309 | 31.7309 | 31.7309 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 10 | 6994 | 10.9 | 10.9 | 6.3125 | 7.3361 | 15 | 90 | 90 | 161.9355 | 142.8562 | 20.6645 | 141.7379 | 0 | 19.5694 | 124.0139 | 155.8127 | 96.3386 | 0 | 0 | 0 | 49.1438 | 68.4586 | 86.1802 | 180.7626 | 209.5589 | 155.7006 | 68.4586 | 68.4586 | 68.4586 | 142.8562 | 68.4586 | 105.7495 | 304.7765 | 365.3716 | 252.0392 | 68.4586 | 68.4586 | 68.4586 | 192 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 11 | 6995 | 12 | 12 | 6.3125 | 7.3361 | 15 | 78 | 78 | 556.2223 | 127.0519 | 25.3626 | 156.9686 | 0 | 0 | 322.2851 | 516.8419 | 408.6397 | 61.062 | 0 | 0 | 219.9481 | 82.997 | 82.997 | 151.0961 | 192.206 | 169.3428 | 95.8994 | 82.997 | 82.997 | 127.0519 | 82.997 | 82.997 | 473.3811 | 709.0479 | 577.9826 | 156.9614 | 82.997 | 82.997 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 12 | 6996 | 12.1 | 12.1 | 6.3125 | 7.3361 | 15 | 74 | 74 | 155.9998 | 212.6167 | 27.7302 | 173.2823 | 0 | 0 | 55.1501 | 130.7283 | 129.7277 | 52.7343 | 0 | 0 | 70.3833 | 101.5525 | 101.5525 | 150.8769 | 218.4717 | 217.5767 | 148.7163 | 101.5525 | 101.5525 | 212.6167 | 101.5525 | 101.5525 | 206.027 | 349.2 | 347.3044 | 201.4507 | 101.5525 | 101.5525 | 283 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 13 | 6997 | 10.7 | 10.7 | 6.3125 | 7.3361 | 15 | 82 | 82 | 32.7411 | 195.7135 | 27.469 | 189.9623 | 0 | 0 | 3.3901 | 22.7489 | 28.7817 | 17.9546 | 0 | 0 | 15.2865 | 90.5622 | 90.5622 | 99.1719 | 148.3365 | 163.6577 | 136.1606 | 90.5622 | 90.5622 | 195.7135 | 90.5622 | 90.5622 | 102.562 | 171.0854 | 192.4394 | 154.1151 | 90.5622 | 90.5622 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 14 | 6998 | 10.8 | 10.8 | 6.3125 | 7.3361 | 15 | 78 | 78 | 55.7894 | 197.369 | 24.6139 | 206.1078 | 0 | 0 | 0 | 28.4185 | 48.7533 | 40.5291 | 8.5635 | 0 | 24.631 | 92.0496 | 92.0496 | 92.0496 | 135.5502 | 166.6769 | 154.088 | 105.1579 | 92.0496 | 197.369 | 92.0496 | 92.0496 | 92.0496 | 163.9687 | 215.4302 | 194.6171 | 113.7214 | 92.0496 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 15 | 6999 | 9.9 | 9.9 | 6.3125 | 7.3361 | 15 | 84 | 84 | 8.5552 | 124.7769 | 19.515 | 221.0822 | 0 | 0 | 0 | 2.5184 | 6.9843 | 7.3589 | 3.4227 | 0 | 3.2231 | 61.1695 | 61.1695 | 61.1695 | 63.9032 | 68.751 | 69.1576 | 64.8849 | 61.1695 | 124.7769 | 61.1695 | 61.1695 | 61.1695 | 66.4216 | 75.7352 | 76.5164 | 68.3077 | 61.1695 | 128 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 16 | 7000 | 8.7 | 8.7 | 6.3125 | 7.3361 | 15 | 90 | 90 | 1.4944 | 41.586 | 12.6825 | 234.7274 | 0 | 0 | 0 | 0.096242 | 1.0617 | 1.4053 | 0.92564 | 0 | 0.41404 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 19.9497 | 41.586 | 19.9497 | 19.9497 | 19.9497 | 20.0459 | 21.0114 | 21.355 | 20.8753 | 19.9497 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 17 | 7001 | 8.7 | 8.7 | 6.3125 | 7.3361 | 15 | 92 | 92 | 3.7839 | 35.4353 | 4.6338 | 247.2697 | 0 | 0 | 0 | 0 | 2.1317 | 3.6385 | 3.0138 | 0.62373 | 0.56471 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 35.4353 | 17.1032 | 17.1032 | 17.1032 | 17.1032 | 19.2349 | 20.7417 | 20.117 | 17.7269 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 19 | 18 | 7002 | 8.7 | 8.7 | 6.3125 | 7.3361 | 15 | 92 | 92 | 3.7973 | 0.495 | -4.1734 | 259.1422 | 0 | 0 | 0 | 0 | 1.4625 | 3.5026 | 3.4909 | 1.4343 | 2.505 | 0.54031 | 0.54031 | 0.54031 | 0.54031 | 1.3915 | 2.5788 | 2.572 | 1.3751 | 0.495 | 0.54031 | 0.54031 | 0.54031 | 0.54031 | 2.8539 | 6.0814 | 6.0629 | 2.8094 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 19 | 7003 | 7.9 | 7.9 | 6.3125 | 7.3361 | 15 | 94 | 94 | 0 | 0 | -13.3365 | 270.8805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 20 | 7004 | 7.5 | 7.5 | 6.3125 | 7.3361 | 15 | 97 | 97 | 0 | 0 | -22.4663 | 283.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 21 | 7005 | 7.5 | 7.5 | 6.3125 | 7.3361 | 15 | 97 | 97 | 0 | 0 | -31.122 | 296.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 22 | 7006 | 7.4 | 7.4 | 6.3125 | 7.3361 | 15 | 96 | 96 | 0 | 0 | -38.7302 | 312.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 23 | 7007 | 7.3 | 7.3 | 6.3125 | 7.3361 | 15 | 98 | 98 | 0 | 0 | -44.5156 | 330.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 19 | 24 | 7008 | 6.8 | 6.8 | 9.0708 | 7.7498 | 15 | 99 | 99 | 0 | 0 | -47.5671 | 351.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 1 | 7009 | 7.1 | 7.1 | 9.0708 | 7.7498 | 15 | 97 | 97 | 0 | 0 | -47.2251 | 13.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 2 | 7010 | 6.5 | 6.5 | 9.0708 | 7.7498 | 15 | 99 | 99 | 0 | 0 | -43.8962 | 33.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 3 | 7011 | 7 | 7 | 9.0708 | 7.7498 | 15 | 95 | 95 | 0 | 0 | -37.6546 | 51.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 4 | 7012 | 7.1 | 7.1 | 9.0708 | 7.7498 | 15 | 95 | 95 | 0 | 0 | -29.7649 | 66.4931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 5 | 7013 | 6.7 | 6.7 | 9.0708 | 7.7498 | 15 | 97 | 97 | 0 | 0 | -20.9639 | 79.6282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 6 | 7014 | 6.6 | 6.6 | 9.0708 | 7.7498 | 15 | 97 | 97 | 0 | 0 | -11.7923 | 91.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 7 | 7015 | 6.3 | 6.3 | 9.0708 | 7.7498 | 15 | 95 | 95 | 0 | 0 | -2.6738 | 103.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 20 | 8 | 7016 | 6.3 | 6.3 | 9.0708 | 7.7498 | 15 | 88 | 88 | 3.8183 | 7.874 | 6.005 | 115.3537 | 0 | 1.9984 | 3.7102 | 3.2487 | 0.88411 | 0 | 0 | 0 | 0.12603 | 3.5049 | 5.3834 | 6.9925 | 6.5587 | 4.336 | 3.5049 | 3.5049 | 3.5049 | 7.874 | 3.5049 | 7.3818 | 10.7028 | 9.8074 | 5.2201 | 3.5049 | 3.5049 | 3.5049 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 9 | 7017 | 7.5 | 7.5 | 9.0708 | 7.7498 | 15 | 84 | 84 | 73.8836 | 80.9707 | 13.8348 | 128.0628 | 0 | 24.7043 | 66.4009 | 69.2008 | 31.4637 | 0 | 0 | 0 | 13.0293 | 35.3889 | 98.9853 | 206.3249 | 213.5325 | 116.386 | 35.3889 | 35.3889 | 35.3889 | 80.9707 | 35.3889 | 123.6896 | 272.7258 | 282.7332 | 147.8497 | 35.3889 | 35.3889 | 35.3889 | 94 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 10 | 7018 | 7.9 | 7.9 | 9.0708 | 7.7498 | 15 | 82 | 82 | 61.5546 | 134.6509 | 20.3472 | 141.9285 | 0 | 7.219 | 47.0582 | 59.3313 | 36.849 | 0 | 0 | 0 | 18.3491 | 61.5993 | 75.161 | 150.003 | 173.0593 | 130.8239 | 61.5993 | 61.5993 | 61.5993 | 134.6509 | 61.5993 | 82.38 | 197.0612 | 232.3907 | 167.6729 | 61.5993 | 61.5993 | 61.5993 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 11 | 7019 | 8.4 | 8.4 | 9.0708 | 7.7498 | 15 | 72 | 72 | 594.8966 | 118.0243 | 25.0221 | 157.1112 | 0 | 0 | 343.9498 | 553.7036 | 439.1054 | 67.2852 | 0 | 0 | 231.9757 | 80.4004 | 80.4004 | 146.0926 | 186.1543 | 164.2668 | 93.2514 | 80.4004 | 80.4004 | 118.0243 | 80.4004 | 80.4004 | 490.0424 | 739.8579 | 603.3722 | 160.5366 | 80.4004 | 80.4004 | 350 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 12 | 7020 | 9 | 9 | 9.0708 | 7.7498 | 15 | 75 | 75 | 83.9537 | 206.5884 | 27.3726 | 173.3595 | 0 | 0 | 29.5885 | 70.4793 | 70.0843 | 28.6348 | 0 | 0 | 37.4116 | 95.8327 | 95.8327 | 132.7268 | 183.7137 | 183.2211 | 131.5376 | 95.8327 | 95.8327 | 206.5884 | 95.8327 | 95.8327 | 162.3154 | 254.193 | 253.3054 | 160.1724 | 95.8327 | 95.8327 | 244 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 13 | 7021 | 8.1 | 8.1 | 9.0708 | 7.7498 | 15 | 82 | 82 | 181.9056 | 216.0834 | 27.1049 | 189.9657 | 0 | 0 | 18.6803 | 126.6677 | 160.4548 | 100.2498 | 0 | 0 | 83.9166 | 104.8914 | 104.8914 | 118.5944 | 197.8092 | 222.5939 | 178.4302 | 104.8914 | 104.8914 | 216.0834 | 104.8914 | 104.8914 | 137.2747 | 324.4768 | 383.0488 | 278.6799 | 104.8914 | 104.8914 | 300 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 14 | 7022 | 7.3 | 7.3 | 9.0708 | 7.7498 | 15 | 77 | 77 | 35.2412 | 184.6363 | 24.2545 | 206.0436 | 0 | 0 | 0 | 18.0089 | 30.8974 | 25.6867 | 5.429 | 0 | 15.3637 | 86.134 | 86.134 | 86.134 | 125.4545 | 153.5952 | 142.2181 | 97.9877 | 86.134 | 184.6363 | 86.134 | 86.134 | 86.134 | 143.4634 | 184.4927 | 167.9048 | 103.4167 | 86.134 | 200 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 15 | 7023 | 6.5 | 6.5 | 9.0708 | 7.7498 | 15 | 83 | 83 | 72.281 | 170.1637 | 19.1678 | 220.9661 | 0 | 0 | 0 | 21.4078 | 59.2092 | 62.3267 | 28.934 | 0 | 26.8363 | 80.8358 | 80.8358 | 80.8358 | 103.43 | 143.3263 | 146.6166 | 111.3733 | 80.8358 | 170.1637 | 80.8358 | 80.8358 | 80.8358 | 124.8378 | 202.5355 | 208.9432 | 140.3073 | 80.8358 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 16 | 7024 | 7.2 | 7.2 | 9.0708 | 7.7498 | 15 | 84 | 84 | 95.7466 | 126.9854 | 12.3497 | 234.5762 | 0 | 0 | 0 | 6.3621 | 68.2899 | 90.2145 | 59.2926 | 0 | 26.0146 | 62.7897 | 62.7897 | 62.7897 | 68.6461 | 125.6515 | 145.8333 | 117.3693 | 62.7897 | 126.9854 | 62.7897 | 62.7897 | 62.7897 | 75.0081 | 193.9414 | 236.0478 | 176.662 | 62.7897 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 17 | 7025 | 5.9 | 5.9 | 9.0708 | 7.7498 | 15 | 86 | 86 | 54.0878 | 64.2096 | 4.3136 | 247.0958 | 0 | 0 | 0 | 0 | 30.6249 | 52.1 | 43.0556 | 8.7898 | 7.7904 | 32.8976 | 32.8976 | 32.8976 | 32.8976 | 62.9857 | 84.0844 | 75.1985 | 41.5333 | 64.2096 | 32.8976 | 32.8976 | 32.8976 | 32.8976 | 93.6107 | 136.1844 | 118.254 | 50.3231 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 18 | 7026 | 4.5 | 4.5 | 9.0708 | 7.7498 | 15 | 93 | 93 | 0 | 6 | -4.4851 | 258.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 6 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 2.8015 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 19 | 7027 | 4 | 4 | 9.0708 | 7.7498 | 15 | 97 | 97 | 0 | 0 | -13.6455 | 270.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 20 | 7028 | 4.7 | 4.7 | 9.0708 | 7.7498 | 15 | 88 | 88 | 0 | 0 | -22.7792 | 282.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 21 | 7029 | 3.9 | 3.9 | 9.0708 | 7.7498 | 15 | 96 | 96 | 0 | 0 | -31.4456 | 296.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 22 | 7030 | 4.6 | 4.6 | 9.0708 | 7.7498 | 15 | 91 | 91 | 0 | 0 | -39.0702 | 311.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 23 | 7031 | 4.9 | 4.9 | 9.0708 | 7.7498 | 15 | 87 | 87 | 0 | 0 | -44.8726 | 330.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 20 | 24 | 7032 | 4 | 4 | 6.3333 | 7.3214 | 15 | 94 | 94 | 0 | 0 | -47.9311 | 351.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 1 | 7033 | 3.6 | 3.6 | 6.3333 | 7.3214 | 15 | 97 | 97 | 0 | 0 | -47.5771 | 13.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 2 | 7034 | 4.3 | 4.3 | 6.3333 | 7.3214 | 15 | 91 | 91 | 0 | 0 | -44.2192 | 33.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 3 | 7035 | 3 | 3 | 6.3333 | 7.3214 | 15 | 99 | 99 | 0 | 0 | -37.9485 | 51.7275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 4 | 7036 | 4.5 | 4.5 | 6.3333 | 7.3214 | 15 | 89 | 89 | 0 | 0 | -30.0365 | 66.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 5 | 7037 | 4.6 | 4.6 | 6.3333 | 7.3214 | 15 | 84 | 84 | 0 | 0 | -21.2229 | 79.8981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 6 | 7038 | 4.4 | 4.4 | 6.3333 | 7.3214 | 15 | 81 | 81 | 0 | 0 | -12.0482 | 91.9555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 7 | 7039 | 4.9 | 4.9 | 6.3333 | 7.3214 | 15 | 80 | 80 | 0 | 0 | -2.9352 | 103.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 21 | 8 | 7040 | 6 | 6 | 6.3333 | 7.3214 | 15 | 80 | 80 | 0.74799 | 2.9791 | 5.7307 | 115.59 | 0 | 0.38861 | 0.7259 | 0.63797 | 0.17632 | 0 | 0 | 0 | 0.020912 | 1.3261 | 2.0299 | 2.6407 | 2.4814 | 1.6454 | 1.3261 | 1.3261 | 1.3261 | 2.9791 | 1.3261 | 2.4185 | 3.3666 | 3.1194 | 1.8218 | 1.3261 | 1.3261 | 1.3261 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 9 | 7041 | 6.9 | 6.9 | 6.3333 | 7.3214 | 15 | 79 | 79 | 2.8747 | 35.508 | 13.5414 | 128.2796 | 0 | 0.95056 | 2.5797 | 2.6977 | 1.2354 | 0 | 0 | 0 | 0.49195 | 16.8548 | 23.4662 | 34.7975 | 35.6183 | 25.4477 | 16.8548 | 16.8548 | 16.8548 | 35.508 | 16.8548 | 24.4167 | 37.3773 | 38.3161 | 26.6831 | 16.8548 | 16.8548 | 16.8548 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 10 | 7042 | 9.5 | 9.5 | 6.3333 | 7.3214 | 15 | 69 | 69 | 209.6851 | 135.6176 | 20.0308 | 142.1144 | 0 | 23.8561 | 160.0264 | 202.4554 | 126.2887 | 0 | 0 | 0 | 61.3824 | 66.757 | 82.9876 | 175.6311 | 204.4977 | 152.6776 | 66.757 | 66.757 | 66.757 | 135.6176 | 66.757 | 106.8437 | 335.6575 | 406.953 | 278.9664 | 66.757 | 66.757 | 66.757 | 197 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 11 | 7043 | 10.3 | 10.3 | 6.3333 | 7.3214 | 15 | 60 | 60 | 704.7093 | 96.0553 | 24.6832 | 157.2492 | 0 | 0 | 406.5753 | 656.983 | 522.539 | 81.9988 | 0 | 0 | 270.9447 | 74.2037 | 74.2037 | 131.1661 | 166.249 | 147.413 | 85.6919 | 74.2037 | 74.2037 | 96.0553 | 74.2037 | 74.2037 | 537.7414 | 823.2321 | 669.952 | 167.6907 | 74.2037 | 74.2037 | 367 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 12 | 7044 | 11 | 11 | 6.3333 | 7.3214 | 15 | 57 | 57 | 532.001 | 146.8711 | 27.0173 | 173.4327 | 0 | 0 | 186.9389 | 447.4015 | 445.7823 | 183.0299 | 0 | 0 | 234.1289 | 92.577 | 92.577 | 137.1276 | 199.2001 | 198.8142 | 136.1961 | 92.577 | 92.577 | 146.8711 | 92.577 | 92.577 | 324.0665 | 646.6016 | 644.5966 | 319.226 | 92.577 | 92.577 | 381 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 13 | 7045 | 11.2 | 11.2 | 6.3333 | 7.3214 | 15 | 55 | 55 | 708.6325 | 113.0267 | 26.7437 | 189.9661 | 0 | 0 | 72.2023 | 494.5215 | 627.1567 | 392.412 | 0 | 0 | 322.9733 | 86.7097 | 86.7097 | 97.2732 | 159.0601 | 178.4652 | 144.1211 | 86.7097 | 86.7097 | 113.0267 | 86.7097 | 86.7097 | 169.4755 | 653.5816 | 805.6219 | 536.5331 | 86.7097 | 86.7097 | 436 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 14 | 7046 | 11 | 11 | 6.3333 | 7.3214 | 15 | 54 | 54 | 493.2577 | 151.6829 | 23.8983 | 205.9773 | 0 | 0 | 0 | 252.8699 | 433.8463 | 360.6814 | 76.2343 | 0 | 212.3171 | 92.2211 | 92.2211 | 92.2211 | 158.4376 | 205.828 | 186.6691 | 112.1838 | 92.2211 | 151.6829 | 92.2211 | 92.2211 | 92.2211 | 411.3075 | 639.6743 | 547.3505 | 188.4181 | 92.2211 | 364 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 15 | 7047 | 10.6 | 10.6 | 6.3333 | 7.3214 | 15 | 55 | 55 | 253.7671 | 165.1635 | 18.824 | 220.8487 | 0 | 0 | 0 | 75.6221 | 208.57 | 219.3404 | 101.6242 | 0 | 92.8365 | 86.4948 | 86.4948 | 86.4948 | 125.5739 | 194.2773 | 199.8431 | 139.011 | 86.4948 | 165.1635 | 86.4948 | 86.4948 | 86.4948 | 201.1961 | 402.8473 | 419.1835 | 240.6352 | 86.4948 | 258 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 16 | 7048 | 11.1 | 11.1 | 6.3333 | 7.3214 | 15 | 53 | 53 | 394.1664 | 106.0036 | 12.0204 | 234.424 | 0 | 0 | 0 | 27.0074 | 282.2153 | 372.1053 | 244.021 | 0 | 104.9964 | 62.5184 | 62.5184 | 62.5184 | 69.9294 | 139.9594 | 164.6255 | 129.4787 | 62.5184 | 106.0036 | 62.5184 | 62.5184 | 62.5184 | 96.9368 | 422.1747 | 536.7308 | 373.4998 | 62.5184 | 211 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 17 | 7049 | 9.9 | 9.9 | 6.3333 | 7.3214 | 15 | 63 | 63 | 446.7282 | 51.9696 | 3.9972 | 246.921 | 0 | 0 | 0 | 0 | 254.1997 | 431.0359 | 355.3771 | 71.5432 | 62.0304 | 33.3133 | 33.3133 | 33.3133 | 33.3133 | 79.7105 | 111.9871 | 98.1777 | 46.3716 | 51.9696 | 33.3133 | 33.3133 | 33.3133 | 33.3133 | 333.9102 | 543.023 | 453.5548 | 117.9148 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 18 | 7050 | 8.7 | 8.7 | 6.3333 | 7.3214 | 15 | 70 | 70 | 0 | 8 | -4.793 | 258.7639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 8 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 3.7656 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 19 | 7051 | 8.3 | 8.3 | 6.3333 | 7.3214 | 15 | 72 | 72 | 0 | 0 | -13.9506 | 270.4832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 20 | 7052 | 8.3 | 8.3 | 6.3333 | 7.3214 | 15 | 73 | 73 | 0 | 0 | -23.0879 | 282.6994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 21 | 7053 | 8.1 | 8.1 | 6.3333 | 7.3214 | 15 | 74 | 74 | 0 | 0 | -31.7651 | 296.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 22 | 7054 | 7.7 | 7.7 | 6.3333 | 7.3214 | 15 | 76 | 76 | 0 | 0 | -39.4063 | 311.6955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 23 | 7055 | 7.8 | 7.8 | 6.3333 | 7.3214 | 15 | 77 | 77 | 0 | 0 | -45.2261 | 330.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 21 | 24 | 7056 | 8 | 8 | 7.6542 | 7.2765 | 15 | 78 | 78 | 0 | 0 | -48.2923 | 351.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 1 | 7057 | 8 | 8 | 7.6542 | 7.2765 | 15 | 81 | 81 | 0 | 0 | -47.9269 | 13.3353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 2 | 7058 | 8.2 | 8.2 | 7.6542 | 7.2765 | 15 | 81 | 81 | 0 | 0 | -44.5402 | 34.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 3 | 7059 | 8.2 | 8.2 | 7.6542 | 7.2765 | 15 | 84 | 84 | 0 | 0 | -38.2409 | 51.9906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 4 | 7060 | 8.1 | 8.1 | 7.6542 | 7.2765 | 15 | 86 | 86 | 0 | 0 | -30.3071 | 67.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 5 | 7061 | 8.2 | 8.2 | 7.6542 | 7.2765 | 15 | 86 | 86 | 0 | 0 | -21.4813 | 80.1646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 6 | 7062 | 8 | 8 | 7.6542 | 7.2765 | 15 | 88 | 88 | 0 | 0 | -12.3037 | 92.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 7 | 7063 | 7.7 | 7.7 | 7.6542 | 7.2765 | 15 | 88 | 88 | 0 | 0 | -3.1962 | 103.8985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 22 | 8 | 7064 | 7.7 | 7.7 | 7.6542 | 7.2765 | 15 | 88 | 88 | 9.4205 | 7.7838 | 5.4568 | 115.822 | 0 | 4.8586 | 9.1304 | 8.0538 | 2.2593 | 0 | 0 | 0 | 0.21616 | 2.813 | 6.9159 | 10.5233 | 9.6141 | 4.7209 | 2.813 | 2.813 | 2.813 | 7.7838 | 2.813 | 11.7746 | 19.6537 | 17.6678 | 6.9802 | 2.813 | 2.813 | 2.813 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 9 | 7065 | 8.1 | 8.1 | 7.6542 | 7.2765 | 15 | 88 | 88 | 4.1588 | 41.3098 | 13.2486 | 128.4918 | 0 | 1.36 | 3.7266 | 3.9102 | 1.8033 | 0 | 0 | 0 | 0.69016 | 18.8478 | 34.7556 | 62.4377 | 64.5854 | 39.9407 | 18.8478 | 18.8478 | 18.8478 | 41.3098 | 18.8478 | 36.1156 | 66.1643 | 68.4957 | 41.744 | 18.8478 | 18.8478 | 18.8478 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 10 | 7066 | 9.2 | 9.2 | 7.6542 | 7.2765 | 15 | 84 | 84 | 20.9161 | 112.9886 | 19.7156 | 142.2954 | 0 | 2.3076 | 15.9353 | 20.2282 | 12.6718 | 0 | 0 | 0 | 6.0114 | 49.7992 | 59.4098 | 116.1653 | 134.0444 | 102.5738 | 49.7992 | 49.7992 | 49.7992 | 112.9886 | 49.7992 | 61.7175 | 132.1005 | 154.2726 | 115.2455 | 49.7992 | 49.7992 | 49.7992 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 11 | 7067 | 10.1 | 10.1 | 7.6542 | 7.2765 | 15 | 82 | 82 | 128.9406 | 179.1267 | 24.3461 | 157.3826 | 0 | 0 | 74.2361 | 120.3993 | 96.0343 | 15.4137 | 0 | 0 | 48.8733 | 84.8681 | 84.8681 | 165.4133 | 215.4998 | 189.0641 | 101.5917 | 84.8681 | 84.8681 | 179.1267 | 84.8681 | 84.8681 | 239.6494 | 335.8992 | 285.0984 | 117.0054 | 84.8681 | 84.8681 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 12 | 7068 | 10.5 | 10.5 | 7.6542 | 7.2765 | 15 | 82 | 82 | 268.5259 | 194.303 | 26.6643 | 173.5018 | 0 | 0 | 94.0851 | 226.2151 | 225.8314 | 93.1587 | 0 | 0 | 116.697 | 100.4087 | 100.4087 | 151.141 | 222.3878 | 222.1809 | 150.6415 | 100.4087 | 100.4087 | 194.303 | 100.4087 | 100.4087 | 245.2262 | 448.603 | 448.0123 | 243.8002 | 100.4087 | 100.4087 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 13 | 7069 | 11.9 | 11.9 | 7.6542 | 7.2765 | 15 | 74 | 74 | 218.0502 | 207.8243 | 26.3854 | 189.9635 | 0 | 0 | 22.0528 | 152.4958 | 193.6088 | 121.3084 | 0 | 0 | 98.1757 | 103.1262 | 103.1262 | 116.1961 | 193.505 | 217.8712 | 175.0213 | 103.1262 | 103.1262 | 207.8243 | 103.1262 | 103.1262 | 138.249 | 346.0008 | 411.48 | 296.3297 | 103.1262 | 103.1262 | 306 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 14 | 7070 | 12.3 | 12.3 | 7.6542 | 7.2765 | 15 | 71 | 71 | 378.698 | 172.0749 | 23.5455 | 205.909 | 0 | 0 | 0 | 194.7614 | 334.1307 | 277.7708 | 58.6965 | 0 | 160.9251 | 96.0371 | 96.0371 | 96.0371 | 164.4463 | 213.3992 | 193.603 | 116.654 | 96.0371 | 172.0749 | 96.0371 | 96.0371 | 96.0371 | 359.2077 | 547.5299 | 471.3738 | 175.3505 | 96.0371 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 15 | 7071 | 11.3 | 11.3 | 7.6542 | 7.2765 | 15 | 75 | 75 | 26.1517 | 146.5745 | 18.4838 | 220.7301 | 0 | 0 | 0 | 7.8413 | 21.5647 | 22.6558 | 10.4754 | 0 | 9.4255 | 69.5625 | 69.5625 | 69.5625 | 87.6143 | 119.2076 | 121.7195 | 93.6785 | 69.5625 | 146.5745 | 69.5625 | 69.5625 | 69.5625 | 95.4555 | 140.7722 | 144.3752 | 104.154 | 69.5625 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 16 | 7072 | 11.1 | 11.1 | 7.6542 | 7.2765 | 15 | 79 | 79 | 1.8441 | 43.5185 | 11.695 | 234.271 | 0 | 0 | 0 | 0.13022 | 1.3254 | 1.7441 | 1.1412 | 0 | 0.48146 | 20.9369 | 20.9369 | 20.9369 | 20.9369 | 20.9369 | 20.9369 | 20.9369 | 20.9369 | 43.5185 | 20.9369 | 20.9369 | 20.9369 | 21.0671 | 22.2622 | 22.681 | 22.0781 | 20.9369 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 17 | 7073 | 10.8 | 10.8 | 7.6542 | 7.2765 | 15 | 81 | 81 | 3.49 | 30.5334 | 3.6846 | 246.7455 | 0 | 0 | 0 | 0 | 1.9957 | 3.3729 | 2.7743 | 0.55057 | 0.46664 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 30.5334 | 14.6807 | 14.6807 | 14.6807 | 14.6807 | 16.6763 | 18.0535 | 17.455 | 15.2313 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 22 | 18 | 7074 | 10 | 10 | 7.6542 | 7.2765 | 15 | 81 | 81 | 0 | 8 | -5.0968 | 258.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 8 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 19 | 7075 | 8.8 | 8.8 | 7.6542 | 7.2765 | 15 | 86 | 86 | 0 | 0 | -14.2514 | 270.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 20 | 7076 | 8.1 | 8.1 | 7.6542 | 7.2765 | 15 | 88 | 88 | 0 | 0 | -23.3925 | 282.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 21 | 7077 | 8.2 | 8.2 | 7.6542 | 7.2765 | 15 | 87 | 87 | 0 | 0 | -32.0804 | 295.9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 22 | 7078 | 8.3 | 8.3 | 7.6542 | 7.2765 | 15 | 85 | 85 | 0 | 0 | -39.7384 | 311.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 23 | 7079 | 7.9 | 7.9 | 7.6542 | 7.2765 | 15 | 84 | 84 | 0 | 0 | -45.5761 | 329.9626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 22 | 24 | 7080 | 7.7 | 7.7 | 9.1 | 7.6523 | 15 | 81 | 81 | 0 | 0 | -48.6506 | 351.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 1 | 7081 | 6.7 | 6.7 | 9.1 | 7.6523 | 15 | 82 | 82 | 0 | 0 | -48.2743 | 13.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 2 | 7082 | 6.9 | 6.9 | 9.1 | 7.6523 | 15 | 81 | 81 | 0 | 0 | -44.8593 | 34.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 3 | 7083 | 7 | 7 | 9.1 | 7.6523 | 15 | 79 | 79 | 0 | 0 | -38.5318 | 52.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 4 | 7084 | 7.5 | 7.5 | 9.1 | 7.6523 | 15 | 77 | 77 | 0 | 0 | -30.5766 | 67.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 5 | 7085 | 6.6 | 6.6 | 9.1 | 7.6523 | 15 | 77 | 77 | 0 | 0 | -21.7389 | 80.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 6 | 7086 | 5.4 | 5.4 | 9.1 | 7.6523 | 15 | 78 | 78 | 0 | 0 | -12.5586 | 92.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 7 | 7087 | 5 | 5 | 9.1 | 7.6523 | 15 | 76 | 76 | 0 | 0 | -3.4568 | 104.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 23 | 8 | 7088 | 4.9 | 4.9 | 9.1 | 7.6523 | 15 | 76 | 76 | 24.8693 | 4.6496 | 5.1833 | 116.0498 | 0 | 12.7332 | 24.0719 | 21.3096 | 6.0644 | 0 | 0 | 0 | 12.3504 | 3.5532 | 4.3042 | 4.973 | 4.8101 | 3.9109 | 3.5532 | 3.5532 | 3.5532 | 4.6496 | 3.5532 | 17.0374 | 29.0449 | 26.1197 | 9.9753 | 3.5532 | 3.5532 | 3.5532 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 9 | 7089 | 5.6 | 5.6 | 9.1 | 7.6523 | 15 | 76 | 76 | 9.3624 | 54.4945 | 12.9565 | 128.6994 | 0 | 3.028 | 8.3769 | 8.8188 | 4.0947 | 0 | 0 | 0 | 1.5055 | 22.7368 | 67.9669 | 147.866 | 154.4661 | 83.901 | 22.7368 | 22.7368 | 22.7368 | 54.4945 | 22.7368 | 70.9949 | 156.2429 | 163.2849 | 87.9957 | 22.7368 | 22.7368 | 22.7368 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 10 | 7090 | 6.7 | 6.7 | 9.1 | 7.6523 | 15 | 76 | 76 | 3.3399 | 63.0578 | 19.4015 | 142.4716 | 0 | 0.3572 | 2.5402 | 3.2352 | 2.035 | 0 | 0 | 0 | 0.9422 | 30.9949 | 31.3822 | 33.7489 | 34.5024 | 33.2012 | 30.9949 | 30.9949 | 30.9949 | 63.0578 | 30.9949 | 31.7394 | 36.2891 | 37.7375 | 35.2363 | 30.9949 | 30.9949 | 30.9949 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 11 | 7091 | 6.4 | 6.4 | 9.1 | 7.6523 | 15 | 82 | 82 | 5.4222 | 105.9741 | 24.0108 | 157.5112 | 0 | 0 | 3.1154 | 5.0708 | 4.0559 | 0.66503 | 0 | 0 | 2.0259 | 51.2284 | 51.2284 | 59.3897 | 64.5124 | 61.8535 | 52.9706 | 51.2284 | 51.2284 | 105.9741 | 51.2284 | 51.2284 | 62.5051 | 69.5832 | 65.9094 | 53.6356 | 51.2284 | 51.2284 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 12 | 7092 | 6.6 | 6.6 | 9.1 | 7.6523 | 15 | 82 | 82 | 1.827 | 71.216 | 26.3139 | 173.5668 | 0 | 0 | 0.63836 | 1.5417 | 1.542 | 0.63897 | 0 | 0 | 0.78397 | 34.7427 | 34.7427 | 34.7427 | 34.7427 | 34.7427 | 34.7427 | 34.7427 | 34.7427 | 71.216 | 34.7427 | 34.7427 | 35.3811 | 36.2845 | 36.2847 | 35.3817 | 34.7427 | 34.7427 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 13 | 7093 | 7 | 7 | 9.1 | 7.6523 | 15 | 82 | 82 | 1.2208 | 60.4571 | 26.0302 | 189.9577 | 0 | 0 | 0.12261 | 0.8556 | 1.0874 | 0.68221 | 0 | 0 | 0.54294 | 29.2266 | 29.2266 | 29.2266 | 29.2266 | 29.2266 | 29.2266 | 29.2266 | 29.2266 | 60.4571 | 29.2266 | 29.2266 | 29.3492 | 30.0822 | 30.314 | 29.9088 | 29.2266 | 29.2266 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 14 | 7094 | 7 | 7 | 9.1 | 7.6523 | 15 | 92 | 92 | 0.35441 | 30.8513 | 23.1962 | 205.8387 | 0 | 0 | 0 | 0.18286 | 0.31367 | 0.26074 | 0.055069 | 0 | 0.14867 | 14.6348 | 14.6348 | 14.6348 | 14.6348 | 14.6348 | 14.6348 | 14.6348 | 14.6348 | 30.8513 | 14.6348 | 14.6348 | 14.6348 | 14.8176 | 14.9485 | 14.8955 | 14.6899 | 14.6348 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 15 | 7095 | 6.7 | 6.7 | 9.1 | 7.6523 | 15 | 93 | 93 | 0.40364 | 27.8567 | 18.1473 | 220.6102 | 0 | 0 | 0 | 0.12178 | 0.33392 | 0.35045 | 0.1617 | 0 | 0.1433 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 13.1903 | 27.8567 | 13.1903 | 13.1903 | 13.1903 | 13.312 | 13.5242 | 13.5407 | 13.352 | 13.1903 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 16 | 7096 | 7.2 | 7.2 | 9.1 | 7.6523 | 15 | 93 | 93 | 0.95297 | 30.7562 | 11.3734 | 234.117 | 0 | 0 | 0 | 0.069314 | 0.68747 | 0.90292 | 0.58944 | 0 | 0.24378 | 14.6306 | 14.6306 | 14.6306 | 14.6306 | 14.6306 | 14.6306 | 14.6306 | 14.6306 | 30.7562 | 14.6306 | 14.6306 | 14.6306 | 14.7 | 15.3181 | 15.5336 | 15.2201 | 14.6306 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 17 | 7097 | 8.2 | 8.2 | 9.1 | 7.6523 | 15 | 91 | 91 | 1.134 | 16.8542 | 3.3761 | 246.5691 | 0 | 0 | 0 | 0 | 0.65162 | 1.0977 | 0.90074 | 0.17616 | 0.14583 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 7.95 | 16.8542 | 7.95 | 7.95 | 7.95 | 7.95 | 8.6017 | 9.0477 | 8.8508 | 8.1262 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 23 | 18 | 7098 | 8.2 | 8.2 | 9.1 | 7.6523 | 15 | 90 | 90 | 0 | 3 | -5.3966 | 258.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 3 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 19 | 7099 | 8.5 | 8.5 | 9.1 | 7.6523 | 15 | 90 | 90 | 0 | 0 | -14.5481 | 270.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 20 | 7100 | 8.3 | 8.3 | 9.1 | 7.6523 | 15 | 92 | 92 | 0 | 0 | -23.6927 | 282.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 21 | 7101 | 8.2 | 8.2 | 9.1 | 7.6523 | 15 | 94 | 94 | 0 | 0 | -32.3913 | 295.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 22 | 7102 | 8.2 | 8.2 | 9.1 | 7.6523 | 15 | 95 | 95 | 0 | 0 | -40.0663 | 311.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 23 | 7103 | 8.5 | 8.5 | 9.1 | 7.6523 | 15 | 93 | 93 | 0 | 0 | -45.9223 | 329.8489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 23 | 24 | 7104 | 8.5 | 8.5 | 7.075 | 7.5328 | 15 | 87 | 87 | 0 | 0 | -49.0058 | 351.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 1 | 7105 | 8.6 | 8.6 | 7.075 | 7.5328 | 15 | 80 | 80 | 0 | 0 | -48.6192 | 13.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 2 | 7106 | 8.8 | 8.8 | 7.075 | 7.5328 | 15 | 75 | 75 | 0 | 0 | -45.1764 | 34.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 3 | 7107 | 8.8 | 8.8 | 7.075 | 7.5328 | 15 | 73 | 73 | 0 | 0 | -38.8212 | 52.5074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 4 | 7108 | 8.5 | 8.5 | 7.075 | 7.5328 | 15 | 76 | 76 | 0 | 0 | -30.845 | 67.5729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 5 | 7109 | 7.5 | 7.5 | 7.075 | 7.5328 | 15 | 84 | 84 | 0 | 0 | -21.9958 | 80.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 6 | 7110 | 7.5 | 7.5 | 7.075 | 7.5328 | 15 | 82 | 82 | 0 | 0 | -12.8131 | 92.7151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 7 | 7111 | 6.5 | 6.5 | 7.075 | 7.5328 | 15 | 88 | 88 | 0 | 0 | -3.7169 | 104.3779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 24 | 8 | 7112 | 6.9 | 6.9 | 7.075 | 7.5328 | 15 | 81 | 81 | 24.7271 | 6.1695 | 4.9105 | 116.2731 | 0 | 12.5688 | 23.9022 | 21.234 | 6.1272 | 0 | 0 | 0 | 1.8305 | 2.6285 | 4.9615 | 7.0652 | 6.5699 | 3.7659 | 2.6285 | 2.6285 | 2.6285 | 6.1695 | 2.6285 | 17.5303 | 30.9674 | 27.8039 | 9.8931 | 2.6285 | 2.6285 | 2.6285 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 9 | 7113 | 8.5 | 8.5 | 7.075 | 7.5328 | 15 | 74 | 74 | 194.2978 | 72.7502 | 12.6653 | 128.9023 | 0 | 62.152 | 173.5863 | 183.3361 | 85.6902 | 0 | 0 | 0 | 30.2498 | 36.203 | 61.5069 | 106.8751 | 110.8445 | 71.09 | 36.203 | 36.203 | 36.203 | 72.7502 | 36.203 | 123.6589 | 280.4614 | 294.1806 | 156.7801 | 36.203 | 36.203 | 36.203 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 10 | 7114 | 10.3 | 10.3 | 7.075 | 7.5328 | 15 | 70 | 70 | 323.174 | 118.5318 | 19.0888 | 142.6429 | 0 | 33.4935 | 245.3801 | 313.5264 | 198.0132 | 0 | 0 | 0 | 89.4682 | 65.2831 | 77.242 | 152.8962 | 177.2279 | 135.9838 | 65.2831 | 65.2831 | 65.2831 | 118.5318 | 65.2831 | 110.7355 | 398.2763 | 490.7543 | 333.997 | 65.2831 | 65.2831 | 65.2831 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 11 | 7115 | 11.7 | 11.7 | 7.075 | 7.5328 | 15 | 57 | 57 | 679.653 | 96.7218 | 23.6775 | 157.6351 | 0 | 0 | 389.7241 | 636.575 | 510.5289 | 85.4219 | 0 | 0 | 250.2782 | 72.2737 | 72.2737 | 129.2426 | 165.3266 | 146.9015 | 84.7604 | 72.2737 | 72.2737 | 96.7218 | 72.2737 | 72.2737 | 518.9666 | 801.9016 | 657.4304 | 170.1824 | 72.2737 | 72.2737 | 347 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 12 | 7116 | 11 | 11 | 7.075 | 7.5328 | 15 | 69 | 69 | 220.696 | 195.5018 | 25.9661 | 173.6278 | 0 | 0 | 76.9067 | 186.5497 | 186.9144 | 77.7872 | 0 | 0 | 93.4982 | 97.1282 | 97.1282 | 143.1052 | 208.653 | 208.8711 | 143.6317 | 97.1282 | 97.1282 | 195.5018 | 97.1282 | 97.1282 | 220.0119 | 395.2027 | 395.7855 | 221.4189 | 97.1282 | 97.1282 | 289 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 13 | 7117 | 8.8 | 8.8 | 7.075 | 7.5328 | 15 | 74 | 74 | 33.6338 | 185.2256 | 25.6783 | 189.949 | 0 | 0 | 3.3561 | 23.6229 | 30.0518 | 18.8767 | 0 | 0 | 14.7744 | 86.0001 | 86.0001 | 94.1291 | 143.2192 | 158.7911 | 131.723 | 86.0001 | 86.0001 | 185.2256 | 86.0001 | 86.0001 | 97.4852 | 166.8421 | 188.8429 | 150.5997 | 86.0001 | 86.0001 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 14 | 7118 | 7.1 | 7.1 | 7.075 | 7.5328 | 15 | 86 | 86 | 252.6008 | 187.4145 | 22.8505 | 205.7664 | 0 | 0 | 0 | 130.7432 | 224.2309 | 186.3672 | 39.3321 | 0 | 104.5855 | 96.5675 | 96.5675 | 96.5675 | 169.6885 | 221.9735 | 200.7974 | 118.5648 | 96.5675 | 187.4145 | 96.5675 | 96.5675 | 96.5675 | 300.4317 | 446.2044 | 387.1646 | 157.8969 | 96.5675 | 292 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 15 | 7119 | 10.9 | 10.9 | 7.075 | 7.5328 | 15 | 74 | 74 | 610.1139 | 103.662 | 17.8147 | 220.4889 | 0 | 0 | 0 | 185.2111 | 506.3322 | 530.8509 | 244.4042 | 0 | 213.338 | 71.8291 | 71.8291 | 71.8291 | 102.533 | 155.7677 | 159.8324 | 112.3459 | 71.8291 | 103.662 | 71.8291 | 71.8291 | 71.8291 | 287.744 | 662.0999 | 690.6832 | 356.7501 | 71.8291 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 16 | 7120 | 9.8 | 9.8 | 7.075 | 7.5328 | 15 | 68 | 68 | 137.3393 | 118.5857 | 11.0558 | 233.9621 | 0 | 0 | 0 | 10.284 | 99.4425 | 130.349 | 84.8988 | 0 | 34.4143 | 59.8841 | 59.8841 | 59.8841 | 66.3213 | 122.1296 | 141.4753 | 113.026 | 59.8841 | 118.5857 | 59.8841 | 59.8841 | 59.8841 | 76.6053 | 221.5721 | 271.8243 | 197.9248 | 59.8841 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 17 | 7121 | 8.5 | 8.5 | 7.075 | 7.5328 | 15 | 74 | 74 | 39.2741 | 53.1486 | 3.0717 | 246.392 | 0 | 0 | 0 | 0 | 22.6769 | 38.0746 | 31.1688 | 6.0046 | 4.8514 | 26.8292 | 26.8292 | 26.8292 | 26.8292 | 41.1988 | 50.9557 | 46.5797 | 30.6342 | 53.1486 | 26.8292 | 26.8292 | 26.8292 | 26.8292 | 63.8757 | 89.0304 | 77.7485 | 36.6388 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 24 | 18 | 7122 | 5.9 | 5.9 | 7.075 | 7.5328 | 15 | 89 | 89 | 0 | 0 | -5.692 | 258.1896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 19 | 7123 | 6.6 | 6.6 | 7.075 | 7.5328 | 15 | 83 | 83 | 0 | 0 | -14.8403 | 269.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 20 | 7124 | 4.9 | 4.9 | 7.075 | 7.5328 | 15 | 91 | 91 | 0 | 0 | -23.9884 | 282.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 21 | 7125 | 5.1 | 5.1 | 7.075 | 7.5328 | 15 | 89 | 89 | 0 | 0 | -32.6978 | 295.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 22 | 7126 | 3.5 | 3.5 | 7.075 | 7.5328 | 15 | 98 | 98 | 0 | 0 | -40.3899 | 311.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 23 | 7127 | 4.7 | 4.7 | 7.075 | 7.5328 | 15 | 91 | 91 | 0 | 0 | -46.2647 | 329.7308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 24 | 24 | 7128 | 4.9 | 4.9 | 7.7208 | 7.6803 | 15 | 93 | 93 | 0 | 0 | -49.3579 | 351.1877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 1 | 7129 | 3 | 3 | 7.7208 | 7.6803 | 15 | 98 | 98 | 0 | 0 | -48.9616 | 13.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 2 | 7130 | 4.2 | 4.2 | 7.7208 | 7.6803 | 15 | 95 | 95 | 0 | 0 | -45.4914 | 34.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 3 | 7131 | 3.2 | 3.2 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -39.109 | 52.7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 4 | 7132 | 2.1 | 2.1 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -31.1123 | 67.8343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 5 | 7133 | 2.1 | 2.1 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -22.2518 | 80.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 6 | 7134 | 2.3 | 2.3 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -13.0669 | 92.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 7 | 7135 | 2.2 | 2.2 | 7.7208 | 7.6803 | 15 | 98 | 98 | 0 | 0 | -3.9765 | 104.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 25 | 8 | 7136 | 2.8 | 2.8 | 7.7208 | 7.6803 | 15 | 94 | 94 | 31.5882 | 2.31 | 4.6382 | 116.4919 | 0 | 15.9408 | 30.493 | 27.1828 | 7.9493 | 0 | 0 | 0 | 11.69 | 2.3259 | 2.6951 | 3.0322 | 2.9555 | 2.51 | 2.3259 | 2.3259 | 2.3259 | 2.31 | 2.3259 | 18.6359 | 33.5252 | 30.1383 | 10.4593 | 2.3259 | 2.3259 | 2.3259 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 9 | 7137 | 6.8 | 6.8 | 7.7208 | 7.6803 | 15 | 81 | 81 | 388.5115 | 60.4853 | 12.375 | 129.1004 | 0 | 122.925 | 346.5782 | 367.2106 | 172.736 | 0 | 0 | 0 | 58.5147 | 34.0059 | 43.3265 | 60.2847 | 61.8492 | 47.1034 | 34.0059 | 34.0059 | 34.0059 | 60.4853 | 34.0059 | 166.2515 | 406.8629 | 429.0597 | 219.8394 | 34.0059 | 34.0059 | 34.0059 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 10 | 7138 | 8.3 | 8.3 | 7.7208 | 7.6803 | 15 | 73 | 73 | 238.9383 | 124.1017 | 18.7775 | 142.8092 | 0 | 23.9888 | 181.1179 | 232.1506 | 147.1927 | 0 | 0 | 0 | 64.8983 | 64.8522 | 76.556 | 153.2166 | 178.1146 | 136.6651 | 64.8522 | 64.8522 | 64.8522 | 124.1017 | 64.8522 | 100.5447 | 334.3345 | 410.2653 | 283.8577 | 64.8522 | 64.8522 | 64.8522 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 11 | 7139 | 9.5 | 9.5 | 7.7208 | 7.6803 | 15 | 68 | 68 | 620.3681 | 105.8714 | 23.3463 | 157.7542 | 0 | 0 | 355.0357 | 581.9023 | 467.8984 | 79.8059 | 0 | 0 | 225.1286 | 73.2617 | 73.2617 | 131.7586 | 169.138 | 150.3543 | 86.4108 | 73.2617 | 73.2617 | 105.8714 | 73.2617 | 73.2617 | 486.7943 | 751.0402 | 618.2526 | 166.2167 | 73.2617 | 73.2617 | 331 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 12 | 7140 | 10.3 | 10.3 | 7.7208 | 7.6803 | 15 | 66 | 66 | 425.2538 | 161.1458 | 25.6211 | 173.6847 | 0 | 0 | 147.8116 | 360.05 | 361.376 | 151.0128 | 0 | 0 | 177.8542 | 92.7031 | 92.7031 | 138.3534 | 203.9014 | 204.3109 | 139.3421 | 92.7031 | 92.7031 | 161.1458 | 92.7031 | 92.7031 | 286.1651 | 563.9514 | 565.6869 | 290.3548 | 92.7031 | 92.7031 | 339 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 13 | 7141 | 10.8 | 10.8 | 7.7208 | 7.6803 | 15 | 58 | 58 | 393.5172 | 173.2801 | 25.3296 | 189.9371 | 0 | 0 | 39.0303 | 276.9744 | 352.6706 | 221.7772 | 0 | 0 | 170.7199 | 97.5572 | 97.5572 | 110.8726 | 192.0481 | 217.8721 | 173.2173 | 97.5572 | 97.5572 | 173.2801 | 97.5572 | 97.5572 | 149.9029 | 469.0225 | 570.5428 | 394.9945 | 97.5572 | 97.5572 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 14 | 7142 | 10.9 | 10.9 | 7.7208 | 7.6803 | 15 | 58 | 58 | 631.3279 | 117.0228 | 22.5085 | 205.692 | 0 | 0 | 0 | 327.8143 | 562.0721 | 467.0757 | 98.4727 | 0 | 257.9772 | 81.8005 | 81.8005 | 81.8005 | 137.0951 | 176.6089 | 160.5853 | 98.4105 | 81.8005 | 117.0228 | 81.8005 | 81.8005 | 81.8005 | 464.9094 | 738.6811 | 627.661 | 196.8832 | 81.8005 | 375 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 15 | 7143 | 11.3 | 11.3 | 7.7208 | 7.6803 | 15 | 58 | 58 | 130.6709 | 163.0042 | 17.486 | 220.3664 | 0 | 0 | 0 | 39.9145 | 108.7823 | 113.927 | 52.3347 | 0 | 44.9958 | 79.8163 | 79.8163 | 79.8163 | 112.5481 | 169.023 | 173.2419 | 122.7333 | 79.8163 | 163.0042 | 79.8163 | 79.8163 | 79.8163 | 152.4626 | 277.8053 | 287.1688 | 175.068 | 79.8163 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 16 | 7144 | 10.8 | 10.8 | 7.7208 | 7.6803 | 15 | 56 | 56 | 494.7591 | 86.5951 | 10.7423 | 233.8064 | 0 | 0 | 0 | 38.1212 | 359.5464 | 470.3542 | 305.6349 | 0 | 121.4049 | 55.0163 | 55.0163 | 55.0163 | 62.3845 | 124.5104 | 145.9276 | 114.0902 | 55.0163 | 86.5951 | 55.0163 | 55.0163 | 55.0163 | 100.5056 | 484.0568 | 616.2818 | 419.7252 | 55.0163 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 17 | 7145 | 9.2 | 9.2 | 7.7208 | 7.6803 | 15 | 69 | 69 | 96.6677 | 55.5455 | 2.7716 | 246.2141 | 0 | 0 | 0 | 0 | 56.0834 | 93.8541 | 76.6462 | 14.5401 | 11.4545 | 29.1018 | 29.1018 | 29.1018 | 29.1018 | 58.2948 | 77.9555 | 68.9983 | 36.6704 | 55.5455 | 29.1018 | 29.1018 | 29.1018 | 29.1018 | 114.3782 | 171.8095 | 145.6446 | 51.2105 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 25 | 18 | 7146 | 6.2 | 6.2 | 7.7208 | 7.6803 | 15 | 88 | 88 | 0 | 3 | -5.9831 | 257.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 3 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 1.3906 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 19 | 7147 | 4.5 | 4.5 | 7.7208 | 7.6803 | 15 | 97 | 97 | 0 | 0 | -15.128 | 269.6738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 20 | 7148 | 3.4 | 3.4 | 7.7208 | 7.6803 | 15 | 97 | 97 | 0 | 0 | -24.2795 | 281.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 21 | 7149 | 2.5 | 2.5 | 7.7208 | 7.6803 | 15 | 98 | 98 | 0 | 0 | -32.9996 | 295.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 22 | 7150 | 1.6 | 1.6 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -40.7091 | 310.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 23 | 7151 | 1.2 | 1.2 | 7.7208 | 7.6803 | 15 | 99 | 99 | 0 | 0 | -46.6031 | 329.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 25 | 24 | 7152 | 0.6 | 0.6 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -49.7066 | 351.1778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 1 | 7153 | 0.1 | 0.1 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -49.3014 | 13.8393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 2 | 7154 | 0.1 | 0.1 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -45.8043 | 35.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 3 | 7155 | 0.5 | 0.5 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -39.3951 | 53.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 4 | 7156 | 0 | 0 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -31.3783 | 68.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 5 | 7157 | 0.7 | 0.7 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -22.507 | 81.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 6 | 7158 | 1.2 | 1.2 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -13.3201 | 93.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 7 | 7159 | 2.9 | 2.9 | 5.4083 | 7.1463 | 15 | 99 | 99 | 0 | 0 | -4.2355 | 104.8406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 26 | 8 | 7160 | 5.8 | 5.8 | 5.4083 | 7.1463 | 15 | 94 | 94 | 22.4938 | 1.815 | 4.3667 | 116.7061 | 0 | 11.2702 | 21.684 | 19.3957 | 5.7456 | 0 | 0 | 0 | 9.185 | 1.8283 | 2.1166 | 2.383 | 2.3244 | 1.9753 | 1.8283 | 1.8283 | 1.8283 | 1.815 | 1.8283 | 13.3868 | 24.067 | 21.7201 | 7.7209 | 1.8283 | 1.8283 | 1.8283 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 9 | 7161 | 7.1 | 7.1 | 5.4083 | 7.1463 | 15 | 86 | 86 | 11.2343 | 51.3645 | 12.0858 | 129.2936 | 0 | 3.5161 | 10.0067 | 10.6355 | 5.0342 | 0 | 0 | 0 | 1.6355 | 20.7907 | 70.6208 | 162.6054 | 171.5168 | 92.1349 | 20.7907 | 20.7907 | 20.7907 | 51.3645 | 20.7907 | 74.1369 | 172.6121 | 182.1523 | 97.1691 | 20.7907 | 20.7907 | 20.7907 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 10 | 7162 | 8.3 | 8.3 | 5.4083 | 7.1463 | 15 | 79 | 79 | 21.4022 | 105.2981 | 18.4678 | 142.9706 | 0 | 2.0809 | 16.1963 | 20.8241 | 13.2535 | 0 | 0 | 0 | 5.7019 | 46.1799 | 55.0991 | 115.6017 | 135.438 | 102.9881 | 46.1799 | 46.1799 | 46.1799 | 105.2981 | 46.1799 | 57.1799 | 131.798 | 156.2621 | 116.2416 | 46.1799 | 46.1799 | 46.1799 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 11 | 7163 | 9.2 | 9.2 | 5.4083 | 7.1463 | 15 | 72 | 72 | 133.1709 | 169.3806 | 23.0172 | 157.8686 | 0 | 0 | 76.0688 | 125.0926 | 100.8389 | 17.5151 | 0 | 0 | 47.6194 | 80.6232 | 80.6232 | 159.5535 | 210.4215 | 185.2554 | 98.7972 | 80.6232 | 80.6232 | 169.3806 | 80.6232 | 80.6232 | 235.6223 | 335.5141 | 286.0943 | 116.3123 | 80.6232 | 80.6232 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 12 | 7164 | 9.7 | 9.7 | 5.4083 | 7.1463 | 15 | 70 | 70 | 18.4728 | 159.3736 | 25.279 | 173.7375 | 0 | 0 | 6.4052 | 15.6657 | 15.7495 | 6.6074 | 0 | 0 | 7.6264 | 73.994 | 73.994 | 90.0774 | 113.3303 | 113.5405 | 90.5849 | 73.994 | 73.994 | 159.3736 | 73.994 | 73.994 | 96.4827 | 128.996 | 129.29 | 97.1923 | 73.994 | 73.994 | 167 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 13 | 7165 | 9.7 | 9.7 | 5.4083 | 7.1463 | 15 | 66 | 66 | 17.7976 | 164.3751 | 24.9844 | 189.9222 | 0 | 0 | 1.7555 | 12.5531 | 15.9973 | 10.0705 | 0 | 0 | 7.6249 | 77.3509 | 77.3509 | 81.0201 | 103.5885 | 110.7872 | 98.3994 | 77.3509 | 77.3509 | 164.3751 | 77.3509 | 77.3509 | 82.7756 | 116.1416 | 126.7845 | 108.4699 | 77.3509 | 77.3509 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 14 | 7166 | 9.6 | 9.6 | 5.4083 | 7.1463 | 15 | 62 | 62 | 28.6392 | 166.4512 | 22.1704 | 205.6156 | 0 | 0 | 0 | 14.9185 | 25.571 | 21.2443 | 4.4731 | 0 | 11.5488 | 78.1027 | 78.1027 | 78.1027 | 114.746 | 140.9111 | 130.2839 | 89.0897 | 78.1027 | 166.4512 | 78.1027 | 78.1027 | 78.1027 | 129.6645 | 166.4821 | 151.5282 | 93.5628 | 78.1027 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 15 | 7167 | 9.2 | 9.2 | 5.4083 | 7.1463 | 15 | 69 | 69 | 6.4902 | 103.7995 | 17.1614 | 220.2426 | 0 | 0 | 0 | 1.9949 | 5.4196 | 5.6697 | 2.5985 | 0 | 2.2005 | 51.4642 | 51.4642 | 51.4642 | 52.3626 | 53.9051 | 54.0177 | 52.6345 | 51.4642 | 103.7995 | 51.4642 | 51.4642 | 51.4642 | 54.3575 | 59.3247 | 59.6873 | 55.2329 | 51.4642 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 16 | 7168 | 8.7 | 8.7 | 5.4083 | 7.1463 | 15 | 68 | 68 | 9.0319 | 80.8303 | 10.4331 | 233.6498 | 0 | 0 | 0 | 0.71573 | 6.5873 | 8.6001 | 5.5751 | 0 | 2.1697 | 40.0498 | 40.0498 | 40.0498 | 40.2359 | 41.7623 | 42.2855 | 41.4992 | 40.0498 | 80.8303 | 40.0498 | 40.0498 | 40.0498 | 40.9516 | 48.3496 | 50.8856 | 47.0742 | 40.0498 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 17 | 7169 | 8.5 | 8.5 | 5.4083 | 7.1463 | 15 | 71 | 71 | 3.1435 | 24.6432 | 2.4758 | 246.0354 | 0 | 0 | 0 | 0 | 1.8324 | 3.0564 | 2.49 | 0.46495 | 0.35679 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 24.6432 | 11.7879 | 11.7879 | 11.7879 | 11.7879 | 13.6203 | 14.8443 | 14.2779 | 12.2529 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 26 | 18 | 7170 | 8.2 | 8.2 | 5.4083 | 7.1463 | 15 | 76 | 76 | 0 | 0 | -6.2697 | 257.8025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 19 | 7171 | 8.3 | 8.3 | 5.4083 | 7.1463 | 15 | 74 | 74 | 0 | 0 | -15.4111 | 269.4686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 20 | 7172 | 8.5 | 8.5 | 5.4083 | 7.1463 | 15 | 71 | 71 | 0 | 0 | -24.5659 | 281.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 21 | 7173 | 7.8 | 7.8 | 5.4083 | 7.1463 | 15 | 79 | 79 | 0 | 0 | -33.2968 | 295.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 22 | 7174 | 7.9 | 7.9 | 5.4083 | 7.1463 | 15 | 79 | 79 | 0 | 0 | -41.0237 | 310.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 23 | 7175 | 7.6 | 7.6 | 5.4083 | 7.1463 | 15 | 83 | 83 | 0 | 0 | -46.9374 | 329.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 26 | 24 | 7176 | 6.7 | 6.7 | 6.0958 | 6.7883 | 15 | 95 | 95 | 0 | 0 | -50.0519 | 351.1633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 1 | 7177 | 6.7 | 6.7 | 6.0958 | 6.7883 | 15 | 97 | 97 | 0 | 0 | -49.6384 | 13.9559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 2 | 7178 | 6.7 | 6.7 | 6.0958 | 6.7883 | 15 | 97 | 97 | 0 | 0 | -46.1149 | 35.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 3 | 7179 | 6.8 | 6.8 | 6.0958 | 6.7883 | 15 | 97 | 97 | 0 | 0 | -39.6796 | 53.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 4 | 7180 | 6.9 | 6.9 | 6.0958 | 6.7883 | 15 | 98 | 98 | 0 | 0 | -31.6432 | 68.3458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 5 | 7181 | 7.1 | 7.1 | 6.0958 | 6.7883 | 15 | 99 | 99 | 0 | 0 | -22.7613 | 81.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 6 | 7182 | 7.6 | 7.6 | 6.0958 | 6.7883 | 15 | 99 | 99 | 0 | 0 | -13.5726 | 93.4392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 7 | 7183 | 8 | 8 | 6.0958 | 6.7883 | 15 | 99 | 99 | 0 | 0 | -4.4939 | 105.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 27 | 8 | 7184 | 8.3 | 8.3 | 6.0958 | 6.7883 | 15 | 97 | 97 | 0 | 0 | 4.096 | 116.9156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 9 | 7185 | 8.5 | 8.5 | 6.0958 | 6.7883 | 15 | 96 | 96 | 0.39648 | 10.9443 | 11.7976 | 129.482 | 0 | 0.12276 | 0.35262 | 0.37593 | 0.17902 | 0 | 0 | 0 | 0.055739 | 5.2062 | 5.2062 | 5.2062 | 5.2062 | 5.2062 | 5.2062 | 5.2062 | 5.2062 | 10.9443 | 5.2062 | 5.3289 | 5.5588 | 5.5821 | 5.3852 | 5.2062 | 5.2062 | 5.2062 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 10 | 7186 | 8.8 | 8.8 | 6.0958 | 6.7883 | 15 | 95 | 95 | 1.0332 | 32.7301 | 18.1597 | 143.1269 | 0 | 0.097252 | 0.7806 | 1.0067 | 0.64306 | 0 | 0 | 0 | 0.26993 | 15.7529 | 15.7529 | 15.7529 | 15.7529 | 15.7529 | 15.7529 | 15.7529 | 15.7529 | 32.7301 | 15.7529 | 15.8502 | 16.5335 | 16.7596 | 16.396 | 15.7529 | 15.7529 | 15.7529 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 11 | 7187 | 9.2 | 9.2 | 6.0958 | 6.7883 | 15 | 92 | 92 | 1.0101 | 43.6441 | 22.6905 | 157.9782 | 0 | 0 | 0.57593 | 0.95018 | 0.76782 | 0.13569 | 0 | 0 | 0.35587 | 20.9933 | 20.9933 | 20.9933 | 20.9933 | 20.9933 | 20.9933 | 20.9933 | 20.9933 | 43.6441 | 20.9933 | 20.9933 | 21.5692 | 21.9434 | 21.7611 | 21.1289 | 20.9933 | 20.9933 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 12 | 7188 | 10 | 10 | 6.0958 | 6.7883 | 15 | 90 | 90 | 2.6867 | 81.9052 | 24.9398 | 173.7863 | 0 | 0 | 0.92945 | 2.2821 | 2.2979 | 0.96767 | 0 | 0 | 1.0948 | 40.3304 | 40.3304 | 40.3304 | 40.3304 | 40.3304 | 40.3304 | 40.3304 | 40.3304 | 81.9052 | 40.3304 | 40.3304 | 41.2598 | 42.6125 | 42.6283 | 41.298 | 40.3304 | 40.3304 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 13 | 7189 | 10.5 | 10.5 | 6.0958 | 6.7883 | 15 | 88 | 88 | 6.3277 | 128.3231 | 24.6428 | 189.9043 | 0 | 0 | 0.62103 | 4.4724 | 5.7039 | 3.5941 | 0 | 0 | 2.6769 | 62.739 | 62.739 | 63.7474 | 70.0008 | 72.0004 | 68.5748 | 62.739 | 62.739 | 128.3231 | 62.739 | 62.739 | 64.3684 | 74.4732 | 77.7043 | 72.1689 | 62.739 | 62.739 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 14 | 7190 | 10.5 | 10.5 | 6.0958 | 6.7883 | 15 | 87 | 87 | 3.2397 | 87.7109 | 21.8362 | 205.5372 | 0 | 0 | 0 | 1.693 | 2.9008 | 2.4093 | 0.50649 | 0 | 1.2891 | 43.2369 | 43.2369 | 43.2369 | 43.2369 | 43.2369 | 43.2369 | 43.2369 | 43.2369 | 87.7109 | 43.2369 | 43.2369 | 43.2369 | 44.9299 | 46.1377 | 45.6462 | 43.7434 | 43.2369 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 15 | 7191 | 10.3 | 10.3 | 6.0958 | 6.7883 | 15 | 93 | 93 | 1.6326 | 52.455 | 16.841 | 220.1176 | 0 | 0 | 0 | 0.50495 | 1.3674 | 1.4289 | 0.65331 | 0 | 0.54497 | 25.3158 | 25.3158 | 25.3158 | 25.3158 | 25.3158 | 25.3158 | 25.3158 | 25.3158 | 52.455 | 25.3158 | 25.3158 | 25.3158 | 25.8207 | 26.6832 | 26.7447 | 25.9691 | 25.3158 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 16 | 7192 | 9.9 | 9.9 | 6.0958 | 6.7883 | 15 | 96 | 96 | 0.91856 | 27.784 | 10.1282 | 233.4923 | 0 | 0 | 0 | 0.074827 | 0.67232 | 0.87598 | 0.5665 | 0 | 0.21596 | 13.193 | 13.193 | 13.193 | 13.193 | 13.193 | 13.193 | 13.193 | 13.193 | 27.784 | 13.193 | 13.193 | 13.193 | 13.2679 | 13.8654 | 14.069 | 13.7595 | 13.193 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 17 | 7193 | 9.8 | 9.8 | 6.0958 | 6.7883 | 15 | 96 | 96 | 0.66502 | 10.9278 | 2.1844 | 245.8561 | 0 | 0 | 0 | 0 | 0.38947 | 0.64748 | 0.5262 | 0.096678 | 0.072188 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 10.9278 | 5.1148 | 5.1148 | 5.1148 | 5.1148 | 5.5043 | 5.7623 | 5.641 | 5.2115 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 18 | 7194 | 9.7 | 9.7 | 6.0958 | 6.7883 | 15 | 96 | 96 | 0 | 0 | -6.5517 | 257.6077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 19 | 7195 | 9.8 | 9.8 | 6.0958 | 6.7883 | 15 | 96 | 96 | 0 | 0 | -15.6895 | 269.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 20 | 7196 | 9.7 | 9.7 | 6.0958 | 6.7883 | 15 | 95 | 95 | 0 | 0 | -24.8475 | 281.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 21 | 7197 | 9.4 | 9.4 | 6.0958 | 6.7883 | 15 | 93 | 93 | 0 | 0 | -33.589 | 294.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 22 | 7198 | 9.1 | 9.1 | 6.0958 | 6.7883 | 15 | 93 | 93 | 0 | 0 | -41.3336 | 310.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 23 | 7199 | 9.3 | 9.3 | 6.0958 | 6.7883 | 15 | 88 | 88 | 0 | 0 | -47.2675 | 329.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 27 | 24 | 7200 | 9.2 | 9.2 | 8.825 | 7.3416 | 15 | 89 | 89 | 0 | 0 | -50.3937 | 351.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 1 | 7201 | 9.1 | 9.1 | 8.825 | 7.3416 | 15 | 92 | 92 | 0 | 0 | -49.9726 | 14.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 2 | 7202 | 8.9 | 8.9 | 8.825 | 7.3416 | 15 | 97 | 97 | 0 | 0 | -46.4232 | 35.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 3 | 7203 | 8.9 | 8.9 | 8.825 | 7.3416 | 15 | 96 | 96 | 0 | 0 | -39.9622 | 53.4994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 4 | 7204 | 9.2 | 9.2 | 8.825 | 7.3416 | 15 | 97 | 97 | 0 | 0 | -31.9067 | 68.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 5 | 7205 | 9.6 | 9.6 | 8.825 | 7.3416 | 15 | 98 | 98 | 0 | 0 | -23.0146 | 81.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 6 | 7206 | 10.2 | 10.2 | 8.825 | 7.3416 | 15 | 94 | 94 | 0 | 0 | -13.8243 | 93.6721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 7 | 7207 | 10.3 | 10.3 | 8.825 | 7.3416 | 15 | 94 | 94 | 0 | 0 | -4.7515 | 105.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 28 | 8 | 7208 | 9.8 | 9.8 | 8.825 | 7.3416 | 15 | 94 | 94 | 0 | 3 | 3.8262 | 117.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 9 | 7209 | 10.1 | 10.1 | 8.825 | 7.3416 | 15 | 93 | 93 | 1.7029 | 21.769 | 11.5107 | 129.6653 | 0 | 0.52165 | 1.5123 | 1.617 | 0.77455 | 0 | 0 | 0 | 0.23097 | 10.5886 | 11.9941 | 14.6634 | 14.9456 | 12.6756 | 10.5886 | 10.5886 | 10.5886 | 21.769 | 10.5886 | 12.5158 | 16.1756 | 16.5627 | 13.4501 | 10.5886 | 10.5886 | 10.5886 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 10 | 7210 | 10.8 | 10.8 | 8.825 | 7.3416 | 15 | 93 | 93 | 2.4663 | 49.3683 | 17.8533 | 143.2782 | 0 | 0.22468 | 1.8603 | 2.4062 | 1.5426 | 0 | 0 | 0 | 0.63174 | 24.3261 | 24.3261 | 24.3261 | 24.3261 | 24.3261 | 24.3261 | 24.3261 | 24.3261 | 49.3683 | 24.3261 | 24.5508 | 26.1864 | 26.7323 | 25.8687 | 24.3261 | 24.3261 | 24.3261 | 50 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 11 | 7211 | 11.7 | 11.7 | 8.825 | 7.3416 | 15 | 90 | 90 | 4.2564 | 87.5227 | 22.3661 | 158.083 | 0 | 0 | 2.4225 | 4.0092 | 3.2474 | 0.58333 | 0 | 0 | 1.4773 | 43.0371 | 43.0371 | 45.8782 | 47.7391 | 46.8457 | 43.7212 | 43.0371 | 43.0371 | 87.5227 | 43.0371 | 43.0371 | 48.3006 | 51.7484 | 50.0931 | 44.3045 | 43.0371 | 43.0371 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 12 | 7212 | 12.2 | 12.2 | 8.825 | 7.3416 | 15 | 89 | 89 | 2.9597 | 84.8097 | 24.6038 | 173.8309 | 0 | 0 | 1.0216 | 2.5179 | 2.5392 | 1.0731 | 0 | 0 | 1.1903 | 41.8709 | 41.8709 | 41.8709 | 41.8709 | 41.8709 | 41.8709 | 41.8709 | 41.8709 | 84.8097 | 41.8709 | 41.8709 | 42.8926 | 44.3889 | 44.4102 | 42.944 | 41.8709 | 41.8709 | 86 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 13 | 7213 | 12.6 | 12.6 | 8.825 | 7.3416 | 15 | 87 | 87 | 2.5555 | 81.9325 | 24.3049 | 189.8833 | 0 | 0 | 0.24969 | 1.81 | 2.3101 | 1.4569 | 0 | 0 | 1.0675 | 40.2292 | 40.2292 | 40.2292 | 40.2292 | 40.2292 | 40.2292 | 40.2292 | 40.2292 | 81.9325 | 40.2292 | 40.2292 | 40.4789 | 42.0392 | 42.5393 | 41.6861 | 40.2292 | 40.2292 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 14 | 7214 | 13 | 13 | 8.825 | 7.3416 | 15 | 85 | 85 | 2.362 | 74.0726 | 21.5061 | 205.4567 | 0 | 0 | 0 | 1.2383 | 2.1207 | 1.7608 | 0.36949 | 0 | 0.92736 | 36.1979 | 36.1979 | 36.1979 | 36.1979 | 36.1979 | 36.1979 | 36.1979 | 36.1979 | 74.0726 | 36.1979 | 36.1979 | 36.1979 | 37.4362 | 38.3186 | 37.9587 | 36.5674 | 36.1979 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 15 | 7215 | 13.5 | 13.5 | 8.825 | 7.3416 | 15 | 83 | 83 | 2.8542 | 68.0621 | 16.5249 | 219.9912 | 0 | 0 | 0 | 0.8883 | 2.3976 | 2.5025 | 1.1414 | 0 | 0.93785 | 33.2543 | 33.2543 | 33.2543 | 33.2543 | 33.2543 | 33.2543 | 33.2543 | 33.2543 | 68.0621 | 33.2543 | 33.2543 | 33.2543 | 34.1426 | 35.652 | 35.7568 | 34.3957 | 33.2543 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 16 | 7216 | 13.5 | 13.5 | 8.825 | 7.3416 | 15 | 82 | 82 | 1.5854 | 35.6353 | 9.8277 | 233.334 | 0 | 0 | 0 | 0.1327 | 1.1645 | 1.5141 | 0.97682 | 0 | 0.36469 | 17.0603 | 17.0603 | 17.0603 | 17.0603 | 17.0603 | 17.0603 | 17.0603 | 17.0603 | 35.6353 | 17.0603 | 17.0603 | 17.0603 | 17.193 | 18.2248 | 18.5744 | 18.0371 | 17.0603 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 17 | 7217 | 13.2 | 13.2 | 8.825 | 7.3416 | 15 | 84 | 84 | 0.72909 | 10.9244 | 1.8977 | 245.6761 | 0 | 0 | 0 | 0 | 0.42899 | 0.71081 | 0.57624 | 0.10413 | 0.075566 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 10.9244 | 5.1149 | 5.1149 | 5.1149 | 5.1149 | 5.5439 | 5.8257 | 5.6911 | 5.219 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 18 | 7218 | 13.2 | 13.2 | 8.825 | 7.3416 | 15 | 83 | 83 | 0 | 0 | -6.829 | 257.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 19 | 7219 | 13.1 | 13.1 | 8.825 | 7.3416 | 15 | 82 | 82 | 0 | 0 | -15.963 | 269.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 20 | 7220 | 12.7 | 12.7 | 8.825 | 7.3416 | 15 | 84 | 84 | 0 | 0 | -25.1241 | 281.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 21 | 7221 | 12.3 | 12.3 | 8.825 | 7.3416 | 15 | 85 | 85 | 0 | 0 | -33.8763 | 294.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 22 | 7222 | 11.7 | 11.7 | 8.825 | 7.3416 | 15 | 89 | 89 | 0 | 0 | -41.6387 | 310.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 23 | 7223 | 10.7 | 10.7 | 8.825 | 7.3416 | 15 | 90 | 90 | 0 | 0 | -47.5931 | 329.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 28 | 24 | 7224 | 9.7 | 9.7 | 11.25 | 8.3428 | 15 | 92 | 92 | 0 | 0 | -50.7318 | 351.1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 1 | 7225 | 9.1 | 9.1 | 11.25 | 8.3428 | 15 | 92 | 92 | 0 | 0 | -50.3039 | 14.1766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 2 | 7226 | 8.6 | 8.6 | 11.25 | 8.3428 | 15 | 93 | 93 | 0 | 0 | -46.7292 | 35.6582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 3 | 7227 | 8.3 | 8.3 | 11.25 | 8.3428 | 15 | 93 | 93 | 0 | 0 | -40.2431 | 53.7378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 4 | 7228 | 7.8 | 7.8 | 11.25 | 8.3428 | 15 | 93 | 93 | 0 | 0 | -32.1688 | 68.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 5 | 7229 | 7.6 | 7.6 | 11.25 | 8.3428 | 15 | 91 | 91 | 0 | 0 | -23.2669 | 81.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 6 | 7230 | 7.3 | 7.3 | 11.25 | 8.3428 | 15 | 92 | 92 | 0 | 0 | -14.0751 | 93.9007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 7 | 7231 | 6.1 | 6.1 | 11.25 | 8.3428 | 15 | 95 | 95 | 0 | 0 | -5.0082 | 105.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 29 | 8 | 7232 | 6.5 | 6.5 | 11.25 | 8.3428 | 15 | 94 | 94 | 0 | 3 | 3.5573 | 117.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 9 | 7233 | 7.2 | 7.2 | 11.25 | 8.3428 | 15 | 91 | 91 | 4.1222 | 32.4611 | 11.2252 | 129.8437 | 0 | 1.2495 | 3.6553 | 3.92 | 1.8883 | 0 | 0 | 0 | 0.53891 | 14.4107 | 31.0413 | 63.0638 | 66.5859 | 39.5445 | 14.4107 | 14.4107 | 14.4107 | 32.4611 | 14.4107 | 32.2908 | 66.7191 | 70.5058 | 41.4328 | 14.4107 | 14.4107 | 14.4107 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 10 | 7234 | 7.2 | 7.2 | 11.25 | 8.3428 | 15 | 92 | 92 | 46.146 | 110.4136 | 17.5488 | 143.4245 | 0 | 4.0679 | 34.7529 | 45.0801 | 29 | 0 | 0 | 0 | 11.5864 | 50.4633 | 60.2856 | 134.3763 | 159.3119 | 120.4855 | 50.4633 | 50.4633 | 50.4633 | 110.4136 | 50.4633 | 64.3535 | 169.1291 | 204.3919 | 149.4854 | 50.4633 | 50.4633 | 50.4633 | 122 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 11 | 7235 | 8.2 | 8.2 | 11.25 | 8.3428 | 15 | 89 | 89 | 97.5724 | 160.6427 | 22.0443 | 158.183 | 0 | 0 | 55.4358 | 92.0276 | 74.711 | 13.6296 | 0 | 0 | 33.3573 | 74.931 | 74.931 | 137.2105 | 178.3198 | 158.8653 | 90.2433 | 74.931 | 74.931 | 160.6427 | 74.931 | 74.931 | 192.6463 | 270.3474 | 233.5763 | 103.8729 | 74.931 | 74.931 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 12 | 7236 | 9.9 | 9.9 | 11.25 | 8.3428 | 15 | 85 | 85 | 81.9326 | 184.4803 | 24.271 | 173.8714 | 0 | 0 | 28.2237 | 69.8106 | 70.5034 | 29.8963 | 0 | 0 | 32.5197 | 85.9776 | 85.9776 | 120.7013 | 171.8658 | 172.7182 | 122.7591 | 85.9776 | 85.9776 | 184.4803 | 85.9776 | 85.9776 | 148.9249 | 241.6764 | 243.2216 | 152.6554 | 85.9776 | 85.9776 | 217 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 13 | 7237 | 11 | 11 | 11.25 | 8.3428 | 15 | 83 | 83 | 71.2831 | 189.6012 | 23.9708 | 189.8592 | 0 | 0 | 6.9375 | 50.5925 | 64.6112 | 40.7814 | 0 | 0 | 29.3988 | 88.5499 | 88.5499 | 97.5719 | 154.3438 | 172.5745 | 141.5848 | 88.5499 | 88.5499 | 189.6012 | 88.5499 | 88.5499 | 104.5094 | 204.9363 | 237.1857 | 182.3662 | 88.5499 | 88.5499 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 14 | 7238 | 11.5 | 11.5 | 11.25 | 8.3428 | 15 | 82 | 82 | 40.0982 | 167.4677 | 21.1802 | 205.3742 | 0 | 0 | 0 | 21.0895 | 36.0988 | 29.9619 | 6.2738 | 0 | 15.5323 | 78.6253 | 78.6253 | 78.6253 | 118.0356 | 146.0838 | 134.6157 | 90.3493 | 78.6253 | 167.4677 | 78.6253 | 78.6253 | 78.6253 | 139.1251 | 182.1826 | 164.5777 | 96.623 | 78.6253 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 15 | 7239 | 12 | 12 | 11.25 | 8.3428 | 15 | 82 | 82 | 24.8709 | 130.9562 | 16.2132 | 219.8636 | 0 | 0 | 0 | 7.7892 | 20.9536 | 21.8436 | 9.938 | 0 | 8.0438 | 62.5314 | 62.5314 | 62.5314 | 80.0553 | 109.6719 | 111.6742 | 84.8894 | 62.5314 | 130.9562 | 62.5314 | 62.5314 | 62.5314 | 87.8446 | 130.6255 | 133.5179 | 94.8273 | 62.5314 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 16 | 7240 | 12 | 12 | 11.25 | 8.3428 | 15 | 80 | 80 | 7.8769 | 73.2277 | 9.5319 | 233.1749 | 0 | 0 | 0 | 0.67715 | 5.8057 | 7.5333 | 4.848 | 0 | 1.7723 | 36.4384 | 36.4384 | 36.4384 | 36.4384 | 36.4384 | 36.4384 | 36.4384 | 36.4384 | 73.2277 | 36.4384 | 36.4384 | 36.4384 | 37.1155 | 42.244 | 43.9717 | 41.2864 | 36.4384 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 17 | 7241 | 11.9 | 11.9 | 11.25 | 8.3428 | 15 | 81 | 81 | 4.1435 | 24.5907 | 1.6157 | 245.4955 | 0 | 0 | 0 | 0 | 2.4492 | 4.0447 | 3.2709 | 0.58105 | 0.40932 | 11.797 | 11.797 | 11.797 | 11.797 | 11.797 | 11.797 | 11.797 | 11.797 | 24.5907 | 11.797 | 11.797 | 11.797 | 11.797 | 14.2462 | 15.8417 | 15.0679 | 12.378 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 29 | 18 | 7242 | 12.2 | 12.2 | 11.25 | 8.3428 | 15 | 79 | 79 | 0 | 0 | -7.1014 | 257.2161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 19 | 7243 | 12.7 | 12.7 | 11.25 | 8.3428 | 15 | 73 | 73 | 0 | 0 | -16.2316 | 268.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 20 | 7244 | 12.9 | 12.9 | 11.25 | 8.3428 | 15 | 69 | 69 | 0 | 0 | -25.3956 | 281.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 21 | 7245 | 12.1 | 12.1 | 11.25 | 8.3428 | 15 | 71 | 71 | 0 | 0 | -34.1585 | 294.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 22 | 7246 | 11.7 | 11.7 | 11.25 | 8.3428 | 15 | 75 | 75 | 0 | 0 | -41.9389 | 310.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 23 | 7247 | 11.4 | 11.4 | 11.25 | 8.3428 | 15 | 76 | 76 | 0 | 0 | -47.9143 | 329.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 29 | 24 | 7248 | 11.5 | 11.5 | 9.8625 | 8.7105 | 15 | 76 | 76 | 0 | 0 | -51.0662 | 351.0908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 1 | 7249 | 12.7 | 12.7 | 9.8625 | 8.7105 | 15 | 70 | 70 | 0 | 0 | -50.6322 | 14.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 2 | 7250 | 12.7 | 12.7 | 9.8625 | 8.7105 | 15 | 69 | 69 | 0 | 0 | -47.0326 | 35.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 3 | 7251 | 12.4 | 12.4 | 9.8625 | 8.7105 | 15 | 71 | 71 | 0 | 0 | -40.5221 | 53.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 4 | 7252 | 12.6 | 12.6 | 9.8625 | 8.7105 | 15 | 71 | 71 | 0 | 0 | -32.4296 | 69.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 5 | 7253 | 12.2 | 12.2 | 9.8625 | 8.7105 | 15 | 73 | 73 | 0 | 0 | -23.5181 | 82.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 6 | 7254 | 12.2 | 12.2 | 9.8625 | 8.7105 | 15 | 75 | 75 | 0 | 0 | -14.3251 | 94.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 7 | 7255 | 12 | 12 | 9.8625 | 8.7105 | 15 | 80 | 80 | 0 | 0 | -5.2641 | 105.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 30 | 8 | 7256 | 11.6 | 11.6 | 9.8625 | 8.7105 | 15 | 88 | 88 | 0 | 3 | 3.2895 | 117.5157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 9 | 7257 | 11.7 | 11.7 | 9.8625 | 8.7105 | 15 | 93 | 93 | 2.5506 | 24.6789 | 10.941 | 130.017 | 0 | 0.76504 | 2.2583 | 2.4287 | 1.1764 | 0 | 0 | 0 | 0.32106 | 11.5094 | 18.1934 | 31.2398 | 32.7285 | 21.7873 | 11.5094 | 11.5094 | 11.5094 | 24.6789 | 11.5094 | 18.9584 | 33.4981 | 35.1572 | 22.9637 | 11.5094 | 11.5094 | 11.5094 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 10 | 7258 | 12.1 | 12.1 | 9.8625 | 8.7105 | 15 | 92 | 92 | 6.7167 | 76.3473 | 17.2463 | 143.5656 | 0 | 0.57281 | 5.0505 | 6.5697 | 4.2404 | 0 | 0 | 0 | 1.6527 | 35.2252 | 38.7679 | 66.4614 | 75.8571 | 61.4513 | 35.2252 | 35.2252 | 35.2252 | 76.3473 | 35.2252 | 39.3407 | 71.5119 | 82.4268 | 65.6917 | 35.2252 | 35.2252 | 35.2252 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 11 | 7259 | 12.4 | 12.4 | 9.8625 | 8.7105 | 15 | 90 | 90 | 6.0506 | 100.9626 | 21.7252 | 158.2782 | 0 | 0 | 3.4319 | 5.7141 | 4.649 | 0.86067 | 0 | 0 | 2.0374 | 48.238 | 48.238 | 59.7608 | 67.4235 | 63.8475 | 51.1278 | 48.238 | 48.238 | 100.9626 | 48.238 | 48.238 | 63.1927 | 73.1375 | 68.4966 | 51.9884 | 48.238 | 48.238 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 12 | 7260 | 12.3 | 12.3 | 9.8625 | 8.7105 | 15 | 92 | 92 | 3.5676 | 90.6026 | 23.9415 | 173.9079 | 0 | 0 | 1.2266 | 3.0444 | 3.0789 | 1.3098 | 0 | 0 | 1.3974 | 44.9763 | 44.9763 | 44.9763 | 44.9763 | 44.9763 | 44.9763 | 44.9763 | 44.9763 | 90.6026 | 44.9763 | 44.9763 | 46.2029 | 48.0208 | 48.0552 | 46.2861 | 44.9763 | 44.9763 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 13 | 7261 | 12.6 | 12.6 | 9.8625 | 8.7105 | 15 | 93 | 93 | 4.3825 | 104.2156 | 23.6405 | 189.8321 | 0 | 0 | 0.42508 | 3.1168 | 3.9828 | 2.5157 | 0 | 0 | 1.7844 | 51.9928 | 51.9928 | 51.9928 | 51.9928 | 51.9928 | 51.9928 | 51.9928 | 51.9928 | 104.2156 | 51.9928 | 51.9928 | 52.4179 | 55.1096 | 55.9756 | 54.5085 | 51.9928 | 51.9928 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 14 | 7262 | 12.9 | 12.9 | 9.8625 | 8.7105 | 15 | 89 | 89 | 5.4559 | 108.9151 | 20.8586 | 205.2897 | 0 | 0 | 0 | 2.8787 | 4.9246 | 4.0857 | 0.85347 | 0 | 2.0849 | 54.1316 | 54.1316 | 54.1316 | 55.2479 | 56.0413 | 55.716 | 54.4626 | 54.1316 | 108.9151 | 54.1316 | 54.1316 | 54.1316 | 58.1266 | 60.9659 | 59.8017 | 55.316 | 54.1316 | 111 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 15 | 7263 | 13.1 | 13.1 | 9.8625 | 8.7105 | 15 | 86 | 86 | 11.6431 | 113.294 | 15.9061 | 219.7348 | 0 | 0 | 0 | 3.6695 | 9.8373 | 10.2426 | 4.6479 | 0 | 3.706 | 55.0173 | 55.0173 | 55.0173 | 59.3643 | 66.671 | 67.1511 | 60.5234 | 55.0173 | 113.294 | 55.0173 | 55.0173 | 55.0173 | 63.0337 | 76.5083 | 77.3937 | 65.1713 | 55.0173 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 16 | 7264 | 13.1 | 13.1 | 9.8625 | 8.7105 | 15 | 84 | 84 | 28.2413 | 90.7868 | 9.2407 | 233.0151 | 0 | 0 | 0 | 2.4924 | 20.8864 | 27.0454 | 17.3616 | 0 | 6.2132 | 44.3567 | 44.3567 | 44.3567 | 48.0309 | 75.1478 | 84.2277 | 69.9516 | 44.3567 | 90.7868 | 44.3567 | 44.3567 | 44.3567 | 50.5233 | 96.0342 | 111.2731 | 87.3132 | 44.3567 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 17 | 7265 | 12.1 | 12.1 | 9.8625 | 8.7105 | 15 | 89 | 89 | 30.2479 | 39.1574 | 1.3385 | 245.3143 | 0 | 0 | 0 | 0 | 17.9611 | 29.5637 | 23.8483 | 4.1628 | 2.8426 | 19.9962 | 19.9962 | 19.9962 | 19.9962 | 30.2625 | 36.8943 | 33.6275 | 22.3756 | 39.1574 | 19.9962 | 19.9962 | 19.9962 | 19.9962 | 48.2236 | 66.458 | 57.4757 | 26.5384 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 30 | 18 | 7266 | 11.1 | 11.1 | 9.8625 | 8.7105 | 15 | 95 | 95 | 0 | 0 | -7.3689 | 257.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 19 | 7267 | 9.9 | 9.9 | 9.8625 | 8.7105 | 15 | 99 | 99 | 0 | 0 | -16.4951 | 268.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 20 | 7268 | 9.2 | 9.2 | 9.8625 | 8.7105 | 15 | 99 | 99 | 0 | 0 | -25.662 | 280.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 21 | 7269 | 8.8 | 8.8 | 9.8625 | 8.7105 | 15 | 99 | 99 | 0 | 0 | -34.4355 | 294.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 22 | 7270 | 8.5 | 8.5 | 9.8625 | 8.7105 | 15 | 98 | 98 | 0 | 0 | -42.2339 | 309.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 23 | 7271 | 8 | 8 | 9.8625 | 8.7105 | 15 | 99 | 99 | 0 | 0 | -48.2308 | 328.9267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 30 | 24 | 7272 | 7.6 | 7.6 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -51.3966 | 351.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 1 | 7273 | 7.5 | 7.5 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -50.9573 | 14.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 2 | 7274 | 5.8 | 5.8 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -47.3336 | 36.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 3 | 7275 | 6.9 | 6.9 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -40.7991 | 54.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 4 | 7276 | 5.9 | 5.9 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -32.6888 | 69.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 5 | 7277 | 6 | 6 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -23.7682 | 82.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 6 | 7278 | 6.4 | 6.4 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -14.574 | 94.3443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 7 | 7279 | 7.2 | 7.2 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -5.5189 | 105.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2010 | 10 | 31 | 8 | 7280 | 7.8 | 7.8 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | 3.0229 | 117.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 9 | 7281 | 8.4 | 8.4 | 11.4083 | 9.491 | 15 | 99 | 99 | 2.134 | 21.7416 | 10.6584 | 130.1852 | 0 | 0.6335 | 1.8867 | 2.0347 | 0.99078 | 0 | 0 | 0 | 0.25837 | 10.268 | 14.7398 | 23.586 | 24.6307 | 17.2619 | 10.268 | 10.268 | 10.268 | 21.7416 | 10.268 | 15.3733 | 25.4727 | 26.6653 | 18.2527 | 10.268 | 10.268 | 10.268 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 10 | 7282 | 9.6 | 9.6 | 11.4083 | 9.491 | 15 | 97 | 97 | 3.7409 | 57.0981 | 16.9458 | 143.7016 | 0 | 0.30858 | 2.8086 | 3.6634 | 2.3722 | 0 | 0 | 0 | 0.90186 | 27.6764 | 28.4754 | 34.949 | 37.1624 | 33.819 | 27.6764 | 27.6764 | 27.6764 | 57.0981 | 27.6764 | 28.784 | 37.7576 | 40.8258 | 36.1912 | 27.6764 | 27.6764 | 27.6764 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 11 | 7283 | 10.3 | 10.3 | 11.4083 | 9.491 | 15 | 95 | 95 | 4.3469 | 84.5585 | 21.4088 | 158.3685 | 0 | 0 | 2.4616 | 4.1103 | 3.3512 | 0.62908 | 0 | 0 | 1.4415 | 41.4726 | 41.4726 | 44.8353 | 47.0876 | 46.0507 | 42.332 | 41.4726 | 41.4726 | 84.5585 | 41.4726 | 41.4726 | 47.2969 | 51.1979 | 49.4019 | 42.961 | 41.4726 | 41.4726 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 12 | 7284 | 11.4 | 11.4 | 11.4083 | 9.491 | 15 | 93 | 93 | 6.2224 | 116.5951 | 23.6155 | 173.9403 | 0 | 0 | 2.1355 | 5.3179 | 5.3851 | 2.2978 | 0 | 0 | 2.4049 | 56.4622 | 56.4622 | 61.3195 | 68.5577 | 68.7106 | 61.6885 | 56.4622 | 56.4622 | 116.5951 | 56.4622 | 56.4622 | 63.455 | 73.8756 | 74.0957 | 63.9863 | 56.4622 | 56.4622 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 13 | 7285 | 12 | 12 | 11.4083 | 9.491 | 15 | 89 | 89 | 12.4416 | 144.9989 | 23.3143 | 189.802 | 0 | 0 | 1.2034 | 8.8667 | 11.336 | 7.1648 | 0 | 0 | 5.0011 | 68.8995 | 68.8995 | 71.6214 | 88.954 | 94.5391 | 85.1048 | 68.8995 | 68.8995 | 144.9989 | 68.8995 | 68.8995 | 72.8248 | 97.8207 | 105.8751 | 92.2696 | 68.8995 | 68.8995 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 14 | 7286 | 12.5 | 12.5 | 11.4083 | 9.491 | 15 | 88 | 88 | 9.7488 | 129.325 | 20.5414 | 205.2033 | 0 | 0 | 0 | 5.1604 | 8.8221 | 7.3159 | 1.5242 | 0 | 3.675 | 62.5422 | 62.5422 | 62.5422 | 71.2587 | 77.4437 | 74.8996 | 65.1167 | 62.5422 | 129.325 | 62.5422 | 62.5422 | 62.5422 | 76.4191 | 86.2658 | 82.2155 | 66.6408 | 62.5422 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 15 | 7287 | 12.6 | 12.6 | 11.4083 | 9.491 | 15 | 86 | 86 | 38.6368 | 134.8983 | 15.6036 | 219.6048 | 0 | 0 | 0 | 12.2537 | 32.736 | 34.042 | 15.4067 | 0 | 12.1017 | 64.3768 | 64.3768 | 64.3768 | 83.9278 | 116.6077 | 118.6915 | 88.9584 | 64.3768 | 134.8983 | 64.3768 | 64.3768 | 64.3768 | 96.1814 | 149.3437 | 152.7335 | 104.3651 | 64.3768 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 16 | 7288 | 13.1 | 13.1 | 11.4083 | 9.491 | 15 | 83 | 83 | 54.1119 | 96.3623 | 8.9543 | 232.8545 | 0 | 0 | 0 | 4.9004 | 40.1546 | 51.8868 | 33.2244 | 0 | 11.6377 | 47.1728 | 47.1728 | 47.1728 | 51.5396 | 82.9547 | 93.4092 | 76.7792 | 47.1728 | 96.3623 | 47.1728 | 47.1728 | 47.1728 | 56.4399 | 123.1092 | 145.296 | 110.0036 | 47.1728 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 17 | 7289 | 11.6 | 11.6 | 11.4083 | 9.491 | 15 | 90 | 90 | 153.2715 | 42.3256 | 1.0662 | 245.1325 | 0 | 0 | 0 | 0 | 91.4238 | 149.9832 | 120.6844 | 20.6904 | 13.6744 | 23.611 | 23.611 | 23.611 | 23.611 | 66.2973 | 93.639 | 79.9593 | 33.2715 | 42.3256 | 23.611 | 23.611 | 23.611 | 23.611 | 157.7211 | 243.6222 | 200.6437 | 53.9618 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2010 | 10 | 31 | 18 | 7290 | 10.8 | 10.8 | 11.4083 | 9.491 | 15 | 97 | 97 | 0 | 0 | -7.6313 | 256.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 19 | 7291 | 11.3 | 11.3 | 11.4083 | 9.491 | 15 | 96 | 96 | 0 | 0 | -16.7535 | 268.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 20 | 7292 | 11.8 | 11.8 | 11.4083 | 9.491 | 15 | 94 | 94 | 0 | 0 | -25.9231 | 280.5725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 21 | 7293 | 11.3 | 11.3 | 11.4083 | 9.491 | 15 | 94 | 94 | 0 | 0 | -34.7071 | 294.0375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 22 | 7294 | 10.1 | 10.1 | 11.4083 | 9.491 | 15 | 98 | 98 | 0 | 0 | -42.5238 | 309.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 23 | 7295 | 9.5 | 9.5 | 11.4083 | 9.491 | 15 | 99 | 99 | 0 | 0 | -48.5426 | 328.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2010 | 10 | 31 | 24 | 7296 | 7.8 | 7.8 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -51.7231 | 351.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 1 | 7297 | 7 | 7 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -51.2793 | 14.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 2 | 7298 | 6.9 | 6.9 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -47.632 | 36.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 3 | 7299 | 6.9 | 6.9 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -41.0741 | 54.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 4 | 7300 | 6.9 | 6.9 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -32.9465 | 69.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 5 | 7301 | 7.3 | 7.3 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -24.017 | 82.6173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 6 | 7302 | 7.8 | 7.8 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -14.8219 | 94.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 7 | 7303 | 8.2 | 8.2 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | -5.7727 | 106.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 1 | 8 | 7304 | 8.5 | 8.5 | 9.4833 | 9.6297 | 15 | 99 | 99 | 0 | 0 | 2.7576 | 117.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 9 | 7305 | 9.1 | 9.1 | 9.4833 | 9.6297 | 15 | 99 | 99 | 4.5882 | 30.4663 | 10.3774 | 130.3483 | 0 | 1.3482 | 4.0505 | 4.3801 | 2.1438 | 0 | 0 | 0 | 0.53371 | 13.0753 | 32.7074 | 72.0568 | 76.8556 | 44.2928 | 13.0753 | 13.0753 | 13.0753 | 30.4663 | 13.0753 | 34.0556 | 76.1073 | 81.2357 | 46.4366 | 13.0753 | 13.0753 | 13.0753 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 10 | 7306 | 9.7 | 9.7 | 9.4833 | 9.6297 | 15 | 99 | 99 | 4.7446 | 62.8795 | 16.6476 | 143.8325 | 0 | 0.37849 | 3.5568 | 4.6516 | 3.0216 | 0 | 0 | 0 | 1.1205 | 29.8482 | 31.5676 | 46.007 | 50.9807 | 43.5752 | 29.8482 | 29.8482 | 29.8482 | 62.8795 | 29.8482 | 31.9461 | 49.5638 | 55.6323 | 46.5968 | 29.8482 | 29.8482 | 29.8482 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 11 | 7307 | 10.2 | 10.2 | 9.4833 | 9.6297 | 15 | 92 | 92 | 21.1042 | 129.1082 | 21.0953 | 158.4541 | 0 | 0 | 11.9326 | 19.9799 | 16.3232 | 3.1047 | 0 | 0 | 6.8918 | 58.4447 | 58.4447 | 95.1881 | 119.9677 | 108.7079 | 68.0047 | 58.4447 | 58.4447 | 129.1082 | 58.4447 | 58.4447 | 107.1207 | 139.9475 | 125.0312 | 71.1094 | 58.4447 | 58.4447 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 12 | 7308 | 10.6 | 10.6 | 9.4833 | 9.6297 | 15 | 89 | 89 | 11.1779 | 134.7372 | 23.2931 | 173.9687 | 0 | 0 | 3.8299 | 9.5672 | 9.7001 | 4.1508 | 0 | 0 | 4.2628 | 63.4775 | 63.4775 | 74.5921 | 91.2416 | 91.6273 | 75.5233 | 63.4775 | 63.4775 | 134.7372 | 63.4775 | 63.4775 | 78.422 | 100.8088 | 101.3274 | 79.6741 | 63.4775 | 63.4775 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 13 | 7309 | 11 | 11 | 9.4833 | 9.6297 | 15 | 83 | 83 | 51.0464 | 176.7443 | 22.9923 | 189.7689 | 0 | 0 | 4.9264 | 36.4533 | 46.6263 | 29.4863 | 0 | 0 | 20.2557 | 82.4452 | 82.4452 | 90.7396 | 143.8208 | 160.949 | 132.0907 | 82.4452 | 82.4452 | 176.7443 | 82.4452 | 82.4452 | 95.666 | 180.2741 | 207.5753 | 161.577 | 82.4452 | 82.4452 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 14 | 7310 | 10.4 | 10.4 | 9.4833 | 9.6297 | 15 | 86 | 86 | 4.1282 | 92.4649 | 20.2287 | 205.1148 | 0 | 0 | 0 | 2.1923 | 3.7452 | 3.1042 | 0.64481 | 0 | 1.5351 | 45.8535 | 45.8535 | 45.8535 | 45.8535 | 45.8535 | 45.8535 | 45.8535 | 45.8535 | 92.4649 | 45.8535 | 45.8535 | 45.8535 | 48.0457 | 49.5986 | 48.9576 | 46.4983 | 45.8535 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 15 | 7311 | 10.3 | 10.3 | 9.4833 | 9.6297 | 15 | 84 | 84 | 1.3168 | 43.5942 | 15.3058 | 219.4736 | 0 | 0 | 0 | 0.42026 | 1.1188 | 1.1619 | 0.52442 | 0 | 0.40582 | 20.9251 | 20.9251 | 20.9251 | 20.9251 | 20.9251 | 20.9251 | 20.9251 | 20.9251 | 43.5942 | 20.9251 | 20.9251 | 20.9251 | 21.3454 | 22.0438 | 22.087 | 21.4495 | 20.9251 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 16 | 7312 | 9.5 | 9.5 | 9.4833 | 9.6297 | 15 | 91 | 91 | 0.52792 | 18.889 | 8.6728 | 232.6931 | 0 | 0 | 0 | 0.049038 | 0.39306 | 0.50683 | 0.32371 | 0 | 0.11096 | 8.8963 | 8.8963 | 8.8963 | 8.8963 | 8.8963 | 8.8963 | 8.8963 | 8.8963 | 18.889 | 8.8963 | 8.8963 | 8.8963 | 8.9453 | 9.2893 | 9.4031 | 9.22 | 8.8963 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 17 | 7313 | 9 | 9 | 9.4833 | 9.6297 | 15 | 95 | 95 | 0.081407 | 2.9931 | 0.79894 | 244.9503 | 0 | 0 | 0 | 0 | 0.048776 | 0.079752 | 0.064011 | 0.010773 | 0.0068798 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 2.9931 | 1.3821 | 1.3821 | 1.3821 | 1.3821 | 1.4309 | 1.4618 | 1.4461 | 1.3929 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 1 | 18 | 7314 | 9.1 | 9.1 | 9.4833 | 9.6297 | 15 | 96 | 96 | 0 | 0 | -7.8887 | 256.6241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 19 | 7315 | 9.2 | 9.2 | 9.4833 | 9.6297 | 15 | 96 | 96 | 0 | 0 | -17.0065 | 268.2176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 20 | 7316 | 9.4 | 9.4 | 9.4833 | 9.6297 | 15 | 97 | 97 | 0 | 0 | -26.1788 | 280.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 21 | 7317 | 9.6 | 9.6 | 9.4833 | 9.6297 | 15 | 94 | 94 | 0 | 0 | -34.9734 | 293.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 22 | 7318 | 9.6 | 9.6 | 9.4833 | 9.6297 | 15 | 91 | 91 | 0 | 0 | -42.8083 | 309.5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 23 | 7319 | 9.9 | 9.9 | 9.4833 | 9.6297 | 15 | 89 | 89 | 0 | 0 | -48.8495 | 328.6214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 1 | 24 | 7320 | 9.7 | 9.7 | 8.9917 | 9.6635 | 15 | 87 | 87 | 0 | 0 | -52.0454 | 350.9722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 1 | 7321 | 7.5 | 7.5 | 8.9917 | 9.6635 | 15 | 93 | 93 | 0 | 0 | -51.5979 | 14.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 2 | 7322 | 6.2 | 6.2 | 8.9917 | 9.6635 | 15 | 97 | 97 | 0 | 0 | -47.9276 | 36.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 3 | 7323 | 6.3 | 6.3 | 8.9917 | 9.6635 | 15 | 97 | 97 | 0 | 0 | -41.3471 | 54.6482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 4 | 7324 | 6.2 | 6.2 | 8.9917 | 9.6635 | 15 | 97 | 97 | 0 | 0 | -33.2026 | 69.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 5 | 7325 | 6.3 | 6.3 | 8.9917 | 9.6635 | 15 | 94 | 94 | 0 | 0 | -24.2645 | 82.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 6 | 7326 | 6.7 | 6.7 | 8.9917 | 9.6635 | 15 | 91 | 91 | 0 | 0 | -15.0687 | 94.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 7 | 7327 | 6.6 | 6.6 | 8.9917 | 9.6635 | 15 | 92 | 92 | 0 | 0 | -6.0254 | 106.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 2 | 8 | 7328 | 6.9 | 6.9 | 8.9917 | 9.6635 | 15 | 92 | 92 | 0 | 0 | 2.4936 | 118.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 9 | 7329 | 7.4 | 7.4 | 8.9917 | 9.6635 | 15 | 91 | 91 | 3.2389 | 24.6385 | 10.0982 | 130.5061 | 0 | 0.94222 | 2.8552 | 3.0957 | 1.5227 | 0 | 0 | 0 | 0.36154 | 11.0112 | 22.2618 | 45.1039 | 47.975 | 29.1932 | 11.0112 | 11.0112 | 11.0112 | 24.6385 | 11.0112 | 23.204 | 47.9592 | 51.0707 | 30.7159 | 11.0112 | 11.0112 | 11.0112 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 10 | 7330 | 8.5 | 8.5 | 8.9917 | 9.6635 | 15 | 87 | 87 | 8.1679 | 76.1109 | 16.3517 | 143.9582 | 0 | 0.63006 | 6.1142 | 8.0167 | 5.2231 | 0 | 0 | 0 | 1.8891 | 34.5428 | 38.7614 | 75.4806 | 88.2189 | 69.5145 | 34.5428 | 34.5428 | 34.5428 | 76.1109 | 34.5428 | 39.3915 | 81.5948 | 96.2356 | 74.7377 | 34.5428 | 34.5428 | 34.5428 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 11 | 7331 | 9.7 | 9.7 | 8.9917 | 9.6635 | 15 | 82 | 82 | 33.7155 | 136.1586 | 20.7848 | 158.5348 | 0 | 0 | 19.035 | 31.9571 | 26.1592 | 5.0376 | 0 | 0 | 10.8414 | 63.0937 | 63.0937 | 113.1249 | 147.0892 | 131.8502 | 76.3345 | 63.0937 | 63.0937 | 136.1586 | 63.0937 | 63.0937 | 132.1598 | 179.0464 | 158.0094 | 81.3721 | 63.0937 | 63.0937 | 147 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 12 | 7332 | 10.7 | 10.7 | 8.9917 | 9.6635 | 15 | 78 | 78 | 71.0909 | 173.2503 | 22.9743 | 173.993 | 0 | 0 | 24.3216 | 60.9356 | 61.8543 | 26.5396 | 0 | 0 | 26.7497 | 80.6976 | 80.6976 | 114.0099 | 164.1584 | 165.4168 | 117.0478 | 80.6976 | 80.6976 | 173.2503 | 80.6976 | 80.6976 | 138.3315 | 225.094 | 227.2711 | 143.5874 | 80.6976 | 80.6976 | 200 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 13 | 7333 | 10.9 | 10.9 | 8.9917 | 9.6635 | 15 | 77 | 77 | 25.1645 | 159.143 | 22.6745 | 189.7329 | 0 | 0 | 2.4246 | 18.0071 | 23.0413 | 14.5782 | 0 | 0 | 9.857 | 74.1626 | 74.1626 | 78.5935 | 107.0705 | 116.2705 | 100.8043 | 74.1626 | 74.1626 | 159.143 | 74.1626 | 74.1626 | 81.0181 | 125.0776 | 139.3118 | 115.3825 | 74.1626 | 74.1626 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 14 | 7334 | 11.5 | 11.5 | 8.9917 | 9.6635 | 15 | 75 | 75 | 15.7477 | 138.2241 | 19.9206 | 205.0245 | 0 | 0 | 0 | 8.3898 | 14.3214 | 11.8638 | 2.4565 | 0 | 5.7759 | 65.8833 | 65.8833 | 65.8833 | 80.1432 | 90.225 | 86.0478 | 70.0584 | 65.8833 | 138.2241 | 65.8833 | 65.8833 | 65.8833 | 88.533 | 104.5464 | 97.9115 | 72.5149 | 65.8833 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 15 | 7335 | 10.8 | 10.8 | 8.9917 | 9.6635 | 15 | 83 | 83 | 1.2389 | 41.6243 | 15.013 | 219.3412 | 0 | 0 | 0 | 0.39791 | 1.0554 | 1.0947 | 0.49271 | 0 | 0.37565 | 19.9528 | 19.9528 | 19.9528 | 19.9528 | 19.9528 | 19.9528 | 19.9528 | 19.9528 | 41.6243 | 19.9528 | 19.9528 | 19.9528 | 20.3507 | 21.0082 | 21.0475 | 20.4455 | 19.9528 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 16 | 7336 | 10 | 10 | 8.9917 | 9.6635 | 15 | 93 | 93 | 0.44255 | 16.9091 | 8.3964 | 232.5312 | 0 | 0 | 0 | 0.042148 | 0.33058 | 0.42536 | 0.27097 | 0 | 0.090876 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 16.9091 | 7.9476 | 7.9476 | 7.9476 | 7.9897 | 8.2782 | 8.373 | 8.2186 | 7.9476 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 17 | 7337 | 10.3 | 10.3 | 8.9917 | 9.6635 | 15 | 94 | 94 | 0.3645 | 5.9709 | 0.5368 | 244.7676 | 0 | 0 | 0 | 0 | 0.21936 | 0.35748 | 0.2862 | 0.047261 | 0.029108 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 5.9709 | 2.7738 | 2.7738 | 2.7738 | 2.7738 | 2.9931 | 3.1312 | 3.06 | 2.821 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 2 | 18 | 7338 | 10.5 | 10.5 | 8.9917 | 9.6635 | 15 | 94 | 94 | 0 | 0 | -8.1407 | 256.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 19 | 7339 | 10.8 | 10.8 | 8.9917 | 9.6635 | 15 | 92 | 92 | 0 | 0 | -17.2542 | 268.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 20 | 7340 | 10.9 | 10.9 | 8.9917 | 9.6635 | 15 | 94 | 94 | 0 | 0 | -26.429 | 280.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 21 | 7341 | 11.4 | 11.4 | 8.9917 | 9.6635 | 15 | 93 | 93 | 0 | 0 | -35.234 | 293.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 22 | 7342 | 11.1 | 11.1 | 8.9917 | 9.6635 | 15 | 94 | 94 | 0 | 0 | -43.0874 | 309.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 23 | 7343 | 11.6 | 11.6 | 8.9917 | 9.6635 | 15 | 92 | 92 | 0 | 0 | -49.1513 | 328.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 2 | 24 | 7344 | 10.7 | 10.7 | 9.1458 | 9.689 | 15 | 91 | 91 | 0 | 0 | -52.3634 | 350.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 1 | 7345 | 11 | 11 | 9.1458 | 9.689 | 15 | 92 | 92 | 0 | 0 | -51.9132 | 14.6478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 2 | 7346 | 10.7 | 10.7 | 9.1458 | 9.689 | 15 | 91 | 91 | 0 | 0 | -48.2206 | 36.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 3 | 7347 | 10.6 | 10.6 | 9.1458 | 9.689 | 15 | 90 | 90 | 0 | 0 | -41.6179 | 54.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 4 | 7348 | 10.5 | 10.5 | 9.1458 | 9.689 | 15 | 90 | 90 | 0 | 0 | -33.4571 | 70.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 5 | 7349 | 10.4 | 10.4 | 9.1458 | 9.689 | 15 | 90 | 90 | 0 | 0 | -24.5107 | 83.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 6 | 7350 | 11 | 11 | 9.1458 | 9.689 | 15 | 87 | 87 | 0 | 0 | -15.3142 | 94.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 7 | 7351 | 11 | 11 | 9.1458 | 9.689 | 15 | 85 | 85 | 0 | 0 | -6.2768 | 106.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 3 | 8 | 7352 | 10.2 | 10.2 | 9.1458 | 9.689 | 15 | 89 | 89 | 0 | 3 | 2.2311 | 118.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 9 | 7353 | 10.2 | 10.2 | 9.1458 | 9.689 | 15 | 88 | 88 | 4.4211 | 27.527 | 9.8209 | 130.6588 | 0 | 1.2734 | 3.8917 | 4.2302 | 2.0908 | 0 | 0 | 0 | 0.47297 | 11.6934 | 30.2204 | 68.3129 | 73.2385 | 42.1117 | 11.6934 | 11.6934 | 11.6934 | 27.527 | 11.6934 | 31.4939 | 72.2046 | 77.4687 | 44.2025 | 11.6934 | 11.6934 | 11.6934 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 10 | 7354 | 10.6 | 10.6 | 9.1458 | 9.689 | 15 | 84 | 84 | 11.416 | 80.4147 | 16.0582 | 144.0787 | 0 | 0.85148 | 8.5333 | 11.2164 | 7.3291 | 0 | 0 | 0 | 2.5853 | 35.8014 | 41.2092 | 89.9967 | 107.0373 | 82.3489 | 35.8014 | 35.8014 | 35.8014 | 80.4147 | 35.8014 | 42.0607 | 98.5299 | 118.2537 | 89.678 | 35.8014 | 35.8014 | 35.8014 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 11 | 7355 | 11 | 11 | 9.1458 | 9.689 | 15 | 85 | 85 | 5.1 | 87.3853 | 20.4774 | 158.6108 | 0 | 0 | 2.8753 | 4.8397 | 3.969 | 0.77335 | 0 | 0 | 1.6147 | 42.2849 | 42.2849 | 49.362 | 54.1969 | 52.0539 | 44.1883 | 42.2849 | 42.2849 | 87.3853 | 42.2849 | 42.2849 | 52.2373 | 59.0366 | 56.0229 | 44.9617 | 42.2849 | 42.2849 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 12 | 7356 | 11.1 | 11.1 | 9.1458 | 9.689 | 15 | 81 | 81 | 6.1714 | 111.7089 | 22.6594 | 174.0133 | 0 | 0 | 2.1085 | 5.2975 | 5.3833 | 2.3156 | 0 | 0 | 2.2911 | 54.0863 | 54.0863 | 58.8492 | 66.0527 | 66.2464 | 59.317 | 54.0863 | 54.0863 | 111.7089 | 54.0863 | 54.0863 | 60.9577 | 71.3501 | 71.6297 | 61.6326 | 54.0863 | 54.0863 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 13 | 7357 | 11.5 | 11.5 | 9.1458 | 9.689 | 15 | 82 | 82 | 2.6266 | 76.9844 | 22.3611 | 189.6938 | 0 | 0 | 0.2528 | 1.8833 | 2.4106 | 1.5258 | 0 | 0 | 1.0156 | 37.7743 | 37.7743 | 37.7743 | 37.7743 | 37.7743 | 37.7743 | 37.7743 | 37.7743 | 76.9844 | 37.7743 | 37.7743 | 38.0271 | 39.6576 | 40.1849 | 39.3001 | 37.7743 | 37.7743 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 14 | 7358 | 12.8 | 12.8 | 9.1458 | 9.689 | 15 | 80 | 80 | 37.533 | 155.4221 | 19.6173 | 204.9322 | 0 | 0 | 0 | 20.0609 | 34.2151 | 28.3265 | 5.8447 | 0 | 13.5779 | 73.2442 | 73.2442 | 73.2442 | 111.4344 | 138.3799 | 127.1698 | 84.3709 | 73.2442 | 155.4221 | 73.2442 | 73.2442 | 73.2442 | 131.4953 | 172.595 | 155.4964 | 90.2155 | 73.2442 | 169 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 15 | 7359 | 12.8 | 12.8 | 9.1458 | 9.689 | 15 | 81 | 81 | 2.0376 | 52.3922 | 14.725 | 219.2078 | 0 | 0 | 0 | 0.65858 | 1.7404 | 1.8028 | 0.80908 | 0 | 0.60778 | 25.35 | 25.35 | 25.35 | 25.35 | 25.35 | 25.35 | 25.35 | 25.35 | 52.3922 | 25.35 | 25.35 | 25.35 | 26.0085 | 27.0904 | 27.1527 | 26.159 | 25.35 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 16 | 7360 | 13.1 | 13.1 | 9.1458 | 9.689 | 15 | 76 | 76 | 3.5442 | 46.2892 | 8.125 | 232.3685 | 0 | 0 | 0 | 0.34593 | 2.656 | 3.4103 | 2.1668 | 0 | 0.71084 | 22.4892 | 22.4892 | 22.4892 | 22.4892 | 22.4892 | 22.4892 | 22.4892 | 22.4892 | 46.2892 | 22.4892 | 22.4892 | 22.4892 | 22.8351 | 25.1452 | 25.8995 | 24.656 | 22.4892 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 17 | 7361 | 12.9 | 12.9 | 9.1458 | 9.689 | 15 | 78 | 78 | 5.5147 | 21.585 | 0.27987 | 244.5845 | 0 | 0 | 0 | 0 | 3.3334 | 5.4142 | 4.3235 | 0.70016 | 0.41505 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 21.585 | 10.3574 | 10.3574 | 10.3574 | 10.3574 | 13.6908 | 15.7716 | 14.6809 | 11.0576 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 18 | 7362 | 12.2 | 12.2 | 9.1458 | 9.689 | 15 | 75 | 75 | 0 | 0 | -8.3875 | 256.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 19 | 7363 | 11.8 | 11.8 | 9.1458 | 9.689 | 15 | 77 | 77 | 0 | 0 | -17.4965 | 267.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 20 | 7364 | 11.5 | 11.5 | 9.1458 | 9.689 | 15 | 77 | 77 | 0 | 0 | -26.6737 | 279.9075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 21 | 7365 | 11.3 | 11.3 | 9.1458 | 9.689 | 15 | 80 | 80 | 0 | 0 | -35.489 | 293.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 22 | 7366 | 11.2 | 11.2 | 9.1458 | 9.689 | 15 | 72 | 72 | 0 | 0 | -43.3609 | 309.1546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 23 | 7367 | 10.9 | 10.9 | 9.1458 | 9.689 | 15 | 71 | 71 | 0 | 0 | -49.448 | 328.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 3 | 24 | 7368 | 10 | 10 | 11.2625 | 10.1284 | 15 | 74 | 74 | 0 | 0 | -52.6771 | 350.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 1 | 7369 | 9 | 9 | 11.2625 | 10.1284 | 15 | 76 | 76 | 0 | 0 | -52.2249 | 14.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 2 | 7370 | 6.9 | 6.9 | 11.2625 | 10.1284 | 15 | 86 | 86 | 0 | 0 | -48.5106 | 36.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 3 | 7371 | 6.8 | 6.8 | 11.2625 | 10.1284 | 15 | 87 | 87 | 0 | 0 | -41.8865 | 55.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 4 | 7372 | 7.4 | 7.4 | 11.2625 | 10.1284 | 15 | 87 | 87 | 0 | 0 | -33.7098 | 70.2224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 5 | 7373 | 7.9 | 7.9 | 11.2625 | 10.1284 | 15 | 85 | 85 | 0 | 0 | -24.7555 | 83.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 6 | 7374 | 6 | 6 | 11.2625 | 10.1284 | 15 | 93 | 93 | 0 | 0 | -15.5585 | 95.1748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 7 | 7375 | 4.8 | 4.8 | 11.2625 | 10.1284 | 15 | 97 | 97 | 0 | 0 | -6.5269 | 106.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 4 | 8 | 7376 | 5 | 5 | 11.2625 | 10.1284 | 15 | 98 | 98 | 0 | 3 | 1.9701 | 118.4165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 1.4592 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 9 | 7377 | 7.4 | 7.4 | 11.2625 | 10.1284 | 15 | 98 | 98 | 95.7335 | 48.1972 | 9.5454 | 130.8062 | 0 | 27.3074 | 84.149 | 91.6972 | 45.5304 | 0 | 0 | 0 | 9.8028 | 19.6466 | 65.3736 | 160.556 | 173.1957 | 95.8884 | 19.6466 | 19.6466 | 19.6466 | 48.1972 | 19.6466 | 92.681 | 244.705 | 264.8928 | 141.4188 | 19.6466 | 19.6466 | 19.6466 | 58 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 10 | 7378 | 10 | 10 | 11.2625 | 10.1284 | 15 | 89 | 89 | 279.1342 | 99.1147 | 15.7672 | 144.1941 | 0 | 20.1307 | 208.3582 | 274.5323 | 179.8891 | 0 | 0 | 0 | 61.8853 | 53.3297 | 61.0932 | 133.6834 | 159.2035 | 122.7042 | 53.3297 | 53.3297 | 53.3297 | 99.1147 | 53.3297 | 81.2238 | 342.0416 | 433.7358 | 302.5933 | 53.3297 | 53.3297 | 53.3297 | 161 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 11 | 7379 | 11.7 | 11.7 | 11.2625 | 10.1284 | 15 | 82 | 82 | 439.7278 | 118.9329 | 20.1733 | 158.682 | 0 | 0 | 247.5792 | 417.7457 | 343.2024 | 67.6159 | 0 | 0 | 137.0671 | 70.8283 | 70.8283 | 133.1725 | 176.023 | 157.2519 | 87.855 | 70.8283 | 70.8283 | 118.9329 | 70.8283 | 70.8283 | 380.7517 | 593.7687 | 500.4543 | 155.4708 | 70.8283 | 70.8283 | 256 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 12 | 7380 | 12.6 | 12.6 | 11.2625 | 10.1284 | 15 | 78 | 78 | 507.7045 | 128.0448 | 22.3484 | 174.0296 | 0 | 0 | 173.2503 | 436.4274 | 443.9512 | 191.4145 | 0 | 0 | 185.9552 | 80.0559 | 80.0559 | 120.4253 | 181.7487 | 183.5018 | 124.6577 | 80.0559 | 80.0559 | 128.0448 | 80.0559 | 80.0559 | 293.6756 | 618.176 | 627.453 | 316.0722 | 80.0559 | 80.0559 | 314 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 13 | 7381 | 12.6 | 12.6 | 11.2625 | 10.1284 | 15 | 78 | 78 | 583.2653 | 119.3985 | 22.0521 | 189.6519 | 0 | 0 | 56.111 | 419.0602 | 536.5296 | 339.7072 | 0 | 0 | 222.6015 | 78.9409 | 78.9409 | 89.3256 | 156.4982 | 178.2387 | 141.812 | 78.9409 | 78.9409 | 119.3985 | 78.9409 | 78.9409 | 145.4366 | 575.5583 | 714.7683 | 481.5192 | 78.9409 | 78.9409 | 342 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 14 | 7382 | 11.1 | 11.1 | 11.2625 | 10.1284 | 15 | 84 | 84 | 434.4118 | 137.0031 | 19.3189 | 204.838 | 0 | 0 | 0 | 232.9396 | 396.932 | 328.4069 | 67.5056 | 0 | 154.9969 | 80.7229 | 80.7229 | 80.7229 | 146.4005 | 192.6384 | 173.3176 | 99.7562 | 80.7229 | 137.0031 | 80.7229 | 80.7229 | 80.7229 | 379.3401 | 589.5703 | 501.7246 | 167.2618 | 80.7229 | 292 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 15 | 7383 | 10.2 | 10.2 | 11.2625 | 10.1284 | 15 | 89 | 89 | 5.1619 | 81.4854 | 14.4422 | 219.0732 | 0 | 0 | 0 | 1.679 | 4.4206 | 4.5727 | 2.0462 | 0 | 1.5146 | 40.4178 | 40.4178 | 40.4178 | 40.4178 | 40.4178 | 40.4178 | 40.4178 | 40.4178 | 81.4854 | 40.4178 | 40.4178 | 40.4178 | 42.0968 | 44.8385 | 44.9906 | 42.464 | 40.4178 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 16 | 7384 | 10.1 | 10.1 | 11.2625 | 10.1284 | 15 | 89 | 89 | 7.3232 | 62.5658 | 7.8588 | 232.2054 | 0 | 0 | 0 | 0.73227 | 5.5056 | 7.0538 | 4.47 | 0 | 1.4342 | 30.9864 | 30.9864 | 30.9864 | 30.9864 | 30.9864 | 30.9864 | 30.9864 | 30.9864 | 62.5658 | 30.9864 | 30.9864 | 30.9864 | 31.7186 | 36.492 | 38.0402 | 35.4564 | 30.9864 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 17 | 7385 | 10 | 10 | 11.2625 | 10.1284 | 15 | 90 | 90 | 3.7272 | 16.7364 | 0.028267 | 244.401 | 0 | 0 | 0 | 0 | 2.2627 | 3.663 | 2.9176 | 0.4631 | 0.2636 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 16.7364 | 7.9595 | 7.9595 | 7.9595 | 7.9595 | 10.2222 | 11.6225 | 10.8771 | 8.4226 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 18 | 7386 | 9.8 | 9.8 | 11.2625 | 10.1284 | 15 | 89 | 89 | 0 | 0 | -8.6288 | 256.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 19 | 7387 | 10 | 10 | 11.2625 | 10.1284 | 15 | 90 | 90 | 0 | 0 | -17.7331 | 267.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 20 | 7388 | 10.2 | 10.2 | 11.2625 | 10.1284 | 15 | 90 | 90 | 0 | 0 | -26.9126 | 279.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 21 | 7389 | 10.2 | 10.2 | 11.2625 | 10.1284 | 15 | 89 | 89 | 0 | 0 | -35.7383 | 293.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 22 | 7390 | 10.1 | 10.1 | 11.2625 | 10.1284 | 15 | 88 | 88 | 0 | 0 | -43.6288 | 308.9357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 23 | 7391 | 10.1 | 10.1 | 11.2625 | 10.1284 | 15 | 87 | 87 | 0 | 0 | -49.7395 | 328.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 4 | 24 | 7392 | 10.1 | 10.1 | 9.1667 | 9.8285 | 15 | 87 | 87 | 0 | 0 | -52.9862 | 350.8046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 1 | 7393 | 9.8 | 9.8 | 9.1667 | 9.8285 | 15 | 89 | 89 | 0 | 0 | -52.533 | 14.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 2 | 7394 | 9.7 | 9.7 | 9.1667 | 9.8285 | 15 | 89 | 89 | 0 | 0 | -48.7978 | 36.9177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 3 | 7395 | 9.4 | 9.4 | 9.1667 | 9.8285 | 15 | 89 | 89 | 0 | 0 | -42.1528 | 55.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 4 | 7396 | 8.7 | 8.7 | 9.1667 | 9.8285 | 15 | 93 | 93 | 0 | 0 | -33.9607 | 70.4358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 5 | 7397 | 8.1 | 8.1 | 9.1667 | 9.8285 | 15 | 93 | 93 | 0 | 0 | -24.9988 | 83.4737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 6 | 7398 | 7.6 | 7.6 | 9.1667 | 9.8285 | 15 | 95 | 95 | 0 | 0 | -15.8014 | 95.3701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 7 | 7399 | 7.7 | 7.7 | 9.1667 | 9.8285 | 15 | 95 | 95 | 0 | 0 | -6.7756 | 106.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 5 | 8 | 7400 | 8.1 | 8.1 | 9.1667 | 9.8285 | 15 | 95 | 95 | 0 | 0 | 1.7107 | 118.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 9 | 7401 | 7.8 | 7.8 | 9.1667 | 9.8285 | 15 | 96 | 96 | 30.8066 | 40.9849 | 9.2721 | 130.9483 | 0 | 8.7038 | 27.0405 | 29.5372 | 14.7314 | 0 | 0 | 0 | 3.0151 | 16.5395 | 55.7204 | 138.2646 | 149.5038 | 82.8543 | 16.5395 | 16.5395 | 16.5395 | 40.9849 | 16.5395 | 64.4242 | 165.3051 | 179.041 | 97.5857 | 16.5395 | 16.5395 | 16.5395 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 10 | 7402 | 8 | 8 | 9.1667 | 9.8285 | 15 | 93 | 93 | 247.9049 | 99.2042 | 15.4789 | 144.3043 | 0 | 17.2874 | 184.7965 | 244.0544 | 160.3485 | 0 | 0 | 0 | 53.7958 | 52.3802 | 59.8435 | 132.1599 | 157.7424 | 121.6053 | 52.3802 | 52.3802 | 52.3802 | 99.2042 | 52.3802 | 77.1308 | 316.9564 | 401.7968 | 281.9537 | 52.3802 | 52.3802 | 52.3802 | 153 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 11 | 7403 | 8.7 | 8.7 | 9.1667 | 9.8285 | 15 | 90 | 90 | 167.6739 | 145.5456 | 19.8725 | 158.7484 | 0 | 0 | 94.2859 | 159.4662 | 131.2333 | 26.1258 | 0 | 0 | 51.4544 | 70.7765 | 70.7765 | 146.4 | 198.6788 | 176.0342 | 91.731 | 70.7765 | 70.7765 | 145.5456 | 70.7765 | 70.7765 | 240.6859 | 358.145 | 307.2675 | 117.8568 | 70.7765 | 70.7765 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 12 | 7404 | 10.9 | 10.9 | 9.1667 | 9.8285 | 15 | 78 | 78 | 572.9079 | 114.9811 | 22.0414 | 174.042 | 0 | 0 | 195.2931 | 493.1688 | 502.1529 | 216.9826 | 0 | 0 | 207.0189 | 76.6556 | 76.6556 | 115.0793 | 173.6861 | 175.4537 | 119.3467 | 76.6556 | 76.6556 | 114.9811 | 76.6556 | 76.6556 | 310.3725 | 666.8549 | 677.6066 | 336.3294 | 76.6556 | 76.6556 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 13 | 7405 | 12.8 | 12.8 | 9.1667 | 9.8285 | 15 | 73 | 73 | 616.2057 | 111.8723 | 21.7478 | 189.607 | 0 | 0 | 59.2872 | 443.6182 | 568.0837 | 359.7735 | 0 | 0 | 232.1277 | 76.953 | 76.953 | 87.0837 | 152.7565 | 174.0246 | 138.4294 | 76.953 | 76.953 | 111.8723 | 76.953 | 76.953 | 146.3709 | 596.3747 | 742.1083 | 498.2029 | 76.953 | 76.953 | 344 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 14 | 7406 | 14.1 | 14.1 | 9.1667 | 9.8285 | 15 | 65 | 65 | 680.6874 | 93.4713 | 19.0254 | 204.742 | 0 | 0 | 0 | 366.1811 | 623.372 | 515.4001 | 105.5138 | 0 | 239.5287 | 70.2166 | 70.2166 | 70.2166 | 122.2855 | 158.8566 | 143.5036 | 85.2201 | 70.2166 | 93.4713 | 70.2166 | 70.2166 | 70.2166 | 488.4666 | 782.2286 | 658.9037 | 190.7339 | 70.2166 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 15 | 7407 | 13.9 | 13.9 | 9.1667 | 9.8285 | 15 | 69 | 69 | 598.8608 | 88.1639 | 14.1645 | 218.9376 | 0 | 0 | 0 | 196.0272 | 514.1761 | 531.1276 | 236.9518 | 0 | 172.8361 | 61.0812 | 61.0812 | 61.0812 | 92.468 | 143.4082 | 146.1224 | 99.0206 | 61.0812 | 88.1639 | 61.0812 | 61.0812 | 61.0812 | 288.4952 | 657.5843 | 677.25 | 335.9724 | 61.0812 | 261 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 16 | 7408 | 13.4 | 13.4 | 9.1667 | 9.8285 | 15 | 68 | 68 | 320.9813 | 82.6356 | 7.598 | 232.0416 | 0 | 0 | 0 | 32.8684 | 242.0784 | 309.4821 | 195.5954 | 0 | 61.3644 | 47.6362 | 47.6362 | 47.6362 | 57.7345 | 122.0106 | 142.7193 | 107.7295 | 47.6362 | 82.6356 | 47.6362 | 47.6362 | 47.6362 | 90.6029 | 364.089 | 452.2013 | 303.3249 | 47.6362 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 17 | 7409 | 12.4 | 12.4 | 9.1667 | 9.8285 | 15 | 71 | 71 | 114.1695 | 31.4366 | -0.21793 | 244.2173 | 0 | 0 | 0 | 0 | 69.6078 | 112.3135 | 89.2275 | 13.8732 | 7.5634 | 17.5538 | 17.5538 | 17.5538 | 17.5538 | 55.8483 | 79.3427 | 66.642 | 25.1861 | 31.4366 | 17.5538 | 17.5538 | 17.5538 | 17.5538 | 125.4561 | 191.6563 | 155.8695 | 39.0593 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 5 | 18 | 7410 | 10.4 | 10.4 | 9.1667 | 9.8285 | 15 | 78 | 78 | 0 | 0 | -8.8645 | 255.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 19 | 7411 | 10.1 | 10.1 | 9.1667 | 9.8285 | 15 | 77 | 77 | 0 | 0 | -17.9642 | 267.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 20 | 7412 | 11.4 | 11.4 | 9.1667 | 9.8285 | 15 | 67 | 67 | 0 | 0 | -27.1458 | 279.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 21 | 7413 | 10.6 | 10.6 | 9.1667 | 9.8285 | 15 | 66 | 66 | 0 | 0 | -35.9817 | 292.8991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 22 | 7414 | 10.3 | 10.3 | 9.1667 | 9.8285 | 15 | 68 | 68 | 0 | 0 | -43.8909 | 308.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 23 | 7415 | 9.4 | 9.4 | 9.1667 | 9.8285 | 15 | 71 | 71 | 0 | 0 | -50.0255 | 327.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 5 | 24 | 7416 | 8.5 | 8.5 | 10.075 | 9.8584 | 15 | 75 | 75 | 0 | 0 | -53.2908 | 350.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 1 | 7417 | 7.9 | 7.9 | 10.075 | 9.8584 | 15 | 79 | 79 | 0 | 0 | -52.8374 | 14.8688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 2 | 7418 | 7.4 | 7.4 | 10.075 | 9.8584 | 15 | 82 | 82 | 0 | 0 | -49.0819 | 37.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 3 | 7419 | 7.1 | 7.1 | 10.075 | 9.8584 | 15 | 84 | 84 | 0 | 0 | -42.4168 | 55.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 4 | 7420 | 6.3 | 6.3 | 10.075 | 9.8584 | 15 | 87 | 87 | 0 | 0 | -34.2098 | 70.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 5 | 7421 | 5.9 | 5.9 | 10.075 | 9.8584 | 15 | 88 | 88 | 0 | 0 | -25.2405 | 83.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 6 | 7422 | 5.5 | 5.5 | 10.075 | 9.8584 | 15 | 89 | 89 | 0 | 0 | -16.0429 | 95.5603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 7 | 7423 | 5.2 | 5.2 | 10.075 | 9.8584 | 15 | 89 | 89 | 0 | 0 | -7.0227 | 107.0533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 6 | 8 | 7424 | 4.5 | 4.5 | 10.075 | 9.8584 | 15 | 93 | 93 | 0 | 0 | 1.4531 | 118.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 9 | 7425 | 6.2 | 6.2 | 10.075 | 9.8584 | 15 | 86 | 86 | 123.788 | 44.4371 | 9.001 | 131.0851 | 0 | 34.6477 | 108.5031 | 118.7988 | 59.5038 | 0 | 0 | 0 | 11.5629 | 19.9412 | 19.9412 | 19.9412 | 19.9412 | 19.9412 | 19.9412 | 19.9412 | 19.9412 | 44.4371 | 19.9412 | 54.5889 | 128.4443 | 138.74 | 79.4451 | 19.9412 | 19.9412 | 19.9412 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 10 | 7426 | 8.1 | 8.1 | 10.075 | 9.8584 | 15 | 79 | 79 | 328.565 | 91.2258 | 15.1934 | 144.4092 | 0 | 22.1566 | 244.6011 | 323.7616 | 213.267 | 0 | 0 | 0 | 69.7742 | 50.715 | 57.8333 | 129.2991 | 154.7313 | 119.2322 | 50.715 | 50.715 | 50.715 | 91.2258 | 50.715 | 79.9899 | 373.9002 | 478.4929 | 332.4991 | 50.715 | 50.715 | 50.715 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 11 | 7427 | 9.7 | 9.7 | 10.075 | 9.8584 | 15 | 74 | 74 | 538.7627 | 101.2425 | 19.5752 | 158.81 | 0 | 0 | 302.5958 | 512.9358 | 422.805 | 85.0008 | 0 | 0 | 162.7575 | 65.9771 | 65.9771 | 125.6419 | 167.116 | 149.3443 | 82.7373 | 65.9771 | 65.9771 | 101.2425 | 65.9771 | 65.9771 | 428.2376 | 680.0518 | 572.1493 | 167.738 | 65.9771 | 65.9771 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 12 | 7428 | 11.6 | 11.6 | 10.075 | 9.8584 | 15 | 68 | 68 | 629.197 | 103.6984 | 21.7386 | 174.0504 | 0 | 0 | 214.286 | 542.3749 | 552.748 | 239.3288 | 0 | 0 | 224.3016 | 72.5786 | 72.5786 | 107.4163 | 160.7558 | 162.4422 | 111.4877 | 72.5786 | 72.5786 | 103.6984 | 72.5786 | 72.5786 | 321.7023 | 703.1307 | 715.1901 | 350.8165 | 72.5786 | 72.5786 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 13 | 7429 | 13.5 | 13.5 | 10.075 | 9.8584 | 15 | 61 | 61 | 686.0574 | 97.9082 | 21.4481 | 189.5593 | 0 | 0 | 66.0552 | 494.8969 | 633.8347 | 401.4807 | 0 | 0 | 255.0918 | 73.619 | 73.619 | 83.169 | 145.1691 | 165.2561 | 131.6634 | 73.619 | 73.619 | 97.9082 | 73.619 | 73.619 | 149.2241 | 640.0659 | 799.0908 | 533.1441 | 73.619 | 73.619 | 353 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 14 | 7430 | 13.6 | 13.6 | 10.075 | 9.8584 | 15 | 60 | 60 | 644.3251 | 98.3884 | 18.7369 | 204.6442 | 0 | 0 | 0 | 347.7452 | 591.3777 | 488.5891 | 99.5917 | 0 | 223.6116 | 70.6436 | 70.6436 | 70.6436 | 124.3955 | 162.0544 | 146.1661 | 86.0377 | 70.6436 | 98.3884 | 70.6436 | 70.6436 | 70.6436 | 472.1407 | 753.4321 | 634.7553 | 185.6294 | 70.6436 | 322 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 15 | 7431 | 13.8 | 13.8 | 10.075 | 9.8584 | 15 | 59 | 59 | 552.0548 | 93.2943 | 13.8921 | 218.8011 | 0 | 0 | 0 | 181.8545 | 475.1786 | 490.1495 | 217.9975 | 0 | 156.7057 | 61.5328 | 61.5328 | 61.5328 | 93.9546 | 146.2498 | 148.9188 | 100.3984 | 61.5328 | 93.2943 | 61.5328 | 61.5328 | 61.5328 | 275.8092 | 621.4284 | 639.0683 | 318.3958 | 61.5328 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 16 | 7432 | 12.9 | 12.9 | 10.075 | 9.8584 | 15 | 64 | 64 | 333.3921 | 79.7974 | 7.3425 | 231.8774 | 0 | 0 | 0 | 34.947 | 252.2214 | 321.7478 | 202.7988 | 0 | 62.2026 | 46.4309 | 46.4309 | 46.4309 | 56.6331 | 120.0629 | 140.36 | 105.6348 | 46.4309 | 79.7974 | 46.4309 | 46.4309 | 46.4309 | 91.5801 | 372.2842 | 462.1079 | 308.4336 | 46.4309 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 17 | 7433 | 8 | 8 | 10.075 | 9.8584 | 15 | 84 | 84 | 31.8989 | 26.0276 | -0.45862 | 244.0334 | 0 | 0 | 0 | 0 | 19.5311 | 31.4096 | 24.8888 | 3.7884 | 1.9724 | 13.8971 | 13.8971 | 13.8971 | 13.8971 | 30.2445 | 40.1867 | 34.7288 | 17.068 | 26.0276 | 13.8971 | 13.8971 | 13.8971 | 13.8971 | 49.7757 | 71.5964 | 59.6176 | 20.8564 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 6 | 18 | 7434 | 5.4 | 5.4 | 10.075 | 9.8584 | 15 | 92 | 92 | 0 | 0 | -9.0947 | 255.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 19 | 7435 | 3.6 | 3.6 | 10.075 | 9.8584 | 15 | 96 | 96 | 0 | 0 | -18.1895 | 267.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 20 | 7436 | 3.7 | 3.7 | 10.075 | 9.8584 | 15 | 98 | 98 | 0 | 0 | -27.3731 | 279.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 21 | 7437 | 4.1 | 4.1 | 10.075 | 9.8584 | 15 | 98 | 98 | 0 | 0 | -36.2191 | 292.6663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 22 | 7438 | 4.8 | 4.8 | 10.075 | 9.8584 | 15 | 97 | 97 | 0 | 0 | -44.147 | 308.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 23 | 7439 | 4.4 | 4.4 | 10.075 | 9.8584 | 15 | 96 | 96 | 0 | 0 | -50.306 | 327.7757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 6 | 24 | 7440 | 3.5 | 3.5 | 7.3625 | 9.1595 | 15 | 94 | 94 | 0 | 0 | -53.5906 | 350.6646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 1 | 7441 | 5.4 | 5.4 | 7.3625 | 9.1595 | 15 | 90 | 90 | 0 | 0 | -53.138 | 14.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 2 | 7442 | 4.5 | 4.5 | 7.3625 | 9.1595 | 15 | 92 | 92 | 0 | 0 | -49.363 | 37.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 3 | 7443 | 3.3 | 3.3 | 7.3625 | 9.1595 | 15 | 93 | 93 | 0 | 0 | -42.6783 | 55.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 4 | 7444 | 4.1 | 4.1 | 7.3625 | 9.1595 | 15 | 88 | 88 | 0 | 0 | -34.4569 | 70.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 5 | 7445 | 3.9 | 3.9 | 7.3625 | 9.1595 | 15 | 85 | 85 | 0 | 0 | -25.4806 | 83.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 6 | 7446 | 3.3 | 3.3 | 7.3625 | 9.1595 | 15 | 86 | 86 | 0 | 0 | -16.2828 | 95.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 7 | 7447 | 2.8 | 2.8 | 7.3625 | 9.1595 | 15 | 87 | 87 | 0 | 0 | -7.2683 | 107.2245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 7 | 8 | 7448 | 2.5 | 2.5 | 7.3625 | 9.1595 | 15 | 87 | 87 | 0 | 0 | 1.1974 | 118.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 9 | 7449 | 3.7 | 3.7 | 7.3625 | 9.1595 | 15 | 84 | 84 | 119.841 | 42.333 | 8.7321 | 131.2165 | 0 | 33.2368 | 104.8989 | 115.1126 | 57.8949 | 0 | 0 | 0 | 10.667 | 18.587 | 18.587 | 18.587 | 18.587 | 18.587 | 18.587 | 18.587 | 18.587 | 42.333 | 18.587 | 51.8238 | 123.4859 | 133.6996 | 76.482 | 18.587 | 18.587 | 18.587 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 10 | 7450 | 5.8 | 5.8 | 7.3625 | 9.1595 | 15 | 77 | 77 | 355.9632 | 87.0373 | 14.9108 | 144.509 | 0 | 23.2163 | 264.6607 | 351.0704 | 231.8279 | 0 | 0 | 0 | 73.9627 | 48.9401 | 54.1105 | 107.8811 | 127.1249 | 100.5691 | 48.9401 | 48.9401 | 48.9401 | 87.0373 | 48.9401 | 77.3268 | 372.5419 | 478.1954 | 332.397 | 48.9401 | 48.9401 | 48.9401 | 161 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 11 | 7451 | 7.8 | 7.8 | 7.3625 | 9.1595 | 15 | 70 | 70 | 565.2718 | 95.899 | 19.2814 | 158.8669 | 0 | 0 | 317.1321 | 538.7322 | 444.7503 | 90.2397 | 0 | 0 | 168.101 | 64.1936 | 64.1936 | 122.7203 | 163.6166 | 146.2722 | 80.8473 | 64.1936 | 64.1936 | 95.899 | 64.1936 | 64.1936 | 439.8524 | 702.3488 | 591.0225 | 171.087 | 64.1936 | 64.1936 | 264 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 12 | 7452 | 9.5 | 9.5 | 7.3625 | 9.1595 | 15 | 65 | 65 | 653.1694 | 98.2854 | 21.44 | 174.0549 | 0 | 0 | 222.282 | 563.811 | 575.0671 | 249.4567 | 0 | 0 | 229.7146 | 70.9341 | 70.9341 | 105.0867 | 157.561 | 159.2905 | 109.262 | 70.9341 | 70.9341 | 98.2854 | 70.9341 | 70.9341 | 327.3687 | 721.372 | 734.3576 | 358.7187 | 70.9341 | 70.9341 | 328 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 13 | 7453 | 10.3 | 10.3 | 7.3625 | 9.1595 | 15 | 63 | 63 | 651.6873 | 102.8287 | 21.1533 | 189.5087 | 0 | 0 | 62.8281 | 471.0438 | 603.3285 | 382.1915 | 0 | 0 | 239.1713 | 74.006 | 74.006 | 83.8125 | 147.5285 | 168.176 | 133.66 | 74.006 | 74.006 | 102.8287 | 74.006 | 74.006 | 146.6406 | 618.5723 | 771.5045 | 515.8515 | 74.006 | 74.006 | 342 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 14 | 7454 | 10.9 | 10.9 | 7.3625 | 9.1595 | 15 | 61 | 61 | 606.2559 | 103.4995 | 18.4537 | 204.5446 | 0 | 0 | 0 | 328.2626 | 557.637 | 460.3553 | 93.4037 | 0 | 207.5005 | 71.0741 | 71.0741 | 71.0741 | 126.3587 | 164.989 | 148.6052 | 86.8048 | 71.0741 | 103.4995 | 71.0741 | 71.0741 | 71.0741 | 454.6213 | 722.626 | 608.9605 | 180.2084 | 71.0741 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 15 | 7455 | 9.5 | 9.5 | 7.3625 | 9.1595 | 15 | 65 | 65 | 503.848 | 98.3395 | 13.6251 | 218.6635 | 0 | 0 | 0 | 167.0295 | 434.7525 | 447.8034 | 198.5371 | 0 | 140.6605 | 62.7777 | 62.7777 | 62.7777 | 97.4804 | 153.1035 | 155.815 | 104.0265 | 62.7777 | 98.3395 | 62.7777 | 62.7777 | 62.7777 | 264.5099 | 587.856 | 603.6184 | 302.5636 | 62.7777 | 239 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 16 | 7456 | 7.9 | 7.9 | 7.3625 | 9.1595 | 15 | 71 | 71 | 268.2676 | 82.1658 | 7.0926 | 231.7128 | 0 | 0 | 0 | 28.7748 | 203.5761 | 259.1252 | 162.8824 | 0 | 48.8342 | 46.1468 | 46.1468 | 46.1468 | 56.3281 | 118.1775 | 137.8323 | 103.779 | 46.1468 | 82.1658 | 46.1468 | 46.1468 | 46.1468 | 85.1028 | 321.7536 | 396.9576 | 266.6614 | 46.1468 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 17 | 7457 | 7.1 | 7.1 | 7.3625 | 9.1595 | 15 | 75 | 75 | 101.4074 | 27.1711 | -0.69373 | 243.8493 | 0 | 0 | 0 | 0 | 62.3516 | 99.9416 | 78.9871 | 11.7631 | 5.8289 | 15.2103 | 15.2103 | 15.2103 | 15.2103 | 51.1848 | 72.8729 | 60.7829 | 21.9971 | 27.1711 | 15.2103 | 15.2103 | 15.2103 | 15.2103 | 113.5365 | 172.8144 | 139.77 | 33.7602 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 7 | 18 | 7458 | 6.6 | 6.6 | 7.3625 | 9.1595 | 15 | 78 | 78 | 0 | 0 | -9.3192 | 255.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 19 | 7459 | 5.9 | 5.9 | 7.3625 | 9.1595 | 15 | 80 | 80 | 0 | 0 | -18.409 | 266.9434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 20 | 7460 | 5.5 | 5.5 | 7.3625 | 9.1595 | 15 | 82 | 82 | 0 | 0 | -27.5945 | 279.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 21 | 7461 | 5.5 | 5.5 | 7.3625 | 9.1595 | 15 | 82 | 82 | 0 | 0 | -36.4505 | 292.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 22 | 7462 | 6.1 | 6.1 | 7.3625 | 9.1595 | 15 | 80 | 80 | 0 | 0 | -44.3972 | 308.2614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 23 | 7463 | 6.6 | 6.6 | 7.3625 | 9.1595 | 15 | 80 | 80 | 0 | 0 | -50.5809 | 327.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 7 | 24 | 7464 | 6.8 | 6.8 | 6.0542 | 8.3209 | 15 | 79 | 79 | 0 | 0 | -53.8855 | 350.5858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 1 | 7465 | 6.6 | 6.6 | 6.0542 | 8.3209 | 15 | 80 | 80 | 0 | 0 | -53.4346 | 14.9878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 2 | 7466 | 6.1 | 6.1 | 6.0542 | 8.3209 | 15 | 82 | 82 | 0 | 0 | -49.6409 | 37.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 3 | 7467 | 5.6 | 5.6 | 6.0542 | 8.3209 | 15 | 85 | 85 | 0 | 0 | -42.9374 | 55.8679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 4 | 7468 | 6.3 | 6.3 | 6.0542 | 8.3209 | 15 | 83 | 83 | 0 | 0 | -34.7021 | 71.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 5 | 7469 | 6.4 | 6.4 | 6.0542 | 8.3209 | 15 | 82 | 82 | 0 | 0 | -25.719 | 84.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 6 | 7470 | 6.5 | 6.5 | 6.0542 | 8.3209 | 15 | 81 | 81 | 0 | 0 | -16.5212 | 95.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 7 | 7471 | 6 | 6 | 6.0542 | 8.3209 | 15 | 83 | 83 | 0 | 0 | -7.5122 | 107.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 8 | 8 | 7472 | 5.9 | 5.9 | 6.0542 | 8.3209 | 15 | 83 | 83 | 0 | 0 | 0.94365 | 119.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 9 | 7473 | 6.2 | 6.2 | 6.0542 | 8.3209 | 15 | 82 | 82 | 63.0476 | 38.6614 | 8.4657 | 131.3426 | 0 | 17.3297 | 55.1119 | 60.6102 | 30.6039 | 0 | 0 | 0 | 5.3386 | 14.9663 | 52.0967 | 133.048 | 144.8286 | 80.5377 | 14.9663 | 14.9663 | 14.9663 | 38.6614 | 14.9663 | 69.4264 | 188.1599 | 205.4389 | 111.1416 | 14.9663 | 14.9663 | 14.9663 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 10 | 7474 | 7.1 | 7.1 | 6.0542 | 8.3209 | 15 | 79 | 79 | 237.8529 | 93.652 | 14.6312 | 144.6036 | 0 | 15.0073 | 176.6278 | 234.7822 | 155.4043 | 0 | 0 | 0 | 48.348 | 49.1589 | 55.7484 | 126.7133 | 152.2479 | 117.3944 | 49.1589 | 49.1589 | 49.1589 | 93.652 | 49.1589 | 70.7556 | 303.341 | 387.03 | 272.7987 | 49.1589 | 49.1589 | 49.1589 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 11 | 7475 | 8.1 | 8.1 | 6.0542 | 8.3209 | 15 | 75 | 75 | 410.3317 | 115.8829 | 18.9914 | 158.919 | 0 | 0 | 229.9692 | 391.4613 | 323.6407 | 66.2357 | 0 | 0 | 120.1171 | 67.6204 | 67.6204 | 127.9537 | 170.3217 | 152.5287 | 84.9976 | 67.6204 | 67.6204 | 115.8829 | 67.6204 | 67.6204 | 357.9229 | 561.783 | 476.1694 | 151.2333 | 67.6204 | 67.6204 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 12 | 7476 | 8.9 | 8.9 | 6.0542 | 8.3209 | 15 | 71 | 71 | 581.6091 | 109.2046 | 21.1459 | 174.0555 | 0 | 0 | 197.81 | 502.7204 | 513.1441 | 222.9749 | 0 | 0 | 201.7954 | 73.641 | 73.641 | 111.1184 | 168.8871 | 170.862 | 115.8861 | 73.641 | 73.641 | 109.2046 | 73.641 | 73.641 | 308.9284 | 671.6075 | 684.006 | 338.861 | 73.641 | 73.641 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 13 | 7477 | 9.5 | 9.5 | 6.0542 | 8.3209 | 15 | 68 | 68 | 626.5329 | 106.0396 | 20.8634 | 189.4554 | 0 | 0 | 60.5177 | 453.7651 | 581.2032 | 368.1802 | 0 | 0 | 226.9604 | 74.034 | 74.034 | 84.0007 | 148.7651 | 169.753 | 134.67 | 74.034 | 74.034 | 106.0396 | 74.034 | 74.034 | 144.5184 | 602.5302 | 750.9561 | 502.8502 | 74.034 | 74.034 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 14 | 7478 | 9.9 | 9.9 | 6.0542 | 8.3209 | 15 | 66 | 66 | 665.2621 | 92.4419 | 18.1757 | 204.4433 | 0 | 0 | 0 | 361.3837 | 613.1967 | 505.8074 | 102.123 | 0 | 224.5581 | 68.2354 | 68.2354 | 68.2354 | 120.8948 | 157.588 | 141.9396 | 83.1163 | 68.2354 | 92.4419 | 68.2354 | 68.2354 | 68.2354 | 482.2785 | 770.7847 | 647.7471 | 185.2394 | 68.2354 | 317 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 15 | 7479 | 9.7 | 9.7 | 6.0542 | 8.3209 | 15 | 66 | 66 | 510.0359 | 95.9691 | 13.3635 | 218.525 | 0 | 0 | 0 | 170.1553 | 441.1545 | 453.7314 | 200.5185 | 0 | 140.0309 | 61.6654 | 61.6654 | 61.6654 | 96.2046 | 151.2138 | 153.7668 | 102.368 | 61.6654 | 95.9691 | 61.6654 | 61.6654 | 61.6654 | 266.36 | 592.3684 | 607.4981 | 302.8865 | 61.6654 | 236 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 16 | 7480 | 8.3 | 8.3 | 6.0542 | 8.3209 | 15 | 70 | 70 | 69.0014 | 81.748 | 6.8482 | 231.5478 | 0 | 0 | 0 | 7.5705 | 52.5206 | 66.7049 | 41.8143 | 0 | 12.252 | 41.2331 | 41.2331 | 41.2331 | 48.7283 | 93.2313 | 107.2744 | 82.6314 | 41.2331 | 81.748 | 41.2331 | 41.2331 | 41.2331 | 56.2988 | 145.7519 | 173.9793 | 124.4457 | 41.2331 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 17 | 7481 | 7.5 | 7.5 | 6.0542 | 8.3209 | 15 | 74 | 74 | 1.4564 | 7.9225 | -0.92315 | 243.6652 | 0 | 0 | 0 | 0 | 0.89923 | 1.4366 | 1.1324 | 0.16489 | 0.077473 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 7.9225 | 3.7044 | 3.7044 | 3.7044 | 3.7044 | 4.6036 | 5.141 | 4.8368 | 3.8693 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 8 | 18 | 7482 | 6.7 | 6.7 | 6.0542 | 8.3209 | 15 | 77 | 77 | 0 | 0 | -9.5379 | 255.2307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 19 | 7483 | 6.5 | 6.5 | 6.0542 | 8.3209 | 15 | 77 | 77 | 0 | 0 | -18.6226 | 266.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 20 | 7484 | 5.5 | 5.5 | 6.0542 | 8.3209 | 15 | 80 | 80 | 0 | 0 | -27.8098 | 278.7819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 21 | 7485 | 5.4 | 5.4 | 6.0542 | 8.3209 | 15 | 82 | 82 | 0 | 0 | -36.6758 | 292.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 22 | 7486 | 4.9 | 4.9 | 6.0542 | 8.3209 | 15 | 84 | 84 | 0 | 0 | -44.6413 | 308.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 23 | 7487 | 4.2 | 4.2 | 6.0542 | 8.3209 | 15 | 87 | 87 | 0 | 0 | -50.85 | 327.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 8 | 24 | 7488 | 3.9 | 3.9 | 6.7375 | 7.8712 | 15 | 88 | 88 | 0 | 0 | -54.1754 | 350.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 1 | 7489 | 3.6 | 3.6 | 6.7375 | 7.8712 | 15 | 92 | 92 | 0 | 0 | -53.7273 | 15.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 2 | 7490 | 3.7 | 3.7 | 6.7375 | 7.8712 | 15 | 89 | 89 | 0 | 0 | -49.9155 | 37.5231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 3 | 7491 | 3.5 | 3.5 | 6.7375 | 7.8712 | 15 | 91 | 91 | 0 | 0 | -43.1939 | 56.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 4 | 7492 | 2.8 | 2.8 | 6.7375 | 7.8712 | 15 | 92 | 92 | 0 | 0 | -34.9451 | 71.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 5 | 7493 | 2.6 | 2.6 | 6.7375 | 7.8712 | 15 | 94 | 94 | 0 | 0 | -25.9556 | 84.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 6 | 7494 | 2 | 2 | 6.7375 | 7.8712 | 15 | 96 | 96 | 0 | 0 | -16.7578 | 96.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 7 | 7495 | 2.9 | 2.9 | 6.7375 | 7.8712 | 15 | 94 | 94 | 0 | 0 | -7.7543 | 107.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 9 | 8 | 7496 | 1.7 | 1.7 | 6.7375 | 7.8712 | 15 | 96 | 96 | 0 | 0 | 0.69194 | 119.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 9 | 7497 | 4.2 | 4.2 | 6.7375 | 7.8712 | 15 | 95 | 95 | 109.79 | 38.1717 | 8.2018 | 131.4634 | 0 | 29.9153 | 95.8432 | 105.6274 | 53.5366 | 0 | 0 | 0 | 8.8283 | 16.0014 | 16.0014 | 16.0014 | 16.0014 | 16.0014 | 16.0014 | 16.0014 | 16.0014 | 38.1717 | 16.0014 | 45.9166 | 111.8445 | 121.6288 | 69.538 | 16.0014 | 16.0014 | 16.0014 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 10 | 7498 | 6.4 | 6.4 | 6.7375 | 7.8712 | 15 | 82 | 82 | 217.9246 | 92.6716 | 14.3547 | 144.6929 | 0 | 13.3056 | 161.6379 | 215.2849 | 142.8209 | 0 | 0 | 0 | 43.3284 | 48.0893 | 54.4071 | 124.8396 | 150.3127 | 115.9048 | 48.0893 | 48.0893 | 48.0893 | 92.6716 | 48.0893 | 67.7127 | 286.4774 | 365.5976 | 258.7257 | 48.0893 | 48.0893 | 48.0893 | 136 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 11 | 7499 | 8.7 | 8.7 | 6.7375 | 7.8712 | 15 | 74 | 74 | 504.9382 | 101.5021 | 18.7052 | 158.9665 | 0 | 0 | 282.722 | 482.1903 | 399.1981 | 82.3611 | 0 | 0 | 145.4979 | 64.2127 | 64.2127 | 123.2688 | 164.9346 | 147.5988 | 81.4166 | 64.2127 | 64.2127 | 101.5021 | 64.2127 | 64.2127 | 405.9908 | 647.1249 | 546.7969 | 163.7777 | 64.2127 | 64.2127 | 247 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 12 | 7500 | 9.7 | 9.7 | 6.7375 | 7.8712 | 15 | 67 | 67 | 605.0598 | 103.8904 | 20.8562 | 174.0523 | 0 | 0 | 205.6939 | 523.6902 | 534.9158 | 232.795 | 0 | 0 | 207.1096 | 70.7588 | 70.7588 | 105.5022 | 159.2145 | 161.1106 | 110.0798 | 70.7588 | 70.7588 | 103.8904 | 70.7588 | 70.7588 | 311.1962 | 682.9046 | 696.0264 | 342.8749 | 70.7588 | 70.7588 | 311 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 13 | 7501 | 10.9 | 10.9 | 6.7375 | 7.8712 | 15 | 65 | 65 | 649.5691 | 100.7398 | 20.5784 | 189.3993 | 0 | 0 | 62.8986 | 471.3845 | 603.7398 | 382.4325 | 0 | 0 | 232.2602 | 72.4127 | 72.4127 | 82.1967 | 145.7376 | 166.3258 | 131.9009 | 72.4127 | 72.4127 | 100.7398 | 72.4127 | 72.4127 | 145.0953 | 617.1222 | 770.0656 | 514.3334 | 72.4127 | 72.4127 | 333 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 14 | 7502 | 10.3 | 10.3 | 6.7375 | 7.8712 | 15 | 69 | 69 | 207.3712 | 155.9665 | 17.903 | 204.3403 | 0 | 0 | 0 | 113.0149 | 191.5328 | 157.8533 | 31.7056 | 0 | 69.0335 | 78.9812 | 78.9812 | 78.9812 | 138.5619 | 179.956 | 162.2004 | 95.6962 | 78.9812 | 155.9665 | 78.9812 | 78.9812 | 78.9812 | 251.5768 | 371.4888 | 320.0538 | 127.4017 | 78.9812 | 225 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 15 | 7503 | 10.7 | 10.7 | 6.7375 | 7.8712 | 15 | 69 | 69 | 66.7357 | 123.9816 | 13.1075 | 218.3857 | 0 | 0 | 0 | 22.4054 | 57.8596 | 59.4204 | 26.1736 | 0 | 18.0184 | 59.8036 | 59.8036 | 59.8036 | 81.2213 | 115.1127 | 116.6047 | 84.8234 | 59.8036 | 123.9816 | 59.8036 | 59.8036 | 59.8036 | 103.6268 | 172.9723 | 176.0251 | 110.997 | 59.8036 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 16 | 7504 | 9.7 | 9.7 | 6.7375 | 7.8712 | 15 | 77 | 77 | 2.7822 | 35.5183 | 6.6095 | 231.3825 | 0 | 0 | 0 | 0.31212 | 2.124 | 2.6917 | 1.6826 | 0 | 0.48175 | 17.1113 | 17.1113 | 17.1113 | 17.1113 | 17.1113 | 17.1113 | 17.1113 | 17.1113 | 35.5183 | 17.1113 | 17.1113 | 17.1113 | 17.4234 | 19.2353 | 19.803 | 18.7939 | 17.1113 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 17 | 7505 | 9.7 | 9.7 | 6.7375 | 7.8712 | 15 | 78 | 78 | 0.96601 | 5.9527 | -1.1468 | 243.481 | 0 | 0 | 0 | 0 | 0.5989 | 0.95364 | 0.74975 | 0.10667 | 0.047311 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 5.9527 | 2.7709 | 2.7709 | 2.7709 | 2.7709 | 3.3698 | 3.7245 | 3.5206 | 2.8775 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 9 | 18 | 7506 | 10 | 10 | 6.7375 | 7.8712 | 15 | 77 | 77 | 0 | 0 | -9.7508 | 255.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 19 | 7507 | 9.7 | 9.7 | 6.7375 | 7.8712 | 15 | 78 | 78 | 0 | 0 | -18.8302 | 266.5167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 20 | 7508 | 9.5 | 9.5 | 6.7375 | 7.8712 | 15 | 79 | 79 | 0 | 0 | -28.0191 | 278.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 21 | 7509 | 10.7 | 10.7 | 6.7375 | 7.8712 | 15 | 72 | 72 | 0 | 0 | -36.8949 | 291.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 22 | 7510 | 8.2 | 8.2 | 6.7375 | 7.8712 | 15 | 80 | 80 | 0 | 0 | -44.8792 | 307.7983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 23 | 7511 | 8.5 | 8.5 | 6.7375 | 7.8712 | 15 | 81 | 81 | 0 | 0 | -51.1133 | 327.2129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 9 | 24 | 7512 | 9 | 9 | 7.0292 | 7.5698 | 15 | 75 | 75 | 0 | 0 | -54.4603 | 350.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 1 | 7513 | 9.5 | 9.5 | 7.0292 | 7.5698 | 15 | 73 | 73 | 0 | 0 | -54.0158 | 15.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 2 | 7514 | 9 | 9 | 7.0292 | 7.5698 | 15 | 75 | 75 | 0 | 0 | -50.1869 | 37.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 3 | 7515 | 9.3 | 9.3 | 7.0292 | 7.5698 | 15 | 74 | 74 | 0 | 0 | -43.4477 | 56.2307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 4 | 7516 | 8.8 | 8.8 | 7.0292 | 7.5698 | 15 | 78 | 78 | 0 | 0 | -35.186 | 71.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 5 | 7517 | 7.5 | 7.5 | 7.0292 | 7.5698 | 15 | 82 | 82 | 0 | 0 | -26.1904 | 84.4289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 6 | 7518 | 7.5 | 7.5 | 7.0292 | 7.5698 | 15 | 84 | 84 | 0 | 0 | -16.9927 | 96.2685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 7 | 7519 | 6.6 | 6.6 | 7.0292 | 7.5698 | 15 | 85 | 85 | 0 | 0 | -7.9945 | 107.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 10 | 8 | 7520 | 6.7 | 6.7 | 7.0292 | 7.5698 | 15 | 89 | 89 | 0 | 0 | 0.44241 | 119.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 9 | 7521 | 6.4 | 6.4 | 7.0292 | 7.5698 | 15 | 91 | 91 | 5.361 | 21.5914 | 7.9405 | 131.5787 | 0 | 1.4484 | 4.6738 | 5.1614 | 2.6255 | 0 | 0 | 0 | 0.40858 | 8.1816 | 30.9438 | 81.6342 | 89.2971 | 49.4436 | 8.1816 | 8.1816 | 8.1816 | 21.5914 | 8.1816 | 32.3922 | 86.3081 | 94.4585 | 52.0692 | 8.1816 | 8.1816 | 8.1816 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 10 | 7522 | 8.9 | 8.9 | 7.0292 | 7.5698 | 15 | 81 | 81 | 20.7875 | 76.958 | 14.0815 | 144.7771 | 0 | 1.2286 | 15.4009 | 20.5515 | 13.6633 | 0 | 0 | 0 | 4.042 | 35.2925 | 41.1487 | 108.6989 | 133.2486 | 100.417 | 35.2925 | 35.2925 | 35.2925 | 76.958 | 35.2925 | 42.3773 | 124.0998 | 153.8001 | 114.0803 | 35.2925 | 35.2925 | 35.2925 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 11 | 7523 | 12 | 12 | 7.0292 | 7.5698 | 15 | 70 | 70 | 129.5186 | 135.2637 | 18.423 | 159.0093 | 0 | 0 | 72.4562 | 123.802 | 102.6262 | 21.3334 | 0 | 0 | 36.7363 | 64.7317 | 64.7317 | 140.0807 | 193.4764 | 171.4552 | 86.9168 | 64.7317 | 64.7317 | 135.2637 | 64.7317 | 64.7317 | 212.5369 | 317.2784 | 274.0814 | 108.2502 | 64.7317 | 64.7317 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 12 | 7524 | 13 | 13 | 7.0292 | 7.5698 | 15 | 65 | 65 | 392.2612 | 136.5329 | 20.5711 | 174.0453 | 0 | 0 | 133.3131 | 339.9584 | 347.4606 | 151.4252 | 0 | 0 | 132.4671 | 78.4846 | 78.4846 | 119.6877 | 183.5556 | 185.8743 | 125.2856 | 78.4846 | 78.4846 | 136.5329 | 78.4846 | 78.4846 | 253.0008 | 523.5139 | 533.3349 | 276.7108 | 78.4846 | 78.4846 | 269 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 13 | 7525 | 14.6 | 14.6 | 7.0292 | 7.5698 | 15 | 61 | 61 | 362.038 | 147.2215 | 20.2987 | 189.3405 | 0 | 0 | 35.164 | 263.2476 | 337.1244 | 213.5183 | 0 | 0 | 127.7785 | 82.6357 | 82.6357 | 94.7654 | 173.4425 | 198.9262 | 156.2885 | 82.6357 | 82.6357 | 147.2215 | 82.6357 | 82.6357 | 129.9294 | 436.6901 | 536.0506 | 369.8067 | 82.6357 | 82.6357 | 275 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 14 | 7526 | 14.3 | 14.3 | 7.0292 | 7.5698 | 15 | 65 | 65 | 102.1945 | 155.4477 | 17.6359 | 204.2356 | 0 | 0 | 0 | 55.8762 | 94.5771 | 77.876 | 15.5562 | 0 | 33.5523 | 74.5422 | 74.5422 | 74.5422 | 119.2282 | 150.1786 | 136.8222 | 86.983 | 74.5422 | 155.4477 | 74.5422 | 74.5422 | 74.5422 | 175.1045 | 244.7557 | 214.6982 | 102.5392 | 74.5422 | 189 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 15 | 7527 | 13.4 | 13.4 | 7.0292 | 7.5698 | 15 | 68 | 68 | 72.2295 | 122.8222 | 12.8572 | 218.2456 | 0 | 0 | 0 | 24.4037 | 62.7681 | 64.3637 | 28.256 | 0 | 19.1778 | 59.3689 | 59.3689 | 59.3689 | 81.0109 | 115.0336 | 116.4487 | 84.4272 | 59.3689 | 122.8222 | 59.3689 | 59.3689 | 59.3689 | 105.4147 | 177.8017 | 180.8124 | 112.6832 | 59.3689 | 142 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 16 | 7528 | 12 | 12 | 7.0292 | 7.5698 | 15 | 73 | 73 | 13.1612 | 61.7782 | 6.3766 | 231.217 | 0 | 0 | 0 | 1.5091 | 10.0772 | 12.7422 | 7.943 | 0 | 2.2218 | 30.5907 | 30.5907 | 30.5907 | 30.8512 | 32.3298 | 32.7898 | 31.9615 | 30.5907 | 61.7782 | 30.5907 | 30.5907 | 30.5907 | 32.3603 | 42.407 | 45.5319 | 39.9045 | 30.5907 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 17 | 7529 | 11.2 | 11.2 | 7.0292 | 7.5698 | 15 | 78 | 78 | 3.874 | 10.8263 | -1.3647 | 243.297 | 0 | 0 | 0 | 0 | 2.4116 | 3.8274 | 3.0012 | 0.41694 | 0.17366 | 5.7668 | 5.7668 | 5.7668 | 5.7668 | 6.2285 | 6.4996 | 6.3414 | 5.8466 | 10.8263 | 5.7668 | 5.7668 | 5.7668 | 5.7668 | 8.6401 | 10.327 | 9.3426 | 6.2635 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 18 | 7530 | 10.2 | 10.2 | 7.0292 | 7.5698 | 15 | 81 | 81 | 0 | 0 | -9.9577 | 254.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 19 | 7531 | 9.2 | 9.2 | 7.0292 | 7.5698 | 15 | 82 | 82 | 0 | 0 | -19.0318 | 266.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 20 | 7532 | 8.2 | 8.2 | 7.0292 | 7.5698 | 15 | 87 | 87 | 0 | 0 | -28.2222 | 278.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 21 | 7533 | 6.4 | 6.4 | 7.0292 | 7.5698 | 15 | 89 | 89 | 0 | 0 | -37.1076 | 291.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 22 | 7534 | 4.7 | 4.7 | 7.0292 | 7.5698 | 15 | 92 | 92 | 0 | 0 | -45.1108 | 307.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 23 | 7535 | 3.9 | 3.9 | 7.0292 | 7.5698 | 15 | 95 | 95 | 0 | 0 | -51.3705 | 327.0164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 10 | 24 | 7536 | 4 | 4 | 9.0542 | 7.7758 | 15 | 95 | 95 | 0 | 0 | -54.7399 | 350.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 1 | 7537 | 3.8 | 3.8 | 9.0542 | 7.7758 | 15 | 95 | 95 | 0 | 0 | -54.3001 | 15.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 2 | 7538 | 3.6 | 3.6 | 9.0542 | 7.7758 | 15 | 97 | 97 | 0 | 0 | -50.4547 | 37.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 3 | 7539 | 3.5 | 3.5 | 9.0542 | 7.7758 | 15 | 97 | 97 | 0 | 0 | -43.6988 | 56.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 4 | 7540 | 3.3 | 3.3 | 9.0542 | 7.7758 | 15 | 97 | 97 | 0 | 0 | -35.4247 | 71.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 5 | 7541 | 3.2 | 3.2 | 9.0542 | 7.7758 | 15 | 97 | 97 | 0 | 0 | -26.4231 | 84.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 6 | 7542 | 3.3 | 3.3 | 9.0542 | 7.7758 | 15 | 98 | 98 | 0 | 0 | -17.2257 | 96.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 7 | 7543 | 2.8 | 2.8 | 9.0542 | 7.7758 | 15 | 98 | 98 | 0 | 0 | -8.2327 | 107.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 11 | 8 | 7544 | 2.6 | 2.6 | 9.0542 | 7.7758 | 15 | 98 | 98 | 0 | 0 | 0.19515 | 119.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 9 | 7545 | 2.8 | 2.8 | 9.0542 | 7.7758 | 15 | 99 | 99 | 0.11138 | 2.992 | 7.6819 | 131.6886 | 0 | 0.029843 | 0.096977 | 0.1073 | 0.054772 | 0 | 0 | 0 | 0.0080289 | 1.4064 | 1.4064 | 1.4064 | 1.4064 | 1.4064 | 1.4064 | 1.4064 | 1.4064 | 2.992 | 1.4064 | 1.4363 | 1.5034 | 1.5137 | 1.4612 | 1.4064 | 1.4064 | 1.4064 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 10 | 7546 | 3.4 | 3.4 | 9.0542 | 7.7758 | 15 | 99 | 99 | 0.86093 | 21.8363 | 13.8117 | 144.8561 | 0 | 0.049283 | 0.63715 | 0.85178 | 0.56745 | 0 | 0 | 0 | 0.1637 | 10.4749 | 10.4749 | 10.4749 | 10.4749 | 10.4749 | 10.4749 | 10.4749 | 10.4749 | 21.8363 | 10.4749 | 10.5242 | 11.1121 | 11.3267 | 11.0424 | 10.4749 | 10.4749 | 10.4749 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 11 | 7547 | 4.1 | 4.1 | 9.0542 | 7.7758 | 15 | 96 | 96 | 1.4553 | 41.5937 | 18.1448 | 159.0474 | 0 | 0 | 0.8135 | 1.3924 | 1.1556 | 0.24191 | 0 | 0 | 0.40632 | 20.1256 | 20.1256 | 20.1256 | 20.1256 | 20.1256 | 20.1256 | 20.1256 | 20.1256 | 41.5937 | 20.1256 | 20.1256 | 20.9391 | 21.5179 | 21.2812 | 20.3675 | 20.1256 | 20.1256 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 12 | 7548 | 4.4 | 4.4 | 9.0542 | 7.7758 | 15 | 93 | 93 | 2.6006 | 66.1335 | 20.2907 | 174.0345 | 0 | 0 | 0.88372 | 2.2568 | 2.3079 | 1.007 | 0 | 0 | 0.86647 | 32.446 | 32.446 | 32.446 | 32.446 | 32.446 | 32.446 | 32.446 | 32.446 | 66.1335 | 32.446 | 32.446 | 33.3297 | 34.7028 | 34.7539 | 33.4531 | 32.446 | 32.446 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 13 | 7549 | 4.7 | 4.7 | 9.0542 | 7.7758 | 15 | 91 | 91 | 2.9803 | 73.9617 | 20.0241 | 189.279 | 0 | 0 | 0.29052 | 2.1713 | 2.7802 | 1.7605 | 0 | 0 | 1.0383 | 36.3576 | 36.3576 | 36.3576 | 36.3576 | 36.3576 | 36.3576 | 36.3576 | 36.3576 | 73.9617 | 36.3576 | 36.3576 | 36.6482 | 38.529 | 39.1378 | 38.1181 | 36.3576 | 36.3576 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 14 | 7550 | 4.9 | 4.9 | 9.0542 | 7.7758 | 15 | 90 | 90 | 4.0241 | 79.697 | 17.3743 | 204.1293 | 0 | 0 | 0 | 2.2074 | 3.7314 | 3.0696 | 0.60963 | 0 | 1.303 | 39.3865 | 39.3865 | 39.3865 | 39.3865 | 39.3865 | 39.3865 | 39.3865 | 39.3865 | 79.697 | 39.3865 | 39.3865 | 39.3865 | 41.5939 | 43.1179 | 42.4561 | 39.9961 | 39.3865 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 15 | 7551 | 5.3 | 5.3 | 9.0542 | 7.7758 | 15 | 88 | 88 | 5.3063 | 73.6145 | 12.6126 | 218.1047 | 0 | 0 | 0 | 1.8042 | 4.6217 | 4.7319 | 2.0702 | 0 | 1.3855 | 36.4594 | 36.4594 | 36.4594 | 36.4594 | 36.4594 | 36.4594 | 36.4594 | 36.4594 | 73.6145 | 36.4594 | 36.4594 | 36.4594 | 38.2636 | 41.0811 | 41.1913 | 38.5297 | 36.4594 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 16 | 7552 | 5.1 | 5.1 | 9.0542 | 7.7758 | 15 | 87 | 87 | 3.6125 | 38.4056 | 6.1495 | 231.0513 | 0 | 0 | 0 | 0.42323 | 2.774 | 3.4998 | 2.1755 | 0 | 0.59444 | 18.5957 | 18.5957 | 18.5957 | 18.5957 | 18.5957 | 18.5957 | 18.5957 | 18.5957 | 38.4056 | 18.5957 | 18.5957 | 18.5957 | 19.0189 | 21.3697 | 22.0955 | 20.7712 | 18.5957 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 17 | 7553 | 4.2 | 4.2 | 9.0542 | 7.7758 | 15 | 87 | 87 | 2.4786 | 7.899 | -1.5766 | 243.113 | 0 | 0 | 0 | 0 | 1.5492 | 2.4506 | 1.9166 | 0.25979 | 0.101 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 7.899 | 4.2312 | 4.2312 | 4.2312 | 4.2312 | 5.7804 | 6.6818 | 6.1478 | 4.491 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 18 | 7554 | 3.3 | 3.3 | 9.0542 | 7.7758 | 15 | 90 | 90 | 0 | 0 | -10.1586 | 254.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 19 | 7555 | 2.9 | 2.9 | 9.0542 | 7.7758 | 15 | 91 | 91 | 0 | 0 | -19.2273 | 266.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 20 | 7556 | 1.8 | 1.8 | 9.0542 | 7.7758 | 15 | 92 | 92 | 0 | 0 | -28.419 | 278.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 21 | 7557 | 1.9 | 1.9 | 9.0542 | 7.7758 | 15 | 95 | 95 | 0 | 0 | -37.314 | 291.4835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 22 | 7558 | 2.6 | 2.6 | 9.0542 | 7.7758 | 15 | 91 | 91 | 0 | 0 | -45.336 | 307.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 23 | 7559 | 2.5 | 2.5 | 9.0542 | 7.7758 | 15 | 91 | 91 | 0 | 0 | -51.6217 | 326.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 11 | 24 | 7560 | 2.3 | 2.3 | 3.4292 | 6.5537 | 15 | 92 | 92 | 0 | 0 | -55.0142 | 350.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 1 | 7561 | 1.9 | 1.9 | 3.4292 | 6.5537 | 15 | 93 | 93 | 0 | 0 | -54.58 | 15.1528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 2 | 7562 | 1.8 | 1.8 | 3.4292 | 6.5537 | 15 | 94 | 94 | 0 | 0 | -50.7191 | 37.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 3 | 7563 | 1.6 | 1.6 | 3.4292 | 6.5537 | 15 | 92 | 92 | 0 | 0 | -43.9472 | 56.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 4 | 7564 | 0.4 | 0.4 | 3.4292 | 6.5537 | 15 | 95 | 95 | 0 | 0 | -35.6611 | 71.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 5 | 7565 | 0.5 | 0.5 | 3.4292 | 6.5537 | 15 | 96 | 96 | 0 | 0 | -26.6539 | 84.7726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 6 | 7566 | 1 | 1 | 3.4292 | 6.5537 | 15 | 94 | 94 | 0 | 0 | -17.4567 | 96.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 7 | 7567 | 1.1 | 1.1 | 3.4292 | 6.5537 | 15 | 95 | 95 | 0 | 0 | -8.4689 | 107.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 12 | 8 | 7568 | 0.9 | 0.9 | 3.4292 | 6.5537 | 15 | 95 | 95 | 0 | 0 | -0.049722 | 119.5847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 9 | 7569 | 1.8 | 1.8 | 3.4292 | 6.5537 | 15 | 92 | 92 | 44.5891 | 29.9663 | 7.4262 | 131.7932 | 0 | 11.8524 | 38.7759 | 42.985 | 22.0141 | 0 | 0 | 0 | 3.0337 | 10.9332 | 18.9845 | 37.2737 | 40.133 | 25.8874 | 10.9332 | 10.9332 | 10.9332 | 29.9663 | 10.9332 | 30.8369 | 76.0496 | 83.118 | 47.9015 | 10.9332 | 10.9332 | 10.9332 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 10 | 7570 | 2.9 | 2.9 | 3.4292 | 6.5537 | 15 | 89 | 89 | 14.5027 | 69.3038 | 13.5453 | 144.93 | 0 | 0.80449 | 10.7219 | 14.3586 | 9.5842 | 0 | 0 | 0 | 2.6962 | 29.9073 | 35.6923 | 107.008 | 133.1591 | 98.8267 | 29.9073 | 29.9073 | 29.9073 | 69.3038 | 29.9073 | 36.4968 | 117.7299 | 147.5176 | 108.4109 | 29.9073 | 29.9073 | 29.9073 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 11 | 7571 | 4.2 | 4.2 | 3.4292 | 6.5537 | 15 | 86 | 86 | 23.1032 | 110.6506 | 17.8707 | 159.0809 | 0 | 0 | 12.9053 | 22.1241 | 18.3828 | 3.8732 | 0 | 0 | 6.3494 | 49.5391 | 49.5391 | 91.0685 | 120.7346 | 108.6953 | 62.0031 | 49.5391 | 49.5391 | 110.6506 | 49.5391 | 49.5391 | 103.9739 | 142.8586 | 127.0781 | 65.8763 | 49.5391 | 49.5391 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 12 | 7572 | 5.3 | 5.3 | 3.4292 | 6.5537 | 15 | 83 | 83 | 59.4492 | 149.4573 | 20.0152 | 174.02 | 0 | 0 | 20.2021 | 51.6566 | 52.8513 | 23.0865 | 0 | 0 | 19.5427 | 69.7663 | 69.7663 | 100.9972 | 149.6235 | 151.4705 | 105.4562 | 69.7663 | 69.7663 | 149.4573 | 69.7663 | 69.7663 | 121.1993 | 201.2801 | 204.3218 | 128.5427 | 69.7663 | 69.7663 | 169 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 13 | 7573 | 6.4 | 6.4 | 3.4292 | 6.5537 | 15 | 83 | 83 | 356.411 | 144.4217 | 19.7549 | 189.2149 | 0 | 0 | 34.8889 | 260.1807 | 333.0621 | 210.8403 | 0 | 0 | 122.5783 | 80.9272 | 80.9272 | 93.0605 | 171.4099 | 196.7558 | 154.2509 | 80.9272 | 80.9272 | 144.4217 | 80.9272 | 80.9272 | 127.9494 | 431.5906 | 529.8179 | 365.0911 | 80.9272 | 80.9272 | 267 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 14 | 7574 | 6.7 | 6.7 | 3.4292 | 6.5537 | 15 | 84 | 84 | 25.8256 | 130.752 | 17.1183 | 204.0215 | 0 | 0 | 0 | 14.2127 | 23.992 | 19.7171 | 3.8923 | 0 | 8.248 | 62.1407 | 62.1407 | 62.1407 | 95.7602 | 118.8928 | 108.7808 | 71.3477 | 62.1407 | 130.752 | 62.1407 | 62.1407 | 62.1407 | 109.9728 | 142.8848 | 128.498 | 75.2399 | 62.1407 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 15 | 7575 | 7.3 | 7.3 | 3.4292 | 6.5537 | 15 | 78 | 78 | 35.4859 | 109.8886 | 12.3738 | 217.9632 | 0 | 0 | 0 | 12.1417 | 30.9766 | 31.6659 | 13.8056 | 0 | 9.1114 | 52.9722 | 52.9722 | 52.9722 | 71.4161 | 100.0273 | 101.0742 | 73.9436 | 52.9722 | 109.8886 | 52.9722 | 52.9722 | 52.9722 | 83.5578 | 131.0039 | 132.7401 | 87.7493 | 52.9722 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 16 | 7576 | 7.3 | 7.3 | 3.4292 | 6.5537 | 15 | 78 | 78 | 1.9599 | 27.6857 | 5.9283 | 230.8854 | 0 | 0 | 0 | 0.23452 | 1.5093 | 1.8999 | 1.1776 | 0 | 0.31428 | 13.2272 | 13.2272 | 13.2272 | 13.2272 | 13.2272 | 13.2272 | 13.2272 | 13.2272 | 27.6857 | 13.2272 | 13.2272 | 13.2272 | 13.4618 | 14.7365 | 15.1272 | 14.4049 | 13.2272 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 17 | 7577 | 7.4 | 7.4 | 3.4292 | 6.5537 | 15 | 78 | 78 | 0.4285 | 2.9843 | -1.7825 | 242.9294 | 0 | 0 | 0 | 0 | 0.26888 | 0.42396 | 0.33069 | 0.043703 | 0.015745 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 2.9843 | 1.3792 | 1.3792 | 1.3792 | 1.3792 | 1.648 | 1.8031 | 1.7099 | 1.4229 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 12 | 18 | 7578 | 7.3 | 7.3 | 3.4292 | 6.5537 | 15 | 80 | 80 | 0 | 0 | -10.3535 | 254.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 19 | 7579 | 7.3 | 7.3 | 3.4292 | 6.5537 | 15 | 81 | 81 | 0 | 0 | -19.4166 | 265.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 20 | 7580 | 8 | 8 | 3.4292 | 6.5537 | 15 | 78 | 78 | 0 | 0 | -28.6095 | 277.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 21 | 7581 | 7.9 | 7.9 | 3.4292 | 6.5537 | 15 | 79 | 79 | 0 | 0 | -37.514 | 291.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 22 | 7582 | 7.8 | 7.8 | 3.4292 | 6.5537 | 15 | 81 | 81 | 0 | 0 | -45.5547 | 307.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 23 | 7583 | 7.4 | 7.4 | 3.4292 | 6.5537 | 15 | 87 | 87 | 0 | 0 | -51.8667 | 326.6107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 12 | 24 | 7584 | 6.8 | 6.8 | 4.625 | 5.8682 | 15 | 94 | 94 | 0 | 0 | -55.283 | 350.1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 1 | 7585 | 7.3 | 7.3 | 4.625 | 5.8682 | 15 | 97 | 97 | 0 | 0 | -54.8555 | 15.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 2 | 7586 | 8 | 8 | 4.625 | 5.8682 | 15 | 98 | 98 | 0 | 0 | -50.9799 | 38.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 3 | 7587 | 9.7 | 9.7 | 4.625 | 5.8682 | 15 | 99 | 99 | 0 | 0 | -44.1927 | 56.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 4 | 7588 | 10.1 | 10.1 | 4.625 | 5.8682 | 15 | 97 | 97 | 0 | 0 | -35.8951 | 71.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 5 | 7589 | 9.9 | 9.9 | 4.625 | 5.8682 | 15 | 95 | 95 | 0 | 0 | -26.8826 | 84.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 6 | 7590 | 8.8 | 8.8 | 4.625 | 5.8682 | 15 | 95 | 95 | 0 | 0 | -17.6857 | 96.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 7 | 7591 | 7.5 | 7.5 | 4.625 | 5.8682 | 15 | 96 | 96 | 0 | 0 | -8.7028 | 108.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 13 | 8 | 7592 | 5.1 | 5.1 | 4.625 | 5.8682 | 15 | 96 | 96 | 0 | 0 | -0.2921 | 119.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 9 | 7593 | 6.8 | 6.8 | 4.625 | 5.8682 | 15 | 98 | 98 | 90.9584 | 30.1734 | 7.1735 | 131.8923 | 0 | 23.9915 | 79.0034 | 87.7361 | 45.0742 | 0 | 0 | 0 | 5.8266 | 12.1062 | 19.7207 | 37.1807 | 39.9523 | 26.4121 | 12.1062 | 12.1062 | 12.1062 | 30.1734 | 12.1062 | 43.7123 | 116.184 | 127.6884 | 71.4863 | 12.1062 | 12.1062 | 12.1062 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 10 | 7594 | 9 | 9 | 4.625 | 5.8682 | 15 | 92 | 92 | 267.8722 | 82.3131 | 13.2825 | 144.9987 | 0 | 14.4087 | 197.8437 | 265.3845 | 177.4667 | 0 | 0 | 0 | 48.6869 | 43.9117 | 49.3 | 117.8984 | 143.1564 | 110.2781 | 43.9117 | 43.9117 | 43.9117 | 82.3131 | 43.9117 | 63.7087 | 315.7421 | 408.5409 | 287.7449 | 43.9117 | 43.9117 | 43.9117 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 11 | 7595 | 10.9 | 10.9 | 4.625 | 5.8682 | 15 | 89 | 89 | 343.4158 | 115.0924 | 17.601 | 159.1099 | 0 | 0 | 191.7124 | 329.1528 | 273.78 | 58.0306 | 0 | 0 | 92.9076 | 64.5811 | 64.5811 | 128.7129 | 174.6896 | 156.1663 | 83.9935 | 64.5811 | 64.5811 | 115.0924 | 64.5811 | 64.5811 | 320.4253 | 503.8424 | 429.9463 | 142.0241 | 64.5811 | 64.5811 | 208 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 12 | 7596 | 11.8 | 11.8 | 4.625 | 5.8682 | 15 | 84 | 84 | 502.7979 | 114.9139 | 19.7446 | 174.0018 | 0 | 0 | 170.893 | 437.4509 | 447.756 | 195.7717 | 0 | 0 | 163.0861 | 72.1179 | 72.1179 | 110.3719 | 170.0404 | 172.3471 | 115.941 | 72.1179 | 72.1179 | 114.9139 | 72.1179 | 72.1179 | 281.2649 | 607.4913 | 620.1031 | 311.7127 | 72.1179 | 72.1179 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 13 | 7597 | 12.8 | 12.8 | 4.625 | 5.8682 | 15 | 84 | 84 | 430.9244 | 131.6887 | 19.4911 | 189.1483 | 0 | 0 | 42.3832 | 315.1944 | 403.369 | 255.2555 | 0 | 0 | 146.3113 | 77.5997 | 77.5997 | 89.3652 | 165.0968 | 189.5738 | 148.4579 | 77.5997 | 77.5997 | 131.6887 | 77.5997 | 77.5997 | 131.7484 | 480.2911 | 592.9427 | 403.7134 | 77.5997 | 77.5997 | 278 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 14 | 7598 | 12.7 | 12.7 | 4.625 | 5.8682 | 15 | 81 | 81 | 147.8542 | 150.4235 | 16.8681 | 203.9122 | 0 | 0 | 0 | 81.6342 | 137.6083 | 112.9734 | 22.1602 | 0 | 46.5765 | 74.239 | 74.239 | 74.239 | 134.7051 | 176.165 | 157.918 | 90.653 | 74.239 | 150.4235 | 74.239 | 74.239 | 74.239 | 216.3393 | 313.7733 | 270.8913 | 112.8131 | 74.239 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 15 | 7599 | 12.5 | 12.5 | 4.625 | 5.8682 | 15 | 84 | 84 | 13.9368 | 93.481 | 12.141 | 217.821 | 0 | 0 | 0 | 4.7987 | 12.1924 | 12.444 | 5.4061 | 0 | 3.519 | 45.3125 | 45.3125 | 45.3125 | 50.1643 | 57.64 | 57.8944 | 50.7784 | 45.3125 | 93.481 | 45.3125 | 45.3125 | 45.3125 | 54.963 | 69.8324 | 70.3384 | 56.1845 | 45.3125 | 97 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 16 | 7600 | 12 | 12 | 4.625 | 5.8682 | 15 | 85 | 85 | 19.0224 | 61.0279 | 5.7131 | 230.7196 | 0 | 0 | 0 | 2.3241 | 14.6903 | 18.4511 | 11.4036 | 0 | 2.9721 | 30.3711 | 30.3711 | 30.3711 | 33.8208 | 52.1767 | 57.7592 | 47.2981 | 30.3711 | 61.0279 | 30.3711 | 30.3711 | 30.3711 | 36.1449 | 66.867 | 76.2103 | 58.7016 | 30.3711 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 17 | 7601 | 10.4 | 10.4 | 4.625 | 5.8682 | 15 | 91 | 91 | 3.8192 | 7.8747 | -1.9824 | 242.746 | 0 | 0 | 0 | 0 | 2.406 | 3.7813 | 2.9416 | 0.37873 | 0.12532 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 7.8747 | 4.2189 | 4.2189 | 4.2189 | 4.2189 | 6.6248 | 8.0002 | 7.1604 | 4.5976 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 13 | 18 | 7602 | 10.3 | 10.3 | 4.625 | 5.8682 | 15 | 94 | 94 | 0 | 0 | -10.5422 | 254.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 19 | 7603 | 9.2 | 9.2 | 4.625 | 5.8682 | 15 | 95 | 95 | 0 | 0 | -19.5996 | 265.6657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 20 | 7604 | 9.1 | 9.1 | 4.625 | 5.8682 | 15 | 97 | 97 | 0 | 0 | -28.7937 | 277.6472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 21 | 7605 | 8.8 | 8.8 | 4.625 | 5.8682 | 15 | 96 | 96 | 0 | 0 | -37.7075 | 291.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 22 | 7606 | 8.2 | 8.2 | 4.625 | 5.8682 | 15 | 95 | 95 | 0 | 0 | -45.7669 | 306.8442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 23 | 7607 | 7.7 | 7.7 | 4.625 | 5.8682 | 15 | 96 | 96 | 0 | 0 | -52.1053 | 326.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 13 | 24 | 7608 | 7.1 | 7.1 | 9.4042 | 6.7717 | 15 | 97 | 97 | 0 | 0 | -55.5462 | 349.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 1 | 7609 | 7.4 | 7.4 | 9.4042 | 6.7717 | 15 | 97 | 97 | 0 | 0 | -55.1264 | 15.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 2 | 7610 | 6.9 | 6.9 | 9.4042 | 6.7717 | 15 | 97 | 97 | 0 | 0 | -51.2369 | 38.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 3 | 7611 | 6.2 | 6.2 | 9.4042 | 6.7717 | 15 | 97 | 97 | 0 | 0 | -44.4352 | 56.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 4 | 7612 | 6 | 6 | 9.4042 | 6.7717 | 15 | 97 | 97 | 0 | 0 | -36.1267 | 72.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 5 | 7613 | 5.8 | 5.8 | 9.4042 | 6.7717 | 15 | 95 | 95 | 0 | 0 | -27.109 | 85.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 6 | 7614 | 5.6 | 5.6 | 9.4042 | 6.7717 | 15 | 95 | 95 | 0 | 0 | -17.9125 | 96.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 7 | 7615 | 6.3 | 6.3 | 9.4042 | 6.7717 | 15 | 90 | 90 | 0 | 0 | -8.9345 | 108.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 14 | 8 | 7616 | 6.3 | 6.3 | 9.4042 | 6.7717 | 15 | 88 | 88 | 0 | 0 | -0.53189 | 119.8223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 9 | 7617 | 6 | 6 | 9.4042 | 6.7717 | 15 | 88 | 88 | 1.1359 | 7.9317 | 6.9239 | 131.9859 | 0 | 0.29739 | 0.98546 | 1.0963 | 0.56489 | 0 | 0 | 0 | 0.068334 | 3.7319 | 4.2281 | 5.376 | 5.5609 | 4.6743 | 3.7319 | 3.7319 | 3.7319 | 7.9317 | 3.7319 | 4.5254 | 6.3615 | 6.6571 | 5.2392 | 3.7319 | 3.7319 | 3.7319 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 10 | 7618 | 6.9 | 6.9 | 9.4042 | 6.7717 | 15 | 83 | 83 | 7.2302 | 56.7154 | 13.0234 | 145.0622 | 0 | 0.3774 | 5.3351 | 7.1675 | 4.8013 | 0 | 0 | 0 | 1.2846 | 25.3438 | 28.8623 | 75.0829 | 92.1671 | 70.107 | 25.3438 | 25.3438 | 25.3438 | 56.7154 | 25.3438 | 29.2397 | 80.418 | 99.3346 | 74.9084 | 25.3438 | 25.3438 | 25.3438 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 11 | 7619 | 7.2 | 7.2 | 9.4042 | 6.7717 | 15 | 81 | 81 | 23.6679 | 107.6966 | 17.3356 | 159.1343 | 0 | 0 | 13.2056 | 22.7044 | 18.9033 | 4.0288 | 0 | 0 | 6.3034 | 48.0865 | 48.0865 | 90.9745 | 121.8237 | 109.4787 | 61.1709 | 48.0865 | 48.0865 | 107.6966 | 48.0865 | 48.0865 | 104.1802 | 144.5282 | 128.382 | 65.1997 | 48.0865 | 48.0865 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 12 | 7620 | 7.5 | 7.5 | 9.4042 | 6.7717 | 15 | 81 | 81 | 6.3915 | 97.9543 | 19.479 | 173.9799 | 0 | 0 | 2.1731 | 5.5679 | 5.7011 | 2.4946 | 0 | 0 | 2.0457 | 47.164 | 47.164 | 52.6236 | 61.1524 | 61.487 | 53.4313 | 47.164 | 47.164 | 97.9543 | 47.164 | 47.164 | 54.7967 | 66.7203 | 67.188 | 55.926 | 47.164 | 47.164 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 13 | 7621 | 8 | 8 | 9.4042 | 6.7717 | 15 | 81 | 81 | 2.7214 | 68.0877 | 19.2329 | 189.0791 | 0 | 0 | 0.26908 | 1.9945 | 2.5515 | 1.6139 | 0 | 0 | 0.91226 | 33.3652 | 33.3652 | 33.3652 | 33.3652 | 33.3652 | 33.3652 | 33.3652 | 33.3652 | 68.0877 | 33.3652 | 33.3652 | 33.6343 | 35.3597 | 35.9167 | 34.9791 | 33.3652 | 33.3652 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 14 | 7622 | 8.3 | 8.3 | 9.4042 | 6.7717 | 15 | 79 | 79 | 0.32196 | 21.9 | 16.6237 | 203.8015 | 0 | 0 | 0 | 0.17834 | 0.30018 | 0.24618 | 0.047969 | 0 | 0.10004 | 10.3254 | 10.3254 | 10.3254 | 10.3254 | 10.3254 | 10.3254 | 10.3254 | 10.3254 | 21.9 | 10.3254 | 10.3254 | 10.3254 | 10.5037 | 10.6256 | 10.5716 | 10.3733 | 10.3254 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 15 | 7623 | 8.6 | 8.6 | 9.4042 | 6.7717 | 15 | 81 | 81 | 2.0167 | 43.4992 | 11.9141 | 217.6782 | 0 | 0 | 0 | 0.69877 | 1.7681 | 1.8017 | 0.77988 | 0 | 0.50078 | 20.9751 | 20.9751 | 20.9751 | 20.9751 | 20.9751 | 20.9751 | 20.9751 | 20.9751 | 43.4992 | 20.9751 | 20.9751 | 20.9751 | 21.6739 | 22.7432 | 22.7768 | 21.755 | 20.9751 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 16 | 7624 | 8.5 | 8.5 | 9.4042 | 6.7717 | 15 | 84 | 84 | 3.0195 | 32.5404 | 5.5041 | 230.5538 | 0 | 0 | 0 | 0.37651 | 2.3383 | 2.9303 | 1.8058 | 0 | 0.45957 | 15.6666 | 15.6666 | 15.6666 | 15.6666 | 15.6666 | 15.6666 | 15.6666 | 15.6666 | 32.5404 | 15.6666 | 15.6666 | 15.6666 | 16.0432 | 18.0049 | 18.597 | 17.4725 | 15.6666 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 17 | 7625 | 8.4 | 8.4 | 9.4042 | 6.7717 | 15 | 89 | 89 | 13.1981 | 10.6178 | -2.1761 | 242.5631 | 0 | 0 | 0 | 0 | 8.3468 | 13.0755 | 10.1448 | 1.2714 | 0.38222 | 5.8369 | 5.8369 | 5.8369 | 5.8369 | 12.951 | 16.9815 | 14.4836 | 6.9205 | 10.6178 | 5.8369 | 5.8369 | 5.8369 | 5.8369 | 21.2978 | 30.057 | 24.6284 | 8.1919 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 14 | 18 | 7626 | 8.2 | 8.2 | 9.4042 | 6.7717 | 15 | 91 | 91 | 0 | 0 | -10.7248 | 254.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 19 | 7627 | 8 | 8 | 9.4042 | 6.7717 | 15 | 91 | 91 | 0 | 0 | -19.7764 | 265.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 20 | 7628 | 7.8 | 7.8 | 9.4042 | 6.7717 | 15 | 90 | 90 | 0 | 0 | -28.9714 | 277.4206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 21 | 7629 | 7.9 | 7.9 | 9.4042 | 6.7717 | 15 | 91 | 91 | 0 | 0 | -37.8943 | 290.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 22 | 7630 | 7.6 | 7.6 | 9.4042 | 6.7717 | 15 | 91 | 91 | 0 | 0 | -45.9724 | 306.6008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 23 | 7631 | 7.6 | 7.6 | 9.4042 | 6.7717 | 15 | 91 | 91 | 0 | 0 | -52.3376 | 326.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 14 | 24 | 7632 | 7.8 | 7.8 | 7.2833 | 6.9406 | 15 | 87 | 87 | 0 | 0 | -55.8037 | 349.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 1 | 7633 | 8.2 | 8.2 | 7.2833 | 6.9406 | 15 | 84 | 84 | 0 | 0 | -55.3927 | 15.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 2 | 7634 | 8.1 | 8.1 | 7.2833 | 6.9406 | 15 | 84 | 84 | 0 | 0 | -51.4902 | 38.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 3 | 7635 | 8 | 8 | 7.2833 | 6.9406 | 15 | 84 | 84 | 0 | 0 | -44.6747 | 57.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 4 | 7636 | 8.6 | 8.6 | 7.2833 | 6.9406 | 15 | 83 | 83 | 0 | 0 | -36.3557 | 72.2665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 5 | 7637 | 8.9 | 8.9 | 7.2833 | 6.9406 | 15 | 83 | 83 | 0 | 0 | -27.3332 | 85.2447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 6 | 7638 | 8.3 | 8.3 | 7.2833 | 6.9406 | 15 | 84 | 84 | 0 | 0 | -18.1372 | 97.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 7 | 7639 | 8.2 | 8.2 | 7.2833 | 6.9406 | 15 | 86 | 86 | 0 | 0 | -9.1638 | 108.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 15 | 8 | 7640 | 8.1 | 8.1 | 7.2833 | 6.9406 | 15 | 87 | 87 | 0 | 0 | -0.76896 | 119.9328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 9 | 7641 | 8.9 | 8.9 | 7.2833 | 6.9406 | 15 | 86 | 86 | 0.72834 | 5.959 | 6.6775 | 132.0742 | 0 | 0.18932 | 0.63113 | 0.70324 | 0.3634 | 0 | 0 | 0 | 0.04103 | 2.8047 | 3.1737 | 4.0347 | 4.1753 | 3.5129 | 2.8047 | 2.8047 | 2.8047 | 5.959 | 2.8047 | 3.363 | 4.6659 | 4.8785 | 3.8763 | 2.8047 | 2.8047 | 2.8047 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 10 | 7642 | 9 | 9 | 7.2833 | 6.9406 | 15 | 91 | 91 | 4.1209 | 43.2843 | 12.7681 | 145.1206 | 0 | 0.20892 | 3.0381 | 4.0876 | 2.7426 | 0 | 0 | 0 | 0.7157 | 20.3769 | 21.6907 | 39.4824 | 46.0823 | 37.6244 | 20.3769 | 20.3769 | 20.3769 | 43.2843 | 20.3769 | 21.8996 | 42.5204 | 50.1699 | 40.367 | 20.3769 | 20.3769 | 20.3769 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 11 | 7643 | 9.6 | 9.6 | 7.2833 | 6.9406 | 15 | 87 | 87 | 7.3332 | 84.0773 | 17.0748 | 159.1541 | 0 | 0 | 4.0898 | 7.0406 | 5.8671 | 1.2567 | 0 | 0 | 1.9227 | 39.332 | 39.332 | 57.6022 | 70.7841 | 65.5418 | 44.9462 | 39.332 | 39.332 | 84.0773 | 39.332 | 39.332 | 61.692 | 77.8247 | 71.4089 | 46.2029 | 39.332 | 39.332 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 12 | 7644 | 10.5 | 10.5 | 7.2833 | 6.9406 | 15 | 86 | 86 | 21.7607 | 126.1269 | 19.2186 | 173.9545 | 0 | 0 | 7.4023 | 18.9803 | 19.4399 | 8.5118 | 0 | 0 | 6.8731 | 57.8913 | 57.8913 | 76.3075 | 105.1124 | 106.2557 | 79.0678 | 57.8913 | 57.8913 | 126.1269 | 57.8913 | 57.8913 | 83.7099 | 124.0927 | 125.6957 | 87.5797 | 57.8913 | 57.8913 | 133 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 13 | 7645 | 10.5 | 10.5 | 7.2833 | 6.9406 | 15 | 84 | 84 | 9.6276 | 113.8135 | 18.9802 | 189.0075 | 0 | 0 | 0.95745 | 7.0696 | 9.0405 | 5.7156 | 0 | 0 | 3.1865 | 54.434 | 54.434 | 56.5789 | 70.2711 | 74.6862 | 67.2378 | 54.434 | 54.434 | 113.8135 | 54.434 | 54.434 | 57.5363 | 77.3407 | 83.7267 | 72.9534 | 54.434 | 54.434 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 14 | 7646 | 10.6 | 10.6 | 7.2833 | 6.9406 | 15 | 85 | 85 | 5.4122 | 87.3409 | 16.3853 | 203.6894 | 0 | 0 | 0 | 3.0077 | 5.0549 | 4.1409 | 0.80129 | 0 | 1.6591 | 43.4207 | 43.4207 | 43.4207 | 43.863 | 44.164 | 44.0296 | 43.5385 | 43.4207 | 87.3409 | 43.4207 | 43.4207 | 43.4207 | 46.8707 | 49.2189 | 48.1705 | 44.3398 | 43.4207 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 15 | 7647 | 10.7 | 10.7 | 7.2833 | 6.9406 | 15 | 84 | 84 | 4.8328 | 65.8198 | 11.6934 | 217.535 | 0 | 0 | 0 | 1.685 | 4.2458 | 4.3195 | 1.8629 | 0 | 1.1802 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 65.8198 | 32.4555 | 32.4555 | 32.4555 | 34.1405 | 36.7013 | 36.775 | 34.3183 | 32.4555 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 16 | 7648 | 11.1 | 11.1 | 7.2833 | 6.9406 | 15 | 82 | 82 | 377.3926 | 61.0548 | 5.3011 | 230.388 | 0 | 0 | 0 | 48.0136 | 293.0545 | 366.4281 | 225.153 | 0 | 55.9452 | 37.0756 | 37.0756 | 37.0756 | 48.3224 | 105.7212 | 122.9083 | 89.8158 | 37.0756 | 61.0548 | 37.0756 | 37.0756 | 37.0756 | 96.336 | 398.7757 | 489.3364 | 314.9689 | 37.0756 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 17 | 7649 | 9.6 | 9.6 | 7.2833 | 6.9406 | 15 | 87 | 87 | 26.1667 | 10.341 | -2.3636 | 242.3807 | 0 | 0 | 0 | 0 | 16.6121 | 25.9397 | 20.0721 | 2.4466 | 0.65899 | 5.8463 | 5.8463 | 5.8463 | 5.8463 | 25.983 | 37.2896 | 30.1771 | 8.8119 | 10.341 | 5.8463 | 5.8463 | 5.8463 | 5.8463 | 42.5951 | 63.2292 | 50.2492 | 11.2585 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 15 | 18 | 7650 | 7.7 | 7.7 | 7.2833 | 6.9406 | 15 | 91 | 91 | 0 | 0 | -10.9011 | 253.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 19 | 7651 | 7.3 | 7.3 | 7.2833 | 6.9406 | 15 | 95 | 95 | 0 | 0 | -19.9469 | 265.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 20 | 7652 | 5.2 | 5.2 | 7.2833 | 6.9406 | 15 | 96 | 96 | 0 | 0 | -29.1427 | 277.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 21 | 7653 | 6.1 | 6.1 | 7.2833 | 6.9406 | 15 | 98 | 98 | 0 | 0 | -38.0746 | 290.5237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 22 | 7654 | 7.3 | 7.3 | 7.2833 | 6.9406 | 15 | 97 | 97 | 0 | 0 | -46.1712 | 306.3559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 23 | 7655 | 5.7 | 5.7 | 7.2833 | 6.9406 | 15 | 96 | 96 | 0 | 0 | -52.5633 | 325.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 15 | 24 | 7656 | 5.3 | 5.3 | 8.3958 | 7.2819 | 15 | 97 | 97 | 0 | 0 | -56.0555 | 349.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 1 | 7657 | 4.7 | 4.7 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -55.6542 | 15.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 2 | 7658 | 4 | 4 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -51.7396 | 38.3455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 3 | 7659 | 3.7 | 3.7 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -44.911 | 57.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 4 | 7660 | 4.1 | 4.1 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -36.5821 | 72.4169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 5 | 7661 | 4.6 | 4.6 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -27.555 | 85.3902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 6 | 7662 | 5 | 5 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -18.3594 | 97.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 7 | 7663 | 4.9 | 4.9 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -9.3906 | 108.5206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 16 | 8 | 7664 | 4.9 | 4.9 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -1.0032 | 120.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 9 | 7665 | 5.3 | 5.3 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0.20884 | 2.989 | 6.4344 | 132.157 | 0 | 0.053912 | 0.18077 | 0.20173 | 0.10452 | 0 | 0 | 0 | 0.010983 | 1.4074 | 1.5904 | 2.0208 | 2.092 | 1.7621 | 1.4074 | 1.4074 | 1.4074 | 2.989 | 1.4074 | 1.6443 | 2.2016 | 2.2937 | 1.8666 | 1.4074 | 1.4074 | 1.4074 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 10 | 7666 | 5.8 | 5.8 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0.80397 | 18.8635 | 12.5168 | 145.174 | 0 | 0.039625 | 0.59223 | 0.79792 | 0.53619 | 0 | 0 | 0 | 0.13648 | 9.0457 | 9.0457 | 9.0457 | 9.0457 | 9.0457 | 9.0457 | 9.0457 | 9.0457 | 18.8635 | 9.0457 | 9.0853 | 9.6379 | 9.8436 | 9.5819 | 9.0457 | 9.0457 | 9.0457 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 11 | 7667 | 6.5 | 6.5 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0.92553 | 30.7611 | 16.8185 | 159.1695 | 0 | 0 | 0.51599 | 0.88932 | 0.7417 | 0.1596 | 0 | 0 | 0.23892 | 14.7359 | 14.7359 | 14.7359 | 14.7359 | 14.7359 | 14.7359 | 14.7359 | 14.7359 | 30.7611 | 14.7359 | 14.7359 | 15.2519 | 15.6252 | 15.4776 | 14.8955 | 14.7359 | 14.7359 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 12 | 7668 | 6.7 | 6.7 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0.63473 | 30.8021 | 18.9634 | 173.9256 | 0 | 0 | 0.21606 | 0.55432 | 0.56786 | 0.24877 | 0 | 0 | 0.19786 | 14.6597 | 14.6597 | 14.6597 | 14.6597 | 14.6597 | 14.6597 | 14.6597 | 14.6597 | 30.8021 | 14.6597 | 14.6597 | 14.8758 | 15.2141 | 15.2276 | 14.9085 | 14.6597 | 14.6597 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 13 | 7669 | 7.1 | 7.1 | 8.3958 | 7.2819 | 15 | 99 | 99 | 1.3273 | 46.5662 | 18.7333 | 188.9334 | 0 | 0 | 0.13283 | 0.97653 | 1.2482 | 0.78868 | 0 | 0 | 0.43379 | 22.4289 | 22.4289 | 22.4289 | 22.4289 | 22.4289 | 22.4289 | 22.4289 | 22.4289 | 46.5662 | 22.4289 | 22.4289 | 22.5617 | 23.4054 | 23.6771 | 23.2176 | 22.4289 | 22.4289 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 14 | 7670 | 7.1 | 7.1 | 8.3958 | 7.2819 | 15 | 98 | 98 | 1.7543 | 49.4695 | 16.1529 | 203.576 | 0 | 0 | 0 | 0.97809 | 1.6412 | 1.3429 | 0.25799 | 0 | 0.53055 | 23.8981 | 23.8981 | 23.8981 | 23.8981 | 23.8981 | 23.8981 | 23.8981 | 23.8981 | 49.4695 | 23.8981 | 23.8981 | 23.8981 | 24.8762 | 25.5393 | 25.241 | 24.156 | 23.8981 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 15 | 7671 | 7.1 | 7.1 | 8.3958 | 7.2819 | 15 | 97 | 97 | 1.0691 | 30.7432 | 11.4788 | 217.3913 | 0 | 0 | 0 | 0.3751 | 0.9412 | 0.95596 | 0.41073 | 0 | 0.25679 | 14.6464 | 14.6464 | 14.6464 | 14.6464 | 14.6464 | 14.6464 | 14.6464 | 14.6464 | 30.7432 | 14.6464 | 14.6464 | 14.6464 | 15.0215 | 15.5876 | 15.6024 | 15.0571 | 14.6464 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 16 | 7672 | 6.9 | 6.9 | 8.3958 | 7.2819 | 15 | 97 | 97 | 0.37263 | 10.9462 | 5.1044 | 230.2225 | 0 | 0 | 0 | 0.048352 | 0.29014 | 0.36196 | 0.22176 | 0 | 0.053794 | 5.1162 | 5.1162 | 5.1162 | 5.1162 | 5.1162 | 5.1162 | 5.1162 | 5.1162 | 10.9462 | 5.1162 | 5.1162 | 5.1162 | 5.1646 | 5.4063 | 5.4782 | 5.338 | 5.1162 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 17 | 7673 | 6.7 | 6.7 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -2.5449 | 242.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 16 | 18 | 7674 | 6.5 | 6.5 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -11.071 | 253.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 19 | 7675 | 6.3 | 6.3 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -20.1109 | 265.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 20 | 7676 | 6.7 | 6.7 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -29.3074 | 276.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 21 | 7677 | 4.9 | 4.9 | 8.3958 | 7.2819 | 15 | 97 | 97 | 0 | 0 | -38.2481 | 290.2832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 22 | 7678 | 6.1 | 6.1 | 8.3958 | 7.2819 | 15 | 99 | 99 | 0 | 0 | -46.3632 | 306.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 23 | 7679 | 6.6 | 6.6 | 8.3958 | 7.2819 | 15 | 98 | 98 | 0 | 0 | -52.7825 | 325.7517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 16 | 24 | 7680 | 6.9 | 6.9 | 5.7958 | 6.9143 | 15 | 96 | 96 | 0 | 0 | -56.3013 | 349.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 1 | 7681 | 6.8 | 6.8 | 5.7958 | 6.9143 | 15 | 94 | 94 | 0 | 0 | -55.9109 | 15.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 2 | 7682 | 7.1 | 7.1 | 5.7958 | 6.9143 | 15 | 93 | 93 | 0 | 0 | -51.9851 | 38.4359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 3 | 7683 | 7.2 | 7.2 | 5.7958 | 6.9143 | 15 | 94 | 94 | 0 | 0 | -45.1442 | 57.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 4 | 7684 | 8 | 8 | 5.7958 | 6.9143 | 15 | 91 | 91 | 0 | 0 | -36.8058 | 72.5608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 5 | 7685 | 6.7 | 6.7 | 5.7958 | 6.9143 | 15 | 93 | 93 | 0 | 0 | -27.7744 | 85.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 6 | 7686 | 6 | 6 | 5.7958 | 6.9143 | 15 | 94 | 94 | 0 | 0 | -18.5793 | 97.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 7 | 7687 | 6.4 | 6.4 | 5.7958 | 6.9143 | 15 | 96 | 96 | 0 | 0 | -9.6149 | 108.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 17 | 8 | 7688 | 7.2 | 7.2 | 5.7958 | 6.9143 | 15 | 93 | 93 | 0 | 0 | -1.2345 | 120.1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 9 | 7689 | 7.5 | 7.5 | 5.7958 | 6.9143 | 15 | 93 | 93 | 0.9647 | 5.9528 | 6.1947 | 132.2344 | 0 | 0.2474 | 0.83411 | 0.93221 | 0.48423 | 0 | 0 | 0 | 0.047202 | 2.8024 | 3.1661 | 4.0285 | 4.1726 | 3.5142 | 2.8024 | 2.8024 | 2.8024 | 5.9528 | 2.8024 | 3.4135 | 4.8626 | 5.1049 | 3.9984 | 2.8024 | 2.8024 | 2.8024 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 10 | 7690 | 8.2 | 8.2 | 5.7958 | 6.9143 | 15 | 88 | 88 | 31.0204 | 69.8529 | 12.2695 | 145.2223 | 0 | 1.488 | 22.8334 | 30.8033 | 20.7291 | 0 | 0 | 0 | 5.1471 | 31.4239 | 37.6133 | 126.3992 | 159.5499 | 117.6462 | 31.4239 | 31.4239 | 31.4239 | 69.8529 | 31.4239 | 39.1013 | 149.2326 | 190.3532 | 138.3752 | 31.4239 | 31.4239 | 31.4239 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 11 | 7691 | 8.7 | 8.7 | 5.7958 | 6.9143 | 15 | 85 | 85 | 143.1984 | 121.6016 | 16.567 | 159.1805 | 0 | 0 | 79.8139 | 137.7065 | 114.9324 | 24.8325 | 0 | 0 | 36.3984 | 58.5643 | 58.5643 | 134.1717 | 189.013 | 167.4392 | 82.0881 | 58.5643 | 58.5643 | 121.6016 | 58.5643 | 58.5643 | 213.9856 | 326.7195 | 282.3717 | 106.9206 | 58.5643 | 58.5643 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 12 | 7692 | 8.6 | 8.6 | 5.7958 | 6.9143 | 15 | 85 | 85 | 20.4187 | 121.7176 | 18.7135 | 173.8932 | 0 | 0 | 6.956 | 17.8539 | 18.2932 | 8.0165 | 0 | 0 | 6.2824 | 55.9157 | 55.9157 | 73.8762 | 102.0142 | 103.1484 | 76.6144 | 55.9157 | 55.9157 | 121.7176 | 55.9157 | 55.9157 | 80.8322 | 119.8681 | 121.4416 | 84.6309 | 55.9157 | 55.9157 | 128 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 13 | 7693 | 8.5 | 8.5 | 5.7958 | 6.9143 | 15 | 87 | 87 | 5.7945 | 95.1298 | 18.4922 | 188.857 | 0 | 0 | 0.58385 | 4.2716 | 5.4571 | 3.4459 | 0 | 0 | 1.8702 | 46.6162 | 46.6162 | 47.3395 | 51.9077 | 53.3763 | 50.8849 | 46.6162 | 46.6162 | 95.1298 | 46.6162 | 46.6162 | 47.9233 | 56.1793 | 58.8334 | 54.3308 | 46.6162 | 46.6162 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 14 | 7694 | 8.8 | 8.8 | 5.7958 | 6.9143 | 15 | 85 | 85 | 15.2691 | 112.4438 | 15.9266 | 203.4613 | 0 | 0 | 0 | 8.5408 | 14.3081 | 11.6939 | 2.2296 | 0 | 4.5562 | 53.6571 | 53.6571 | 53.6571 | 67.2776 | 76.475 | 72.3061 | 57.2128 | 53.6571 | 112.4438 | 53.6571 | 53.6571 | 53.6571 | 75.8184 | 90.7831 | 83.9999 | 59.4424 | 53.6571 | 117 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 15 | 7695 | 9.1 | 9.1 | 5.7958 | 6.9143 | 15 | 85 | 85 | 12.6539 | 86.0105 | 11.2704 | 217.2472 | 0 | 0 | 0 | 4.4673 | 11.1623 | 11.3185 | 4.8445 | 0 | 2.9895 | 41.8539 | 41.8539 | 41.8539 | 45.8742 | 51.8994 | 52.04 | 46.2137 | 41.8539 | 86.0105 | 41.8539 | 41.8539 | 41.8539 | 50.3415 | 63.0616 | 63.3585 | 51.0582 | 41.8539 | 89 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 16 | 7696 | 8.9 | 8.9 | 5.7958 | 6.9143 | 15 | 87 | 87 | 3.5359 | 32.503 | 4.9139 | 230.0573 | 0 | 0 | 0 | 0.46779 | 2.7604 | 3.436 | 2.0989 | 0 | 0.49703 | 15.6791 | 15.6791 | 15.6791 | 15.6791 | 15.6791 | 15.6791 | 15.6791 | 15.6791 | 32.503 | 15.6791 | 15.6791 | 15.6791 | 16.1469 | 18.4395 | 19.1151 | 17.778 | 15.6791 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 17 | 7697 | 8.2 | 8.2 | 5.7958 | 6.9143 | 15 | 95 | 95 | 1.8076 | 2.9677 | -2.7199 | 242.0177 | 0 | 0 | 0 | 0 | 1.1563 | 1.794 | 1.3808 | 0.15876 | 0.032307 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 2.9677 | 1.5851 | 1.5851 | 1.5851 | 1.5851 | 2.7413 | 3.379 | 2.9659 | 1.7438 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 18 | 7698 | 8.3 | 8.3 | 5.7958 | 6.9143 | 15 | 97 | 97 | 0 | 0 | -11.2347 | 253.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 19 | 7699 | 8.7 | 8.7 | 5.7958 | 6.9143 | 15 | 97 | 97 | 0 | 0 | -20.2685 | 264.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 20 | 7700 | 8.7 | 8.7 | 5.7958 | 6.9143 | 15 | 97 | 97 | 0 | 0 | -29.4655 | 276.7441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 21 | 7701 | 8.9 | 8.9 | 5.7958 | 6.9143 | 15 | 95 | 95 | 0 | 0 | -38.4149 | 290.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 22 | 7702 | 9 | 9 | 5.7958 | 6.9143 | 15 | 94 | 94 | 0 | 0 | -46.5484 | 305.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 23 | 7703 | 9 | 9 | 5.7958 | 6.9143 | 15 | 94 | 94 | 0 | 0 | -52.9949 | 325.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 17 | 24 | 7704 | 9.1 | 9.1 | 8.0667 | 7.1625 | 15 | 94 | 94 | 0 | 0 | -56.5411 | 349.4699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 1 | 7705 | 8.8 | 8.8 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -56.1626 | 15.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 2 | 7706 | 9 | 9 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -52.2264 | 38.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 3 | 7707 | 9.2 | 9.2 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -45.3741 | 57.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 4 | 7708 | 9.7 | 9.7 | 8.0667 | 7.1625 | 15 | 98 | 98 | 0 | 0 | -37.0267 | 72.6983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 5 | 7709 | 10.6 | 10.6 | 8.0667 | 7.1625 | 15 | 98 | 98 | 0 | 0 | -27.9912 | 85.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 6 | 7710 | 11.2 | 11.2 | 8.0667 | 7.1625 | 15 | 98 | 98 | 0 | 0 | -18.7967 | 97.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 7 | 7711 | 11.8 | 11.8 | 8.0667 | 7.1625 | 15 | 99 | 99 | 0 | 0 | -9.8364 | 108.7467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 18 | 8 | 7712 | 12.1 | 12.1 | 8.0667 | 7.1625 | 15 | 98 | 98 | 0 | 0 | -1.4628 | 120.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 9 | 7713 | 12.1 | 12.1 | 8.0667 | 7.1625 | 15 | 97 | 97 | 1.1225 | 5.9491 | 5.9586 | 132.3064 | 0 | 0.28607 | 0.96953 | 1.0851 | 0.56497 | 0 | 0 | 0 | 0.050907 | 2.8011 | 3.1622 | 4.025 | 4.1709 | 3.5143 | 2.8011 | 2.8011 | 2.8011 | 5.9491 | 2.8011 | 3.4483 | 4.9946 | 5.2559 | 4.0793 | 2.8011 | 2.8011 | 2.8011 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 10 | 7714 | 12.3 | 12.3 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0.47791 | 13.9225 | 12.0264 | 145.2655 | 0 | 0.022338 | 0.35153 | 0.47481 | 0.31994 | 0 | 0 | 0 | 0.077506 | 6.6117 | 6.6117 | 6.6117 | 6.6117 | 6.6117 | 6.6117 | 6.6117 | 6.6117 | 13.9225 | 6.6117 | 6.6341 | 6.9633 | 7.0866 | 6.9317 | 6.6117 | 6.6117 | 6.6117 | 14 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 11 | 7715 | 12.8 | 12.8 | 8.0667 | 7.1625 | 15 | 95 | 95 | 1.3266 | 35.6679 | 16.3204 | 159.1871 | 0 | 0 | 0.73927 | 1.2767 | 1.0663 | 0.23122 | 0 | 0 | 0.33205 | 17.2167 | 17.2167 | 17.2167 | 17.2167 | 17.2167 | 17.2167 | 17.2167 | 17.2167 | 35.6679 | 17.2167 | 17.2167 | 17.956 | 18.4934 | 18.283 | 17.4479 | 17.2167 | 17.2167 | 36 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 12 | 7716 | 12.8 | 12.8 | 8.0667 | 7.1625 | 15 | 94 | 94 | 0.33648 | 21.8978 | 18.4691 | 173.8573 | 0 | 0 | 0.11474 | 0.29458 | 0.30185 | 0.13231 | 0 | 0 | 0.1022 | 10.3346 | 10.3346 | 10.3346 | 10.3346 | 10.3346 | 10.3346 | 10.3346 | 10.3346 | 21.8978 | 10.3346 | 10.3346 | 10.4493 | 10.6291 | 10.6364 | 10.4669 | 10.3346 | 10.3346 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 13 | 7717 | 12.7 | 12.7 | 8.0667 | 7.1625 | 15 | 95 | 95 | 0.39443 | 24.8743 | 18.2571 | 188.7784 | 0 | 0 | 0.040032 | 0.29132 | 0.37196 | 0.23471 | 0 | 0 | 0.12573 | 11.7603 | 11.7603 | 11.7603 | 11.7603 | 11.7603 | 11.7603 | 11.7603 | 11.7603 | 24.8743 | 11.7603 | 11.7603 | 11.8004 | 12.0516 | 12.1323 | 11.995 | 11.7603 | 11.7603 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 14 | 7718 | 12.5 | 12.5 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0.4623 | 24.8639 | 15.7065 | 203.3454 | 0 | 0 | 0 | 0.25943 | 0.43388 | 0.35418 | 0.067001 | 0 | 0.13612 | 11.7574 | 11.7574 | 11.7574 | 11.7574 | 11.7574 | 11.7574 | 11.7574 | 11.7574 | 24.8639 | 11.7574 | 11.7574 | 11.7574 | 12.0168 | 12.1912 | 12.1115 | 11.8244 | 11.7574 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 15 | 7719 | 12.6 | 12.6 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0.34317 | 16.9202 | 11.0683 | 217.1029 | 0 | 0 | 0 | 0.1219 | 0.30331 | 0.30704 | 0.13091 | 0 | 0.079751 | 7.9488 | 7.9488 | 7.9488 | 7.9488 | 7.9488 | 7.9488 | 7.9488 | 7.9488 | 16.9202 | 7.9488 | 7.9488 | 7.9488 | 8.0707 | 8.2521 | 8.2558 | 8.0797 | 7.9488 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 16 | 7720 | 12.7 | 12.7 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0.12327 | 5.9831 | 4.7299 | 229.8924 | 0 | 0 | 0 | 0.016622 | 0.096485 | 0.11983 | 0.072979 | 0 | 0.01687 | 2.7764 | 2.7764 | 2.7764 | 2.7764 | 2.7764 | 2.7764 | 2.7764 | 2.7764 | 5.9831 | 2.7764 | 2.7764 | 2.7764 | 2.793 | 2.8729 | 2.8962 | 2.8493 | 2.7764 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 17 | 7721 | 12.5 | 12.5 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -2.8885 | 241.8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 18 | 7722 | 12.4 | 12.4 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -11.3919 | 253.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 19 | 7723 | 12.2 | 12.2 | 8.0667 | 7.1625 | 15 | 97 | 97 | 0 | 0 | -20.4196 | 264.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 20 | 7724 | 12.1 | 12.1 | 8.0667 | 7.1625 | 15 | 96 | 96 | 0 | 0 | -29.617 | 276.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 21 | 7725 | 12.1 | 12.1 | 8.0667 | 7.1625 | 15 | 93 | 93 | 0 | 0 | -38.575 | 289.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 22 | 7726 | 11.7 | 11.7 | 8.0667 | 7.1625 | 15 | 92 | 92 | 0 | 0 | -46.7267 | 305.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 23 | 7727 | 11.9 | 11.9 | 8.0667 | 7.1625 | 15 | 92 | 92 | 0 | 0 | -53.2005 | 325.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 18 | 24 | 7728 | 12 | 12 | 11.6583 | 8.5386 | 15 | 92 | 92 | 0 | 0 | -56.7747 | 349.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 1 | 7729 | 12.1 | 12.1 | 11.6583 | 8.5386 | 15 | 92 | 92 | 0 | 0 | -56.4091 | 15.1862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 2 | 7730 | 12.1 | 12.1 | 11.6583 | 8.5386 | 15 | 93 | 93 | 0 | 0 | -52.4637 | 38.5952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 3 | 7731 | 11.9 | 11.9 | 11.6583 | 8.5386 | 15 | 95 | 95 | 0 | 0 | -45.6006 | 57.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 4 | 7732 | 11.8 | 11.8 | 11.6583 | 8.5386 | 15 | 96 | 96 | 0 | 0 | -37.2447 | 72.8292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 5 | 7733 | 11.9 | 11.9 | 11.6583 | 8.5386 | 15 | 94 | 94 | 0 | 0 | -28.2054 | 85.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 6 | 7734 | 11.7 | 11.7 | 11.6583 | 8.5386 | 15 | 95 | 95 | 0 | 0 | -19.0114 | 97.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 7 | 7735 | 11.8 | 11.8 | 11.6583 | 8.5386 | 15 | 94 | 94 | 0 | 0 | -10.0552 | 108.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 19 | 8 | 7736 | 11.9 | 11.9 | 11.6583 | 8.5386 | 15 | 94 | 94 | 0 | 0 | -1.688 | 120.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 9 | 7737 | 12 | 12 | 11.6583 | 8.5386 | 15 | 93 | 93 | 0.32929 | 2.9862 | 5.7261 | 132.3729 | 0 | 0.083422 | 0.28413 | 0.3184 | 0.16616 | 0 | 0 | 0 | 0.013784 | 1.4064 | 1.5857 | 2.0173 | 2.091 | 1.7636 | 1.4064 | 1.4064 | 1.4064 | 2.9862 | 1.4064 | 1.6692 | 2.3014 | 2.4094 | 1.9298 | 1.4064 | 1.4064 | 1.4064 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 10 | 7738 | 12.3 | 12.3 | 11.6583 | 8.5386 | 15 | 93 | 93 | 0.50006 | 13.9207 | 11.7876 | 145.3037 | 0 | 0.022806 | 0.36759 | 0.49704 | 0.33534 | 0 | 0 | 0 | 0.079267 | 6.618 | 6.618 | 6.618 | 6.618 | 6.618 | 6.618 | 6.618 | 6.618 | 13.9207 | 6.618 | 6.6408 | 6.9856 | 7.115 | 6.9533 | 6.618 | 6.618 | 6.618 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 11 | 7739 | 12.5 | 12.5 | 11.6583 | 8.5386 | 15 | 92 | 92 | 1.1488 | 32.7168 | 16.0787 | 159.1893 | 0 | 0 | 0.64015 | 1.1065 | 0.92462 | 0.20115 | 0 | 0 | 0.2832 | 15.7413 | 15.7413 | 15.7413 | 15.7413 | 15.7413 | 15.7413 | 15.7413 | 15.7413 | 32.7168 | 15.7413 | 15.7413 | 16.3814 | 16.8477 | 16.6659 | 15.9424 | 15.7413 | 15.7413 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 12 | 7740 | 12.7 | 12.7 | 11.6583 | 8.5386 | 15 | 91 | 91 | 2.2359 | 55.3295 | 18.2303 | 173.8181 | 0 | 0 | 0.76332 | 1.9598 | 2.0083 | 0.88035 | 0 | 0 | 0.67046 | 27.006 | 27.006 | 27.006 | 27.006 | 27.006 | 27.006 | 27.006 | 27.006 | 55.3295 | 27.006 | 27.006 | 27.7693 | 28.9658 | 29.0143 | 27.8863 | 27.006 | 27.006 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 13 | 7741 | 13 | 13 | 11.6583 | 8.5386 | 15 | 89 | 89 | 5.1211 | 87.3874 | 18.0279 | 188.6975 | 0 | 0 | 0.52379 | 3.7898 | 4.8358 | 3.049 | 0 | 0 | 1.6126 | 43.1915 | 43.1915 | 43.4983 | 45.4117 | 46.0245 | 44.9778 | 43.1915 | 43.1915 | 87.3874 | 43.1915 | 43.1915 | 44.0221 | 49.2015 | 50.8603 | 48.0268 | 43.1915 | 43.1915 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 14 | 7742 | 13.3 | 13.3 | 11.6583 | 8.5386 | 15 | 89 | 89 | 5.2297 | 81.4803 | 15.4926 | 203.2284 | 0 | 0 | 0 | 2.9443 | 4.9158 | 4.0077 | 0.752 | 0 | 1.5197 | 40.5385 | 40.5385 | 40.5385 | 40.5385 | 40.5385 | 40.5385 | 40.5385 | 40.5385 | 81.4803 | 40.5385 | 40.5385 | 40.5385 | 43.4828 | 45.4543 | 44.5463 | 41.2905 | 40.5385 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 15 | 7743 | 13.1 | 13.1 | 11.6583 | 8.5386 | 15 | 89 | 89 | 0.9615 | 27.7802 | 10.8727 | 216.9583 | 0 | 0 | 0 | 0.34367 | 0.85145 | 0.86047 | 0.36543 | 0 | 0.21983 | 13.2038 | 13.2038 | 13.2038 | 13.2038 | 13.2038 | 13.2038 | 13.2038 | 13.2038 | 27.7802 | 13.2038 | 13.2038 | 13.2038 | 13.5474 | 14.0552 | 14.0642 | 13.5692 | 13.2038 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 16 | 7744 | 13.1 | 13.1 | 11.6583 | 8.5386 | 15 | 88 | 88 | 0.13002 | 5.9827 | 4.5522 | 229.728 | 0 | 0 | 0 | 0.017863 | 0.10203 | 0.12643 | 0.076769 | 0 | 0.017322 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 2.7762 | 5.9827 | 2.7762 | 2.7762 | 2.7762 | 2.7941 | 2.8782 | 2.9026 | 2.853 | 2.7762 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 17 | 7745 | 12.8 | 12.8 | 11.6583 | 8.5386 | 15 | 89 | 89 | 0 | 0 | -3.0507 | 241.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 19 | 18 | 7746 | 12.7 | 12.7 | 11.6583 | 8.5386 | 15 | 90 | 90 | 0 | 0 | -11.5426 | 253.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 19 | 7747 | 12.6 | 12.6 | 11.6583 | 8.5386 | 15 | 91 | 91 | 0 | 0 | -20.5642 | 264.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 20 | 7748 | 12.4 | 12.4 | 11.6583 | 8.5386 | 15 | 92 | 92 | 0 | 0 | -29.7619 | 276.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 21 | 7749 | 12.2 | 12.2 | 11.6583 | 8.5386 | 15 | 93 | 93 | 0 | 0 | -38.7281 | 289.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 22 | 7750 | 12 | 12 | 11.6583 | 8.5386 | 15 | 94 | 94 | 0 | 0 | -46.8979 | 305.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 23 | 7751 | 12 | 12 | 11.6583 | 8.5386 | 15 | 94 | 94 | 0 | 0 | -53.3993 | 325.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 19 | 24 | 7752 | 12 | 12 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0 | 0 | -57.0021 | 349.1753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 1 | 7753 | 11.9 | 11.9 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0 | 0 | -56.6505 | 15.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 2 | 7754 | 11.7 | 11.7 | 12.3292 | 9.6889 | 15 | 95 | 95 | 0 | 0 | -52.6967 | 38.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 3 | 7755 | 11.4 | 11.4 | 12.3292 | 9.6889 | 15 | 97 | 97 | 0 | 0 | -45.8237 | 57.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 4 | 7756 | 11.2 | 11.2 | 12.3292 | 9.6889 | 15 | 97 | 97 | 0 | 0 | -37.4598 | 72.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 5 | 7757 | 11.1 | 11.1 | 12.3292 | 9.6889 | 15 | 95 | 95 | 0 | 0 | -28.4169 | 85.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 6 | 7758 | 10.9 | 10.9 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0 | 0 | -19.2234 | 97.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 7 | 7759 | 11 | 11 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0 | 0 | -10.271 | 108.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 20 | 8 | 7760 | 11.1 | 11.1 | 12.3292 | 9.6889 | 15 | 92 | 92 | 0 | 0 | -1.9099 | 120.4009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 9 | 7761 | 11 | 11 | 12.3292 | 9.6889 | 15 | 92 | 92 | 0 | 0 | 5.4974 | 132.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 10 | 7762 | 10.7 | 10.7 | 12.3292 | 9.6889 | 15 | 92 | 92 | 0.096098 | 5.9851 | 11.5532 | 145.3369 | 0 | 0.0042824 | 0.0706 | 0.09556 | 0.064543 | 0 | 0 | 0 | 0.01489 | 2.7873 | 2.7873 | 2.7873 | 2.7873 | 2.7873 | 2.7873 | 2.7873 | 2.7873 | 5.9851 | 2.7873 | 2.7916 | 2.8579 | 2.8828 | 2.8518 | 2.7873 | 2.7873 | 2.7873 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 11 | 7763 | 10.3 | 10.3 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0.13152 | 10.9681 | 15.842 | 159.1872 | 0 | 0 | 0.073285 | 0.12676 | 0.10598 | 0.023121 | 0 | 0 | 0.031934 | 5.1241 | 5.1241 | 5.1241 | 5.1241 | 5.1241 | 5.1241 | 5.1241 | 5.1241 | 10.9681 | 5.1241 | 5.1241 | 5.1973 | 5.2508 | 5.23 | 5.1472 | 5.1241 | 5.1241 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 12 | 7764 | 9.8 | 9.8 | 12.3292 | 9.6889 | 15 | 95 | 95 | 0.35382 | 21.8952 | 17.9971 | 173.7755 | 0 | 0 | 0.12094 | 0.3105 | 0.31817 | 0.13946 | 0 | 0 | 0.10476 | 10.3362 | 10.3362 | 10.3362 | 10.3362 | 10.3362 | 10.3362 | 10.3362 | 10.3362 | 21.8952 | 10.3362 | 10.3362 | 10.4572 | 10.6467 | 10.6544 | 10.4757 | 10.3362 | 10.3362 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 13 | 7765 | 9.5 | 9.5 | 12.3292 | 9.6889 | 15 | 94 | 94 | 0.63634 | 30.802 | 17.8048 | 188.6144 | 0 | 0 | 0.065618 | 0.47182 | 0.60163 | 0.37902 | 0 | 0 | 0.19796 | 14.645 | 14.645 | 14.645 | 14.645 | 14.645 | 14.645 | 14.645 | 14.645 | 30.802 | 14.645 | 14.645 | 14.7106 | 15.1168 | 15.2466 | 15.024 | 14.645 | 14.645 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 14 | 7766 | 9.8 | 9.8 | 12.3292 | 9.6889 | 15 | 86 | 86 | 0.48682 | 24.8604 | 15.2851 | 203.1104 | 0 | 0 | 0 | 0.27496 | 0.45827 | 0.37314 | 0.069425 | 0 | 0.13964 | 11.7582 | 11.7582 | 11.7582 | 11.7582 | 11.7582 | 11.7582 | 11.7582 | 11.7582 | 24.8604 | 11.7582 | 11.7582 | 11.7582 | 12.0331 | 12.2164 | 12.1313 | 11.8276 | 11.7582 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 15 | 7767 | 10.1 | 10.1 | 12.3292 | 9.6889 | 15 | 85 | 85 | 3.5571 | 52.1998 | 10.6834 | 216.8136 | 0 | 0 | 0 | 1.2792 | 3.1559 | 3.1839 | 1.3468 | 0 | 0.8002 | 25.468 | 25.468 | 25.468 | 25.468 | 25.468 | 25.468 | 25.468 | 25.468 | 52.1998 | 25.468 | 25.468 | 25.468 | 26.7472 | 28.6239 | 28.6519 | 26.8148 | 25.468 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 16 | 7768 | 9.8 | 9.8 | 12.3292 | 9.6889 | 15 | 90 | 90 | 1.844 | 21.7608 | 4.381 | 229.564 | 0 | 0 | 0 | 0.25803 | 1.4507 | 1.7936 | 1.0858 | 0 | 0.23916 | 10.3484 | 10.3484 | 10.3484 | 10.3484 | 10.3484 | 10.3484 | 10.3484 | 10.3484 | 21.7608 | 10.3484 | 10.3484 | 10.3484 | 10.6064 | 11.7991 | 12.142 | 11.4342 | 10.3484 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 17 | 7769 | 9.9 | 9.9 | 12.3292 | 9.6889 | 15 | 90 | 90 | 0 | 0 | -3.2064 | 241.4793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 20 | 18 | 7770 | 9.9 | 9.9 | 12.3292 | 9.6889 | 15 | 91 | 91 | 0 | 0 | -11.6869 | 252.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 19 | 7771 | 9.6 | 9.6 | 12.3292 | 9.6889 | 15 | 90 | 90 | 0 | 0 | -20.7022 | 264.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 20 | 7772 | 9.2 | 9.2 | 12.3292 | 9.6889 | 15 | 92 | 92 | 0 | 0 | -29.9001 | 276.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 21 | 7773 | 9 | 9 | 12.3292 | 9.6889 | 15 | 92 | 92 | 0 | 0 | -38.8745 | 289.3248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 22 | 7774 | 8.9 | 8.9 | 12.3292 | 9.6889 | 15 | 90 | 90 | 0 | 0 | -47.0622 | 305.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 23 | 7775 | 8.7 | 8.7 | 12.3292 | 9.6889 | 15 | 90 | 90 | 0 | 0 | -53.5911 | 324.8375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 20 | 24 | 7776 | 8.6 | 8.6 | 10.2125 | 9.8416 | 15 | 92 | 92 | 0 | 0 | -57.2231 | 349.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 1 | 7777 | 8.5 | 8.5 | 10.2125 | 9.8416 | 15 | 91 | 91 | 0 | 0 | -56.8866 | 15.1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 2 | 7778 | 8.3 | 8.3 | 10.2125 | 9.8416 | 15 | 92 | 92 | 0 | 0 | -52.9253 | 38.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 3 | 7779 | 8.5 | 8.5 | 10.2125 | 9.8416 | 15 | 92 | 92 | 0 | 0 | -46.0432 | 57.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 4 | 7780 | 8.5 | 8.5 | 10.2125 | 9.8416 | 15 | 93 | 93 | 0 | 0 | -37.6718 | 73.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 5 | 7781 | 8.7 | 8.7 | 10.2125 | 9.8416 | 15 | 92 | 92 | 0 | 0 | -28.6255 | 86.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 6 | 7782 | 8.3 | 8.3 | 10.2125 | 9.8416 | 15 | 92 | 92 | 0 | 0 | -19.4326 | 97.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 7 | 7783 | 7.9 | 7.9 | 10.2125 | 9.8416 | 15 | 93 | 93 | 0 | 0 | -10.4839 | 109.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 21 | 8 | 7784 | 7.7 | 7.7 | 10.2125 | 9.8416 | 15 | 93 | 93 | 0 | 0 | -2.1284 | 120.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 9 | 7785 | 7.9 | 7.9 | 10.2125 | 9.8416 | 15 | 95 | 95 | 0.46708 | 2.9836 | 5.2725 | 132.4898 | 0 | 0.11704 | 0.40227 | 0.45185 | 0.23674 | 0 | 0 | 0 | 0.01641 | 1.4054 | 1.5827 | 2.0146 | 2.0897 | 1.7639 | 1.4054 | 1.4054 | 1.4054 | 2.9836 | 1.4054 | 1.6997 | 2.4169 | 2.5416 | 2.0007 | 1.4054 | 1.4054 | 1.4054 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 10 | 7786 | 8.3 | 8.3 | 10.2125 | 9.8416 | 15 | 92 | 92 | 3.0411 | 32.5394 | 11.3233 | 145.3651 | 0 | 0.13263 | 2.233 | 3.0253 | 2.0455 | 0 | 0 | 0 | 0.4606 | 15.5229 | 16.2761 | 28.2055 | 32.7056 | 27.1402 | 15.5229 | 15.5229 | 15.5229 | 32.5394 | 15.5229 | 16.4088 | 30.4385 | 35.7309 | 29.1857 | 15.5229 | 15.5229 | 15.5229 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 11 | 7787 | 8.7 | 8.7 | 10.2125 | 9.8416 | 15 | 91 | 91 | 3.7661 | 57.0991 | 15.6105 | 159.1809 | 0 | 0 | 2.0988 | 3.6326 | 3.0384 | 0.66442 | 0 | 0 | 0.90089 | 27.9765 | 27.9765 | 30.6153 | 32.5437 | 31.7967 | 28.8119 | 27.9765 | 27.9765 | 57.0991 | 27.9765 | 27.9765 | 32.7141 | 36.1762 | 34.8351 | 29.4763 | 27.9765 | 27.9765 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 12 | 7788 | 9.5 | 9.5 | 10.2125 | 9.8416 | 15 | 89 | 89 | 8.4168 | 97.539 | 17.7696 | 173.7297 | 0 | 0 | 2.8811 | 7.395 | 7.577 | 3.3205 | 0 | 0 | 2.461 | 46.1557 | 46.1557 | 55.2554 | 69.512 | 70.0868 | 56.6431 | 46.1557 | 46.1557 | 97.539 | 46.1557 | 46.1557 | 58.1365 | 76.9071 | 77.6638 | 59.9636 | 46.1557 | 46.1557 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 13 | 7789 | 9.8 | 9.8 | 10.2125 | 9.8416 | 15 | 88 | 88 | 4.6705 | 81.5643 | 17.5879 | 188.5292 | 0 | 0 | 0.48577 | 3.4697 | 4.4211 | 2.7827 | 0 | 0 | 1.4357 | 40.5544 | 40.5544 | 40.5879 | 40.7934 | 40.8589 | 40.7461 | 40.5544 | 40.5544 | 81.5643 | 40.5544 | 40.5544 | 41.0736 | 44.263 | 45.28 | 43.5287 | 40.5544 | 40.5544 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 14 | 7790 | 10.6 | 10.6 | 10.2125 | 9.8416 | 15 | 87 | 87 | 9.5239 | 97.3031 | 15.084 | 202.9914 | 0 | 0 | 0 | 5.3965 | 8.9783 | 7.3007 | 1.3465 | 0 | 2.6969 | 47.1112 | 47.1112 | 47.1112 | 54.976 | 60.1961 | 57.7512 | 49.0736 | 47.1112 | 97.3031 | 47.1112 | 47.1112 | 47.1112 | 60.3725 | 69.1744 | 65.052 | 50.4201 | 47.1112 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 15 | 7791 | 10.8 | 10.8 | 10.2125 | 9.8416 | 15 | 86 | 86 | 9.4365 | 75.911 | 10.5007 | 216.6688 | 0 | 0 | 0 | 3.4144 | 8.3876 | 8.4474 | 3.5588 | 0 | 2.089 | 37.3028 | 37.3028 | 37.3028 | 39.3116 | 42.2375 | 42.2727 | 39.3966 | 37.3028 | 75.911 | 37.3028 | 37.3028 | 37.3028 | 42.7261 | 50.6251 | 50.7201 | 42.9554 | 37.3028 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 16 | 7792 | 10.5 | 10.5 | 10.2125 | 9.8416 | 15 | 87 | 87 | 3.8626 | 30.5124 | 4.2163 | 229.4007 | 0 | 0 | 0 | 0.5503 | 3.0463 | 3.7579 | 2.2681 | 0 | 0.48764 | 14.7148 | 14.7148 | 14.7148 | 14.7148 | 14.7148 | 14.7148 | 14.7148 | 14.7148 | 30.5124 | 14.7148 | 14.7148 | 14.7148 | 15.2651 | 17.7612 | 18.4727 | 16.9829 | 14.7148 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 17 | 7793 | 10.2 | 10.2 | 10.2125 | 9.8416 | 15 | 89 | 89 | 3.9725 | 0.99 | -3.3556 | 241.3019 | 0 | 0 | 0 | 0 | 2.5782 | 3.9501 | 3.0081 | 0.30399 | 5.01 | 1.0708 | 1.0708 | 1.0708 | 1.0708 | 3.2958 | 4.4797 | 3.6668 | 1.3331 | 0.99 | 1.0708 | 1.0708 | 1.0708 | 1.0708 | 5.8739 | 8.4298 | 6.6749 | 1.6371 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 21 | 18 | 7794 | 10.3 | 10.3 | 10.2125 | 9.8416 | 15 | 89 | 89 | 0 | 0 | -11.8247 | 252.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 19 | 7795 | 10.6 | 10.6 | 10.2125 | 9.8416 | 15 | 87 | 87 | 0 | 0 | -20.8337 | 263.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 20 | 7796 | 10.2 | 10.2 | 10.2125 | 9.8416 | 15 | 90 | 90 | 0 | 0 | -30.0315 | 275.8559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 21 | 7797 | 10 | 10 | 10.2125 | 9.8416 | 15 | 90 | 90 | 0 | 0 | -39.0139 | 289.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 22 | 7798 | 9.8 | 9.8 | 10.2125 | 9.8416 | 15 | 90 | 90 | 0 | 0 | -47.2194 | 304.8646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 23 | 7799 | 9.8 | 9.8 | 10.2125 | 9.8416 | 15 | 90 | 90 | 0 | 0 | -53.7759 | 324.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 21 | 24 | 7800 | 9.1 | 9.1 | 9.2708 | 9.819 | 15 | 93 | 93 | 0 | 0 | -57.4376 | 348.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 1 | 7801 | 9.1 | 9.1 | 9.2708 | 9.819 | 15 | 94 | 94 | 0 | 0 | -57.1173 | 15.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 2 | 7802 | 9.4 | 9.4 | 9.2708 | 9.819 | 15 | 93 | 93 | 0 | 0 | -53.1495 | 38.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 3 | 7803 | 9.6 | 9.6 | 9.2708 | 9.819 | 15 | 94 | 94 | 0 | 0 | -46.2591 | 57.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 4 | 7804 | 9.3 | 9.3 | 9.2708 | 9.819 | 15 | 95 | 95 | 0 | 0 | -37.8807 | 73.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 5 | 7805 | 9.5 | 9.5 | 9.2708 | 9.819 | 15 | 95 | 95 | 0 | 0 | -28.8313 | 86.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 6 | 7806 | 9.5 | 9.5 | 9.2708 | 9.819 | 15 | 95 | 95 | 0 | 0 | -19.6389 | 97.8504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 7 | 7807 | 9.4 | 9.4 | 9.2708 | 9.819 | 15 | 95 | 95 | 0 | 0 | -10.6937 | 109.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 22 | 8 | 7808 | 9.2 | 9.2 | 9.2708 | 9.819 | 15 | 95 | 95 | 0 | 0 | -2.3435 | 120.5487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 9 | 7809 | 9.4 | 9.4 | 9.2708 | 9.819 | 15 | 96 | 96 | 0 | 0 | 5.0517 | 132.5402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 10 | 7810 | 9.7 | 9.7 | 9.2708 | 9.819 | 15 | 97 | 97 | 0.84414 | 16.875 | 11.0979 | 145.3885 | 0 | 0.036088 | 0.61955 | 0.84008 | 0.56851 | 0 | 0 | 0 | 0.12499 | 8.1206 | 8.1206 | 8.1206 | 8.1206 | 8.1206 | 8.1206 | 8.1206 | 8.1206 | 16.875 | 8.1206 | 8.1567 | 8.7402 | 8.9607 | 8.6892 | 8.1206 | 8.1206 | 8.1206 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 11 | 7811 | 10.8 | 10.8 | 9.2708 | 9.819 | 15 | 95 | 95 | 4.2894 | 59.989 | 15.3842 | 159.1703 | 0 | 0 | 2.3908 | 4.1402 | 3.4642 | 0.759 | 0 | 0 | 1.011 | 29.0835 | 29.0835 | 34.61 | 38.6535 | 37.0911 | 30.838 | 29.0835 | 29.0835 | 59.989 | 29.0835 | 29.0835 | 37.0008 | 42.7937 | 40.5553 | 31.597 | 29.0835 | 29.0835 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 12 | 7812 | 11.2 | 11.2 | 9.2708 | 9.819 | 15 | 96 | 96 | 2.5827 | 57.2541 | 17.548 | 173.6807 | 0 | 0 | 0.88547 | 2.2718 | 2.3274 | 1.0196 | 0 | 0 | 0.74591 | 28.0512 | 28.0512 | 28.0512 | 28.0512 | 28.0512 | 28.0512 | 28.0512 | 28.0512 | 57.2541 | 28.0512 | 28.0512 | 28.9366 | 30.323 | 30.3785 | 29.0707 | 28.0512 | 28.0512 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 13 | 7813 | 12.3 | 12.3 | 9.2708 | 9.819 | 15 | 91 | 91 | 7.3757 | 97.7594 | 17.3772 | 188.442 | 0 | 0 | 0.77405 | 5.4898 | 6.9897 | 4.3951 | 0 | 0 | 2.2406 | 47.2317 | 47.2317 | 48.7529 | 58.0207 | 60.9685 | 55.8694 | 47.2317 | 47.2317 | 97.7594 | 47.2317 | 47.2317 | 49.527 | 63.5106 | 67.9582 | 60.2645 | 47.2317 | 47.2317 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 14 | 7814 | 13.5 | 13.5 | 9.2708 | 9.819 | 15 | 86 | 86 | 135.8929 | 134.0052 | 14.8894 | 202.8714 | 0 | 0 | 0 | 77.2484 | 128.2854 | 104.1746 | 19.0397 | 0 | 37.9948 | 66.2965 | 66.2965 | 66.2965 | 125.6014 | 164.7834 | 146.2731 | 80.9136 | 66.2965 | 134.0052 | 66.2965 | 66.2965 | 66.2965 | 202.8498 | 293.0688 | 250.4477 | 99.9533 | 66.2965 | 172 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 15 | 7815 | 13.8 | 13.8 | 9.2708 | 9.819 | 15 | 84 | 84 | 72.3438 | 101.2369 | 10.3246 | 216.5241 | 0 | 0 | 0 | 26.3359 | 64.418 | 64.7649 | 27.1734 | 0 | 15.7631 | 49.4309 | 49.4309 | 49.4309 | 70.0949 | 99.9754 | 100.2476 | 70.752 | 49.4309 | 101.2369 | 49.4309 | 49.4309 | 49.4309 | 96.4308 | 164.3934 | 165.0124 | 97.9254 | 49.4309 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 16 | 7816 | 13.7 | 13.7 | 9.2708 | 9.819 | 15 | 84 | 84 | 10.0646 | 42.7632 | 4.0582 | 229.2381 | 0 | 0 | 0 | 1.4594 | 7.957 | 9.7935 | 5.8931 | 0 | 1.2368 | 21.0566 | 21.0566 | 21.0566 | 21.0566 | 21.0566 | 21.0566 | 21.0566 | 21.0566 | 42.7632 | 21.0566 | 21.0566 | 21.0566 | 22.516 | 29.0136 | 30.8501 | 26.9497 | 21.0566 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 17 | 7817 | 13.6 | 13.6 | 9.2708 | 9.819 | 15 | 84 | 84 | 1.9064 | 0.495 | -3.4982 | 241.1256 | 0 | 0 | 0 | 0 | 1.2416 | 1.8964 | 1.4403 | 0.14053 | 2.505 | 0.53602 | 0.53602 | 0.53602 | 0.53602 | 1.6545 | 2.2443 | 1.8335 | 0.66261 | 0.495 | 0.53602 | 0.53602 | 0.53602 | 0.53602 | 2.896 | 4.1407 | 3.2738 | 0.80314 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 22 | 18 | 7818 | 13.7 | 13.7 | 9.2708 | 9.819 | 15 | 82 | 82 | 0 | 0 | -11.9558 | 252.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 19 | 7819 | 13.4 | 13.4 | 9.2708 | 9.819 | 15 | 83 | 83 | 0 | 0 | -20.9585 | 263.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 20 | 7820 | 13.5 | 13.5 | 9.2708 | 9.819 | 15 | 81 | 81 | 0 | 0 | -30.1562 | 275.6374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 21 | 7821 | 13.4 | 13.4 | 9.2708 | 9.819 | 15 | 81 | 81 | 0 | 0 | -39.1463 | 288.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 22 | 7822 | 13.3 | 13.3 | 9.2708 | 9.819 | 15 | 81 | 81 | 0 | 0 | -47.3694 | 304.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 23 | 7823 | 13.4 | 13.4 | 9.2708 | 9.819 | 15 | 80 | 80 | 0 | 0 | -53.9535 | 324.3636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 22 | 24 | 7824 | 13.6 | 13.6 | 11.5542 | 10.3962 | 15 | 79 | 79 | 0 | 0 | -57.6456 | 348.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 1 | 7825 | 13.5 | 13.5 | 11.5542 | 10.3962 | 15 | 80 | 80 | 0 | 0 | -57.3424 | 15.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 2 | 7826 | 13.5 | 13.5 | 11.5542 | 10.3962 | 15 | 79 | 79 | 0 | 0 | -53.3692 | 38.8239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 3 | 7827 | 13.1 | 13.1 | 11.5542 | 10.3962 | 15 | 81 | 81 | 0 | 0 | -46.4713 | 57.9641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 4 | 7828 | 12.9 | 12.9 | 11.5542 | 10.3962 | 15 | 83 | 83 | 0 | 0 | -38.0864 | 73.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 5 | 7829 | 12.4 | 12.4 | 11.5542 | 10.3962 | 15 | 84 | 84 | 0 | 0 | -29.034 | 86.2343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 6 | 7830 | 11.9 | 11.9 | 11.5542 | 10.3962 | 15 | 86 | 86 | 0 | 0 | -19.8423 | 97.9434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 7 | 7831 | 11.5 | 11.5 | 11.5542 | 10.3962 | 15 | 87 | 87 | 0 | 0 | -10.9002 | 109.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 23 | 8 | 7832 | 11.1 | 11.1 | 11.5542 | 10.3962 | 15 | 90 | 90 | 0 | 0 | -2.555 | 120.6141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 9 | 7833 | 11.6 | 11.6 | 11.5542 | 10.3962 | 15 | 95 | 95 | 0 | 0 | 4.8349 | 132.5853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 10 | 7834 | 12 | 12 | 11.5542 | 10.3962 | 15 | 96 | 96 | 1.4783 | 21.786 | 10.8773 | 145.4069 | 0 | 0.062063 | 1.0846 | 1.4717 | 0.99679 | 0 | 0 | 0 | 0.21402 | 10.6552 | 10.6552 | 10.6552 | 10.6552 | 10.6552 | 10.6552 | 10.6552 | 10.6552 | 21.786 | 10.6552 | 10.7172 | 11.7397 | 12.1269 | 11.652 | 10.6552 | 10.6552 | 10.6552 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 11 | 7835 | 12.2 | 12.2 | 11.5542 | 10.3962 | 15 | 94 | 94 | 0.93021 | 27.7839 | 15.1633 | 159.1557 | 0 | 0 | 0.51863 | 0.89847 | 0.752 | 0.16501 | 0 | 0 | 0.21607 | 13.3096 | 13.3096 | 13.3096 | 13.3096 | 13.3096 | 13.3096 | 13.3096 | 13.3096 | 27.7839 | 13.3096 | 13.3096 | 13.8282 | 14.2081 | 14.0616 | 13.4746 | 13.3096 | 13.3096 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 12 | 7836 | 12.9 | 12.9 | 11.5542 | 10.3962 | 15 | 88 | 88 | 1.7371 | 46.5044 | 17.3323 | 173.6286 | 0 | 0 | 0.59658 | 1.5298 | 1.5669 | 0.68609 | 0 | 0 | 0.49562 | 22.545 | 22.545 | 22.545 | 22.545 | 22.545 | 22.545 | 22.545 | 22.545 | 46.5044 | 22.545 | 22.545 | 23.1415 | 24.0747 | 24.1118 | 23.231 | 22.545 | 22.545 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 13 | 7837 | 14.3 | 14.3 | 11.5542 | 10.3962 | 15 | 79 | 79 | 10.2459 | 104.9234 | 17.1729 | 188.3529 | 0 | 0 | 1.0854 | 7.6407 | 9.7202 | 6.1058 | 0 | 0 | 3.0766 | 50.0087 | 50.0087 | 52.4692 | 67.3297 | 72.0438 | 63.8501 | 50.0087 | 50.0087 | 104.9234 | 50.0087 | 50.0087 | 53.5546 | 74.9705 | 81.7641 | 69.9558 | 50.0087 | 50.0087 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 14 | 7838 | 14.1 | 14.1 | 11.5542 | 10.3962 | 15 | 82 | 82 | 4.7231 | 73.6959 | 14.7013 | 202.7507 | 0 | 0 | 0 | 2.6935 | 4.4647 | 3.6205 | 0.65553 | 0 | 1.3041 | 36.5043 | 36.5043 | 36.5043 | 36.5043 | 36.5043 | 36.5043 | 36.5043 | 36.5043 | 73.6959 | 36.5043 | 36.5043 | 36.5043 | 39.1977 | 40.9689 | 40.1248 | 37.1598 | 36.5043 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 15 | 7839 | 14.2 | 14.2 | 11.5542 | 10.3962 | 15 | 79 | 79 | 5.1772 | 59.8895 | 10.1551 | 216.3794 | 0 | 0 | 0 | 1.8961 | 4.6181 | 4.6349 | 1.9366 | 0 | 1.1105 | 29.5129 | 29.5129 | 29.5129 | 29.5129 | 29.5129 | 29.5129 | 29.5129 | 29.5129 | 59.8895 | 29.5129 | 29.5129 | 29.5129 | 31.409 | 34.131 | 34.1478 | 31.4495 | 29.5129 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 16 | 7840 | 13.3 | 13.3 | 11.5542 | 10.3962 | 15 | 88 | 88 | 0.87675 | 13.8951 | 3.9068 | 229.0763 | 0 | 0 | 0 | 0.12936 | 0.69482 | 0.85326 | 0.51188 | 0 | 0.10488 | 6.5328 | 6.5328 | 6.5328 | 6.5328 | 6.5328 | 6.5328 | 6.5328 | 6.5328 | 13.8951 | 6.5328 | 6.5328 | 6.5328 | 6.6622 | 7.2276 | 7.3861 | 7.0447 | 6.5328 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 17 | 7841 | 12.4 | 12.4 | 11.5542 | 10.3962 | 15 | 94 | 94 | 0 | 0 | -3.6342 | 240.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 23 | 18 | 7842 | 12.3 | 12.3 | 11.5542 | 10.3962 | 15 | 95 | 95 | 0 | 0 | -12.0804 | 252.3078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 19 | 7843 | 11.4 | 11.4 | 11.5542 | 10.3962 | 15 | 95 | 95 | 0 | 0 | -21.0766 | 263.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 20 | 7844 | 11.3 | 11.3 | 11.5542 | 10.3962 | 15 | 95 | 95 | 0 | 0 | -30.2742 | 275.4206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 21 | 7845 | 10.9 | 10.9 | 11.5542 | 10.3962 | 15 | 95 | 95 | 0 | 0 | -39.2719 | 288.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 22 | 7846 | 9.6 | 9.6 | 11.5542 | 10.3962 | 15 | 97 | 97 | 0 | 0 | -47.5123 | 304.3645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 23 | 7847 | 9.8 | 9.8 | 11.5542 | 10.3962 | 15 | 97 | 97 | 0 | 0 | -54.124 | 324.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 23 | 24 | 7848 | 9.7 | 9.7 | 12.1625 | 11.0834 | 15 | 96 | 96 | 0 | 0 | -57.8469 | 348.5183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 1 | 7849 | 9.5 | 9.5 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -57.562 | 14.9962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 2 | 7850 | 9.8 | 9.8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -53.5842 | 38.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 3 | 7851 | 9.8 | 9.8 | 12.1625 | 11.0834 | 15 | 98 | 98 | 0 | 0 | -46.6796 | 58.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 4 | 7852 | 9.8 | 9.8 | 12.1625 | 11.0834 | 15 | 99 | 99 | 0 | 0 | -38.2888 | 73.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 5 | 7853 | 9.8 | 9.8 | 12.1625 | 11.0834 | 15 | 99 | 99 | 0 | 0 | -29.2337 | 86.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 6 | 7854 | 10 | 10 | 12.1625 | 11.0834 | 15 | 99 | 99 | 0 | 0 | -20.0425 | 98.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 7 | 7855 | 9.3 | 9.3 | 12.1625 | 11.0834 | 15 | 98 | 98 | 0 | 0 | -11.1035 | 109.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 24 | 8 | 7856 | 8.4 | 8.4 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -2.7628 | 120.6739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 9 | 7857 | 8 | 8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | 4.6224 | 132.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 10 | 7858 | 7.9 | 7.9 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0.38635 | 10.9453 | 10.6615 | 145.4205 | 0 | 0.015958 | 0.28335 | 0.38476 | 0.26078 | 0 | 0 | 0 | 0.054696 | 5.1882 | 5.1882 | 5.1882 | 5.1882 | 5.1882 | 5.1882 | 5.1882 | 5.1882 | 10.9453 | 5.1882 | 5.2042 | 5.4716 | 5.573 | 5.449 | 5.1882 | 5.1882 | 5.1882 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 11 | 7859 | 7.8 | 7.8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0.44068 | 18.8991 | 14.9479 | 159.1369 | 0 | 0 | 0.24579 | 0.42593 | 0.35657 | 0.07833 | 0 | 0 | 0.1009 | 8.9401 | 8.9401 | 8.9401 | 8.9401 | 8.9401 | 8.9401 | 8.9401 | 8.9401 | 18.8991 | 8.9401 | 8.9401 | 9.1859 | 9.3661 | 9.2967 | 9.0185 | 8.9401 | 8.9401 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 12 | 7860 | 7.4 | 7.4 | 12.1625 | 11.0834 | 15 | 95 | 95 | 0.6312 | 27.822 | 17.1226 | 173.5734 | 0 | 0 | 0.21719 | 0.55652 | 0.56986 | 0.24938 | 0 | 0 | 0.17796 | 13.2271 | 13.2271 | 13.2271 | 13.2271 | 13.2271 | 13.2271 | 13.2271 | 13.2271 | 27.822 | 13.2271 | 13.2271 | 13.4443 | 13.7837 | 13.797 | 13.4765 | 13.2271 | 13.2271 | 28 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 13 | 7861 | 7.5 | 7.5 | 12.1625 | 11.0834 | 15 | 95 | 95 | 0.69782 | 30.7928 | 16.975 | 188.2618 | 0 | 0 | 0.074646 | 0.52139 | 0.6627 | 0.41582 | 0 | 0 | 0.20716 | 14.651 | 14.651 | 14.651 | 14.651 | 14.651 | 14.651 | 14.651 | 14.651 | 30.7928 | 14.651 | 14.651 | 14.7256 | 15.1723 | 15.3137 | 15.0668 | 14.651 | 14.651 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 14 | 7862 | 7.3 | 7.3 | 12.1625 | 11.0834 | 15 | 96 | 96 | 0.31056 | 18.9153 | 14.5199 | 202.6291 | 0 | 0 | 0 | 0.17767 | 0.29395 | 0.23804 | 0.042683 | 0 | 0.084704 | 8.8989 | 8.8989 | 8.8989 | 8.8989 | 8.8989 | 8.8989 | 8.8989 | 8.8989 | 18.9153 | 8.8989 | 8.8989 | 8.8989 | 9.0766 | 9.1928 | 9.1369 | 8.9416 | 8.8989 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 15 | 7863 | 7.2 | 7.2 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0.17359 | 10.9633 | 9.9923 | 216.2349 | 0 | 0 | 0 | 0.063957 | 0.15511 | 0.1554 | 0.064657 | 0 | 0.036663 | 5.1181 | 5.1181 | 5.1181 | 5.1181 | 5.1181 | 5.1181 | 5.1181 | 5.1181 | 10.9633 | 5.1181 | 5.1181 | 5.1181 | 5.1821 | 5.2733 | 5.2735 | 5.1828 | 5.1181 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 16 | 7864 | 7 | 7 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0.30196 | 7.9648 | 3.762 | 228.9154 | 0 | 0 | 0 | 0.045316 | 0.23987 | 0.29391 | 0.17578 | 0 | 0.035168 | 3.7089 | 3.7089 | 3.7089 | 3.7089 | 3.7089 | 3.7089 | 3.7089 | 3.7089 | 7.9648 | 3.7089 | 3.7089 | 3.7089 | 3.7542 | 3.9487 | 4.0028 | 3.8847 | 3.7089 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 17 | 7865 | 6.9 | 6.9 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -3.7636 | 240.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 18 | 7866 | 6.8 | 6.8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -12.1984 | 252.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 19 | 7867 | 6.8 | 6.8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -21.1881 | 263.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 20 | 7868 | 6.7 | 6.7 | 12.1625 | 11.0834 | 15 | 98 | 98 | 0 | 0 | -30.3853 | 275.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 21 | 7869 | 6.8 | 6.8 | 12.1625 | 11.0834 | 15 | 97 | 97 | 0 | 0 | -39.3904 | 288.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 22 | 7870 | 6.8 | 6.8 | 12.1625 | 11.0834 | 15 | 98 | 98 | 0 | 0 | -47.648 | 304.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 23 | 7871 | 6.8 | 6.8 | 12.1625 | 11.0834 | 15 | 98 | 98 | 0 | 0 | -54.2873 | 323.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 24 | 24 | 7872 | 6.7 | 6.7 | 7.95 | 10.3588 | 15 | 97 | 97 | 0 | 0 | -58.0415 | 348.3406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 1 | 7873 | 5.7 | 5.7 | 7.95 | 10.3588 | 15 | 97 | 97 | 0 | 0 | -57.7758 | 14.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 2 | 7874 | 3.8 | 3.8 | 7.95 | 10.3588 | 15 | 98 | 98 | 0 | 0 | -53.7945 | 38.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 3 | 7875 | 4.7 | 4.7 | 7.95 | 10.3588 | 15 | 98 | 98 | 0 | 0 | -46.8841 | 58.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 4 | 7876 | 5.2 | 5.2 | 7.95 | 10.3588 | 15 | 99 | 99 | 0 | 0 | -38.4878 | 73.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 5 | 7877 | 4.4 | 4.4 | 7.95 | 10.3588 | 15 | 99 | 99 | 0 | 0 | -29.4302 | 86.4176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 6 | 7878 | 5 | 5 | 7.95 | 10.3588 | 15 | 99 | 99 | 0 | 0 | -20.2395 | 98.1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 7 | 7879 | 3 | 3 | 7.95 | 10.3588 | 15 | 99 | 99 | 0 | 0 | -11.3033 | 109.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 25 | 8 | 7880 | 2.5 | 2.5 | 7.95 | 10.3588 | 15 | 99 | 99 | 0 | 0 | -2.9668 | 120.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 9 | 7881 | 2.5 | 2.5 | 7.95 | 10.3588 | 15 | 99 | 99 | 4.442 | 5.8989 | 4.4141 | 132.6594 | 0 | 1.0936 | 3.8132 | 4.2991 | 2.2667 | 0 | 0 | 0 | 0.10115 | 2.1874 | 3.4428 | 6.5647 | 7.1224 | 4.7893 | 2.1874 | 2.1874 | 2.1874 | 5.8989 | 2.1874 | 4.5364 | 10.3779 | 11.4216 | 7.056 | 2.1874 | 2.1874 | 2.1874 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 10 | 7882 | 4.3 | 4.3 | 7.95 | 10.3588 | 15 | 99 | 99 | 43.2121 | 61.0164 | 10.4507 | 145.4293 | 0 | 1.7596 | 31.6837 | 43.048 | 29.1953 | 0 | 0 | 0 | 5.9836 | 26.6386 | 33.2437 | 145.5727 | 188.2318 | 136.2317 | 26.6386 | 26.6386 | 26.6386 | 61.0164 | 26.6386 | 35.0032 | 177.2565 | 231.2798 | 165.4271 | 26.6386 | 26.6386 | 26.6386 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 11 | 7883 | 6.6 | 6.6 | 7.95 | 10.3588 | 15 | 99 | 99 | 234.9421 | 104.9627 | 14.738 | 159.1141 | 0 | 0 | 131.1002 | 227.2277 | 190.2483 | 41.8241 | 0 | 0 | 53.0373 | 55.3338 | 55.3338 | 117.2628 | 162.6715 | 145.2032 | 75.0906 | 55.3338 | 55.3338 | 104.9627 | 55.3338 | 55.3338 | 248.3629 | 389.8992 | 335.4515 | 116.9147 | 55.3338 | 55.3338 | 158 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 12 | 7884 | 8.5 | 8.5 | 7.95 | 10.3588 | 15 | 99 | 99 | 292.1516 | 124.5925 | 16.9191 | 173.5152 | 0 | 0 | 100.7278 | 257.8835 | 263.9745 | 115.4328 | 0 | 0 | 81.4075 | 67.7842 | 67.7842 | 108.6692 | 172.4581 | 174.9305 | 114.6379 | 67.7842 | 67.7842 | 124.5925 | 67.7842 | 67.7842 | 209.397 | 430.3416 | 438.905 | 230.0708 | 67.7842 | 67.7842 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 13 | 7885 | 9.7 | 9.7 | 7.95 | 10.3588 | 15 | 83 | 83 | 633.1383 | 86.1349 | 16.7836 | 188.1689 | 0 | 0 | 68.4118 | 473.9525 | 601.8583 | 377.2037 | 0 | 0 | 185.8651 | 61.2667 | 61.2667 | 71.684 | 133.4371 | 152.9137 | 118.7048 | 61.2667 | 61.2667 | 86.1349 | 61.2667 | 61.2667 | 140.0958 | 607.3896 | 754.7721 | 495.9085 | 61.2667 | 61.2667 | 272 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 14 | 7886 | 9.4 | 9.4 | 7.95 | 10.3588 | 15 | 83 | 83 | 207.5041 | 127.0844 | 14.3452 | 202.5069 | 0 | 0 | 0 | 119.0912 | 196.6491 | 159.0126 | 28.2286 | 0 | 55.9156 | 66.7228 | 66.7228 | 66.7228 | 134.5539 | 178.7287 | 157.292 | 82.8011 | 66.7228 | 127.0844 | 66.7228 | 66.7228 | 66.7228 | 253.6451 | 375.3778 | 316.3046 | 111.0297 | 66.7228 | 183 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 15 | 7887 | 8.7 | 8.7 | 7.95 | 10.3588 | 15 | 87 | 87 | 61.2309 | 95.2632 | 9.8362 | 216.0907 | 0 | 0 | 0 | 22.6949 | 54.8035 | 54.8089 | 22.708 | 0 | 12.7368 | 46.5152 | 46.5152 | 46.5152 | 66.2728 | 94.2258 | 94.2305 | 66.2843 | 46.5152 | 95.2632 | 46.5152 | 46.5152 | 46.5152 | 88.9677 | 149.0292 | 149.0394 | 88.9923 | 46.5152 | 108 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 16 | 7888 | 7.9 | 7.9 | 7.95 | 10.3588 | 15 | 88 | 88 | 19.8229 | 44.7522 | 3.6239 | 228.7554 | 0 | 0 | 0 | 3.0249 | 15.7831 | 19.2958 | 11.5053 | 0 | 2.2478 | 22.6083 | 22.6083 | 22.6083 | 25.7509 | 39.0055 | 42.6548 | 34.5612 | 22.6083 | 44.7522 | 22.6083 | 22.6083 | 22.6083 | 28.7757 | 54.7886 | 61.9506 | 46.0665 | 22.6083 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 17 | 7889 | 6.9 | 6.9 | 7.95 | 10.3588 | 15 | 91 | 91 | 0 | 6 | -3.8863 | 240.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 6 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 2.8074 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 18 | 7890 | 6.9 | 6.9 | 7.95 | 10.3588 | 15 | 93 | 93 | 0 | 0 | -12.3097 | 251.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 19 | 7891 | 6.7 | 6.7 | 7.95 | 10.3588 | 15 | 93 | 93 | 0 | 0 | -21.293 | 263.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 20 | 7892 | 6.6 | 6.6 | 7.95 | 10.3588 | 15 | 93 | 93 | 0 | 0 | -30.4897 | 274.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 21 | 7893 | 6.5 | 6.5 | 7.95 | 10.3588 | 15 | 94 | 94 | 0 | 0 | -39.502 | 288.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 22 | 7894 | 6.4 | 6.4 | 7.95 | 10.3588 | 15 | 95 | 95 | 0 | 0 | -47.7765 | 303.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 23 | 7895 | 6.5 | 6.5 | 7.95 | 10.3588 | 15 | 95 | 95 | 0 | 0 | -54.4432 | 323.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 25 | 24 | 7896 | 6.3 | 6.3 | 6.0292 | 9.132 | 15 | 96 | 96 | 0 | 0 | -58.2292 | 348.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 1 | 7897 | 6.8 | 6.8 | 6.0292 | 9.132 | 15 | 95 | 95 | 0 | 0 | -57.9837 | 14.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 2 | 7898 | 6.8 | 6.8 | 6.0292 | 9.132 | 15 | 95 | 95 | 0 | 0 | -54 | 38.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 3 | 7899 | 6.8 | 6.8 | 6.0292 | 9.132 | 15 | 93 | 93 | 0 | 0 | -47.0846 | 58.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 4 | 7900 | 7 | 7 | 6.0292 | 9.132 | 15 | 90 | 90 | 0 | 0 | -38.6833 | 73.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 5 | 7901 | 6.9 | 6.9 | 6.0292 | 9.132 | 15 | 90 | 90 | 0 | 0 | -29.6234 | 86.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 6 | 7902 | 7.3 | 7.3 | 6.0292 | 9.132 | 15 | 90 | 90 | 0 | 0 | -20.4332 | 98.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 7 | 7903 | 7.8 | 7.8 | 6.0292 | 9.132 | 15 | 87 | 87 | 0 | 0 | -11.4997 | 109.4178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 26 | 8 | 7904 | 8.1 | 8.1 | 6.0292 | 9.132 | 15 | 85 | 85 | 0 | 0 | -3.1669 | 120.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 9 | 7905 | 8 | 8 | 6.0292 | 9.132 | 15 | 85 | 85 | 24.7579 | 9.3592 | 4.2103 | 132.6884 | 0 | 6.0739 | 21.2388 | 23.9623 | 12.649 | 0 | 0 | 0 | 1.6408 | 3.7973 | 6.0278 | 11.5969 | 12.5971 | 8.4424 | 3.7973 | 3.7973 | 3.7973 | 9.3592 | 3.7973 | 12.1017 | 32.8357 | 36.5593 | 21.0915 | 3.7973 | 3.7973 | 3.7973 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 10 | 7906 | 8.3 | 8.3 | 6.0292 | 9.132 | 15 | 86 | 86 | 2.1782 | 24.7049 | 10.2448 | 145.4333 | 0 | 0.087616 | 1.5968 | 2.1705 | 1.4728 | 0 | 0 | 0 | 0.29507 | 11.9505 | 12.2602 | 17.5934 | 19.6211 | 17.1555 | 11.9505 | 11.9505 | 11.9505 | 24.7049 | 11.9505 | 12.3478 | 19.1901 | 21.7916 | 18.6283 | 11.9505 | 11.9505 | 11.9505 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 11 | 7907 | 8.3 | 8.3 | 6.0292 | 9.132 | 15 | 90 | 90 | 1.6723 | 35.6277 | 14.5338 | 159.0873 | 0 | 0 | 0.93366 | 1.6184 | 1.3551 | 0.298 | 0 | 0 | 0.3723 | 17.3038 | 17.3038 | 17.3038 | 17.3038 | 17.3038 | 17.3038 | 17.3038 | 17.3038 | 35.6277 | 17.3038 | 17.3038 | 18.2374 | 18.9222 | 18.6589 | 17.6018 | 17.3038 | 17.3038 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 12 | 7908 | 10.2 | 10.2 | 6.0292 | 9.132 | 15 | 81 | 81 | 10.6232 | 97.0737 | 16.7217 | 173.454 | 0 | 0 | 3.6705 | 9.3878 | 9.6058 | 4.1969 | 0 | 0 | 2.9263 | 45.38 | 45.38 | 57.5339 | 76.4648 | 77.1866 | 59.2766 | 45.38 | 45.38 | 97.0737 | 45.38 | 45.38 | 61.2045 | 85.8526 | 86.7924 | 63.4735 | 45.38 | 45.38 | 100 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 13 | 7909 | 10.5 | 10.5 | 6.0292 | 9.132 | 15 | 79 | 79 | 11.8139 | 104.5697 | 16.5987 | 188.0743 | 0 | 0 | 1.2898 | 8.8604 | 11.2406 | 7.0363 | 0 | 0 | 3.4303 | 49.5732 | 49.5732 | 52.5119 | 69.7605 | 75.1836 | 65.6045 | 49.5732 | 49.5732 | 104.5697 | 49.5732 | 49.5732 | 53.8018 | 78.6209 | 86.4242 | 72.6407 | 49.5732 | 49.5732 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 14 | 7910 | 10.7 | 10.7 | 6.0292 | 9.132 | 15 | 79 | 79 | 6.3139 | 81.3186 | 14.1773 | 202.384 | 0 | 0 | 0 | 3.6352 | 5.9908 | 4.8371 | 0.84987 | 0 | 1.6814 | 40.0847 | 40.0847 | 40.0847 | 42.3501 | 43.818 | 43.0991 | 40.6143 | 40.0847 | 81.3186 | 40.0847 | 40.0847 | 40.0847 | 45.9852 | 49.8088 | 47.9361 | 41.4642 | 40.0847 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 15 | 7911 | 10.7 | 10.7 | 6.0292 | 9.132 | 15 | 78 | 78 | 3.8075 | 49.2198 | 9.687 | 215.9468 | 0 | 0 | 0 | 1.4196 | 3.4134 | 3.4077 | 1.4058 | 0 | 0.78024 | 24.0125 | 24.0125 | 24.0125 | 24.0125 | 24.0125 | 24.0125 | 24.0125 | 24.0125 | 49.2198 | 24.0125 | 24.0125 | 24.0125 | 25.4321 | 27.4259 | 27.4201 | 25.4182 | 24.0125 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 16 | 7912 | 10.7 | 10.7 | 6.0292 | 9.132 | 15 | 77 | 77 | 1.5159 | 16.8326 | 3.4927 | 228.5965 | 0 | 0 | 0 | 0.23512 | 1.2097 | 1.4756 | 0.87718 | 0 | 0.16738 | 7.9594 | 7.9594 | 7.9594 | 7.9594 | 7.9594 | 7.9594 | 7.9594 | 7.9594 | 16.8326 | 7.9594 | 7.9594 | 7.9594 | 8.1946 | 9.1691 | 9.4351 | 8.8366 | 7.9594 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 17 | 7913 | 10.6 | 10.6 | 6.0292 | 9.132 | 15 | 76 | 76 | 0 | 3 | -4.0023 | 240.4345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 3 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 1.3882 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 26 | 18 | 7914 | 10.1 | 10.1 | 6.0292 | 9.132 | 15 | 79 | 79 | 0 | 0 | -12.4143 | 251.7575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 19 | 7915 | 9.4 | 9.4 | 6.0292 | 9.132 | 15 | 83 | 83 | 0 | 0 | -21.3911 | 263.0074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 20 | 7916 | 8.9 | 8.9 | 6.0292 | 9.132 | 15 | 88 | 88 | 0 | 0 | -30.5872 | 274.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 21 | 7917 | 8.7 | 8.7 | 6.0292 | 9.132 | 15 | 90 | 90 | 0 | 0 | -39.6065 | 287.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 22 | 7918 | 8.2 | 8.2 | 6.0292 | 9.132 | 15 | 94 | 94 | 0 | 0 | -47.8977 | 303.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 23 | 7919 | 8 | 8 | 6.0292 | 9.132 | 15 | 94 | 94 | 0 | 0 | -54.5918 | 323.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 26 | 24 | 7920 | 7.5 | 7.5 | 8.5958 | 8.8726 | 15 | 92 | 92 | 0 | 0 | -58.4099 | 347.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 1 | 7921 | 5.8 | 5.8 | 8.5958 | 8.8726 | 15 | 94 | 94 | 0 | 0 | -58.1857 | 14.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 2 | 7922 | 5.1 | 5.1 | 8.5958 | 8.8726 | 15 | 96 | 96 | 0 | 0 | -54.2005 | 38.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 3 | 7923 | 4.5 | 4.5 | 8.5958 | 8.8726 | 15 | 97 | 97 | 0 | 0 | -47.281 | 58.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 4 | 7924 | 4.6 | 4.6 | 8.5958 | 8.8726 | 15 | 98 | 98 | 0 | 0 | -38.8752 | 73.6299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 5 | 7925 | 4.4 | 4.4 | 8.5958 | 8.8726 | 15 | 98 | 98 | 0 | 0 | -29.8132 | 86.5743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 6 | 7926 | 4.8 | 4.8 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -20.6235 | 98.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 7 | 7927 | 5.6 | 5.6 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -11.6924 | 109.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 27 | 8 | 7928 | 5.6 | 5.6 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -3.363 | 120.8193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 9 | 7929 | 5.3 | 5.3 | 8.5958 | 8.8726 | 15 | 99 | 99 | 1.9553 | 2.9665 | 4.011 | 132.7123 | 0 | 0.47819 | 1.6763 | 1.8924 | 1 | 0 | 0 | 0 | 0.033543 | 1.0996 | 1.7273 | 3.3 | 3.5837 | 2.4123 | 1.0996 | 1.0996 | 1.0996 | 2.9665 | 1.0996 | 2.2055 | 4.9762 | 5.4761 | 3.4123 | 1.0996 | 1.0996 | 1.0996 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 10 | 7930 | 5.2 | 5.2 | 8.5958 | 8.8726 | 15 | 99 | 99 | 1.7609 | 21.7666 | 10.0441 | 145.4326 | 0 | 0.070121 | 1.2907 | 1.7552 | 1.1916 | 0 | 0 | 0 | 0.23343 | 10.6675 | 10.7424 | 12.0469 | 12.5433 | 11.9409 | 10.6675 | 10.6675 | 10.6675 | 21.7666 | 10.6675 | 10.8126 | 13.3376 | 14.2985 | 13.1324 | 10.6675 | 10.6675 | 10.6675 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 11 | 7931 | 5.6 | 5.6 | 8.5958 | 8.8726 | 15 | 99 | 99 | 5.9505 | 65.6932 | 14.3353 | 159.0565 | 0 | 0 | 3.3244 | 5.7624 | 4.8249 | 1.061 | 0 | 0 | 1.3068 | 30.8039 | 30.8039 | 47.5065 | 59.7556 | 55.0451 | 36.1345 | 30.8039 | 30.8039 | 65.6932 | 30.8039 | 30.8039 | 50.8309 | 65.518 | 59.87 | 37.1955 | 30.8039 | 30.8039 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 12 | 7932 | 5.8 | 5.8 | 8.5958 | 8.8726 | 15 | 99 | 99 | 5.2427 | 76.572 | 16.5306 | 173.3899 | 0 | 0 | 1.8157 | 4.6383 | 4.7439 | 2.0706 | 0 | 0 | 1.428 | 37.219 | 37.219 | 40.609 | 45.8791 | 46.0763 | 41.085 | 37.219 | 37.219 | 76.572 | 37.219 | 37.219 | 42.4246 | 50.5175 | 50.8202 | 43.1556 | 37.219 | 37.219 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 13 | 7933 | 5.9 | 5.9 | 8.5958 | 8.8726 | 15 | 99 | 99 | 7.2144 | 91.9276 | 16.4206 | 187.9779 | 0 | 0 | 0.79613 | 5.4209 | 6.8702 | 4.295 | 0 | 0 | 2.0724 | 44.4311 | 44.4311 | 45.9672 | 54.8904 | 57.6867 | 52.7181 | 44.4311 | 44.4311 | 91.9276 | 44.4311 | 44.4311 | 46.7633 | 60.3113 | 64.5569 | 57.0131 | 44.4311 | 44.4311 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 14 | 7934 | 6.2 | 6.2 | 8.5958 | 8.8726 | 15 | 99 | 99 | 9.0875 | 89.6079 | 14.0161 | 202.2606 | 0 | 0 | 0 | 5.2486 | 8.6325 | 6.9596 | 1.2098 | 0 | 2.3921 | 43.4846 | 43.4846 | 43.4846 | 50.5122 | 55.0429 | 52.803 | 45.1045 | 43.4846 | 89.6079 | 43.4846 | 43.4846 | 43.4846 | 55.7608 | 63.6754 | 59.7626 | 46.3143 | 43.4846 | 92 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 15 | 7935 | 6.3 | 6.3 | 8.5958 | 8.8726 | 15 | 99 | 99 | 22.6494 | 81.4264 | 9.5446 | 215.8033 | 0 | 0 | 0 | 8.4942 | 20.3373 | 20.267 | 8.3246 | 0 | 4.5736 | 39.8195 | 39.8195 | 39.8195 | 54.9299 | 75.9976 | 75.8726 | 54.6282 | 39.8195 | 81.4264 | 39.8195 | 39.8195 | 39.8195 | 63.4242 | 96.3349 | 96.1396 | 62.9528 | 39.8195 | 86 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 16 | 7936 | 6.1 | 6.1 | 8.5958 | 8.8726 | 15 | 99 | 99 | 6.0193 | 32.3526 | 3.3682 | 228.4388 | 0 | 0 | 0 | 0.94872 | 4.8143 | 5.8597 | 3.4726 | 0 | 0.64738 | 15.7127 | 15.7127 | 15.7127 | 15.7127 | 15.7127 | 15.7127 | 15.7127 | 15.7127 | 32.3526 | 15.7127 | 15.7127 | 15.7127 | 16.6614 | 20.527 | 21.5724 | 19.1853 | 15.7127 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 17 | 7937 | 5.9 | 5.9 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 3 | -4.1116 | 240.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 3 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 1.3885 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 27 | 18 | 7938 | 5 | 5 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -12.5123 | 251.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 19 | 7939 | 4.9 | 4.9 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -21.4825 | 262.8155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 20 | 7940 | 4.7 | 4.7 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -30.678 | 274.5745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 21 | 7941 | 3.7 | 3.7 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -39.704 | 287.6914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 22 | 7942 | 3.3 | 3.3 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -48.0116 | 303.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 23 | 7943 | 2.9 | 2.9 | 8.5958 | 8.8726 | 15 | 99 | 99 | 0 | 0 | -54.7329 | 323.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 27 | 24 | 7944 | 1.5 | 1.5 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -58.5836 | 347.7775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 1 | 7945 | 0.5 | 0.5 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -58.3817 | 14.7108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 2 | 7946 | 0.2 | 0.2 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -54.396 | 38.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 3 | 7947 | -0.7 | -0.7 | 4.9458 | 7.7896 | 15 | 100 | 100 | 0 | 0 | -47.4732 | 58.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 4 | 7948 | -0.9 | -0.9 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -39.0634 | 73.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 5 | 7949 | -1.3 | -1.3 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -29.9996 | 86.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 6 | 7950 | -1.6 | -1.6 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -20.8103 | 98.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 7 | 7951 | -1.7 | -1.7 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -11.8814 | 109.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 28 | 8 | 7952 | -1.9 | -1.9 | 4.9458 | 7.7896 | 15 | 100 | 100 | 0 | 0 | -3.555 | 120.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 9 | 7953 | -1.3 | -1.3 | 4.9458 | 7.7896 | 15 | 100 | 100 | 81.9305 | 6.8126 | 3.8163 | 132.7308 | 0 | 19.9813 | 70.1983 | 79.294 | 41.9404 | 0 | 0 | 0 | 1.1874 | 3.502 | 4.0242 | 5.3368 | 5.5745 | 4.5982 | 3.502 | 3.502 | 3.502 | 6.8126 | 3.502 | 24.0056 | 75.5351 | 84.8686 | 46.5386 | 3.502 | 3.502 | 3.502 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 10 | 7954 | 1.1 | 1.1 | 4.9458 | 7.7896 | 15 | 99 | 99 | 160.298 | 62.1997 | 9.8486 | 145.4272 | 0 | 6.3327 | 117.4857 | 159.8171 | 108.5299 | 0 | 0 | 0 | 20.8003 | 30.3534 | 32.6132 | 72.279 | 87.3853 | 69.0831 | 30.3534 | 30.3534 | 30.3534 | 62.1997 | 30.3534 | 38.946 | 189.7647 | 247.2025 | 177.6129 | 30.3534 | 30.3534 | 30.3534 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 11 | 7955 | 4.5 | 4.5 | 4.9458 | 7.7896 | 15 | 99 | 99 | 318.8119 | 94.9103 | 14.1426 | 159.0219 | 0 | 0 | 178.2448 | 308.9263 | 258.6429 | 56.85 | 0 | 0 | 69.0897 | 52.6465 | 52.6465 | 113.0379 | 157.3142 | 140.2777 | 71.908 | 52.6465 | 52.6465 | 94.9103 | 52.6465 | 52.6465 | 291.2827 | 466.2405 | 398.9206 | 128.758 | 52.6465 | 52.6465 | 164 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 12 | 7956 | 7.8 | 7.8 | 4.9458 | 7.7896 | 15 | 95 | 95 | 476.239 | 99.6949 | 16.3459 | 173.3231 | 0 | 0 | 165.3311 | 421.8075 | 431.1948 | 187.994 | 0 | 0 | 128.3051 | 61.7416 | 61.7416 | 98.3236 | 155.0728 | 157.1499 | 103.3381 | 61.7416 | 61.7416 | 99.6949 | 61.7416 | 61.7416 | 263.6547 | 576.8803 | 588.3447 | 291.3321 | 61.7416 | 61.7416 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 13 | 7957 | 9 | 9 | 4.9458 | 7.7896 | 15 | 76 | 76 | 539.8273 | 96.5427 | 16.2491 | 187.88 | 0 | 0 | 60.2289 | 406.3907 | 514.4943 | 321.2141 | 0 | 0 | 153.4573 | 63.2159 | 63.2159 | 74.9505 | 142.3942 | 163.4564 | 125.799 | 63.2159 | 63.2159 | 96.5427 | 63.2159 | 63.2159 | 135.1795 | 548.7849 | 677.9507 | 447.0131 | 63.2159 | 63.2159 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 14 | 7958 | 8.8 | 8.8 | 4.9458 | 7.7896 | 15 | 74 | 74 | 467.1281 | 97.4216 | 13.8619 | 202.1368 | 0 | 0 | 0 | 270.6448 | 444.2337 | 357.5966 | 61.4842 | 0 | 121.5784 | 60.4027 | 60.4027 | 60.4027 | 121.5911 | 160.8367 | 141.2495 | 74.3033 | 60.4027 | 97.4216 | 60.4027 | 60.4027 | 60.4027 | 392.2358 | 605.0705 | 498.8461 | 135.7876 | 60.4027 | 219 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 15 | 7959 | 8.6 | 8.6 | 4.9458 | 7.7896 | 15 | 75 | 75 | 380.7844 | 82.2073 | 9.4091 | 215.6603 | 0 | 0 | 0 | 143.6383 | 342.4431 | 340.6494 | 139.3079 | 0 | 75.7927 | 48.8978 | 48.8978 | 48.8978 | 86.2591 | 137.9696 | 137.503 | 85.1327 | 48.8978 | 82.2073 | 48.8978 | 48.8978 | 48.8978 | 229.8974 | 480.4127 | 478.1525 | 224.4407 | 48.8978 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 16 | 7960 | 6.3 | 6.3 | 4.9458 | 7.7896 | 15 | 86 | 86 | 181.7072 | 49.961 | 3.2505 | 228.2823 | 0 | 0 | 0 | 29.0919 | 145.6485 | 176.8861 | 104.5063 | 0 | 19.039 | 27.8751 | 27.8751 | 27.8751 | 40.493 | 91.0464 | 104.5949 | 73.202 | 27.8751 | 49.961 | 27.8751 | 27.8751 | 27.8751 | 69.5849 | 236.6949 | 281.481 | 177.7083 | 27.8751 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 17 | 7961 | 3.6 | 3.6 | 4.9458 | 7.7896 | 15 | 94 | 94 | 0 | 6 | -4.2141 | 240.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 6 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 2.8119 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 28 | 18 | 7962 | 3.7 | 3.7 | 4.9458 | 7.7896 | 15 | 97 | 97 | 0 | 0 | -12.6035 | 251.4009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 19 | 7963 | 3.9 | 3.9 | 4.9458 | 7.7896 | 15 | 98 | 98 | 0 | 0 | -21.5672 | 262.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 20 | 7964 | 3.6 | 3.6 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -30.7619 | 274.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 21 | 7965 | 3.4 | 3.4 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -39.7945 | 287.4659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 22 | 7966 | 3.1 | 3.1 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -48.1182 | 303.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 23 | 7967 | 3 | 3 | 4.9458 | 7.7896 | 15 | 99 | 99 | 0 | 0 | -54.8666 | 322.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 28 | 24 | 7968 | 3.2 | 3.2 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -58.7501 | 347.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 1 | 7969 | 2.8 | 2.8 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -58.5715 | 14.6209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 2 | 7970 | 2.2 | 2.2 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -54.5864 | 38.9299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 3 | 7971 | 2.3 | 2.3 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -47.6612 | 58.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 4 | 7972 | 2.6 | 2.6 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -39.2479 | 73.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 5 | 7973 | 2.2 | 2.2 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -30.1824 | 86.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 6 | 7974 | 2.2 | 2.2 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -20.9935 | 98.3705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 7 | 7975 | 2.3 | 2.3 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | -12.0665 | 109.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 29 | 8 | 7976 | 2.4 | 2.4 | 2.7042 | 6.3086 | 15 | 100 | 100 | 0 | 0 | -3.7428 | 120.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 9 | 7977 | 2.6 | 2.6 | 2.7042 | 6.3086 | 15 | 99 | 99 | 0 | 0 | 3.6264 | 132.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 10 | 7978 | 2.3 | 2.3 | 2.7042 | 6.3086 | 15 | 99 | 99 | 1.9156 | 21.7566 | 9.6585 | 145.4171 | 0 | 0.075246 | 1.404 | 1.9102 | 1.2975 | 0 | 0 | 0 | 0.24339 | 10.5368 | 10.7786 | 15.0492 | 16.6765 | 14.7072 | 10.5368 | 10.5368 | 10.5368 | 21.7566 | 10.5368 | 10.8539 | 16.4532 | 18.5867 | 16.0047 | 10.5368 | 10.5368 | 10.5368 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 11 | 7979 | 2.9 | 2.9 | 2.7042 | 6.3086 | 15 | 97 | 97 | 2.7035 | 43.4217 | 13.9559 | 158.9835 | 0 | 0 | 1.5128 | 2.6213 | 2.1943 | 0.4819 | 0 | 0 | 0.5783 | 21.4063 | 21.4063 | 21.4063 | 21.4063 | 21.4063 | 21.4063 | 21.4063 | 21.4063 | 43.4217 | 21.4063 | 21.4063 | 22.9191 | 24.0276 | 23.6006 | 21.8882 | 21.4063 | 21.4063 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 12 | 7980 | 3.3 | 3.3 | 2.7042 | 6.3086 | 15 | 92 | 92 | 4.0371 | 65.9239 | 16.1676 | 173.2535 | 0 | 0 | 1.4051 | 3.5797 | 3.6573 | 1.5925 | 0 | 0 | 1.0761 | 32.6288 | 32.6288 | 33.0096 | 33.5989 | 33.62 | 33.0604 | 32.6288 | 32.6288 | 65.9239 | 32.6288 | 32.6288 | 34.4148 | 37.1786 | 37.2773 | 34.653 | 32.6288 | 32.6288 | 67 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 13 | 7981 | 4.3 | 4.3 | 2.7042 | 6.3086 | 15 | 89 | 89 | 152.5554 | 135.0725 | 16.0844 | 187.7805 | 0 | 0 | 17.2129 | 115.0607 | 145.5075 | 90.7179 | 0 | 0 | 42.9275 | 66.6628 | 66.6628 | 79.5258 | 152.6466 | 175.3992 | 134.4555 | 66.6628 | 66.6628 | 135.0725 | 66.6628 | 66.6628 | 96.7388 | 267.7073 | 320.9067 | 225.1734 | 66.6628 | 66.6628 | 178 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 14 | 7982 | 4.9 | 4.9 | 2.7042 | 6.3086 | 15 | 86 | 86 | 105.4524 | 122.855 | 13.7146 | 202.0126 | 0 | 0 | 0 | 61.2881 | 100.3916 | 80.687 | 13.7171 | 0 | 27.145 | 60.3897 | 60.3897 | 60.3897 | 118.4343 | 155.4684 | 136.8066 | 73.3809 | 60.3897 | 122.855 | 60.3897 | 60.3897 | 60.3897 | 179.7225 | 255.86 | 217.4937 | 87.098 | 60.3897 | 150 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 15 | 7983 | 5.3 | 5.3 | 2.7042 | 6.3086 | 15 | 84 | 84 | 126.3723 | 94.1977 | 9.2806 | 215.518 | 0 | 0 | 0 | 47.945 | 113.8196 | 113.0202 | 46.0151 | 0 | 24.8023 | 47.8322 | 47.8322 | 47.8322 | 78.5775 | 120.8203 | 120.3076 | 77.3399 | 47.8322 | 94.1977 | 47.8322 | 47.8322 | 47.8322 | 126.5225 | 234.6399 | 233.3279 | 123.355 | 47.8322 | 119 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 16 | 7984 | 4.9 | 4.9 | 2.7042 | 6.3086 | 15 | 82 | 82 | 33.4483 | 43.5846 | 3.1398 | 228.1272 | 0 | 0 | 0 | 5.4381 | 26.8684 | 32.5595 | 19.1777 | 0 | 3.4154 | 22.1107 | 22.1107 | 22.1107 | 25.6026 | 39.3635 | 43.0179 | 34.4251 | 22.1107 | 43.5846 | 22.1107 | 22.1107 | 22.1107 | 31.0407 | 66.2318 | 75.5774 | 53.6029 | 22.1107 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 17 | 7985 | 4.6 | 4.6 | 2.7042 | 6.3086 | 15 | 81 | 81 | 0 | 3 | -4.3098 | 239.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 3 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 1.3891 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 29 | 18 | 7986 | 4.6 | 4.6 | 2.7042 | 6.3086 | 15 | 81 | 81 | 0 | 0 | -12.688 | 251.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 19 | 7987 | 5 | 5 | 2.7042 | 6.3086 | 15 | 81 | 81 | 0 | 0 | -21.6452 | 262.4392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 20 | 7988 | 4.9 | 4.9 | 2.7042 | 6.3086 | 15 | 75 | 75 | 0 | 0 | -30.839 | 274.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 21 | 7989 | 5.2 | 5.2 | 2.7042 | 6.3086 | 15 | 71 | 71 | 0 | 0 | -39.878 | 287.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 22 | 7990 | 5.4 | 5.4 | 2.7042 | 6.3086 | 15 | 66 | 66 | 0 | 0 | -48.2176 | 302.8826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 23 | 7991 | 5.9 | 5.9 | 2.7042 | 6.3086 | 15 | 62 | 62 | 0 | 0 | -54.9928 | 322.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 29 | 24 | 7992 | 4.1 | 4.1 | 3.7167 | 5.3617 | 15 | 84 | 84 | 0 | 0 | -58.9095 | 347.3792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 1 | 7993 | 3.6 | 3.6 | 3.7167 | 5.3617 | 15 | 95 | 95 | 0 | 0 | -58.7551 | 14.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 2 | 7994 | 3.8 | 3.8 | 3.7167 | 5.3617 | 15 | 96 | 96 | 0 | 0 | -54.7716 | 38.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 3 | 7995 | 4 | 4 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -47.8448 | 58.3891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 4 | 7996 | 4.1 | 4.1 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -39.4285 | 73.8122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 5 | 7997 | 4.3 | 4.3 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -30.3616 | 86.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 6 | 7998 | 4.6 | 4.6 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -21.1731 | 98.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 7 | 7999 | 4.9 | 4.9 | 3.7167 | 5.3617 | 15 | 98 | 98 | 0 | 0 | -12.2478 | 109.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 11 | 30 | 8 | 8000 | 5.1 | 5.1 | 3.7167 | 5.3617 | 15 | 98 | 98 | 0 | 0 | -3.9262 | 120.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 9 | 8001 | 5.3 | 5.3 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | 3.4413 | 132.7524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 10 | 8002 | 5.8 | 5.8 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0.037109 | 2.9954 | 9.4738 | 145.4025 | 0 | 0.0014527 | 0.0272 | 0.037014 | 0.025146 | 0 | 0 | 0 | 0.0046189 | 1.3866 | 1.3866 | 1.3866 | 1.3866 | 1.3866 | 1.3866 | 1.3866 | 1.3866 | 2.9954 | 1.3866 | 1.388 | 1.4138 | 1.4236 | 1.4117 | 1.3866 | 1.3866 | 1.3866 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 11 | 8003 | 6.2 | 6.2 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0.28065 | 13.9407 | 13.7752 | 158.9413 | 0 | 0 | 0.15718 | 0.27227 | 0.22787 | 0.049983 | 0 | 0 | 0.059277 | 6.556 | 6.556 | 6.556 | 6.556 | 6.556 | 6.556 | 6.556 | 6.556 | 13.9407 | 6.556 | 6.556 | 6.7132 | 6.8283 | 6.7839 | 6.606 | 6.556 | 6.556 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 12 | 8004 | 6.7 | 6.7 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0.57372 | 24.8487 | 15.9958 | 173.1812 | 0 | 0 | 0.20022 | 0.50927 | 0.52 | 0.22612 | 0 | 0 | 0.15134 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 11.7909 | 24.8487 | 11.7909 | 11.7909 | 11.9911 | 12.3002 | 12.3109 | 12.017 | 11.7909 | 11.7909 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 13 | 8005 | 7.4 | 7.4 | 3.7167 | 5.3617 | 15 | 98 | 98 | 0.64513 | 27.8203 | 15.9265 | 187.6795 | 0 | 0 | 0.07363 | 0.48748 | 0.61577 | 0.38335 | 0 | 0 | 0.17975 | 13.2116 | 13.2116 | 13.2116 | 13.2116 | 13.2116 | 13.2116 | 13.2116 | 13.2116 | 27.8203 | 13.2116 | 13.2116 | 13.2852 | 13.6991 | 13.8274 | 13.5949 | 13.2116 | 13.2116 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 14 | 8006 | 8.3 | 8.3 | 3.7167 | 5.3617 | 15 | 98 | 98 | 2.4623 | 49.3729 | 13.5743 | 201.888 | 0 | 0 | 0 | 1.4355 | 2.3465 | 1.883 | 0.31641 | 0 | 0.62707 | 23.9702 | 23.9702 | 23.9702 | 23.9702 | 23.9702 | 23.9702 | 23.9702 | 23.9702 | 49.3729 | 23.9702 | 23.9702 | 23.9702 | 25.4057 | 26.3167 | 25.8531 | 24.2866 | 23.9702 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 15 | 8007 | 8.7 | 8.7 | 3.7167 | 5.3617 | 15 | 97 | 97 | 3.7651 | 46.2711 | 9.1591 | 215.3763 | 0 | 0 | 0 | 1.4366 | 3.3961 | 3.3662 | 1.3644 | 0 | 0.7289 | 22.5393 | 22.5393 | 22.5393 | 22.5393 | 22.5393 | 22.5393 | 22.5393 | 22.5393 | 46.2711 | 22.5393 | 22.5393 | 22.5393 | 23.976 | 25.9355 | 25.9055 | 23.9037 | 22.5393 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 16 | 8008 | 8.5 | 8.5 | 3.7167 | 5.3617 | 15 | 94 | 94 | 1.863 | 16.8145 | 3.0359 | 227.9736 | 0 | 0 | 0 | 0.30748 | 1.4997 | 1.8134 | 1.0648 | 0 | 0.18545 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 16.8145 | 7.9607 | 7.9607 | 7.9607 | 8.2682 | 9.4603 | 9.774 | 9.0255 | 7.9607 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 17 | 8009 | 8 | 8 | 3.7167 | 5.3617 | 15 | 94 | 94 | 0 | 0 | -4.3988 | 239.7707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 11 | 30 | 18 | 8010 | 7.2 | 7.2 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -12.7658 | 251.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 19 | 8011 | 7.8 | 7.8 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -21.7165 | 262.2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 20 | 8012 | 7.9 | 7.9 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -30.9094 | 273.9666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 21 | 8013 | 6.9 | 6.9 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -39.9545 | 287.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 22 | 8014 | 7.1 | 7.1 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -48.3096 | 302.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 23 | 8015 | 7 | 7 | 3.7167 | 5.3617 | 15 | 97 | 97 | 0 | 0 | -55.1115 | 322.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 11 | 30 | 24 | 8016 | 7.1 | 7.1 | 6.2625 | 5.3075 | 15 | 97 | 97 | 0 | 0 | -59.0615 | 347.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 1 | 8017 | 7.2 | 7.2 | 6.2625 | 5.3075 | 15 | 96 | 96 | 0 | 0 | -58.9323 | 14.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 2 | 8018 | 7.3 | 7.3 | 6.2625 | 5.3075 | 15 | 96 | 96 | 0 | 0 | -54.9515 | 38.8996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 3 | 8019 | 7.4 | 7.4 | 6.2625 | 5.3075 | 15 | 97 | 97 | 0 | 0 | -48.0239 | 58.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 4 | 8020 | 7.7 | 7.7 | 6.2625 | 5.3075 | 15 | 96 | 96 | 0 | 0 | -39.6052 | 73.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 5 | 8021 | 8.1 | 8.1 | 6.2625 | 5.3075 | 15 | 96 | 96 | 0 | 0 | -30.537 | 86.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 6 | 8022 | 8.3 | 8.3 | 6.2625 | 5.3075 | 15 | 95 | 95 | 0 | 0 | -21.3488 | 98.4624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 7 | 8023 | 8.6 | 8.6 | 6.2625 | 5.3075 | 15 | 95 | 95 | 0 | 0 | -12.425 | 109.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 1 | 8 | 8024 | 9.1 | 9.1 | 6.2625 | 5.3075 | 15 | 95 | 95 | 0 | 0 | -4.1053 | 120.9344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 9 | 8025 | 9.7 | 9.7 | 6.2625 | 5.3075 | 15 | 92 | 92 | 21.541 | 2.8469 | 3.2611 | 132.7555 | 0 | 5.2217 | 18.4295 | 20.8416 | 11.0449 | 0 | 0 | 0 | 0.15312 | 1.4397 | 1.6581 | 2.2105 | 2.3114 | 1.9017 | 1.4397 | 1.4397 | 1.4397 | 2.8469 | 1.4397 | 6.8798 | 20.6401 | 23.153 | 12.9465 | 1.4397 | 1.4397 | 1.4397 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 10 | 8026 | 10.1 | 10.1 | 6.2625 | 5.3075 | 15 | 90 | 90 | 1.2404 | 16.8487 | 9.2946 | 145.3834 | 0 | 0.0485 | 0.90928 | 1.2374 | 0.84069 | 0 | 0 | 0 | 0.1513 | 8.2574 | 8.2574 | 8.2574 | 8.2574 | 8.2574 | 8.2574 | 8.2574 | 8.2574 | 16.8487 | 8.2574 | 8.3059 | 9.1666 | 9.4948 | 9.098 | 8.2574 | 8.2574 | 8.2574 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 11 | 8027 | 10.7 | 10.7 | 6.2625 | 5.3075 | 15 | 88 | 88 | 3.2409 | 46.3238 | 13.6006 | 158.8954 | 0 | 0 | 1.8169 | 3.146 | 2.6322 | 0.57646 | 0 | 0 | 0.67616 | 22.7502 | 22.7502 | 24.452 | 25.6968 | 25.2155 | 23.2901 | 22.7502 | 22.7502 | 46.3238 | 22.7502 | 22.7502 | 26.2689 | 28.8428 | 27.8477 | 23.8666 | 22.7502 | 22.7502 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 12 | 8028 | 11 | 11 | 6.2625 | 5.3075 | 15 | 88 | 88 | 5.6968 | 76.5123 | 15.8306 | 173.1064 | 0 | 0 | 1.9937 | 5.0625 | 5.1657 | 2.2429 | 0 | 0 | 1.4877 | 36.8818 | 36.8818 | 41.8078 | 49.3899 | 49.6449 | 42.4234 | 36.8818 | 36.8818 | 76.5123 | 36.8818 | 36.8818 | 43.8016 | 54.4523 | 54.8105 | 44.6663 | 36.8818 | 36.8818 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 13 | 8029 | 11.8 | 11.8 | 6.2625 | 5.3075 | 15 | 85 | 85 | 16.9747 | 106.3156 | 15.7756 | 187.5772 | 0 | 0 | 1.9601 | 12.8503 | 16.2129 | 10.0782 | 0 | 0 | 4.6844 | 49.8063 | 49.8063 | 54.0069 | 77.3449 | 84.5511 | 71.4043 | 49.8063 | 49.8063 | 106.3156 | 49.8063 | 49.8063 | 55.9671 | 90.1952 | 100.764 | 81.4824 | 49.8063 | 49.8063 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 14 | 8030 | 12.6 | 12.6 | 6.2625 | 5.3075 | 15 | 83 | 83 | 15.8824 | 95.997 | 13.441 | 201.7633 | 0 | 0 | 0 | 9.2881 | 15.1507 | 12.1383 | 2.0154 | 0 | 4.003 | 45.8438 | 45.8438 | 45.8438 | 59.3471 | 67.8703 | 63.4908 | 48.7739 | 45.8438 | 95.997 | 45.8438 | 45.8438 | 45.8438 | 68.6351 | 83.021 | 75.6291 | 50.7893 | 45.8438 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 15 | 8031 | 12.3 | 12.3 | 6.2625 | 5.3075 | 15 | 83 | 83 | 9.1822 | 65.246 | 9.0445 | 215.2354 | 0 | 0 | 0 | 3.5234 | 8.2941 | 8.2062 | 3.3113 | 0 | 1.754 | 32.2378 | 32.2378 | 32.2378 | 33.2318 | 34.5777 | 34.5529 | 33.1719 | 32.2378 | 65.246 | 32.2378 | 32.2378 | 32.2378 | 36.7552 | 42.8719 | 42.7592 | 36.4832 | 32.2378 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 16 | 8032 | 11.6 | 11.6 | 6.2625 | 5.3075 | 15 | 88 | 88 | 16.8673 | 37.3624 | 2.939 | 227.8214 | 0 | 0 | 0 | 2.8251 | 13.6057 | 16.4162 | 9.6103 | 0 | 1.6376 | 19.0377 | 19.0377 | 19.0377 | 21.6995 | 31.8568 | 34.5048 | 28.0924 | 19.0377 | 37.3624 | 19.0377 | 19.0377 | 19.0377 | 24.5246 | 45.4625 | 50.9211 | 37.7028 | 19.0377 | 39 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 17 | 8033 | 11 | 11 | 6.2625 | 5.3075 | 15 | 90 | 90 | 0 | 3 | -4.4809 | 239.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 3 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 1.3898 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 18 | 8034 | 11 | 11 | 6.2625 | 5.3075 | 15 | 88 | 88 | 0 | 0 | -12.8369 | 250.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 19 | 8035 | 11.3 | 11.3 | 6.2625 | 5.3075 | 15 | 83 | 83 | 0 | 0 | -21.781 | 262.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 20 | 8036 | 10.6 | 10.6 | 6.2625 | 5.3075 | 15 | 88 | 88 | 0 | 0 | -30.9729 | 273.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 21 | 8037 | 10.9 | 10.9 | 6.2625 | 5.3075 | 15 | 78 | 78 | 0 | 0 | -40.024 | 286.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 22 | 8038 | 10.5 | 10.5 | 6.2625 | 5.3075 | 15 | 75 | 75 | 0 | 0 | -48.3943 | 302.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 23 | 8039 | 9.8 | 9.8 | 6.2625 | 5.3075 | 15 | 74 | 74 | 0 | 0 | -55.2226 | 322.1519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 1 | 24 | 8040 | 8.9 | 8.9 | 9.8958 | 6.3818 | 15 | 78 | 78 | 0 | 0 | -59.2062 | 346.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 1 | 8041 | 8.4 | 8.4 | 9.8958 | 6.3818 | 15 | 79 | 79 | 0 | 0 | -59.103 | 14.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 2 | 8042 | 7.8 | 7.8 | 9.8958 | 6.3818 | 15 | 87 | 87 | 0 | 0 | -55.1259 | 38.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 3 | 8043 | 7.9 | 7.9 | 9.8958 | 6.3818 | 15 | 85 | 85 | 0 | 0 | -48.1985 | 58.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 4 | 8044 | 6.9 | 6.9 | 9.8958 | 6.3818 | 15 | 91 | 91 | 0 | 0 | -39.7779 | 73.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 5 | 8045 | 6.9 | 6.9 | 9.8958 | 6.3818 | 15 | 88 | 88 | 0 | 0 | -30.7086 | 86.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 6 | 8046 | 7 | 7 | 9.8958 | 6.3818 | 15 | 89 | 89 | 0 | 0 | -21.5207 | 98.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 7 | 8047 | 6.6 | 6.6 | 9.8958 | 6.3818 | 15 | 90 | 90 | 0 | 0 | -12.5981 | 109.6721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 2 | 8 | 8048 | 6.3 | 6.3 | 9.8958 | 6.3818 | 15 | 89 | 89 | 0 | 0 | -4.2798 | 120.9492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 9 | 8049 | 6.3 | 6.3 | 9.8958 | 6.3818 | 15 | 90 | 90 | 0 | 0 | 3.086 | 132.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 10 | 8050 | 6.7 | 6.7 | 9.8958 | 6.3818 | 15 | 87 | 87 | 3.3359 | 24.6352 | 9.121 | 145.3597 | 0 | 0.13058 | 2.446 | 3.3285 | 2.2613 | 0 | 0 | 0 | 0.36484 | 11.4175 | 12.3884 | 29.605 | 36.1675 | 28.2318 | 11.4175 | 11.4175 | 11.4175 | 24.6352 | 11.4175 | 12.519 | 32.0509 | 39.4961 | 30.4931 | 11.4175 | 11.4175 | 11.4175 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 11 | 8051 | 7.2 | 7.2 | 9.8958 | 6.3818 | 15 | 85 | 85 | 6.8331 | 62.6401 | 13.4322 | 158.8459 | 0 | 0 | 3.835 | 6.6367 | 5.5507 | 1.2132 | 0 | 0 | 1.3599 | 29.1133 | 29.1133 | 49.39 | 64.2037 | 58.4619 | 35.5281 | 29.1133 | 29.1133 | 62.6401 | 29.1133 | 29.1133 | 53.2249 | 70.8404 | 64.0126 | 36.7413 | 29.1133 | 29.1133 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 12 | 8052 | 7.6 | 7.6 | 9.8958 | 6.3818 | 15 | 85 | 85 | 5.0872 | 70.7024 | 15.6721 | 173.029 | 0 | 0 | 1.7856 | 4.5256 | 4.6146 | 2.0004 | 0 | 0 | 1.2976 | 34.4503 | 34.4503 | 37.3502 | 41.8002 | 41.9446 | 37.699 | 34.4503 | 34.4503 | 70.7024 | 34.4503 | 34.4503 | 39.1359 | 46.3258 | 46.5592 | 39.6994 | 34.4503 | 34.4503 | 72 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 13 | 8053 | 7.9 | 7.9 | 9.8958 | 6.3818 | 15 | 85 | 85 | 3.8263 | 65.9528 | 15.6316 | 187.4735 | 0 | 0 | 0.44712 | 2.9019 | 3.6568 | 2.2696 | 0 | 0 | 1.0472 | 32.5696 | 32.5696 | 32.5696 | 32.5696 | 32.5696 | 32.5696 | 32.5696 | 32.5696 | 65.9528 | 32.5696 | 32.5696 | 33.0168 | 35.4716 | 36.2265 | 34.8392 | 32.5696 | 32.5696 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 14 | 8054 | 8.8 | 8.8 | 9.8958 | 6.3818 | 15 | 83 | 83 | 29.583 | 106.498 | 13.3148 | 201.6384 | 0 | 0 | 0 | 17.3533 | 28.2468 | 22.5937 | 3.7055 | 0 | 7.502 | 51.0126 | 51.0126 | 51.0126 | 84.9908 | 106.3204 | 95.2515 | 58.2681 | 51.0126 | 106.498 | 51.0126 | 51.0126 | 51.0126 | 102.3441 | 134.5672 | 117.8452 | 61.9735 | 51.0126 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 15 | 8055 | 8 | 8 | 9.8958 | 6.3818 | 15 | 86 | 86 | 13.3083 | 72.3893 | 8.9371 | 215.0953 | 0 | 0 | 0 | 5.1353 | 12.0379 | 11.8889 | 4.7755 | 0 | 2.6107 | 35.2165 | 35.2165 | 35.2165 | 39.4183 | 45.0661 | 44.9441 | 39.1238 | 35.2165 | 72.3893 | 35.2165 | 35.2165 | 35.2165 | 44.5536 | 57.104 | 56.833 | 43.8993 | 35.2165 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 16 | 8056 | 7.7 | 7.7 | 9.8958 | 6.3818 | 15 | 90 | 90 | 3.596 | 24.6212 | 2.849 | 227.671 | 0 | 0 | 0 | 0.61104 | 2.9065 | 3.4994 | 2.0424 | 0 | 0.3788 | 11.8266 | 11.8266 | 11.8266 | 11.8266 | 11.8266 | 11.8266 | 11.8266 | 11.8266 | 24.6212 | 11.8266 | 11.8266 | 11.8266 | 12.4377 | 14.7332 | 15.326 | 13.869 | 11.8266 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 17 | 8057 | 7.5 | 7.5 | 9.8958 | 6.3818 | 15 | 90 | 90 | 0 | 3 | -4.5562 | 239.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 3 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 1.3901 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 18 | 8058 | 6.8 | 6.8 | 9.8958 | 6.3818 | 15 | 90 | 90 | 0 | 0 | -12.9013 | 250.7167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 19 | 8059 | 6 | 6 | 9.8958 | 6.3818 | 15 | 88 | 88 | 0 | 0 | -21.8389 | 261.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 20 | 8060 | 5.1 | 5.1 | 9.8958 | 6.3818 | 15 | 91 | 91 | 0 | 0 | -31.0296 | 273.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 21 | 8061 | 3.7 | 3.7 | 9.8958 | 6.3818 | 15 | 94 | 94 | 0 | 0 | -40.0864 | 286.5922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 22 | 8062 | 4 | 4 | 9.8958 | 6.3818 | 15 | 96 | 96 | 0 | 0 | -48.4717 | 302.1648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 23 | 8063 | 3.5 | 3.5 | 9.8958 | 6.3818 | 15 | 96 | 96 | 0 | 0 | -55.326 | 321.9038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 2 | 24 | 8064 | 3.3 | 3.3 | 6.5792 | 6.4201 | 15 | 96 | 96 | 0 | 0 | -59.3435 | 346.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 1 | 8065 | 3 | 3 | 6.5792 | 6.4201 | 15 | 96 | 96 | 0 | 0 | -59.2672 | 14.1881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 2 | 8066 | 3.3 | 3.3 | 6.5792 | 6.4201 | 15 | 97 | 97 | 0 | 0 | -55.2948 | 38.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 3 | 8067 | 2.7 | 2.7 | 6.5792 | 6.4201 | 15 | 97 | 97 | 0 | 0 | -48.3685 | 58.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 4 | 8068 | 1.5 | 1.5 | 6.5792 | 6.4201 | 15 | 98 | 98 | 0 | 0 | -39.9464 | 73.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 5 | 8069 | 1.4 | 1.4 | 6.5792 | 6.4201 | 15 | 99 | 99 | 0 | 0 | -30.8762 | 86.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 6 | 8070 | 2.2 | 2.2 | 6.5792 | 6.4201 | 15 | 99 | 99 | 0 | 0 | -21.6886 | 98.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 7 | 8071 | 1.9 | 1.9 | 6.5792 | 6.4201 | 15 | 98 | 98 | 0 | 0 | -12.7669 | 109.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 3 | 8 | 8072 | 1.9 | 1.9 | 6.5792 | 6.4201 | 15 | 99 | 99 | 0 | 0 | -4.4497 | 120.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 9 | 8073 | 2.6 | 2.6 | 6.5792 | 6.4201 | 15 | 99 | 99 | 0 | 3 | 2.9159 | 132.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 10 | 8074 | 3 | 3 | 6.5792 | 6.4201 | 15 | 99 | 99 | 19.4887 | 41.9279 | 8.953 | 145.3317 | 0 | 0.76538 | 14.2933 | 19.4484 | 13.2109 | 0 | 0 | 0 | 2.0721 | 18.4685 | 22.4532 | 92.8809 | 119.7188 | 87.2457 | 18.4685 | 18.4685 | 18.4685 | 41.9279 | 18.4685 | 23.2185 | 107.1742 | 139.1672 | 100.4566 | 18.4685 | 18.4685 | 18.4685 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 11 | 8075 | 3 | 3 | 6.5792 | 6.4201 | 15 | 99 | 99 | 13.3135 | 72.389 | 13.27 | 158.7929 | 0 | 0 | 7.4808 | 12.9381 | 10.8164 | 2.3586 | 0 | 0 | 2.611 | 32.4882 | 32.4882 | 69.966 | 97.3063 | 86.677 | 44.3047 | 32.4882 | 32.4882 | 72.389 | 32.4882 | 32.4882 | 77.4468 | 110.2444 | 97.4934 | 46.6633 | 32.4882 | 32.4882 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 12 | 8076 | 3.5 | 3.5 | 6.5792 | 6.4201 | 15 | 99 | 99 | 7.3021 | 81.1571 | 15.5203 | 172.9491 | 0 | 0 | 2.5709 | 6.5031 | 6.6259 | 2.8673 | 0 | 0 | 1.8429 | 38.5675 | 38.5675 | 46.5768 | 58.8269 | 59.2092 | 47.4999 | 38.5675 | 38.5675 | 81.1571 | 38.5675 | 38.5675 | 49.1478 | 65.33 | 65.8351 | 50.3672 | 38.5675 | 38.5675 | 83 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 13 | 8077 | 3.6 | 3.6 | 6.5792 | 6.4201 | 15 | 99 | 99 | 5.2776 | 76.5684 | 15.4947 | 187.3687 | 0 | 0 | 0.62421 | 4.0099 | 5.0467 | 3.1272 | 0 | 0 | 1.4316 | 37.6936 | 37.6936 | 38.1726 | 40.7705 | 41.566 | 40.0931 | 37.6936 | 37.6936 | 76.5684 | 37.6936 | 37.6936 | 38.7968 | 44.7805 | 46.6128 | 43.2203 | 37.6936 | 37.6936 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 14 | 8078 | 3.6 | 3.6 | 6.5792 | 6.4201 | 15 | 99 | 99 | 2.2295 | 46.4393 | 13.1958 | 201.5134 | 0 | 0 | 0 | 1.3118 | 2.1307 | 1.7015 | 0.27555 | 0 | 0.56067 | 22.4992 | 22.4992 | 22.4992 | 22.4992 | 22.4992 | 22.4992 | 22.4992 | 22.4992 | 46.4393 | 22.4992 | 22.4992 | 22.4992 | 23.811 | 24.6299 | 24.2007 | 22.7747 | 22.4992 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 15 | 8079 | 4.5 | 4.5 | 6.5792 | 6.4201 | 15 | 99 | 99 | 2.1893 | 35.5744 | 8.8367 | 214.9562 | 0 | 0 | 0 | 0.84947 | 1.983 | 1.9549 | 0.78165 | 0 | 0.42556 | 17.1243 | 17.1243 | 17.1243 | 17.1243 | 17.1243 | 17.1243 | 17.1243 | 17.1243 | 35.5744 | 17.1243 | 17.1243 | 17.1243 | 17.9738 | 19.1073 | 19.0792 | 17.906 | 17.1243 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 16 | 8080 | 5 | 5 | 6.5792 | 6.4201 | 15 | 99 | 99 | 0.21297 | 5.9779 | 2.766 | 227.5222 | 0 | 0 | 0 | 0.0367 | 0.17247 | 0.20721 | 0.12057 | 0 | 0.022121 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 5.9779 | 2.7754 | 2.7754 | 2.7754 | 2.8121 | 2.9479 | 2.9826 | 2.896 | 2.7754 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 17 | 8081 | 5.3 | 5.3 | 6.5792 | 6.4201 | 15 | 98 | 98 | 0 | 0 | -4.6247 | 239.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 3 | 18 | 8082 | 5.6 | 5.6 | 6.5792 | 6.4201 | 15 | 95 | 95 | 0 | 0 | -12.9589 | 250.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 19 | 8083 | 5.7 | 5.7 | 6.5792 | 6.4201 | 15 | 94 | 94 | 0 | 0 | -21.8901 | 261.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 20 | 8084 | 5.8 | 5.8 | 6.5792 | 6.4201 | 15 | 94 | 94 | 0 | 0 | -31.0796 | 273.3868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 21 | 8085 | 5.9 | 5.9 | 6.5792 | 6.4201 | 15 | 95 | 95 | 0 | 0 | -40.142 | 286.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 22 | 8086 | 5.9 | 5.9 | 6.5792 | 6.4201 | 15 | 95 | 95 | 0 | 0 | -48.5417 | 301.9307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 23 | 8087 | 5.9 | 5.9 | 6.5792 | 6.4201 | 15 | 95 | 95 | 0 | 0 | -55.4219 | 321.6564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 3 | 24 | 8088 | 6 | 6 | 3.8667 | 5.6542 | 15 | 94 | 94 | 0 | 0 | -59.4733 | 346.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 1 | 8089 | 6.1 | 6.1 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -59.4248 | 14.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 2 | 8090 | 6.1 | 6.1 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -55.4582 | 38.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 3 | 8091 | 6.1 | 6.1 | 3.8667 | 5.6542 | 15 | 91 | 91 | 0 | 0 | -48.5337 | 58.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 4 | 8092 | 6 | 6 | 3.8667 | 5.6542 | 15 | 91 | 91 | 0 | 0 | -40.1106 | 73.9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 5 | 8093 | 6.1 | 6.1 | 3.8667 | 5.6542 | 15 | 90 | 90 | 0 | 0 | -31.0398 | 86.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 6 | 8094 | 6 | 6 | 3.8667 | 5.6542 | 15 | 89 | 89 | 0 | 0 | -21.8524 | 98.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 7 | 8095 | 5.8 | 5.8 | 3.8667 | 5.6542 | 15 | 88 | 88 | 0 | 0 | -12.9315 | 109.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 4 | 8 | 8096 | 5.4 | 5.4 | 3.8667 | 5.6542 | 15 | 92 | 92 | 0 | 0 | -4.615 | 120.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 9 | 8097 | 5.3 | 5.3 | 3.8667 | 5.6542 | 15 | 94 | 94 | 0 | 0 | 2.7511 | 132.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 10 | 8098 | 5.1 | 5.1 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0.05373 | 2.9944 | 8.7909 | 145.2992 | 0 | 0.0021218 | 0.039419 | 0.053626 | 0.036419 | 0 | 0 | 0 | 0.0055549 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 1.3884 | 2.9944 | 1.3884 | 1.3905 | 1.4278 | 1.442 | 1.4248 | 1.3884 | 1.3884 | 1.3884 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 11 | 8099 | 5.2 | 5.2 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0.33466 | 13.9353 | 13.1142 | 158.7363 | 0 | 0 | 0.18828 | 0.3254 | 0.2719 | 0.05913 | 0 | 0 | 0.064696 | 6.5614 | 6.5614 | 6.5614 | 6.5614 | 6.5614 | 6.5614 | 6.5614 | 6.5614 | 13.9353 | 6.5614 | 6.5614 | 6.7496 | 6.8867 | 6.8333 | 6.6205 | 6.5614 | 6.5614 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 12 | 8100 | 5.2 | 5.2 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0.49498 | 21.8764 | 15.3753 | 172.8669 | 0 | 0 | 0.17483 | 0.44129 | 0.44925 | 0.19405 | 0 | 0 | 0.12364 | 10.3522 | 10.3522 | 10.3522 | 10.3522 | 10.3522 | 10.3522 | 10.3522 | 10.3522 | 21.8764 | 10.3522 | 10.3522 | 10.527 | 10.7935 | 10.8015 | 10.5463 | 10.3522 | 10.3522 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 13 | 8101 | 5.1 | 5.1 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0.55138 | 24.8517 | 15.3648 | 187.2626 | 0 | 0 | 0.066017 | 0.4197 | 0.52753 | 0.32634 | 0 | 0 | 0.14829 | 11.7722 | 11.7722 | 11.7722 | 11.7722 | 11.7722 | 11.7722 | 11.7722 | 11.7722 | 24.8517 | 11.7722 | 11.7722 | 11.8383 | 12.1919 | 12.2998 | 12.0986 | 11.7722 | 11.7722 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 14 | 8102 | 5.4 | 5.4 | 3.8667 | 5.6542 | 15 | 92 | 92 | 0.64082 | 24.8401 | 13.084 | 201.3885 | 0 | 0 | 0 | 0.37819 | 0.61296 | 0.48866 | 0.078115 | 0 | 0.15987 | 11.7679 | 11.7679 | 11.7679 | 11.7679 | 11.7679 | 11.7679 | 11.7679 | 11.7679 | 24.8401 | 11.7679 | 11.7679 | 11.7679 | 12.1461 | 12.3809 | 12.2566 | 11.846 | 11.7679 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 15 | 8103 | 5.5 | 5.5 | 3.8667 | 5.6542 | 15 | 91 | 91 | 0.49662 | 16.9043 | 8.7435 | 214.8181 | 0 | 0 | 0 | 0.19375 | 0.45041 | 0.44323 | 0.17641 | 0 | 0.095699 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 7.9529 | 16.9043 | 7.9529 | 7.9529 | 7.9529 | 8.1466 | 8.4033 | 8.3961 | 8.1293 | 7.9529 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 16 | 8104 | 5.4 | 5.4 | 3.8667 | 5.6542 | 15 | 92 | 92 | 0.2186 | 5.9776 | 2.69 | 227.3753 | 0 | 0 | 0 | 0.038194 | 0.17738 | 0.21266 | 0.12336 | 0 | 0.022409 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 5.9776 | 2.7754 | 2.7754 | 2.7754 | 2.8136 | 2.9528 | 2.9881 | 2.8988 | 2.7754 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 17 | 8105 | 5.1 | 5.1 | 3.8667 | 5.6542 | 15 | 92 | 92 | 0 | 0 | -4.6863 | 239.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 4 | 18 | 8106 | 5.1 | 5.1 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -13.0098 | 250.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 19 | 8107 | 5 | 5 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -21.9346 | 261.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 20 | 8108 | 4.8 | 4.8 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -31.1228 | 273.2005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 21 | 8109 | 4.8 | 4.8 | 3.8667 | 5.6542 | 15 | 94 | 94 | 0 | 0 | -40.1905 | 286.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 22 | 8110 | 4.9 | 4.9 | 3.8667 | 5.6542 | 15 | 92 | 92 | 0 | 0 | -48.6045 | 301.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 23 | 8111 | 4.7 | 4.7 | 3.8667 | 5.6542 | 15 | 93 | 93 | 0 | 0 | -55.5101 | 321.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 4 | 24 | 8112 | 4.3 | 4.3 | 5.3542 | 5.6589 | 15 | 95 | 95 | 0 | 0 | -59.5955 | 346.3155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 1 | 8113 | 4 | 4 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -59.5756 | 13.9288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 2 | 8114 | 3.7 | 3.7 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -55.6158 | 38.7384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 3 | 8115 | 3.6 | 3.6 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -48.6941 | 58.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 4 | 8116 | 3.6 | 3.6 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -40.2706 | 73.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 5 | 8117 | 3.5 | 3.5 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -31.1993 | 86.9293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 6 | 8118 | 3.5 | 3.5 | 5.3542 | 5.6589 | 15 | 94 | 94 | 0 | 0 | -22.012 | 98.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 7 | 8119 | 3.5 | 3.5 | 5.3542 | 5.6589 | 15 | 96 | 96 | 0 | 0 | -13.0916 | 109.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 5 | 8 | 8120 | 3.6 | 3.6 | 5.3542 | 5.6589 | 15 | 97 | 97 | 0 | 0 | -4.7754 | 120.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 9 | 8121 | 3.7 | 3.7 | 5.3542 | 5.6589 | 15 | 96 | 96 | 0 | 0 | 2.5916 | 132.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 10 | 8122 | 4 | 4 | 5.3542 | 5.6589 | 15 | 96 | 96 | 1.8232 | 16.8167 | 8.6347 | 145.2624 | 0 | 0.072552 | 1.3382 | 1.8199 | 1.2356 | 0 | 0 | 0 | 0.18334 | 8.1663 | 8.3175 | 10.9537 | 11.9571 | 10.7399 | 8.1663 | 8.1663 | 8.1663 | 16.8167 | 8.1663 | 8.39 | 12.2918 | 13.777 | 11.9755 | 8.1663 | 8.1663 | 8.1663 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 11 | 8123 | 4.6 | 4.6 | 5.3542 | 5.6589 | 15 | 91 | 91 | 1.3762 | 27.7376 | 12.9648 | 158.6763 | 0 | 0 | 0.77529 | 1.3388 | 1.1181 | 0.2424 | 0 | 0 | 0.26236 | 13.3931 | 13.3931 | 13.3931 | 13.3931 | 13.3931 | 13.3931 | 13.3931 | 13.3931 | 27.7376 | 13.3931 | 13.3931 | 14.1684 | 14.732 | 14.5112 | 13.6355 | 13.3931 | 13.3931 | 28 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 12 | 8124 | 4.9 | 4.9 | 5.3542 | 5.6589 | 15 | 87 | 87 | 2.9296 | 52.2754 | 15.2371 | 172.7823 | 0 | 0 | 1.0381 | 2.6146 | 2.6594 | 1.1464 | 0 | 0 | 0.72456 | 25.6765 | 25.6765 | 25.6765 | 25.6765 | 25.6765 | 25.6765 | 25.6765 | 25.6765 | 52.2754 | 25.6765 | 25.6765 | 26.7146 | 28.2911 | 28.3359 | 26.8229 | 25.6765 | 25.6765 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 13 | 8125 | 5 | 5 | 5.3542 | 5.6589 | 15 | 87 | 87 | 3.3361 | 60.1101 | 15.2421 | 187.1555 | 0 | 0 | 0.40442 | 2.544 | 3.1934 | 1.9721 | 0 | 0 | 0.88991 | 29.5496 | 29.5496 | 29.5496 | 29.5496 | 29.5496 | 29.5496 | 29.5496 | 29.5496 | 60.1101 | 29.5496 | 29.5496 | 29.954 | 32.0936 | 32.7429 | 31.5216 | 29.5496 | 29.5496 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 14 | 8126 | 5.2 | 5.2 | 5.3542 | 5.6589 | 15 | 86 | 86 | 3.2638 | 55.1919 | 12.9793 | 201.2637 | 0 | 0 | 0 | 1.932 | 3.1245 | 2.4867 | 0.39225 | 0 | 0.80807 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 55.1919 | 27 | 27 | 27 | 28.932 | 30.1246 | 29.4868 | 27.3923 | 27 | 56 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 15 | 8127 | 5.5 | 5.5 | 5.3542 | 5.6589 | 15 | 86 | 86 | 4.3657 | 49.1656 | 8.6575 | 214.6812 | 0 | 0 | 0 | 1.7124 | 3.9646 | 3.8943 | 1.5428 | 0 | 0.83444 | 24.0773 | 24.0773 | 24.0773 | 24.0773 | 24.0773 | 24.0773 | 24.0773 | 24.0773 | 49.1656 | 24.0773 | 24.0773 | 24.0773 | 25.7897 | 28.0418 | 27.9716 | 25.6201 | 24.0773 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 16 | 8128 | 5.4 | 5.4 | 5.3542 | 5.6589 | 15 | 88 | 88 | 5.9792 | 30.3945 | 2.621 | 227.2303 | 0 | 0 | 0 | 1.0588 | 4.8609 | 5.8155 | 3.3635 | 0 | 0.60545 | 14.7728 | 14.7728 | 14.7728 | 14.7728 | 14.7728 | 14.7728 | 14.7728 | 14.7728 | 30.3945 | 14.7728 | 14.7728 | 14.7728 | 15.8317 | 19.6337 | 20.5883 | 18.1363 | 14.7728 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 17 | 8129 | 5 | 5 | 5.3542 | 5.6589 | 15 | 91 | 91 | 0 | 3 | -4.7411 | 238.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 3 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 1.3909 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 5 | 18 | 8130 | 4.7 | 4.7 | 5.3542 | 5.6589 | 15 | 93 | 93 | 0 | 0 | -13.054 | 250.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 19 | 8131 | 4.7 | 4.7 | 5.3542 | 5.6589 | 15 | 95 | 95 | 0 | 0 | -21.9724 | 261.3814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 20 | 8132 | 4.5 | 4.5 | 5.3542 | 5.6589 | 15 | 95 | 95 | 0 | 0 | -31.1594 | 273.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 21 | 8133 | 4.5 | 4.5 | 5.3542 | 5.6589 | 15 | 96 | 96 | 0 | 0 | -40.2321 | 285.9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 22 | 8134 | 4.5 | 4.5 | 5.3542 | 5.6589 | 15 | 97 | 97 | 0 | 0 | -48.66 | 301.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 23 | 8135 | 4.6 | 4.6 | 5.3542 | 5.6589 | 15 | 97 | 97 | 0 | 0 | -55.5907 | 321.1646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 5 | 24 | 8136 | 4.7 | 4.7 | 4.3542 | 5.4809 | 15 | 97 | 97 | 0 | 0 | -59.71 | 346.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 1 | 8137 | 4.9 | 4.9 | 4.3542 | 5.4809 | 15 | 95 | 95 | 0 | 0 | -59.7196 | 13.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 2 | 8138 | 5.1 | 5.1 | 4.3542 | 5.4809 | 15 | 95 | 95 | 0 | 0 | -55.7676 | 38.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 3 | 8139 | 5.9 | 5.9 | 4.3542 | 5.4809 | 15 | 95 | 95 | 0 | 0 | -48.8496 | 58.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 4 | 8140 | 6.7 | 6.7 | 4.3542 | 5.4809 | 15 | 96 | 96 | 0 | 0 | -40.4261 | 73.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 5 | 8141 | 7.2 | 7.2 | 4.3542 | 5.4809 | 15 | 98 | 98 | 0 | 0 | -31.3546 | 86.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 6 | 8142 | 9.2 | 9.2 | 4.3542 | 5.4809 | 15 | 98 | 98 | 0 | 0 | -22.1673 | 98.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 7 | 8143 | 8.3 | 8.3 | 4.3542 | 5.4809 | 15 | 95 | 95 | 0 | 0 | -13.2473 | 109.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 6 | 8 | 8144 | 7.4 | 7.4 | 4.3542 | 5.4809 | 15 | 82 | 82 | 0 | 0 | -4.9309 | 120.9534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 9 | 8145 | 6.5 | 6.5 | 4.3542 | 5.4809 | 15 | 79 | 79 | 0 | 3 | 2.4375 | 132.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 10 | 8146 | 7 | 7 | 4.3542 | 5.4809 | 15 | 68 | 68 | 6.5514 | 30.359 | 8.4844 | 145.2214 | 0 | 0.26325 | 4.8107 | 6.5402 | 4.4384 | 0 | 0 | 0 | 0.64102 | 12.7744 | 15.8129 | 68.2999 | 88.2609 | 64.0029 | 12.7744 | 12.7744 | 12.7744 | 30.359 | 12.7744 | 16.0761 | 73.1107 | 94.8011 | 68.4413 | 12.7744 | 12.7744 | 12.7744 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 11 | 8147 | 6.8 | 6.8 | 4.3542 | 5.4809 | 15 | 65 | 65 | 4.5079 | 49.1522 | 12.8219 | 158.613 | 0 | 0 | 2.5432 | 4.3878 | 3.6621 | 0.79118 | 0 | 0 | 0.84781 | 23.5964 | 23.5964 | 31.8073 | 37.7627 | 35.4197 | 26.1508 | 23.5964 | 23.5964 | 49.1522 | 23.5964 | 23.5964 | 34.3504 | 42.1505 | 39.0818 | 26.9419 | 23.5964 | 23.5964 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 12 | 8148 | 7.5 | 7.5 | 4.3542 | 5.4809 | 15 | 63 | 63 | 92.5611 | 116.3246 | 15.1059 | 172.6955 | 0 | 0 | 32.9122 | 82.6963 | 84.0381 | 36.1515 | 0 | 0 | 22.6754 | 54.9953 | 54.9953 | 89.2378 | 141.0342 | 142.4302 | 92.608 | 54.9953 | 54.9953 | 116.3246 | 54.9953 | 54.9953 | 122.1499 | 223.7305 | 226.4683 | 128.7595 | 54.9953 | 54.9953 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 13 | 8149 | 7.5 | 7.5 | 4.3542 | 5.4809 | 15 | 58 | 58 | 333.4578 | 114.7436 | 15.1266 | 187.0474 | 0 | 0 | 40.9317 | 254.7384 | 319.3228 | 196.8523 | 0 | 0 | 88.2564 | 64.52 | 64.52 | 78.4692 | 151.3327 | 173.3425 | 131.6056 | 64.52 | 64.52 | 114.7436 | 64.52 | 64.52 | 119.4009 | 406.0711 | 492.6653 | 328.4578 | 64.52 | 64.52 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 14 | 8150 | 7.1 | 7.1 | 4.3542 | 5.4809 | 15 | 60 | 60 | 316.7898 | 108.1305 | 12.8819 | 201.1391 | 0 | 0 | 0 | 188.0782 | 303.5031 | 241.14 | 37.5204 | 0 | 77.8695 | 60.684 | 60.684 | 60.684 | 125.9167 | 165.9505 | 144.3206 | 73.6975 | 60.684 | 108.1305 | 60.684 | 60.684 | 60.684 | 313.995 | 469.4536 | 385.4606 | 111.2178 | 60.684 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 15 | 8151 | 6 | 6 | 4.3542 | 5.4809 | 15 | 52 | 52 | 120.6737 | 91.1108 | 8.5786 | 214.5454 | 0 | 0 | 0 | 47.5861 | 109.7205 | 107.5821 | 42.4236 | 0 | 22.8892 | 46.098 | 46.098 | 46.098 | 78.732 | 121.3431 | 119.8766 | 75.1916 | 46.098 | 91.1108 | 46.098 | 46.098 | 46.098 | 126.3181 | 231.0636 | 227.4587 | 117.6152 | 46.098 | 114 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 16 | 8152 | 5.2 | 5.2 | 4.3542 | 5.4809 | 15 | 53 | 53 | 218.5014 | 47.1249 | 2.559 | 227.0874 | 0 | 0 | 0 | 39.2048 | 177.9611 | 212.4702 | 122.5171 | 0 | 21.8751 | 26.8075 | 26.8075 | 26.8075 | 41.893 | 95.2847 | 108.5634 | 73.9506 | 26.8075 | 47.1249 | 26.8075 | 26.8075 | 26.8075 | 81.0978 | 273.2458 | 321.0336 | 196.4677 | 26.8075 | 69 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 17 | 8153 | 4.1 | 4.1 | 4.3542 | 5.4809 | 15 | 59 | 59 | 0 | 6 | -4.789 | 238.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 6 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 2.8226 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 6 | 18 | 8154 | 2.7 | 2.7 | 4.3542 | 5.4809 | 15 | 59 | 59 | 0 | 0 | -13.0915 | 250.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 19 | 8155 | 1 | 1 | 4.3542 | 5.4809 | 15 | 68 | 68 | 0 | 0 | -22.0036 | 261.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 20 | 8156 | -0.1 | -0.1 | 4.3542 | 5.4809 | 15 | 72 | 72 | 0 | 0 | -31.1892 | 272.8394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 21 | 8157 | -0.3 | -0.3 | 4.3542 | 5.4809 | 15 | 75 | 75 | 0 | 0 | -40.2669 | 285.7735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 22 | 8158 | -2.4 | -2.4 | 4.3542 | 5.4809 | 15 | 87 | 87 | 0 | 0 | -48.7083 | 301.2478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 23 | 8159 | -1.7 | -1.7 | 4.3542 | 5.4809 | 15 | 88 | 88 | 0 | 0 | -55.6636 | 320.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 6 | 24 | 8160 | -0.1 | -0.1 | 4.6458 | 5.2968 | 15 | 77 | 77 | 0 | 0 | -59.8169 | 345.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 1 | 8161 | -0.7 | -0.7 | 4.6458 | 5.2968 | 15 | 78 | 78 | 0 | 0 | -59.8567 | 13.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 2 | 8162 | -0.8 | -0.8 | 4.6458 | 5.2968 | 15 | 78 | 78 | 0 | 0 | -55.9135 | 38.6075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 3 | 8163 | -1.3 | -1.3 | 4.6458 | 5.2968 | 15 | 80 | 80 | 0 | 0 | -49.0001 | 58.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 4 | 8164 | -1.6 | -1.6 | 4.6458 | 5.2968 | 15 | 82 | 82 | 0 | 0 | -40.5772 | 73.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 5 | 8165 | -2 | -2 | 4.6458 | 5.2968 | 15 | 84 | 84 | 0 | 0 | -31.5055 | 86.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 6 | 8166 | -2.2 | -2.2 | 4.6458 | 5.2968 | 15 | 83 | 83 | 0 | 0 | -22.3183 | 98.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 7 | 8167 | -2.6 | -2.6 | 4.6458 | 5.2968 | 15 | 85 | 85 | 0 | 0 | -13.3983 | 109.7206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 7 | 8 | 8168 | -3.1 | -3.1 | 4.6458 | 5.2968 | 15 | 87 | 87 | 0 | 0 | -5.0814 | 120.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 9 | 8169 | -2.7 | -2.7 | 4.6458 | 5.2968 | 15 | 84 | 84 | 0 | 6 | 2.2889 | 132.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 10 | 8170 | -1.3 | -1.3 | 4.6458 | 5.2968 | 15 | 77 | 77 | 315.4276 | 41.9577 | 8.3401 | 145.1762 | 0 | 12.8243 | 231.7466 | 314.9149 | 213.6103 | 0 | 0 | 0 | 30.0423 | 21.5994 | 21.5994 | 21.5994 | 21.5994 | 21.5994 | 21.5994 | 21.5994 | 21.5994 | 41.9577 | 21.5994 | 34.4237 | 253.3461 | 336.5143 | 235.2098 | 21.5994 | 21.5994 | 21.5994 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 11 | 8171 | -0.2 | -0.2 | 4.6458 | 5.2968 | 15 | 71 | 71 | 462.5944 | 70.1311 | 12.6855 | 158.5464 | 0 | 0 | 261.3731 | 450.5022 | 375.7332 | 80.8648 | 0 | 0 | 85.8689 | 43.289 | 43.289 | 93.2426 | 129.3888 | 115.099 | 58.7439 | 43.289 | 43.289 | 70.1311 | 43.289 | 43.289 | 354.6157 | 579.891 | 490.8322 | 139.6086 | 43.289 | 43.289 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 12 | 8172 | 1 | 1 | 4.6458 | 5.2968 | 15 | 63 | 63 | 654.0981 | 69.2199 | 14.9817 | 172.6065 | 0 | 0 | 233.3955 | 584.9989 | 593.9179 | 254.9278 | 0 | 0 | 158.7801 | 50.6135 | 50.6135 | 83.0676 | 131.9587 | 133.1989 | 86.0617 | 50.6135 | 50.6135 | 69.2199 | 50.6135 | 50.6135 | 316.4631 | 716.9576 | 727.1168 | 340.9895 | 50.6135 | 50.6135 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 13 | 8173 | 1.7 | 1.7 | 4.6458 | 5.2968 | 15 | 59 | 59 | 700.0675 | 69.0852 | 15.0183 | 186.9384 | 0 | 0 | 87.0242 | 535.7556 | 670.6486 | 412.6848 | 0 | 0 | 183.9148 | 53.597 | 53.597 | 64.7225 | 122.0898 | 139.335 | 106.356 | 53.597 | 53.597 | 69.0852 | 53.597 | 53.597 | 151.7467 | 657.8454 | 809.9836 | 519.0408 | 53.597 | 53.597 | 253 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 14 | 8174 | 2 | 2 | 4.6458 | 5.2968 | 15 | 54 | 54 | 643.552 | 70.8761 | 12.7918 | 201.0147 | 0 | 0 | 0 | 383.2036 | 617.0184 | 489.3921 | 75.0866 | 0 | 157.1239 | 51.6918 | 51.6918 | 51.6918 | 105.5634 | 138.4336 | 120.4916 | 62.2476 | 51.6918 | 70.8761 | 51.6918 | 51.6918 | 51.6918 | 488.7671 | 755.452 | 609.8837 | 137.3342 | 51.6918 | 228 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 15 | 8175 | 1.8 | 1.8 | 4.6458 | 5.2968 | 15 | 50 | 50 | 459.819 | 71.3989 | 8.5069 | 214.411 | 0 | 0 | 0 | 182.2782 | 418.5824 | 409.6868 | 160.8022 | 0 | 86.6011 | 44.3146 | 44.3146 | 44.3146 | 80.6374 | 127.7261 | 125.9535 | 76.3579 | 44.3146 | 71.3989 | 44.3146 | 44.3146 | 44.3146 | 262.9156 | 546.3085 | 535.6402 | 237.16 | 44.3146 | 158 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 16 | 8176 | 1 | 1 | 4.6458 | 5.2968 | 15 | 53 | 53 | 367.1702 | 41.621 | 2.504 | 226.9465 | 0 | 0 | 0 | 66.7299 | 299.5846 | 356.9467 | 205.2143 | 0 | 36.379 | 25.4542 | 25.4542 | 25.4542 | 40.2584 | 91.918 | 104.6439 | 70.9816 | 25.4542 | 41.621 | 25.4542 | 25.4542 | 25.4542 | 106.9883 | 391.5026 | 461.5906 | 276.1959 | 25.4542 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 17 | 8177 | -0.7 | -0.7 | 4.6458 | 5.2968 | 15 | 58 | 58 | 0 | 6 | -4.8301 | 238.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 6 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 7 | 18 | 8178 | -1.3 | -1.3 | 4.6458 | 5.2968 | 15 | 63 | 63 | 0 | 0 | -13.1223 | 249.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 19 | 8179 | -2.1 | -2.1 | 4.6458 | 5.2968 | 15 | 69 | 69 | 0 | 0 | -22.0282 | 261.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 20 | 8180 | -2.1 | -2.1 | 4.6458 | 5.2968 | 15 | 71 | 71 | 0 | 0 | -31.2123 | 272.6649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 21 | 8181 | -2.4 | -2.4 | 4.6458 | 5.2968 | 15 | 72 | 72 | 0 | 0 | -40.2947 | 285.5789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 22 | 8182 | -2.6 | -2.6 | 4.6458 | 5.2968 | 15 | 74 | 74 | 0 | 0 | -48.7493 | 301.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 23 | 8183 | -3.8 | -3.8 | 4.6458 | 5.2968 | 15 | 79 | 79 | 0 | 0 | -55.7289 | 320.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 7 | 24 | 8184 | -3.7 | -3.7 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -59.9161 | 345.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 1 | 8185 | -3.5 | -3.5 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -59.9867 | 13.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 2 | 8186 | -4 | -4 | -1.2375 | 3.4917 | 15 | 82 | 82 | 0 | 0 | -56.0534 | 38.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 3 | 8187 | -3.8 | -3.8 | -1.2375 | 3.4917 | 15 | 81 | 81 | 0 | 0 | -49.1454 | 58.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 4 | 8188 | -4.4 | -4.4 | -1.2375 | 3.4917 | 15 | 83 | 83 | 0 | 0 | -40.7236 | 73.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 5 | 8189 | -5.5 | -5.5 | -1.2375 | 3.4917 | 15 | 86 | 86 | 0 | 0 | -31.6521 | 86.9486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 6 | 8190 | -5.4 | -5.4 | -1.2375 | 3.4917 | 15 | 88 | 88 | 0 | 0 | -22.4648 | 98.5831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 7 | 8191 | -3.9 | -3.9 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -13.5446 | 109.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 8 | 8 | 8192 | -3.9 | -3.9 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -5.2268 | 120.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 9 | 8193 | -4.1 | -4.1 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 6 | 2.1458 | 132.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 10 | 8194 | -2.3 | -2.3 | -1.2375 | 3.4917 | 15 | 76 | 76 | 296.3191 | 41.5154 | 8.202 | 145.1268 | 0 | 12.2128 | 217.8399 | 295.8593 | 200.5684 | 0 | 0 | 0 | 27.4846 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 41.5154 | 20.7573 | 32.9701 | 238.5972 | 316.6166 | 221.3257 | 20.7573 | 20.7573 | 20.7573 | 69 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 11 | 8195 | -0.4 | -0.4 | -1.2375 | 3.4917 | 15 | 71 | 71 | 421.7932 | 72.6889 | 12.5558 | 158.4765 | 0 | 0 | 238.6986 | 410.9749 | 342.5077 | 73.404 | 0 | 0 | 77.3111 | 43.4133 | 43.4133 | 92.2702 | 127.5318 | 113.5179 | 58.4377 | 43.4133 | 43.4133 | 72.6889 | 43.4133 | 43.4133 | 330.9689 | 538.5067 | 456.0256 | 131.8417 | 43.4133 | 43.4133 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 12 | 8196 | 0.6 | 0.6 | -1.2375 | 3.4917 | 15 | 72 | 72 | 580.43 | 77.3284 | 14.8645 | 172.5155 | 0 | 0 | 207.8571 | 519.6519 | 527.0417 | 225.6976 | 0 | 0 | 139.6716 | 51.8787 | 51.8787 | 84.9954 | 134.6721 | 135.8495 | 87.8379 | 51.8787 | 51.8787 | 77.3284 | 51.8787 | 51.8787 | 292.8525 | 654.324 | 662.8912 | 313.5355 | 51.8787 | 51.8787 | 217 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 13 | 8197 | 1.2 | 1.2 | -1.2375 | 3.4917 | 15 | 69 | 69 | 631.2026 | 77.3387 | 14.9173 | 186.8285 | 0 | 0 | 79.4678 | 483.9082 | 604.8818 | 371.5238 | 0 | 0 | 164.6613 | 55.1204 | 55.1204 | 66.9087 | 126.9037 | 144.849 | 110.2325 | 55.1204 | 55.1204 | 77.3387 | 55.1204 | 55.1204 | 146.3765 | 610.8119 | 749.7308 | 481.7563 | 55.1204 | 55.1204 | 242 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 14 | 8198 | 1.8 | 1.8 | -1.2375 | 3.4917 | 15 | 67 | 67 | 582.1817 | 77.7557 | 12.7091 | 200.8907 | 0 | 0 | 0 | 347.6729 | 558.5709 | 442.2656 | 66.8872 | 0 | 141.2443 | 52.9625 | 52.9625 | 52.9625 | 108.9697 | 142.9436 | 124.2078 | 63.7374 | 52.9625 | 77.7557 | 52.9625 | 52.9625 | 52.9625 | 456.6426 | 701.5145 | 566.4734 | 130.6246 | 52.9625 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 15 | 8199 | 1.8 | 1.8 | -1.2375 | 3.4917 | 15 | 68 | 68 | 391.9688 | 76.6583 | 8.4424 | 214.2779 | 0 | 0 | 0 | 156.1879 | 357.2295 | 349.011 | 136.3465 | 0 | 73.3417 | 46.0497 | 46.0497 | 46.0497 | 84.6842 | 134.4137 | 132.3808 | 79.7762 | 46.0497 | 76.6583 | 46.0497 | 46.0497 | 46.0497 | 240.872 | 491.6432 | 481.3917 | 216.1228 | 46.0497 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 16 | 8200 | 0.9 | 0.9 | -1.2375 | 3.4917 | 15 | 72 | 72 | 209.6419 | 46.4226 | 2.4561 | 226.8079 | 0 | 0 | 0 | 38.5802 | 171.3531 | 203.7497 | 116.7925 | 0 | 20.5774 | 26.3289 | 26.3289 | 26.3289 | 41.7606 | 94.8684 | 107.8268 | 73.0447 | 26.3289 | 46.4226 | 26.3289 | 26.3289 | 26.3289 | 80.3407 | 266.2216 | 311.5765 | 189.8373 | 26.3289 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 17 | 8201 | -0.4 | -0.4 | -1.2375 | 3.4917 | 15 | 76 | 76 | 0 | 6 | -4.8644 | 238.5523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 6 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 2.8245 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 18 | 8202 | -1.2 | -1.2 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -13.1464 | 249.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 19 | 8203 | -0.9 | -0.9 | -1.2375 | 3.4917 | 15 | 80 | 80 | 0 | 0 | -22.0462 | 260.8993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 20 | 8204 | -1.3 | -1.3 | -1.2375 | 3.4917 | 15 | 81 | 81 | 0 | 0 | -31.2289 | 272.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 21 | 8205 | -2.2 | -2.2 | -1.2375 | 3.4917 | 15 | 84 | 84 | 0 | 0 | -40.3158 | 285.3887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 22 | 8206 | -2.4 | -2.4 | -1.2375 | 3.4917 | 15 | 87 | 87 | 0 | 0 | -48.783 | 300.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 23 | 8207 | -3.5 | -3.5 | -1.2375 | 3.4917 | 15 | 88 | 88 | 0 | 0 | -55.7865 | 320.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 8 | 24 | 8208 | -2.9 | -2.9 | -2.0708 | 1.7161 | 15 | 93 | 93 | 0 | 0 | -60.0075 | 345.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 1 | 8209 | -2.7 | -2.7 | -2.0708 | 1.7161 | 15 | 85 | 85 | 0 | 0 | -60.1097 | 13.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 2 | 8210 | -3.6 | -3.6 | -2.0708 | 1.7161 | 15 | 88 | 88 | 0 | 0 | -56.1872 | 38.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 3 | 8211 | -3.4 | -3.4 | -2.0708 | 1.7161 | 15 | 91 | 91 | 0 | 0 | -49.2856 | 58.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 4 | 8212 | -3.8 | -3.8 | -2.0708 | 1.7161 | 15 | 89 | 89 | 0 | 0 | -40.8654 | 73.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 5 | 8213 | -4 | -4 | -2.0708 | 1.7161 | 15 | 91 | 91 | 0 | 0 | -31.7941 | 86.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 6 | 8214 | -4.5 | -4.5 | -2.0708 | 1.7161 | 15 | 91 | 91 | 0 | 0 | -22.6068 | 98.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 7 | 8215 | -3.7 | -3.7 | -2.0708 | 1.7161 | 15 | 90 | 90 | 0 | 0 | -13.6862 | 109.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 9 | 8 | 8216 | -4 | -4 | -2.0708 | 1.7161 | 15 | 93 | 93 | 0 | 0 | -5.3671 | 120.8995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 9 | 8217 | -5.3 | -5.3 | -2.0708 | 1.7161 | 15 | 92 | 92 | 0 | 3 | 2.0084 | 132.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 10 | 8218 | -1.9 | -1.9 | -2.0708 | 1.7161 | 15 | 82 | 82 | 243.6031 | 41.9837 | 8.07 | 145.0733 | 0 | 10.1963 | 179.2064 | 243.2398 | 164.7866 | 0 | 0 | 0 | 22.0163 | 19.69 | 19.69 | 19.69 | 19.69 | 19.69 | 19.69 | 19.69 | 19.69 | 41.9837 | 19.69 | 29.8864 | 198.8964 | 262.9298 | 184.4766 | 19.69 | 19.69 | 19.69 | 64 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 11 | 8219 | 0.3 | 0.3 | -2.0708 | 1.7161 | 15 | 73 | 73 | 380.5397 | 75.0934 | 12.4328 | 158.4035 | 0 | 0 | 215.712 | 370.9633 | 308.9093 | 65.9004 | 0 | 0 | 68.9066 | 43.4655 | 43.4655 | 90.8893 | 125.0209 | 111.3785 | 57.9535 | 43.4655 | 43.4655 | 75.0934 | 43.4655 | 43.4655 | 306.6013 | 495.9842 | 420.2878 | 123.8539 | 43.4655 | 43.4655 | 144 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 12 | 8220 | 1.9 | 1.9 | -2.0708 | 1.7161 | 15 | 65 | 65 | 505.3022 | 85.4133 | 14.7544 | 172.4224 | 0 | 0 | 181.6241 | 452.8564 | 458.8115 | 196.0011 | 0 | 0 | 120.5867 | 54.553 | 54.553 | 90.5424 | 144.2879 | 145.4679 | 93.3912 | 54.553 | 54.553 | 85.4133 | 54.553 | 54.553 | 272.1665 | 597.1443 | 604.2794 | 289.3923 | 54.553 | 54.553 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 13 | 8221 | 3.5 | 3.5 | -2.0708 | 1.7161 | 15 | 55 | 55 | 470.8718 | 96.9743 | 14.8235 | 186.7178 | 0 | 0 | 60.0456 | 361.6248 | 451.3691 | 276.7075 | 0 | 0 | 122.0257 | 60.091 | 60.091 | 73.5299 | 141.0267 | 161.1125 | 122.0212 | 60.091 | 60.091 | 96.9743 | 60.091 | 60.091 | 133.5755 | 502.6515 | 612.4815 | 398.7287 | 60.091 | 60.091 | 219 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 14 | 8222 | 4.6 | 4.6 | -2.0708 | 1.7161 | 15 | 47 | 47 | 487.9004 | 88.3222 | 12.6337 | 200.7672 | 0 | 0 | 0 | 292.2111 | 468.4239 | 370.2404 | 55.1751 | 0 | 117.6778 | 55.9094 | 55.9094 | 55.9094 | 116.9001 | 153.6794 | 133.1864 | 67.4257 | 55.9094 | 88.3222 | 55.9094 | 55.9094 | 55.9094 | 409.1111 | 622.1033 | 503.4268 | 122.6007 | 55.9094 | 206 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 15 | 8223 | 5.2 | 5.2 | -2.0708 | 1.7161 | 15 | 41 | 41 | 372.0205 | 77.8038 | 8.3852 | 214.1464 | 0 | 0 | 0 | 148.997 | 339.4279 | 331.0264 | 128.7142 | 0 | 69.1962 | 46.1334 | 46.1334 | 46.1334 | 85.1913 | 135.1105 | 132.9082 | 79.8744 | 46.1334 | 77.8038 | 46.1334 | 46.1334 | 46.1334 | 234.1883 | 474.5384 | 463.9346 | 208.5886 | 46.1334 | 147 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 16 | 8224 | 3.6 | 3.6 | -2.0708 | 1.7161 | 15 | 52 | 52 | 216.8598 | 45.8904 | 2.4152 | 226.6716 | 0 | 0 | 0 | 40.3983 | 177.556 | 210.7038 | 120.4241 | 0 | 21.1096 | 26.124 | 26.124 | 26.124 | 41.6944 | 94.558 | 107.3339 | 72.5381 | 26.124 | 45.8904 | 26.124 | 26.124 | 26.124 | 82.0927 | 272.114 | 318.0377 | 192.9623 | 26.124 | 67 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 17 | 8225 | 1.8 | 1.8 | -2.0708 | 1.7161 | 15 | 63 | 63 | 0 | 3 | -4.8918 | 238.4122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 3 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 1.3917 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 18 | 8226 | 0.9 | 0.9 | -2.0708 | 1.7161 | 15 | 67 | 67 | 0 | 0 | -13.1639 | 249.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 19 | 8227 | -1.8 | -1.8 | -2.0708 | 1.7161 | 15 | 76 | 76 | 0 | 0 | -22.0576 | 260.7464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 20 | 8228 | -1.9 | -1.9 | -2.0708 | 1.7161 | 15 | 76 | 76 | 0 | 0 | -31.2388 | 272.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 21 | 8229 | -2.7 | -2.7 | -2.0708 | 1.7161 | 15 | 78 | 78 | 0 | 0 | -40.33 | 285.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 22 | 8230 | -3.6 | -3.6 | -2.0708 | 1.7161 | 15 | 81 | 81 | 0 | 0 | -48.8097 | 300.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 23 | 8231 | -2.3 | -2.3 | -2.0708 | 1.7161 | 15 | 74 | 74 | 0 | 0 | -55.8364 | 320.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 9 | 24 | 8232 | -3.5 | -3.5 | -1.2875 | 0.72566 | 15 | 82 | 82 | 0 | 0 | -60.091 | 345.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 1 | 8233 | -4.2 | -4.2 | -1.2875 | 0.72566 | 15 | 81 | 81 | 0 | 0 | -60.2254 | 13.1633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 2 | 8234 | -4.2 | -4.2 | -1.2875 | 0.72566 | 15 | 85 | 85 | 0 | 0 | -56.3148 | 38.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 3 | 8235 | -5.8 | -5.8 | -1.2875 | 0.72566 | 15 | 91 | 91 | 0 | 0 | -49.4204 | 58.3109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 4 | 8236 | -5.4 | -5.4 | -1.2875 | 0.72566 | 15 | 91 | 91 | 0 | 0 | -41.0024 | 73.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 5 | 8237 | -6.7 | -6.7 | -1.2875 | 0.72566 | 15 | 92 | 92 | 0 | 0 | -31.9315 | 86.9267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 6 | 8238 | -6.7 | -6.7 | -1.2875 | 0.72566 | 15 | 94 | 94 | 0 | 0 | -22.7442 | 98.5604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 7 | 8239 | -7.2 | -7.2 | -1.2875 | 0.72566 | 15 | 92 | 92 | 0 | 0 | -13.8229 | 109.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 10 | 8 | 8240 | -5.9 | -5.9 | -1.2875 | 0.72566 | 15 | 94 | 94 | 0 | 0 | -5.5021 | 120.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 9 | 8241 | -5.7 | -5.7 | -1.2875 | 0.72566 | 15 | 92 | 92 | 0 | 3 | 1.8768 | 132.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 10 | 8242 | -2 | -2 | -1.2875 | 0.72566 | 15 | 80 | 80 | 482.0943 | 32.5195 | 7.9443 | 145.0158 | 0 | 20.5276 | 354.9152 | 481.3982 | 325.8847 | 0 | 0 | 0 | 42.4805 | 17.2639 | 17.2639 | 17.2639 | 17.2639 | 17.2639 | 17.2639 | 17.2639 | 17.2639 | 32.5195 | 17.2639 | 37.7915 | 372.179 | 498.6621 | 343.1486 | 17.2639 | 17.2639 | 17.2639 | 75 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 11 | 8243 | 0.4 | 0.4 | -1.2875 | 0.72566 | 15 | 72 | 72 | 396.6658 | 73.0051 | 12.3165 | 158.3274 | 0 | 0 | 225.2458 | 386.8717 | 321.8735 | 68.3261 | 0 | 0 | 70.9949 | 42.7721 | 42.7721 | 90.4764 | 124.7068 | 110.941 | 57.2427 | 42.7721 | 42.7721 | 73.0051 | 42.7721 | 42.7721 | 315.7222 | 511.5786 | 432.8145 | 125.5688 | 42.7721 | 42.7721 | 144 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 12 | 8244 | 1.6 | 1.6 | -1.2875 | 0.72566 | 15 | 66 | 66 | 385.5509 | 97.7125 | 14.6514 | 172.3274 | 0 | 0 | 139.1079 | 345.8865 | 350.0494 | 149.1582 | 0 | 0 | 91.2875 | 56.7445 | 56.7445 | 93.2998 | 147.6379 | 148.7319 | 95.9409 | 56.7445 | 56.7445 | 97.7125 | 56.7445 | 56.7445 | 232.4077 | 493.5244 | 498.7813 | 245.0991 | 56.7445 | 56.7445 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 13 | 8245 | 2.9 | 2.9 | -1.2875 | 0.72566 | 15 | 65 | 65 | 422.9763 | 102.0627 | 14.7372 | 186.6065 | 0 | 0 | 54.6359 | 325.4066 | 405.5586 | 248.1398 | 0 | 0 | 108.9373 | 60.9244 | 60.9244 | 74.7231 | 143.1082 | 163.3512 | 123.5939 | 60.9244 | 60.9244 | 102.0627 | 60.9244 | 60.9244 | 129.3589 | 468.5148 | 568.9097 | 371.7337 | 60.9244 | 60.9244 | 211 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 14 | 8246 | 3.2 | 3.2 | -1.2875 | 0.72566 | 15 | 67 | 67 | 346.4676 | 102.885 | 12.5656 | 200.6442 | 0 | 0 | 0 | 208.0979 | 332.8449 | 262.6158 | 38.5499 | 0 | 83.115 | 58.7043 | 58.7043 | 58.7043 | 123.0513 | 161.6249 | 139.909 | 70.6245 | 58.7043 | 102.885 | 58.7043 | 58.7043 | 58.7043 | 331.1492 | 494.4698 | 402.5248 | 109.1744 | 58.7043 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 15 | 8247 | 2.9 | 2.9 | -1.2875 | 0.72566 | 15 | 72 | 72 | 200.6081 | 87.8859 | 8.3352 | 214.0164 | 0 | 0 | 0 | 80.7496 | 183.2301 | 178.3769 | 69.033 | 0 | 37.1141 | 47.413 | 47.413 | 47.413 | 88.3485 | 140.3005 | 137.8402 | 82.4089 | 47.413 | 87.8859 | 47.413 | 47.413 | 47.413 | 169.0981 | 323.5306 | 316.2171 | 151.4418 | 47.413 | 125 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 16 | 8248 | 1.2 | 1.2 | -1.2875 | 0.72566 | 15 | 79 | 79 | 59.2836 | 44.2707 | 2.3814 | 226.5377 | 0 | 0 | 0 | 11.1759 | 48.6198 | 57.5829 | 32.8147 | 0 | 5.7293 | 23.0184 | 23.0184 | 23.0184 | 32.1029 | 62.5398 | 69.8256 | 49.6924 | 23.0184 | 44.2707 | 23.0184 | 23.0184 | 23.0184 | 43.2788 | 111.1596 | 127.4084 | 82.507 | 23.0184 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 17 | 8249 | -1.5 | -1.5 | -1.2875 | 0.72566 | 15 | 85 | 85 | 0 | 3 | -4.9125 | 238.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 3 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 1.3919 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 10 | 18 | 8250 | -2.9 | -2.9 | -1.2875 | 0.72566 | 15 | 90 | 90 | 0 | 0 | -13.1748 | 249.4912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 19 | 8251 | -1.5 | -1.5 | -1.2875 | 0.72566 | 15 | 90 | 90 | 0 | 0 | -22.0625 | 260.5976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 20 | 8252 | -1.4 | -1.4 | -1.2875 | 0.72566 | 15 | 91 | 91 | 0 | 0 | -31.2422 | 272.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 21 | 8253 | -0.3 | -0.3 | -1.2875 | 0.72566 | 15 | 88 | 88 | 0 | 0 | -40.3375 | 285.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 22 | 8254 | 0.3 | 0.3 | -1.2875 | 0.72566 | 15 | 87 | 87 | 0 | 0 | -48.8291 | 300.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 23 | 8255 | -1.2 | -1.2 | -1.2875 | 0.72566 | 15 | 88 | 88 | 0 | 0 | -55.8787 | 319.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 10 | 24 | 8256 | -1.3 | -1.3 | -2.1417 | -0.20987 | 15 | 90 | 90 | 0 | 0 | -60.1668 | 344.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 1 | 8257 | -0.5 | -0.5 | -2.1417 | -0.20987 | 15 | 94 | 94 | 0 | 0 | -60.334 | 12.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 2 | 8258 | 1 | 1 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -56.4361 | 38.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 3 | 8259 | 2 | 2 | -2.1417 | -0.20987 | 15 | 99 | 99 | 0 | 0 | -49.5499 | 58.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 4 | 8260 | 2.3 | 2.3 | -2.1417 | -0.20987 | 15 | 98 | 98 | 0 | 0 | -41.1345 | 73.9024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 5 | 8261 | 2.2 | 2.2 | -2.1417 | -0.20987 | 15 | 98 | 98 | 0 | 0 | -32.0643 | 86.9054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 6 | 8262 | 1.5 | 1.5 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -22.8768 | 98.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 7 | 8263 | 1.5 | 1.5 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -13.9546 | 109.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 11 | 8 | 8264 | 1.6 | 1.6 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -5.6318 | 120.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 9 | 8265 | 1.8 | 1.8 | -2.1417 | -0.20987 | 15 | 96 | 96 | 0 | 0 | 1.7509 | 132.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 10 | 8266 | 1.7 | 1.7 | -2.1417 | -0.20987 | 15 | 95 | 95 | 0.55172 | 7.9526 | 7.8249 | 144.9544 | 0 | 0.023936 | 0.4065 | 0.55094 | 0.37265 | 0 | 0 | 0 | 0.047432 | 3.8125 | 3.8125 | 3.8125 | 3.8125 | 3.8125 | 3.8125 | 3.8125 | 3.8125 | 7.9526 | 3.8125 | 3.8364 | 4.219 | 4.3634 | 4.1851 | 3.8125 | 3.8125 | 3.8125 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 11 | 8267 | 2 | 2 | -2.1417 | -0.20987 | 15 | 92 | 92 | 1.271 | 24.775 | 12.2071 | 158.2483 | 0 | 0 | 0.72308 | 1.2403 | 1.0309 | 0.21767 | 0 | 0 | 0.22498 | 11.9424 | 11.9424 | 11.9424 | 11.9424 | 11.9424 | 11.9424 | 11.9424 | 11.9424 | 24.775 | 11.9424 | 11.9424 | 12.6655 | 13.1826 | 12.9733 | 12.1601 | 11.9424 | 11.9424 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 12 | 8268 | 2.2 | 2.2 | -2.1417 | -0.20987 | 15 | 89 | 89 | 2.5481 | 46.4011 | 14.5557 | 172.2306 | 0 | 0 | 0.92293 | 2.2883 | 2.3131 | 0.98303 | 0 | 0 | 0.59886 | 22.692 | 22.692 | 22.692 | 22.692 | 22.692 | 22.692 | 22.692 | 22.692 | 46.4011 | 22.692 | 22.692 | 23.615 | 24.9803 | 25.0052 | 23.6751 | 22.692 | 22.692 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 13 | 8269 | 2.4 | 2.4 | -2.1417 | -0.20987 | 15 | 87 | 87 | 1.8811 | 43.5183 | 14.6582 | 186.4946 | 0 | 0 | 0.24614 | 1.4497 | 1.804 | 1.1016 | 0 | 0 | 0.4817 | 21.0595 | 21.0595 | 21.0595 | 21.0595 | 21.0595 | 21.0595 | 21.0595 | 21.0595 | 43.5183 | 21.0595 | 21.0595 | 21.3056 | 22.5091 | 22.8635 | 22.161 | 21.0595 | 21.0595 | 44 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 14 | 8270 | 2.6 | 2.6 | -2.1417 | -0.20987 | 15 | 88 | 88 | 1.7006 | 38.594 | 12.505 | 200.5218 | 0 | 0 | 0 | 1.0243 | 1.6347 | 1.2875 | 0.1861 | 0 | 0.40596 | 18.5753 | 18.5753 | 18.5753 | 18.5753 | 18.5753 | 18.5753 | 18.5753 | 18.5753 | 38.594 | 18.5753 | 18.5753 | 18.5753 | 19.5997 | 20.2101 | 19.8628 | 18.7614 | 18.5753 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 15 | 8271 | 2.4 | 2.4 | -2.1417 | -0.20987 | 15 | 92 | 92 | 1.1745 | 24.7837 | 8.2924 | 213.888 | 0 | 0 | 0 | 0.47511 | 1.0739 | 1.0436 | 0.40197 | 0 | 0.21626 | 11.786 | 11.786 | 11.786 | 11.786 | 11.786 | 11.786 | 11.786 | 11.786 | 24.7837 | 11.786 | 11.786 | 11.786 | 12.2611 | 12.8598 | 12.8296 | 12.1879 | 11.786 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 16 | 8272 | 2.6 | 2.6 | -2.1417 | -0.20987 | 15 | 94 | 94 | 0.2486 | 5.9761 | 2.3545 | 226.4064 | 0 | 0 | 0 | 0.047411 | 0.20421 | 0.24139 | 0.13716 | 0 | 0.023879 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 2.7754 | 5.9761 | 2.7754 | 2.7754 | 2.7754 | 2.8228 | 2.9796 | 3.0168 | 2.9126 | 2.7754 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 17 | 8273 | 2.6 | 2.6 | -2.1417 | -0.20987 | 15 | 96 | 96 | 0 | 0 | -4.9263 | 238.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 11 | 18 | 8274 | 3.1 | 3.1 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -13.1791 | 249.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 19 | 8275 | 3.5 | 3.5 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -22.061 | 260.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 20 | 8276 | 4.5 | 4.5 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -31.2391 | 272.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 21 | 8277 | 4.5 | 4.5 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -40.3383 | 284.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 22 | 8278 | 5.1 | 5.1 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -48.8415 | 300.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 23 | 8279 | 5.9 | 5.9 | -2.1417 | -0.20987 | 15 | 97 | 97 | 0 | 0 | -55.9134 | 319.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 11 | 24 | 8280 | 6 | 6 | 2.6875 | 0.24627 | 15 | 96 | 96 | 0 | 0 | -60.2346 | 344.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 1 | 8281 | 3.4 | 3.4 | 2.6875 | 0.24627 | 15 | 96 | 96 | 0 | 0 | -60.4352 | 12.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 2 | 8282 | 1.5 | 1.5 | 2.6875 | 0.24627 | 15 | 97 | 97 | 0 | 0 | -56.5511 | 38.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 3 | 8283 | 1.5 | 1.5 | 2.6875 | 0.24627 | 15 | 98 | 98 | 0 | 0 | -49.6738 | 58.1962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 4 | 8284 | 0.9 | 0.9 | 2.6875 | 0.24627 | 15 | 98 | 98 | 0 | 0 | -41.2616 | 73.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 5 | 8285 | 0 | 0 | 2.6875 | 0.24627 | 15 | 99 | 99 | 0 | 0 | -32.1923 | 86.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 6 | 8286 | -1.1 | -1.1 | 2.6875 | 0.24627 | 15 | 98 | 98 | 0 | 0 | -23.0046 | 98.5124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 7 | 8287 | -1.7 | -1.7 | 2.6875 | 0.24627 | 15 | 98 | 98 | 0 | 0 | -14.0812 | 109.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 12 | 8 | 8288 | -1.7 | -1.7 | 2.6875 | 0.24627 | 15 | 99 | 99 | 0 | 0 | -5.7561 | 120.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 9 | 8289 | -1.4 | -1.4 | 2.6875 | 0.24627 | 15 | 98 | 98 | 0 | 6 | 1.631 | 132.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 2.9206 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 10 | 8290 | -0.1 | -0.1 | 2.6875 | 0.24627 | 15 | 98 | 98 | 23.1181 | 34.0595 | 7.712 | 144.889 | 0 | 1.0235 | 17.048 | 23.0861 | 15.6006 | 0 | 0 | 0 | 1.9405 | 14.5351 | 18.7016 | 83.9374 | 108.5183 | 78.0451 | 14.5351 | 14.5351 | 14.5351 | 34.0595 | 14.5351 | 19.7251 | 100.9854 | 131.6044 | 93.6457 | 14.5351 | 14.5351 | 14.5351 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 11 | 8291 | 1 | 1 | 2.6875 | 0.24627 | 15 | 99 | 99 | 18.7112 | 68.7228 | 12.1045 | 158.1662 | 0 | 0 | 10.6646 | 18.2665 | 15.168 | 3.1844 | 0 | 0 | 3.2772 | 32.0773 | 32.0773 | 78.4395 | 111.4868 | 98.0171 | 45.9208 | 32.0773 | 32.0773 | 68.7228 | 32.0773 | 32.0773 | 89.1041 | 129.7532 | 113.1852 | 49.1052 | 32.0773 | 32.0773 | 72 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 12 | 8292 | 2.6 | 2.6 | 2.6875 | 0.24627 | 15 | 99 | 99 | 26.7029 | 96.7677 | 14.4671 | 172.132 | 0 | 0 | 9.7104 | 24.0039 | 24.2363 | 10.2713 | 0 | 0 | 6.2323 | 45.5866 | 45.5866 | 72.1404 | 111.2271 | 111.8625 | 73.6744 | 45.5866 | 45.5866 | 96.7677 | 45.5866 | 45.5866 | 81.8508 | 135.231 | 136.0987 | 83.9457 | 45.5866 | 45.5866 | 103 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 13 | 8293 | 4 | 4 | 2.6875 | 0.24627 | 15 | 99 | 99 | 32.6925 | 108.6726 | 14.5867 | 186.3822 | 0 | 0 | 4.3334 | 25.2375 | 31.3579 | 19.1091 | 0 | 0 | 8.3274 | 51.539 | 51.539 | 60.58 | 104.1934 | 116.9625 | 91.4074 | 51.539 | 51.539 | 108.6726 | 51.539 | 51.539 | 64.9135 | 129.4309 | 148.3203 | 110.5165 | 51.539 | 51.539 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 14 | 8294 | 4.1 | 4.1 | 2.6875 | 0.24627 | 15 | 98 | 98 | 7.2259 | 76.2827 | 12.4518 | 200.4001 | 0 | 0 | 0 | 4.3645 | 6.9497 | 5.4638 | 0.77734 | 0 | 1.7173 | 37.2561 | 37.2561 | 37.2561 | 42.0256 | 44.8506 | 43.2269 | 38.1055 | 37.2561 | 76.2827 | 37.2561 | 37.2561 | 37.2561 | 46.3901 | 51.8003 | 48.6907 | 38.8829 | 37.2561 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 15 | 8295 | 4.1 | 4.1 | 2.6875 | 0.24627 | 15 | 97 | 97 | 3.3417 | 41.3872 | 8.257 | 213.7614 | 0 | 0 | 0 | 1.3584 | 3.0584 | 2.9669 | 1.1374 | 0 | 0.61279 | 20.1088 | 20.1088 | 20.1088 | 20.1088 | 20.1088 | 20.1088 | 20.1088 | 20.1088 | 41.3872 | 20.1088 | 20.1088 | 20.1088 | 21.4671 | 23.1672 | 23.0757 | 21.2462 | 20.1088 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 16 | 8296 | 4 | 4 | 2.6875 | 0.24627 | 15 | 97 | 97 | 1.3667 | 13.8694 | 2.3347 | 226.2776 | 0 | 0 | 0 | 0.26359 | 1.1244 | 1.3266 | 0.75163 | 0 | 0.13063 | 6.5429 | 6.5429 | 6.5429 | 6.5429 | 6.5429 | 6.5429 | 6.5429 | 6.5429 | 13.8694 | 6.5429 | 6.5429 | 6.5429 | 6.8065 | 7.6673 | 7.8694 | 7.2945 | 6.5429 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 17 | 8297 | 3.8 | 3.8 | 2.6875 | 0.24627 | 15 | 96 | 96 | 0 | 0 | -4.9334 | 238.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 12 | 18 | 8298 | 3.5 | 3.5 | 2.6875 | 0.24627 | 15 | 95 | 95 | 0 | 0 | -13.1767 | 249.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 19 | 8299 | 3.7 | 3.7 | 2.6875 | 0.24627 | 15 | 95 | 95 | 0 | 0 | -22.0529 | 260.3128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 20 | 8300 | 4.4 | 4.4 | 2.6875 | 0.24627 | 15 | 95 | 95 | 0 | 0 | -31.2295 | 271.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 21 | 8301 | 5.2 | 5.2 | 2.6875 | 0.24627 | 15 | 95 | 95 | 0 | 0 | -40.3325 | 284.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 22 | 8302 | 6 | 6 | 2.6875 | 0.24627 | 15 | 97 | 97 | 0 | 0 | -48.8468 | 299.9912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 23 | 8303 | 7.2 | 7.2 | 2.6875 | 0.24627 | 15 | 97 | 97 | 0 | 0 | -55.9405 | 319.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 12 | 24 | 8304 | 8.3 | 8.3 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0 | 0 | -60.2946 | 344.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 1 | 8305 | 9.3 | 9.3 | 2.6333 | 0.68004 | 15 | 98 | 98 | 0 | 0 | -60.5289 | 12.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 2 | 8306 | 10.3 | 10.3 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0 | 0 | -56.6596 | 38.0167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 3 | 8307 | 10.7 | 10.7 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0 | 0 | -49.7922 | 58.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 4 | 8308 | 11 | 11 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0 | 0 | -41.3837 | 73.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 5 | 8309 | 11.4 | 11.4 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0 | 0 | -32.3154 | 86.8421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 6 | 8310 | 11.4 | 11.4 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0 | 0 | -23.1274 | 98.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 7 | 8311 | 11.5 | 11.5 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0 | 0 | -14.2027 | 109.5858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 13 | 8 | 8312 | 11.9 | 11.9 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -5.8748 | 120.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 9 | 8313 | 11.8 | 11.8 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | 1.517 | 132.4064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 10 | 8314 | 12.1 | 12.1 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0.085196 | 2.993 | 7.6055 | 144.8199 | 0 | 0.003854 | 0.062885 | 0.085079 | 0.057435 | 0 | 0 | 0 | 0.0069883 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 1.3941 | 2.993 | 1.3941 | 1.3979 | 1.457 | 1.4792 | 1.4515 | 1.3941 | 1.3941 | 1.3941 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 11 | 8315 | 12 | 12 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0.13556 | 7.9765 | 12.0089 | 158.0813 | 0 | 0 | 0.077415 | 0.1324 | 0.10982 | 0.022916 | 0 | 0 | 0.023507 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 3.72 | 7.9765 | 3.72 | 3.72 | 3.7974 | 3.8524 | 3.8298 | 3.7429 | 3.72 | 3.72 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 12 | 8316 | 12 | 12 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0.23215 | 13.9462 | 14.3859 | 172.0316 | 0 | 0 | 0.084763 | 0.20889 | 0.21065 | 0.089019 | 0 | 0 | 0.053834 | 6.5398 | 6.5398 | 6.5398 | 6.5398 | 6.5398 | 6.5398 | 6.5398 | 6.5398 | 13.9462 | 6.5398 | 6.5398 | 6.6245 | 6.7487 | 6.7504 | 6.6288 | 6.5398 | 6.5398 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 13 | 8317 | 12 | 12 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0.19428 | 13.9508 | 14.5226 | 186.2693 | 0 | 0 | 0.026087 | 0.15023 | 0.18637 | 0.11334 | 0 | 0 | 0.049247 | 6.5339 | 6.5339 | 6.5339 | 6.5339 | 6.5339 | 6.5339 | 6.5339 | 6.5339 | 13.9508 | 6.5339 | 6.5339 | 6.56 | 6.6841 | 6.7203 | 6.6472 | 6.5339 | 6.5339 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 14 | 8318 | 11.9 | 11.9 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0.13753 | 10.9674 | 12.406 | 200.2791 | 0 | 0 | 0 | 0.083295 | 0.13234 | 0.10386 | 0.014538 | 0 | 0.032556 | 5.1194 | 5.1194 | 5.1194 | 5.1194 | 5.1194 | 5.1194 | 5.1194 | 5.1194 | 10.9674 | 5.1194 | 5.1194 | 5.1194 | 5.2027 | 5.2517 | 5.2232 | 5.1339 | 5.1194 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 15 | 8319 | 11.8 | 11.8 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0.017165 | 2.9969 | 8.2288 | 213.6367 | 0 | 0 | 0 | 0.0070109 | 0.015725 | 0.015228 | 0.0058105 | 0 | 0.0031368 | 1.3849 | 1.3849 | 1.3849 | 1.3849 | 1.3849 | 1.3849 | 1.3849 | 1.3849 | 2.9969 | 1.3849 | 1.3849 | 1.3849 | 1.3919 | 1.4007 | 1.4002 | 1.3907 | 1.3849 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 16 | 8320 | 11.5 | 11.5 | 2.6333 | 0.68004 | 15 | 97 | 97 | 0.063215 | 2.994 | 2.322 | 226.1514 | 0 | 0 | 0 | 0.012327 | 0.052089 | 0.061338 | 0.034656 | 0 | 0.0060197 | 1.3822 | 1.3822 | 1.3822 | 1.3822 | 1.3822 | 1.3822 | 1.3822 | 1.3822 | 2.994 | 1.3822 | 1.3822 | 1.3822 | 1.3945 | 1.4343 | 1.4436 | 1.4169 | 1.3822 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 17 | 8321 | 11.6 | 11.6 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -4.9337 | 237.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 13 | 18 | 8322 | 11.7 | 11.7 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -13.1679 | 249.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 19 | 8323 | 11.5 | 11.5 | 2.6333 | 0.68004 | 15 | 96 | 96 | 0 | 0 | -22.0385 | 260.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 20 | 8324 | 11.8 | 11.8 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -31.2135 | 271.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 21 | 8325 | 11.8 | 11.8 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -40.32 | 284.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 22 | 8326 | 11.8 | 11.8 | 2.6333 | 0.68004 | 15 | 95 | 95 | 0 | 0 | -48.8452 | 299.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 23 | 8327 | 11.4 | 11.4 | 2.6333 | 0.68004 | 15 | 92 | 92 | 0 | 0 | -55.96 | 319.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 13 | 24 | 8328 | 10.4 | 10.4 | 11.4417 | 3.3438 | 15 | 83 | 83 | 0 | 0 | -60.3466 | 344.2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 1 | 8329 | 9.9 | 9.9 | 11.4417 | 3.3438 | 15 | 79 | 79 | 0 | 0 | -60.6152 | 12.4416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 2 | 8330 | 9.8 | 9.8 | 11.4417 | 3.3438 | 15 | 82 | 82 | 0 | 0 | -56.7615 | 37.8901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 3 | 8331 | 9.1 | 9.1 | 11.4417 | 3.3438 | 15 | 88 | 88 | 0 | 0 | -49.905 | 58.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 4 | 8332 | 6.8 | 6.8 | 11.4417 | 3.3438 | 15 | 87 | 87 | 0 | 0 | -41.5006 | 73.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 5 | 8333 | 7.6 | 7.6 | 11.4417 | 3.3438 | 15 | 83 | 83 | 0 | 0 | -32.4336 | 86.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 6 | 8334 | 7.9 | 7.9 | 11.4417 | 3.3438 | 15 | 81 | 81 | 0 | 0 | -23.2453 | 98.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 7 | 8335 | 7.7 | 7.7 | 11.4417 | 3.3438 | 15 | 79 | 79 | 0 | 0 | -14.319 | 109.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 14 | 8 | 8336 | 6.5 | 6.5 | 11.4417 | 3.3438 | 15 | 89 | 89 | 0 | 0 | -5.988 | 120.7042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 9 | 8337 | 6.5 | 6.5 | 11.4417 | 3.3438 | 15 | 88 | 88 | 0 | 0 | 1.409 | 132.3466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 10 | 8338 | 7 | 7 | 11.4417 | 3.3438 | 15 | 85 | 85 | 29.0078 | 33.6727 | 7.5055 | 144.7469 | 0 | 1.3425 | 21.4327 | 28.968 | 19.5342 | 0 | 0 | 0 | 2.3273 | 14.1773 | 18.7481 | 87.1496 | 112.805 | 80.6856 | 14.1773 | 14.1773 | 14.1773 | 33.6727 | 14.1773 | 20.0905 | 108.5823 | 141.773 | 100.2198 | 14.1773 | 14.1773 | 14.1773 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 11 | 8339 | 7.8 | 7.8 | 11.4417 | 3.3438 | 15 | 83 | 83 | 59.5104 | 78.7766 | 11.9202 | 157.9936 | 0 | 0 | 34.0545 | 58.1489 | 48.1805 | 9.9886 | 0 | 0 | 10.2234 | 36.2781 | 36.2781 | 101.8211 | 148.1945 | 129.0088 | 55.5027 | 36.2781 | 36.2781 | 78.7766 | 36.2781 | 36.2781 | 135.8756 | 206.3434 | 177.1893 | 65.4913 | 36.2781 | 36.2781 | 89 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 12 | 8340 | 8.7 | 8.7 | 11.4417 | 3.3438 | 15 | 81 | 81 | 201.533 | 109.5441 | 14.312 | 171.9297 | 0 | 0 | 73.8881 | 181.5203 | 182.8205 | 77.0268 | 0 | 0 | 46.4559 | 57.2534 | 57.2534 | 98.9084 | 159.5871 | 160.32 | 100.6779 | 57.2534 | 57.2534 | 109.5441 | 57.2534 | 57.2534 | 172.7965 | 341.1074 | 343.1405 | 177.7048 | 57.2534 | 57.2534 | 156 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 13 | 8341 | 7.7 | 7.7 | 11.4417 | 3.3438 | 15 | 89 | 89 | 4.0949 | 62.9665 | 14.466 | 186.1561 | 0 | 0 | 0.55704 | 3.1718 | 3.9285 | 2.384 | 0 | 0 | 1.0335 | 31.1452 | 31.1452 | 31.1452 | 31.1452 | 31.1452 | 31.1452 | 31.1452 | 31.1452 | 62.9665 | 31.1452 | 31.1452 | 31.7022 | 34.3169 | 35.0737 | 33.5292 | 31.1452 | 31.1452 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 14 | 8342 | 9.5 | 9.5 | 11.4417 | 3.3438 | 15 | 80 | 80 | 765.9849 | 45.8085 | 12.3676 | 200.1591 | 0 | 0 | 0 | 465.195 | 737.4232 | 577.6789 | 79.5381 | 0 | 204.1915 | 46.2875 | 46.2875 | 46.2875 | 81.8891 | 102.7228 | 90.4975 | 52.3746 | 46.2875 | 45.8085 | 46.2875 | 46.2875 | 46.2875 | 547.0841 | 840.1461 | 668.1764 | 131.9127 | 46.2875 | 250 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 15 | 8343 | 7.6 | 7.6 | 11.4417 | 3.3438 | 15 | 88 | 88 | 7.6925 | 59.5982 | 8.2078 | 213.5138 | 0 | 0 | 0 | 3.1566 | 7.0537 | 6.8188 | 2.5895 | 0 | 1.4018 | 29.4675 | 29.4675 | 29.4675 | 30.1749 | 31.0483 | 30.9957 | 30.0478 | 29.4675 | 59.5982 | 29.4675 | 29.4675 | 29.4675 | 33.3315 | 38.102 | 37.8144 | 32.6373 | 29.4675 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 16 | 8344 | 7.6 | 7.6 | 11.4417 | 3.3438 | 15 | 91 | 91 | 7.0994 | 30.3257 | 2.3162 | 226.0281 | 0 | 0 | 0 | 1.3992 | 5.8585 | 6.886 | 3.8797 | 0 | 0.67433 | 14.7773 | 14.7773 | 14.7773 | 14.7773 | 14.7773 | 14.7773 | 14.7773 | 14.7773 | 30.3257 | 14.7773 | 14.7773 | 14.7773 | 16.1766 | 20.6358 | 21.6633 | 18.657 | 14.7773 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 17 | 8345 | 7.5 | 7.5 | 11.4417 | 3.3438 | 15 | 86 | 86 | 0 | 6 | -4.9273 | 237.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 6 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 2.8271 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 14 | 18 | 8346 | 7.6 | 7.6 | 11.4417 | 3.3438 | 15 | 84 | 84 | 0 | 0 | -13.1526 | 248.9645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 19 | 8347 | 6.8 | 6.8 | 11.4417 | 3.3438 | 15 | 86 | 86 | 0 | 0 | -22.0177 | 260.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 20 | 8348 | 7.2 | 7.2 | 11.4417 | 3.3438 | 15 | 86 | 86 | 0 | 0 | -31.1911 | 271.5701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 21 | 8349 | 6.1 | 6.1 | 11.4417 | 3.3438 | 15 | 91 | 91 | 0 | 0 | -40.301 | 284.3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 22 | 8350 | 5.7 | 5.7 | 11.4417 | 3.3438 | 15 | 83 | 83 | 0 | 0 | -48.8365 | 299.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 23 | 8351 | 5.5 | 5.5 | 11.4417 | 3.3438 | 15 | 75 | 75 | 0 | 0 | -55.9719 | 319.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 14 | 24 | 8352 | 5.2 | 5.2 | 7.4708 | 4.7081 | 15 | 68 | 68 | 0 | 0 | -60.3907 | 344.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 1 | 8353 | 3.5 | 3.5 | 7.4708 | 4.7081 | 15 | 80 | 80 | 0 | 0 | -60.694 | 12.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 2 | 8354 | 2.1 | 2.1 | 7.4708 | 4.7081 | 15 | 90 | 90 | 0 | 0 | -56.8569 | 37.7558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 3 | 8355 | 1.5 | 1.5 | 7.4708 | 4.7081 | 15 | 89 | 89 | 0 | 0 | -50.0119 | 57.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 4 | 8356 | 2.7 | 2.7 | 7.4708 | 4.7081 | 15 | 79 | 79 | 0 | 0 | -41.6123 | 73.7074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 5 | 8357 | 2.3 | 2.3 | 7.4708 | 4.7081 | 15 | 85 | 85 | 0 | 0 | -32.5468 | 86.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 6 | 8358 | 1.9 | 1.9 | 7.4708 | 4.7081 | 15 | 87 | 87 | 0 | 0 | -23.3581 | 98.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 7 | 8359 | 1.2 | 1.2 | 7.4708 | 4.7081 | 15 | 89 | 89 | 0 | 0 | -14.43 | 109.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 15 | 8 | 8360 | 3 | 3 | 7.4708 | 4.7081 | 15 | 80 | 80 | 0 | 0 | -6.0955 | 120.6497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 9 | 8361 | 2.6 | 2.6 | 7.4708 | 4.7081 | 15 | 82 | 82 | 0 | 3 | 1.3072 | 132.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 1.4591 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 10 | 8362 | 3.9 | 3.9 | 7.4708 | 4.7081 | 15 | 76 | 76 | 86.5907 | 37.1984 | 7.4121 | 144.6703 | 0 | 4.1045 | 64.0464 | 86.4708 | 58.2418 | 0 | 0 | 0 | 6.8016 | 15.6498 | 21.0974 | 100.656 | 130.419 | 92.9518 | 15.6498 | 15.6498 | 15.6498 | 37.1984 | 15.6498 | 25.2019 | 164.7023 | 216.8898 | 151.1936 | 15.6498 | 15.6498 | 15.6498 | 44 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 11 | 8363 | 4.5 | 4.5 | 7.4708 | 4.7081 | 15 | 74 | 74 | 123.4256 | 81.981 | 11.8386 | 157.9032 | 0 | 0 | 70.7782 | 120.6551 | 99.8539 | 20.5596 | 0 | 0 | 21.019 | 39.0563 | 39.0563 | 121.1063 | 178.9264 | 154.8125 | 62.8902 | 39.0563 | 39.0563 | 81.981 | 39.0563 | 39.0563 | 191.8845 | 299.5815 | 254.6664 | 83.4498 | 39.0563 | 39.0563 | 103 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 12 | 8364 | 4.8 | 4.8 | 7.4708 | 4.7081 | 15 | 75 | 75 | 174.5433 | 109.9846 | 14.2454 | 171.8262 | 0 | 0 | 64.2619 | 157.363 | 158.283 | 66.483 | 0 | 0 | 40.0154 | 54.5604 | 54.5604 | 99.1589 | 163.7722 | 164.4107 | 100.7004 | 54.5604 | 54.5604 | 109.9846 | 54.5604 | 54.5604 | 163.4208 | 321.1353 | 322.6937 | 167.1834 | 54.5604 | 54.5604 | 150 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 13 | 8365 | 5.7 | 5.7 | 7.4708 | 4.7081 | 15 | 75 | 75 | 210.7937 | 119.0053 | 14.4168 | 186.0426 | 0 | 0 | 29.0484 | 163.5431 | 202.2364 | 122.4624 | 0 | 0 | 52.9947 | 62.5666 | 62.5666 | 78.6455 | 153.0912 | 174.5088 | 130.3521 | 62.5666 | 62.5666 | 119.0053 | 62.5666 | 62.5666 | 107.6939 | 316.6342 | 376.7451 | 252.8145 | 62.5666 | 62.5666 | 172 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 14 | 8366 | 5.7 | 5.7 | 7.4708 | 4.7081 | 15 | 69 | 69 | 111.0266 | 112.8834 | 12.3367 | 200.04 | 0 | 0 | 0 | 67.6089 | 106.9329 | 83.6171 | 11.3195 | 0 | 26.1166 | 55.7217 | 55.7217 | 55.7217 | 116.3152 | 151.5588 | 130.6623 | 65.8667 | 55.7217 | 112.8834 | 55.7217 | 55.7217 | 55.7217 | 183.9241 | 258.4917 | 214.2794 | 77.1862 | 55.7217 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 15 | 8367 | 4.2 | 4.2 | 7.4708 | 4.7081 | 15 | 84 | 84 | 31.613 | 77.2518 | 8.1941 | 213.393 | 0 | 0 | 0 | 13.0322 | 29.0131 | 27.9986 | 10.5829 | 0 | 5.7482 | 37.7419 | 37.7419 | 37.7419 | 56.0508 | 78.5025 | 77.0771 | 52.6097 | 37.7419 | 77.2518 | 37.7419 | 37.7419 | 37.7419 | 69.083 | 107.5156 | 105.0757 | 63.1926 | 37.7419 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 16 | 8368 | 4.2 | 4.2 | 7.4708 | 4.7081 | 15 | 75 | 75 | 27.0967 | 39.4297 | 2.3174 | 225.9076 | 0 | 0 | 0 | 5.3961 | 22.3925 | 26.2716 | 14.7612 | 0 | 2.5703 | 19.967 | 19.967 | 19.967 | 24.2262 | 37.6416 | 40.7034 | 31.6181 | 19.967 | 39.4297 | 19.967 | 19.967 | 19.967 | 29.6224 | 60.034 | 66.975 | 46.3793 | 19.967 | 42 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 17 | 8369 | 2.9 | 2.9 | 7.4708 | 4.7081 | 15 | 90 | 90 | 0 | 3 | -4.9142 | 237.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 3 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 1.3922 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 18 | 8370 | 2.5 | 2.5 | 7.4708 | 4.7081 | 15 | 89 | 89 | 0 | 0 | -13.1307 | 248.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 19 | 8371 | 2.1 | 2.1 | 7.4708 | 4.7081 | 15 | 91 | 91 | 0 | 0 | -21.9905 | 259.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 20 | 8372 | 3.4 | 3.4 | 7.4708 | 4.7081 | 15 | 82 | 82 | 0 | 0 | -31.1624 | 271.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 21 | 8373 | 2.5 | 2.5 | 7.4708 | 4.7081 | 15 | 85 | 85 | 0 | 0 | -40.2755 | 284.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 22 | 8374 | 2.5 | 2.5 | 7.4708 | 4.7081 | 15 | 88 | 88 | 0 | 0 | -48.821 | 299.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 23 | 8375 | 4.1 | 4.1 | 7.4708 | 4.7081 | 15 | 83 | 83 | 0 | 0 | -55.9763 | 318.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 15 | 24 | 8376 | 3.7 | 3.7 | 3.2292 | 4.6217 | 15 | 85 | 85 | 0 | 0 | -60.4268 | 343.7863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 1 | 8377 | 3.9 | 3.9 | 3.2292 | 4.6217 | 15 | 87 | 87 | 0 | 0 | -60.7652 | 12.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 2 | 8378 | 4.3 | 4.3 | 3.2292 | 4.6217 | 15 | 81 | 81 | 0 | 0 | -56.9455 | 37.6139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 3 | 8379 | 3.7 | 3.7 | 3.2292 | 4.6217 | 15 | 83 | 83 | 0 | 0 | -50.1131 | 57.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 4 | 8380 | 4 | 4 | 3.2292 | 4.6217 | 15 | 86 | 86 | 0 | 0 | -41.7186 | 73.6399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 5 | 8381 | 4.3 | 4.3 | 3.2292 | 4.6217 | 15 | 87 | 87 | 0 | 0 | -32.6548 | 86.6959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 6 | 8382 | 3.1 | 3.1 | 3.2292 | 4.6217 | 15 | 91 | 91 | 0 | 0 | -23.4658 | 98.3417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 7 | 8383 | 1.7 | 1.7 | 3.2292 | 4.6217 | 15 | 94 | 94 | 0 | 0 | -14.5356 | 109.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 16 | 8 | 8384 | 1.3 | 1.3 | 3.2292 | 4.6217 | 15 | 96 | 96 | 0 | 0 | -6.1972 | 120.5902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 9 | 8385 | 2.7 | 2.7 | 3.2292 | 4.6217 | 15 | 97 | 97 | 0 | 0 | 1.2115 | 132.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 10 | 8386 | 4 | 4 | 3.2292 | 4.6217 | 15 | 95 | 95 | 22.9972 | 31.2295 | 7.3253 | 144.5901 | 0 | 1.1176 | 17.0289 | 22.9649 | 15.4484 | 0 | 0 | 0 | 1.7705 | 13.1838 | 17.5417 | 79.5833 | 102.729 | 73.4204 | 13.1838 | 13.1838 | 13.1838 | 31.2295 | 13.1838 | 18.6593 | 96.6122 | 125.6939 | 88.8688 | 13.1838 | 13.1838 | 13.1838 | 33 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 11 | 8387 | 6.1 | 6.1 | 3.2292 | 4.6217 | 15 | 85 | 85 | 97.206 | 80.5794 | 11.7641 | 157.8101 | 0 | 0 | 55.8636 | 95.0652 | 78.5789 | 16.0622 | 0 | 0 | 16.4206 | 38.0336 | 38.0336 | 119.3374 | 176.3914 | 152.3973 | 61.4104 | 38.0336 | 38.0336 | 80.5794 | 38.0336 | 38.0336 | 175.201 | 271.4566 | 230.9762 | 77.4726 | 38.0336 | 38.0336 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 12 | 8388 | 7.1 | 7.1 | 3.2292 | 4.6217 | 15 | 84 | 84 | 193.8448 | 108.7787 | 14.1862 | 171.7212 | 0 | 0 | 71.6731 | 174.932 | 175.7181 | 73.5709 | 0 | 0 | 44.2213 | 54.492 | 54.492 | 98.88 | 162.8293 | 163.3161 | 100.0553 | 54.492 | 54.492 | 108.7787 | 54.492 | 54.492 | 170.5531 | 337.7613 | 339.0342 | 173.6262 | 54.492 | 54.492 | 153 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 13 | 8389 | 7.4 | 7.4 | 3.2292 | 4.6217 | 15 | 84 | 84 | 62.1653 | 115.4244 | 14.3752 | 185.9289 | 0 | 0 | 8.6782 | 48.3093 | 59.6414 | 36.0365 | 0 | 0 | 15.5756 | 54.7567 | 54.7567 | 65.8559 | 116.5428 | 131.0363 | 100.8463 | 54.7567 | 54.7567 | 115.4244 | 54.7567 | 54.7567 | 74.5341 | 164.8521 | 190.6778 | 136.8827 | 54.7567 | 54.7567 | 131 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 14 | 8390 | 7.7 | 7.7 | 3.2292 | 4.6217 | 15 | 83 | 83 | 9.4048 | 80.793 | 12.3133 | 199.9219 | 0 | 0 | 0 | 5.7421 | 9.0616 | 7.0729 | 0.94104 | 0 | 2.207 | 39.0378 | 39.0378 | 39.0378 | 47.5644 | 52.4935 | 49.5405 | 40.4352 | 39.0378 | 80.793 | 39.0378 | 39.0378 | 39.0378 | 53.3064 | 61.5551 | 56.6135 | 41.3763 | 39.0378 | 83 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 15 | 8391 | 7.3 | 7.3 | 3.2292 | 4.6217 | 15 | 85 | 85 | 5.425 | 52.015 | 8.1877 | 213.2742 | 0 | 0 | 0 | 2.2465 | 4.983 | 4.8006 | 1.806 | 0 | 0.98496 | 25.6295 | 25.6295 | 25.6295 | 25.6295 | 25.6295 | 25.6295 | 25.6295 | 25.6295 | 52.015 | 25.6295 | 25.6295 | 25.6295 | 27.876 | 30.6125 | 30.43 | 27.4355 | 25.6295 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 16 | 8392 | 7 | 7 | 3.2292 | 4.6217 | 15 | 86 | 86 | 0.45288 | 7.957 | 2.3256 | 225.7901 | 0 | 0 | 0 | 0.091099 | 0.37477 | 0.43891 | 0.24594 | 0 | 0.042956 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 7.957 | 3.7103 | 3.7103 | 3.7103 | 3.8014 | 4.0851 | 4.1492 | 3.9563 | 3.7103 | 8 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 17 | 8393 | 7 | 7 | 3.2292 | 4.6217 | 15 | 86 | 86 | 0 | 0 | -4.8944 | 237.5237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 18 | 8394 | 6.1 | 6.1 | 3.2292 | 4.6217 | 15 | 85 | 85 | 0 | 0 | -13.1025 | 248.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 19 | 8395 | 5.8 | 5.8 | 3.2292 | 4.6217 | 15 | 85 | 85 | 0 | 0 | -21.9571 | 259.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 20 | 8396 | 5.8 | 5.8 | 3.2292 | 4.6217 | 15 | 85 | 85 | 0 | 0 | -31.1274 | 271.3021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 21 | 8397 | 5.4 | 5.4 | 3.2292 | 4.6217 | 15 | 86 | 86 | 0 | 0 | -40.2435 | 284.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 22 | 8398 | 5.4 | 5.4 | 3.2292 | 4.6217 | 15 | 87 | 87 | 0 | 0 | -48.7986 | 299.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 23 | 8399 | 5.3 | 5.3 | 3.2292 | 4.6217 | 15 | 86 | 86 | 0 | 0 | -55.9733 | 318.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 16 | 24 | 8400 | 5.1 | 5.1 | 5.0625 | 5.0738 | 15 | 86 | 86 | 0 | 0 | -60.455 | 343.5546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 1 | 8401 | 5 | 5 | 5.0625 | 5.0738 | 15 | 86 | 86 | 0 | 0 | -60.8287 | 11.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 2 | 8402 | 4.8 | 4.8 | 5.0625 | 5.0738 | 15 | 84 | 84 | 0 | 0 | -57.0273 | 37.4645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 3 | 8403 | 4.8 | 4.8 | 5.0625 | 5.0738 | 15 | 82 | 82 | 0 | 0 | -50.2083 | 57.7674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 4 | 8404 | 4.6 | 4.6 | 5.0625 | 5.0738 | 15 | 84 | 84 | 0 | 0 | -41.8196 | 73.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 5 | 8405 | 4.4 | 4.4 | 5.0625 | 5.0738 | 15 | 84 | 84 | 0 | 0 | -32.7576 | 86.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 6 | 8406 | 4 | 4 | 5.0625 | 5.0738 | 15 | 86 | 86 | 0 | 0 | -23.5682 | 98.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 7 | 8407 | 4.3 | 4.3 | 5.0625 | 5.0738 | 15 | 86 | 86 | 0 | 0 | -14.6358 | 109.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 17 | 8 | 8408 | 4.2 | 4.2 | 5.0625 | 5.0738 | 15 | 86 | 86 | 0 | 0 | -6.2932 | 120.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 9 | 8409 | 4.6 | 4.6 | 5.0625 | 5.0738 | 15 | 83 | 83 | 0 | 0 | 1.122 | 132.1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 10 | 8410 | 4 | 4 | 5.0625 | 5.0738 | 15 | 86 | 86 | 2.1863 | 13.8348 | 7.2453 | 144.5063 | 0 | 0.10903 | 1.6208 | 2.1832 | 1.4666 | 0 | 0 | 0 | 0.16516 | 6.4666 | 7.046 | 15.0789 | 18.0669 | 14.2596 | 6.4666 | 6.4666 | 6.4666 | 13.8348 | 6.4666 | 7.155 | 16.6997 | 20.25 | 15.7262 | 6.4666 | 6.4666 | 6.4666 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 11 | 8411 | 5.3 | 5.3 | 5.0625 | 5.0738 | 15 | 83 | 83 | 86.823 | 79.4418 | 11.6966 | 157.7145 | 0 | 0 | 50.0081 | 84.947 | 70.1251 | 14.2249 | 0 | 0 | 14.5582 | 37.3803 | 37.3803 | 118.2555 | 174.7602 | 150.7896 | 60.3853 | 37.3803 | 37.3803 | 79.4418 | 37.3803 | 37.3803 | 168.2636 | 259.7072 | 220.9147 | 74.6102 | 37.3803 | 37.3803 | 94 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 12 | 8412 | 6.3 | 6.3 | 5.0625 | 5.0738 | 15 | 74 | 74 | 421.1817 | 90.3399 | 14.1344 | 171.6148 | 0 | 0 | 156.4049 | 380.4475 | 381.629 | 159.2575 | 0 | 0 | 95.6601 | 53.9501 | 53.9501 | 90.9106 | 143.8547 | 144.134 | 91.5847 | 53.9501 | 53.9501 | 90.3399 | 53.9501 | 53.9501 | 247.3156 | 524.3022 | 525.763 | 250.8422 | 53.9501 | 53.9501 | 186 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 13 | 8413 | 6.6 | 6.6 | 5.0625 | 5.0738 | 15 | 67 | 67 | 491.1406 | 91.3006 | 14.3412 | 185.8151 | 0 | 0 | 69.4531 | 382.2855 | 471.1803 | 284.064 | 0 | 0 | 122.6994 | 57.6289 | 57.6289 | 72.2223 | 137.9544 | 156.6329 | 117.3162 | 57.6289 | 57.6289 | 91.3006 | 57.6289 | 57.6289 | 141.6754 | 520.2399 | 627.8132 | 401.3802 | 57.6289 | 57.6289 | 214 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 14 | 8414 | 7 | 7 | 5.0625 | 5.0738 | 15 | 66 | 66 | 438.1217 | 91.3779 | 12.2973 | 199.8049 | 0 | 0 | 0 | 268.19 | 422.2846 | 329.0105 | 43.0066 | 0 | 102.6221 | 55.6858 | 55.6858 | 55.6858 | 118.9094 | 155.2359 | 133.2473 | 65.8243 | 55.6858 | 91.3779 | 55.6858 | 55.6858 | 55.6858 | 387.0994 | 577.5204 | 462.2578 | 108.8308 | 55.6858 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 15 | 8415 | 6.4 | 6.4 | 5.0625 | 5.0738 | 15 | 67 | 67 | 330.3739 | 79.0674 | 8.1885 | 213.1576 | 0 | 0 | 0 | 137.4137 | 303.701 | 292.0843 | 109.3686 | 0 | 59.9326 | 45.7141 | 45.7141 | 45.7141 | 86.5299 | 135.922 | 132.4715 | 78.1997 | 45.7141 | 79.0674 | 45.7141 | 45.7141 | 45.7141 | 223.9437 | 439.6229 | 424.5558 | 187.5683 | 45.7141 | 139 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 16 | 8416 | 4.9 | 4.9 | 5.0625 | 5.0738 | 15 | 72 | 72 | 161.0651 | 45.7052 | 2.3407 | 225.6756 | 0 | 0 | 0 | 32.7167 | 133.464 | 156.0298 | 87.1955 | 0 | 15.2948 | 25.3458 | 25.3458 | 25.3458 | 41.4366 | 90.9864 | 102.0848 | 68.2305 | 25.3458 | 45.7052 | 25.3458 | 25.3458 | 25.3458 | 74.1534 | 224.4504 | 258.1146 | 155.4261 | 25.3458 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 17 | 8417 | 2.7 | 2.7 | 5.0625 | 5.0738 | 15 | 81 | 81 | 0 | 3 | -4.8679 | 237.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 3 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 1.392 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 17 | 18 | 8418 | 1.3 | 1.3 | 5.0625 | 5.0738 | 15 | 87 | 87 | 0 | 0 | -13.0679 | 248.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 19 | 8419 | 0.3 | 0.3 | 5.0625 | 5.0738 | 15 | 92 | 92 | 0 | 0 | -21.9175 | 259.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 20 | 8420 | 0.9 | 0.9 | 5.0625 | 5.0738 | 15 | 92 | 92 | 0 | 0 | -31.0863 | 271.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 21 | 8421 | 0.9 | 0.9 | 5.0625 | 5.0738 | 15 | 90 | 90 | 0 | 0 | -40.2052 | 283.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 22 | 8422 | -0.4 | -0.4 | 5.0625 | 5.0738 | 15 | 92 | 92 | 0 | 0 | -48.7694 | 299.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 23 | 8423 | -1.1 | -1.1 | 5.0625 | 5.0738 | 15 | 94 | 94 | 0 | 0 | -55.9629 | 318.4372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 17 | 24 | 8424 | -1.2 | -1.2 | 3.525 | 5.04 | 15 | 96 | 96 | 0 | 0 | -60.4752 | 343.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 1 | 8425 | -0.6 | -0.6 | 3.525 | 5.04 | 15 | 96 | 96 | 0 | 0 | -60.8845 | 11.6388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 2 | 8426 | -0.9 | -0.9 | 3.525 | 5.04 | 15 | 96 | 96 | 0 | 0 | -57.1022 | 37.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 3 | 8427 | -1.3 | -1.3 | 3.525 | 5.04 | 15 | 95 | 95 | 0 | 0 | -50.2974 | 57.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 4 | 8428 | -2 | -2 | 3.525 | 5.04 | 15 | 96 | 96 | 0 | 0 | -41.915 | 73.4826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 5 | 8429 | -2.4 | -2.4 | 3.525 | 5.04 | 15 | 97 | 97 | 0 | 0 | -32.8551 | 86.5647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 6 | 8430 | -1.4 | -1.4 | 3.525 | 5.04 | 15 | 97 | 97 | 0 | 0 | -23.6652 | 98.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 7 | 8431 | -0.2 | -0.2 | 3.525 | 5.04 | 15 | 96 | 96 | 0 | 0 | -14.7304 | 109.3176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 18 | 8 | 8432 | -0.1 | -0.1 | 3.525 | 5.04 | 15 | 91 | 91 | 0 | 0 | -6.3833 | 120.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 9 | 8433 | -1.2 | -1.2 | 3.525 | 5.04 | 15 | 93 | 93 | 0 | 0 | 1.0389 | 132.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 10 | 8434 | 1 | 1 | 3.525 | 5.04 | 15 | 86 | 86 | 197.4116 | 35.3491 | 7.172 | 144.4191 | 0 | 10.1108 | 146.5343 | 197.12 | 132.2355 | 0 | 0 | 0 | 14.6509 | 14.6527 | 14.6527 | 14.6527 | 14.6527 | 14.6527 | 14.6527 | 14.6527 | 14.6527 | 35.3491 | 14.6527 | 24.7634 | 161.187 | 211.7727 | 146.8882 | 14.6527 | 14.6527 | 14.6527 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 11 | 8435 | 2.5 | 2.5 | 3.525 | 5.04 | 15 | 81 | 81 | 364.1288 | 70.3544 | 11.6364 | 157.6163 | 0 | 0 | 210.2116 | 356.409 | 293.8268 | 59.1249 | 0 | 0 | 60.6456 | 40.2254 | 40.2254 | 85.286 | 116.6247 | 103.2097 | 52.8993 | 40.2254 | 40.2254 | 70.3544 | 40.2254 | 40.2254 | 295.4976 | 473.0337 | 397.0365 | 112.0242 | 40.2254 | 40.2254 | 131 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 12 | 8436 | 4 | 4 | 3.525 | 5.04 | 15 | 75 | 75 | 492.6707 | 82.5359 | 14.0901 | 171.5072 | 0 | 0 | 183.7564 | 445.4376 | 446.1876 | 185.5669 | 0 | 0 | 111.4641 | 52.2268 | 52.2268 | 89.0064 | 141.3829 | 141.533 | 89.3688 | 52.2268 | 52.2268 | 82.5359 | 52.2268 | 52.2268 | 272.7627 | 586.8205 | 587.7206 | 274.9357 | 52.2268 | 52.2268 | 194 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 13 | 8437 | 4.8 | 4.8 | 3.525 | 5.04 | 15 | 73 | 73 | 556.888 | 83.2093 | 14.3147 | 185.7013 | 0 | 0 | 79.7698 | 434.1497 | 534.2106 | 321.3382 | 0 | 0 | 138.7907 | 54.6683 | 54.6683 | 68.3107 | 128.9171 | 146.0296 | 109.6239 | 54.6683 | 54.6683 | 83.2093 | 54.6683 | 54.6683 | 148.0805 | 563.0668 | 680.2402 | 430.9621 | 54.6683 | 54.6683 | 222 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 14 | 8438 | 5.6 | 5.6 | 3.525 | 5.04 | 15 | 70 | 70 | 512.4215 | 83.1329 | 12.2888 | 199.6892 | 0 | 0 | 0 | 314.4727 | 494.056 | 384.228 | 49.3244 | 0 | 119.8671 | 52.8229 | 52.8229 | 52.8229 | 111.3777 | 144.8162 | 124.3662 | 62.0071 | 52.8229 | 83.1329 | 52.8229 | 52.8229 | 52.8229 | 425.8505 | 638.8722 | 508.5942 | 111.3316 | 52.8229 | 203 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 15 | 8439 | 5.8 | 5.8 | 3.525 | 5.04 | 15 | 72 | 72 | 357.8984 | 77.0838 | 8.1966 | 213.0433 | 0 | 0 | 0 | 149.506 | 329.2526 | 316.1275 | 117.8192 | 0 | 64.9162 | 45.3385 | 45.3385 | 45.3385 | 86.0038 | 134.8945 | 131.3245 | 77.3851 | 45.3385 | 77.0838 | 45.3385 | 45.3385 | 45.3385 | 235.5098 | 464.1471 | 447.452 | 195.2043 | 45.3385 | 142 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 16 | 8440 | 4.5 | 4.5 | 3.525 | 5.04 | 15 | 79 | 79 | 195.7263 | 45.3691 | 2.3628 | 225.5642 | 0 | 0 | 0 | 40.1348 | 162.3932 | 189.5239 | 105.6341 | 0 | 18.6309 | 25.606 | 25.606 | 25.606 | 42.7625 | 95.0249 | 106.6226 | 70.7618 | 25.606 | 45.3691 | 25.606 | 25.606 | 25.606 | 82.8973 | 257.4181 | 296.1465 | 176.3959 | 25.606 | 64 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 17 | 8441 | 2.4 | 2.4 | 3.525 | 5.04 | 15 | 86 | 86 | 0 | 6 | -4.8349 | 237.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 6 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 2.8261 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 18 | 18 | 8442 | 1.5 | 1.5 | 3.525 | 5.04 | 15 | 89 | 89 | 0 | 0 | -13.0269 | 248.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 19 | 8443 | 1.1 | 1.1 | 3.525 | 5.04 | 15 | 92 | 92 | 0 | 0 | -21.8717 | 259.5689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 20 | 8444 | 2.7 | 2.7 | 3.525 | 5.04 | 15 | 85 | 85 | 0 | 0 | -31.039 | 271.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 21 | 8445 | 2.8 | 2.8 | 3.525 | 5.04 | 15 | 83 | 83 | 0 | 0 | -40.1606 | 283.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 22 | 8446 | 2.2 | 2.2 | 3.525 | 5.04 | 15 | 85 | 85 | 0 | 0 | -48.7334 | 298.9223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 23 | 8447 | 1.4 | 1.4 | 3.525 | 5.04 | 15 | 88 | 88 | 0 | 0 | -55.945 | 318.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 18 | 24 | 8448 | 0.7 | 0.7 | 1.3708 | 4.1554 | 15 | 90 | 90 | 0 | 0 | -60.4875 | 343.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 1 | 8449 | 0.3 | 0.3 | 1.3708 | 4.1554 | 15 | 92 | 92 | 0 | 0 | -60.9325 | 11.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 2 | 8450 | 0.4 | 0.4 | 1.3708 | 4.1554 | 15 | 92 | 92 | 0 | 0 | -57.1702 | 37.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 3 | 8451 | -0.2 | -0.2 | 1.3708 | 4.1554 | 15 | 93 | 93 | 0 | 0 | -50.3805 | 57.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 4 | 8452 | -0.4 | -0.4 | 1.3708 | 4.1554 | 15 | 94 | 94 | 0 | 0 | -42.0049 | 73.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 5 | 8453 | -0.1 | -0.1 | 1.3708 | 4.1554 | 15 | 94 | 94 | 0 | 0 | -32.9473 | 86.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 6 | 8454 | -0.5 | -0.5 | 1.3708 | 4.1554 | 15 | 96 | 96 | 0 | 0 | -23.7569 | 98.1496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 7 | 8455 | 0.6 | 0.6 | 1.3708 | 4.1554 | 15 | 97 | 97 | 0 | 0 | -14.8194 | 109.2475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 19 | 8 | 8456 | 1.6 | 1.6 | 1.3708 | 4.1554 | 15 | 97 | 97 | 0 | 0 | -6.4675 | 120.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 9 | 8457 | 1.9 | 1.9 | 1.3708 | 4.1554 | 15 | 97 | 97 | 0 | 0 | 0.9621 | 131.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 10 | 8458 | 2.4 | 2.4 | 1.3708 | 4.1554 | 15 | 96 | 96 | 0.42983 | 5.9686 | 7.1055 | 144.3284 | 0 | 0.022625 | 0.31947 | 0.42918 | 0.28747 | 0 | 0 | 0 | 0.03138 | 2.8527 | 2.8527 | 2.8527 | 2.8527 | 2.8527 | 2.8527 | 2.8527 | 2.8527 | 5.9686 | 2.8527 | 2.8753 | 3.1722 | 3.2819 | 3.1402 | 2.8527 | 2.8527 | 2.8527 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 11 | 8459 | 2.7 | 2.7 | 1.3708 | 4.1554 | 15 | 96 | 96 | 0.67108 | 16.8889 | 11.5833 | 157.5158 | 0 | 0 | 0.38833 | 0.65712 | 0.54098 | 0.10794 | 0 | 0 | 0.1111 | 8.036 | 8.036 | 8.036 | 8.036 | 8.036 | 8.036 | 8.036 | 8.036 | 16.8889 | 8.036 | 8.036 | 8.4244 | 8.6932 | 8.577 | 8.144 | 8.036 | 8.036 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 12 | 8460 | 2.7 | 2.7 | 1.3708 | 4.1554 | 15 | 97 | 97 | 0.78223 | 24.8236 | 14.0532 | 171.3983 | 0 | 0 | 0.29305 | 0.70788 | 0.70805 | 0.29344 | 0 | 0 | 0.17639 | 11.8205 | 11.8205 | 11.8205 | 11.8205 | 11.8205 | 11.8205 | 11.8205 | 11.8205 | 24.8236 | 11.8205 | 11.8205 | 12.1136 | 12.5284 | 12.5286 | 12.114 | 11.8205 | 11.8205 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 13 | 8461 | 3.8 | 3.8 | 1.3708 | 4.1554 | 15 | 97 | 97 | 2.8889 | 52.2814 | 14.2957 | 185.5875 | 0 | 0 | 0.41914 | 2.2557 | 2.7709 | 1.6629 | 0 | 0 | 0.71862 | 25.5804 | 25.5804 | 25.5804 | 25.5804 | 25.5804 | 25.5804 | 25.5804 | 25.5804 | 52.2814 | 25.5804 | 25.5804 | 25.9996 | 27.8361 | 28.3513 | 27.2434 | 25.5804 | 25.5804 | 53 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 14 | 8462 | 4.8 | 4.8 | 1.3708 | 4.1554 | 15 | 93 | 93 | 4.3342 | 59.9869 | 12.2878 | 199.5747 | 0 | 0 | 0 | 2.6666 | 4.1801 | 3.2449 | 0.40894 | 0 | 1.0131 | 29.5835 | 29.5835 | 29.5835 | 29.5835 | 29.5835 | 29.5835 | 29.5835 | 29.5835 | 59.9869 | 29.5835 | 29.5835 | 29.5835 | 32.2501 | 33.7636 | 32.8285 | 29.9925 | 29.5835 | 61 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 15 | 8463 | 5.6 | 5.6 | 1.3708 | 4.1554 | 15 | 91 | 91 | 6.6796 | 56.7878 | 8.2119 | 212.9314 | 0 | 0 | 0 | 2.8021 | 6.1494 | 5.8945 | 2.1866 | 0 | 1.2122 | 28.1568 | 28.1568 | 28.1568 | 28.1568 | 28.1568 | 28.1568 | 28.1568 | 28.1568 | 56.7878 | 28.1568 | 28.1568 | 28.1568 | 30.959 | 34.3063 | 34.0513 | 30.3435 | 28.1568 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 16 | 8464 | 5.5 | 5.5 | 1.3708 | 4.1554 | 15 | 91 | 91 | 3.3747 | 21.6776 | 2.3917 | 225.4561 | 0 | 0 | 0 | 0.69836 | 2.8034 | 3.2663 | 1.8158 | 0 | 0.3224 | 10.3849 | 10.3849 | 10.3849 | 10.3849 | 10.3849 | 10.3849 | 10.3849 | 10.3849 | 21.6776 | 10.3849 | 10.3849 | 10.3849 | 11.0833 | 13.1884 | 13.6512 | 12.2007 | 10.3849 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 17 | 8465 | 5.7 | 5.7 | 1.3708 | 4.1554 | 15 | 90 | 90 | 0 | 0 | -4.7953 | 237.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 19 | 18 | 8466 | 5.6 | 5.6 | 1.3708 | 4.1554 | 15 | 89 | 89 | 0 | 0 | -12.9797 | 248.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 19 | 8467 | 5.4 | 5.4 | 1.3708 | 4.1554 | 15 | 89 | 89 | 0 | 0 | -21.8198 | 259.4622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 20 | 8468 | 5.4 | 5.4 | 1.3708 | 4.1554 | 15 | 91 | 91 | 0 | 0 | -30.9857 | 270.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 21 | 8469 | 5.3 | 5.3 | 1.3708 | 4.1554 | 15 | 92 | 92 | 0 | 0 | -40.1097 | 283.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 22 | 8470 | 5.4 | 5.4 | 1.3708 | 4.1554 | 15 | 93 | 93 | 0 | 0 | -48.6909 | 298.7655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 23 | 8471 | 5.5 | 5.5 | 1.3708 | 4.1554 | 15 | 93 | 93 | 0 | 0 | -55.9198 | 318.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 19 | 24 | 8472 | 5.5 | 5.5 | 3.1208 | 3.8645 | 15 | 94 | 94 | 0 | 0 | -60.4919 | 342.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 1 | 8473 | 5.6 | 5.6 | 3.1208 | 3.8645 | 15 | 93 | 93 | 0 | 0 | -60.9728 | 11.2124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 2 | 8474 | 4.7 | 4.7 | 3.1208 | 3.8645 | 15 | 95 | 95 | 0 | 0 | -57.2311 | 36.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 3 | 8475 | 5 | 5 | 3.1208 | 3.8645 | 15 | 95 | 95 | 0 | 0 | -50.4574 | 57.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 4 | 8476 | 5 | 5 | 3.1208 | 3.8645 | 15 | 96 | 96 | 0 | 0 | -42.089 | 73.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 5 | 8477 | 5.3 | 5.3 | 3.1208 | 3.8645 | 15 | 95 | 95 | 0 | 0 | -33.0339 | 86.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 6 | 8478 | 5.3 | 5.3 | 3.1208 | 3.8645 | 15 | 96 | 96 | 0 | 0 | -23.8431 | 98.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 7 | 8479 | 5.5 | 5.5 | 3.1208 | 3.8645 | 15 | 96 | 96 | 0 | 0 | -14.9027 | 109.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 20 | 8 | 8480 | 5.8 | 5.8 | 3.1208 | 3.8645 | 15 | 97 | 97 | 0 | 0 | -6.5456 | 120.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 9 | 8481 | 5.9 | 5.9 | 3.1208 | 3.8645 | 15 | 97 | 97 | 0 | 0 | 0.89173 | 131.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 10 | 8482 | 6.3 | 6.3 | 3.1208 | 3.8645 | 15 | 98 | 98 | 0 | 0 | 7.0458 | 144.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 11 | 8483 | 7.2 | 7.2 | 3.1208 | 3.8645 | 15 | 98 | 98 | 0.45995 | 13.9243 | 11.5374 | 157.413 | 0 | 0 | 0.2668 | 0.45057 | 0.3704 | 0.073253 | 0 | 0 | 0.075739 | 6.5843 | 6.5843 | 6.5843 | 6.5843 | 6.5843 | 6.5843 | 6.5843 | 6.5843 | 13.9243 | 6.5843 | 6.5843 | 6.8511 | 7.0349 | 6.9547 | 6.6576 | 6.5843 | 6.5843 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 12 | 8484 | 7.9 | 7.9 | 3.1208 | 3.8645 | 15 | 95 | 95 | 1.914 | 38.5696 | 14.0239 | 171.2883 | 0 | 0 | 0.7203 | 1.7337 | 1.7315 | 0.71503 | 0 | 0 | 0.4304 | 18.7151 | 18.7151 | 18.7151 | 18.7151 | 18.7151 | 18.7151 | 18.7151 | 18.7151 | 38.5696 | 18.7151 | 18.7151 | 19.4354 | 20.4488 | 20.4466 | 19.4301 | 18.7151 | 18.7151 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 13 | 8485 | 8.3 | 8.3 | 3.1208 | 3.8645 | 15 | 94 | 94 | 0.49909 | 21.876 | 14.2843 | 185.4739 | 0 | 0 | 0.073341 | 0.3903 | 0.47863 | 0.28658 | 0 | 0 | 0.12398 | 10.3415 | 10.3415 | 10.3415 | 10.3415 | 10.3415 | 10.3415 | 10.3415 | 10.3415 | 21.876 | 10.3415 | 10.3415 | 10.4148 | 10.7318 | 10.8201 | 10.628 | 10.3415 | 10.3415 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 14 | 8486 | 8.8 | 8.8 | 3.1208 | 3.8645 | 15 | 90 | 90 | 0.56397 | 21.8682 | 12.2942 | 199.4616 | 0 | 0 | 0 | 0.34783 | 0.54404 | 0.42156 | 0.052135 | 0 | 0.13179 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 21.8682 | 10.336 | 10.336 | 10.336 | 10.6839 | 10.8801 | 10.7576 | 10.3882 | 10.336 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 15 | 8487 | 8.8 | 8.8 | 3.1208 | 3.8645 | 15 | 92 | 92 | 0.12335 | 7.9776 | 8.2343 | 212.8218 | 0 | 0 | 0 | 0.05196 | 0.11364 | 0.10875 | 0.040155 | 0 | 0.022413 | 3.7113 | 3.7113 | 3.7113 | 3.7113 | 3.7113 | 3.7113 | 3.7113 | 3.7113 | 7.9776 | 3.7113 | 3.7113 | 3.7113 | 3.7632 | 3.8249 | 3.82 | 3.7514 | 3.7113 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 16 | 8488 | 9.2 | 9.2 | 3.1208 | 3.8645 | 15 | 92 | 92 | 0.24855 | 5.9761 | 2.4275 | 225.3512 | 0 | 0 | 0 | 0.051893 | 0.20672 | 0.24046 | 0.13333 | 0 | 0.023861 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 5.9761 | 2.7755 | 2.7755 | 2.7755 | 2.8274 | 2.9822 | 3.0159 | 2.9088 | 2.7755 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 17 | 8489 | 9.3 | 9.3 | 3.1208 | 3.8645 | 15 | 92 | 92 | 0 | 0 | -4.7491 | 237.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 20 | 18 | 8490 | 9.2 | 9.2 | 3.1208 | 3.8645 | 15 | 95 | 95 | 0 | 0 | -12.9262 | 248.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 19 | 8491 | 10 | 10 | 3.1208 | 3.8645 | 15 | 92 | 92 | 0 | 0 | -21.7619 | 259.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 20 | 8492 | 10.4 | 10.4 | 3.1208 | 3.8645 | 15 | 94 | 94 | 0 | 0 | -30.9263 | 270.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 21 | 8493 | 9.1 | 9.1 | 3.1208 | 3.8645 | 15 | 93 | 93 | 0 | 0 | -40.0527 | 283.5147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 22 | 8494 | 9.7 | 9.7 | 3.1208 | 3.8645 | 15 | 81 | 81 | 0 | 0 | -48.6417 | 298.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 23 | 8495 | 9 | 9 | 3.1208 | 3.8645 | 15 | 81 | 81 | 0 | 0 | -55.8874 | 317.8537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 20 | 24 | 8496 | 7.9 | 7.9 | 7.4667 | 4.4832 | 15 | 80 | 80 | 0 | 0 | -60.4883 | 342.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 1 | 8497 | 7.5 | 7.5 | 7.4667 | 4.4832 | 15 | 81 | 81 | 0 | 0 | -61.0052 | 10.9941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 2 | 8498 | 7.2 | 7.2 | 7.4667 | 4.4832 | 15 | 81 | 81 | 0 | 0 | -57.2849 | 36.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 3 | 8499 | 6.6 | 6.6 | 7.4667 | 4.4832 | 15 | 84 | 84 | 0 | 0 | -50.5279 | 57.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 4 | 8500 | 4.5 | 4.5 | 7.4667 | 4.4832 | 15 | 85 | 85 | 0 | 0 | -42.1675 | 73.1922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 5 | 8501 | 4.9 | 4.9 | 7.4667 | 4.4832 | 15 | 81 | 81 | 0 | 0 | -33.1151 | 86.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 6 | 8502 | 5 | 5 | 7.4667 | 4.4832 | 15 | 78 | 78 | 0 | 0 | -23.9237 | 97.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 7 | 8503 | 4.8 | 4.8 | 7.4667 | 4.4832 | 15 | 80 | 80 | 0 | 0 | -14.9803 | 109.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 21 | 8 | 8504 | 4.6 | 4.6 | 7.4667 | 4.4832 | 15 | 88 | 88 | 0 | 0 | -6.6177 | 120.2197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 9 | 8505 | 4.3 | 4.3 | 7.4667 | 4.4832 | 15 | 93 | 93 | 0 | 0 | 0.82782 | 131.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 10 | 8506 | 5.8 | 5.8 | 7.4667 | 4.4832 | 15 | 93 | 93 | 0.45508 | 5.9677 | 6.993 | 144.1372 | 0 | 0.025342 | 0.33918 | 0.45433 | 0.30334 | 0 | 0 | 0 | 0.032286 | 2.8575 | 2.8575 | 2.8575 | 2.8575 | 2.8575 | 2.8575 | 2.8575 | 2.8575 | 5.9677 | 2.8575 | 2.8828 | 3.1966 | 3.3118 | 3.1608 | 2.8575 | 2.8575 | 2.8575 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 11 | 8507 | 7 | 7 | 7.4667 | 4.4832 | 15 | 81 | 81 | 5.2313 | 46.1425 | 11.4988 | 157.3078 | 0 | 0 | 3.042 | 5.1265 | 4.208 | 0.82455 | 0 | 0 | 0.85747 | 21.6814 | 21.6814 | 37.8121 | 48.866 | 43.9956 | 26.0538 | 21.6814 | 21.6814 | 46.1425 | 21.6814 | 21.6814 | 40.8541 | 53.9926 | 48.2036 | 26.8783 | 21.6814 | 21.6814 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 12 | 8508 | 8.1 | 8.1 | 7.4667 | 4.4832 | 15 | 71 | 71 | 61.2296 | 103.2621 | 14.002 | 171.1772 | 0 | 0 | 23.147 | 55.5101 | 55.3561 | 22.7752 | 0 | 0 | 13.7379 | 48.4625 | 48.4625 | 82.9764 | 131.2321 | 131.0024 | 82.422 | 48.4625 | 48.4625 | 103.2621 | 48.4625 | 48.4625 | 106.1235 | 186.7422 | 186.3585 | 105.1973 | 48.4625 | 48.4625 | 117 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 13 | 8509 | 7.7 | 7.7 | 7.4667 | 4.4832 | 15 | 74 | 74 | 6.3948 | 76.4129 | 14.2805 | 185.3604 | 0 | 0 | 0.95168 | 5.0084 | 6.1313 | 3.6626 | 0 | 0 | 1.5871 | 37.0566 | 37.0566 | 38.716 | 45.7892 | 47.747 | 43.4426 | 37.0566 | 37.0566 | 76.4129 | 37.0566 | 37.0566 | 39.6676 | 50.7977 | 53.8784 | 47.1051 | 37.0566 | 37.0566 | 78 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 14 | 8510 | 7.9 | 7.9 | 7.4667 | 4.4832 | 15 | 70 | 70 | 1.7711 | 38.586 | 12.3081 | 199.3499 | 0 | 0 | 0 | 1.095 | 1.7088 | 1.3217 | 0.16034 | 0 | 0.414 | 18.585 | 18.585 | 18.585 | 18.585 | 18.585 | 18.585 | 18.585 | 18.585 | 38.586 | 18.585 | 18.585 | 18.585 | 19.6799 | 20.2938 | 19.9067 | 18.7453 | 18.585 | 39 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 15 | 8511 | 8.2 | 8.2 | 7.4667 | 4.4832 | 15 | 67 | 67 | 3.3867 | 41.3835 | 8.264 | 212.7148 | 0 | 0 | 0 | 1.4323 | 3.122 | 2.9828 | 1.0964 | 0 | 0.61653 | 20.1152 | 20.1152 | 20.1152 | 20.1152 | 20.1152 | 20.1152 | 20.1152 | 20.1152 | 41.3835 | 20.1152 | 20.1152 | 20.1152 | 21.5475 | 23.2371 | 23.098 | 21.2115 | 20.1152 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 16 | 8512 | 7.9 | 7.9 | 7.4667 | 4.4832 | 15 | 64 | 64 | 6.7549 | 30.3476 | 2.4702 | 225.2498 | 0 | 0 | 0 | 1.4224 | 5.6244 | 6.5317 | 3.6128 | 0 | 0.65243 | 14.7812 | 14.7812 | 14.7812 | 14.7812 | 14.7812 | 14.7812 | 14.7812 | 14.7812 | 30.3476 | 14.7812 | 14.7812 | 14.7812 | 16.2035 | 20.4055 | 21.3128 | 18.394 | 14.7812 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 17 | 8513 | 7.6 | 7.6 | 7.4667 | 4.4832 | 15 | 66 | 66 | 0 | 3 | -4.6965 | 236.9991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 3 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 1.3915 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 21 | 18 | 8514 | 7 | 7 | 7.4667 | 4.4832 | 15 | 61 | 61 | 0 | 0 | -12.8665 | 248.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 19 | 8515 | 6.6 | 6.6 | 7.4667 | 4.4832 | 15 | 74 | 74 | 0 | 0 | -21.698 | 259.2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 20 | 8516 | 5.7 | 5.7 | 7.4667 | 4.4832 | 15 | 82 | 82 | 0 | 0 | -30.861 | 270.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 21 | 8517 | 3.5 | 3.5 | 7.4667 | 4.4832 | 15 | 85 | 85 | 0 | 0 | -39.9896 | 283.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 22 | 8518 | 3.3 | 3.3 | 7.4667 | 4.4832 | 15 | 91 | 91 | 0 | 0 | -48.586 | 298.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 23 | 8519 | 3.5 | 3.5 | 7.4667 | 4.4832 | 15 | 89 | 89 | 0 | 0 | -55.8477 | 317.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 21 | 24 | 8520 | 1.5 | 1.5 | 5.8625 | 4.7285 | 15 | 94 | 94 | 0 | 0 | -60.4768 | 342.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 1 | 8521 | 0.9 | 0.9 | 5.8625 | 4.7285 | 15 | 96 | 96 | 0 | 0 | -61.0297 | 10.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 2 | 8522 | 1.7 | 1.7 | 5.8625 | 4.7285 | 15 | 96 | 96 | 0 | 0 | -57.3316 | 36.6124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 3 | 8523 | 2.2 | 2.2 | 5.8625 | 4.7285 | 15 | 94 | 94 | 0 | 0 | -50.5922 | 57.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 4 | 8524 | 1.7 | 1.7 | 5.8625 | 4.7285 | 15 | 91 | 91 | 0 | 0 | -42.2401 | 73.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 5 | 8525 | 2.4 | 2.4 | 5.8625 | 4.7285 | 15 | 81 | 81 | 0 | 0 | -33.1906 | 86.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 6 | 8526 | 1.5 | 1.5 | 5.8625 | 4.7285 | 15 | 90 | 90 | 0 | 0 | -23.9987 | 97.9042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 7 | 8527 | 1 | 1 | 5.8625 | 4.7285 | 15 | 90 | 90 | 0 | 0 | -15.052 | 109.0054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 22 | 8 | 8528 | 0.3 | 0.3 | 5.8625 | 4.7285 | 15 | 92 | 92 | 0 | 0 | -6.6836 | 120.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 9 | 8529 | 0.5 | 0.5 | 5.8625 | 4.7285 | 15 | 79 | 79 | 0 | 0 | 0.77042 | 131.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 10 | 8530 | 2.4 | 2.4 | 5.8625 | 4.7285 | 15 | 72 | 72 | 26.8578 | 29.1175 | 6.9472 | 144.0368 | 0 | 1.5394 | 20.047 | 26.8113 | 17.8699 | 0 | 0 | 0 | 1.8825 | 12.055 | 17.2089 | 79.1718 | 101.8186 | 71.883 | 12.055 | 12.055 | 12.055 | 29.1175 | 12.055 | 18.7484 | 99.2188 | 128.6298 | 89.7529 | 12.055 | 12.055 | 12.055 | 31 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 11 | 8531 | 3.1 | 3.1 | 5.8625 | 4.7285 | 15 | 76 | 76 | 204.7561 | 77.5681 | 11.4675 | 157.2006 | 0 | 0 | 119.3634 | 200.7299 | 164.5116 | 31.9246 | 0 | 0 | 33.4319 | 40.4707 | 40.4707 | 99.2617 | 139.3377 | 121.4989 | 56.1948 | 40.4707 | 40.4707 | 77.5681 | 40.4707 | 40.4707 | 218.625 | 340.0677 | 286.0105 | 88.1194 | 40.4707 | 40.4707 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 12 | 8532 | 2.7 | 2.7 | 5.8625 | 4.7285 | 15 | 76 | 76 | 226.3038 | 105.3091 | 13.9877 | 171.0651 | 0 | 0 | 85.9436 | 205.3446 | 204.4574 | 83.8019 | 0 | 0 | 50.6909 | 55.787 | 55.787 | 98.3837 | 157.5629 | 157.1232 | 97.3222 | 55.787 | 55.787 | 105.3091 | 55.787 | 55.787 | 184.3273 | 362.9075 | 361.5806 | 181.1241 | 55.787 | 55.787 | 156 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 13 | 8533 | 1.4 | 1.4 | 5.8625 | 4.7285 | 15 | 86 | 86 | 355.9044 | 105.6993 | 14.2843 | 185.2473 | 0 | 0 | 53.6374 | 279.1641 | 341.1603 | 203.3094 | 0 | 0 | 88.3007 | 60.2343 | 60.2343 | 76.2861 | 143.7783 | 162.3315 | 121.0776 | 60.2343 | 60.2343 | 105.6993 | 60.2343 | 60.2343 | 129.9234 | 422.9424 | 503.4919 | 324.3871 | 60.2343 | 60.2343 | 194 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 14 | 8534 | 1.4 | 1.4 | 5.8625 | 4.7285 | 15 | 90 | 90 | 43.7732 | 103.7592 | 12.3294 | 199.2397 | 0 | 0 | 0 | 27.1265 | 42.2421 | 32.6129 | 3.8795 | 0 | 10.2408 | 49.7183 | 49.7183 | 49.7183 | 88.9983 | 110.8862 | 96.9428 | 55.336 | 49.7183 | 103.7592 | 49.7183 | 49.7183 | 49.7183 | 116.1248 | 153.1283 | 129.5557 | 59.2154 | 49.7183 | 114 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 15 | 8535 | 1.1 | 1.1 | 5.8625 | 4.7285 | 15 | 91 | 91 | 77.7244 | 85.8144 | 8.3008 | 212.6104 | 0 | 0 | 0 | 33.0005 | 71.6909 | 68.3857 | 25.0212 | 0 | 14.1856 | 42.8773 | 42.8773 | 42.8773 | 76.6926 | 116.3383 | 112.9515 | 68.5163 | 42.8773 | 85.8144 | 42.8773 | 42.8773 | 42.8773 | 109.693 | 188.0292 | 181.3373 | 93.5374 | 42.8773 | 100 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 16 | 8536 | 1.3 | 1.3 | 5.8625 | 4.7285 | 15 | 86 | 86 | 75.61 | 45.6439 | 2.5196 | 225.1517 | 0 | 0 | 0 | 16.0528 | 63.0232 | 73.0754 | 40.3211 | 0 | 7.3561 | 23.7974 | 23.7974 | 23.7974 | 34.529 | 65.9298 | 72.65 | 50.7529 | 23.7974 | 45.6439 | 23.7974 | 23.7974 | 23.7974 | 50.5818 | 128.953 | 145.7254 | 91.074 | 23.7974 | 53 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 17 | 8537 | 0.4 | 0.4 | 5.8625 | 4.7285 | 15 | 91 | 91 | 0 | 3 | -4.6375 | 236.9064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 3 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 1.3913 | 3 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 18 | 8538 | 0.6 | 0.6 | 5.8625 | 4.7285 | 15 | 87 | 87 | 0 | 0 | -12.8008 | 248.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 19 | 8539 | -0.1 | -0.1 | 5.8625 | 4.7285 | 15 | 91 | 91 | 0 | 0 | -21.6281 | 259.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 20 | 8540 | 0.3 | 0.3 | 5.8625 | 4.7285 | 15 | 93 | 93 | 0 | 0 | -30.7898 | 270.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 21 | 8541 | 0.8 | 0.8 | 5.8625 | 4.7285 | 15 | 92 | 92 | 0 | 0 | -39.9204 | 283.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 22 | 8542 | 0.7 | 0.7 | 5.8625 | 4.7285 | 15 | 92 | 92 | 0 | 0 | -48.5239 | 298.3353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 23 | 8543 | 0 | 0 | 5.8625 | 4.7285 | 15 | 95 | 95 | 0 | 0 | -55.8009 | 317.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 22 | 24 | 8544 | 0.7 | 0.7 | 1.2083 | 3.8308 | 15 | 94 | 94 | 0 | 0 | -60.4575 | 342.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 1 | 8545 | -0.5 | -0.5 | 1.2083 | 3.8308 | 15 | 94 | 94 | 0 | 0 | -61.0462 | 10.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 2 | 8546 | 0.5 | 0.5 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0 | 0 | -57.371 | 36.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 3 | 8547 | 0.8 | 0.8 | 1.2083 | 3.8308 | 15 | 95 | 95 | 0 | 0 | -50.65 | 56.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 4 | 8548 | 0.5 | 0.5 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0 | 0 | -42.3067 | 72.9632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 5 | 8549 | 0.2 | 0.2 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0 | 0 | -33.2604 | 86.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 6 | 8550 | 0.8 | 0.8 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0 | 0 | -24.068 | 97.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 7 | 8551 | 1.2 | 1.2 | 1.2083 | 3.8308 | 15 | 95 | 95 | 0 | 0 | -15.1179 | 108.9144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 23 | 8 | 8552 | 1.3 | 1.3 | 1.2083 | 3.8308 | 15 | 93 | 93 | 0 | 0 | -6.7434 | 120.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 9 | 8553 | 1.3 | 1.3 | 1.2083 | 3.8308 | 15 | 94 | 94 | 0 | 0 | 0.71959 | 131.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 10 | 8554 | 1.2 | 1.2 | 1.2083 | 3.8308 | 15 | 95 | 95 | 0 | 0 | 6.9083 | 143.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 11 | 8555 | 0.6 | 0.6 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0.29054 | 10.9527 | 11.4435 | 157.0912 | 0 | 0 | 0.16981 | 0.28493 | 0.23315 | 0.044789 | 0 | 0 | 0.04729 | 5.1472 | 5.1472 | 5.1472 | 5.1472 | 5.1472 | 5.1472 | 5.1472 | 5.1472 | 10.9527 | 5.1472 | 5.1472 | 5.317 | 5.4322 | 5.3804 | 5.192 | 5.1472 | 5.1472 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 12 | 8556 | 0.6 | 0.6 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0.615 | 21.8624 | 13.9809 | 170.9521 | 0 | 0 | 0.23464 | 0.55852 | 0.55523 | 0.22669 | 0 | 0 | 0.13761 | 10.3707 | 10.3707 | 10.3707 | 10.3707 | 10.3707 | 10.3707 | 10.3707 | 10.3707 | 21.8624 | 10.3707 | 10.3707 | 10.6053 | 10.9292 | 10.9259 | 10.5974 | 10.3707 | 10.3707 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 13 | 8557 | 0.7 | 0.7 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0.64571 | 24.8398 | 14.2957 | 185.1345 | 0 | 0 | 0.098536 | 0.50722 | 0.61878 | 0.36787 | 0 | 0 | 0.16023 | 11.7832 | 11.7832 | 11.7832 | 11.7832 | 11.7832 | 11.7832 | 11.7832 | 11.7832 | 24.8398 | 11.7832 | 11.7832 | 11.8817 | 12.2904 | 12.402 | 12.1511 | 11.7832 | 11.7832 | 25 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 14 | 8558 | 1 | 1 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0.56097 | 21.8686 | 12.3581 | 199.1312 | 0 | 0 | 0 | 0.34844 | 0.54142 | 0.41724 | 0.048649 | 0 | 0.13142 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 10.336 | 21.8686 | 10.336 | 10.336 | 10.336 | 10.6844 | 10.8774 | 10.7532 | 10.3846 | 10.336 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 15 | 8559 | 1.4 | 1.4 | 1.2083 | 3.8308 | 15 | 96 | 96 | 0.54835 | 16.8996 | 8.3447 | 212.5086 | 0 | 0 | 0 | 0.23371 | 0.50606 | 0.48197 | 0.17555 | 0 | 0.1004 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 7.9554 | 16.8996 | 7.9554 | 7.9554 | 7.9554 | 8.1891 | 8.4615 | 8.4374 | 8.131 | 7.9554 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 16 | 8560 | 1.6 | 1.6 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0.23789 | 5.9767 | 2.5758 | 225.0573 | 0 | 0 | 0 | 0.05091 | 0.19849 | 0.2298 | 0.1265 | 0 | 0.023341 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 2.7755 | 5.9767 | 2.7755 | 2.7755 | 2.7755 | 2.8264 | 2.974 | 3.0053 | 2.902 | 2.7755 | 6 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 17 | 8561 | 1.8 | 1.8 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0 | 0 | -4.572 | 236.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 18 | 8562 | 2 | 2 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0 | 0 | -12.7289 | 248.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 19 | 8563 | 2.2 | 2.2 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0 | 0 | -21.5524 | 259.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 20 | 8564 | 2.2 | 2.2 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0 | 0 | -30.7128 | 270.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 21 | 8565 | 2.3 | 2.3 | 1.2083 | 3.8308 | 15 | 97 | 97 | 0 | 0 | -39.8453 | 283.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 22 | 8566 | 2.3 | 2.3 | 1.2083 | 3.8308 | 15 | 98 | 98 | 0 | 0 | -48.4553 | 298.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 23 | 8567 | 2.3 | 2.3 | 1.2083 | 3.8308 | 15 | 99 | 99 | 0 | 0 | -55.7469 | 317.3241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 23 | 24 | 8568 | 2.5 | 2.5 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -60.4303 | 341.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 1 | 8569 | 2.2 | 2.2 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -61.0549 | 10.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 2 | 8570 | 2.2 | 2.2 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -57.4031 | 36.2262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 3 | 8571 | 2.1 | 2.1 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -50.7013 | 56.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 4 | 8572 | 2.2 | 2.2 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -42.3674 | 72.8384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 5 | 8573 | 2.3 | 2.3 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -33.3245 | 86.0144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 6 | 8574 | 2.5 | 2.5 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -24.1315 | 97.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 7 | 8575 | 2.4 | 2.4 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -15.1778 | 108.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 24 | 8 | 8576 | 2.4 | 2.4 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -6.7969 | 119.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 9 | 8577 | 2.6 | 2.6 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | 0.67537 | 131.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 10 | 8578 | 2.9 | 2.9 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.86158 | 7.9408 | 6.8764 | 143.8268 | 0 | 0.052366 | 0.64509 | 0.85993 | 0.57103 | 0 | 0 | 0 | 0.059224 | 3.8722 | 3.8722 | 3.8722 | 3.8722 | 3.8722 | 3.8722 | 3.8722 | 3.8722 | 7.9408 | 3.8722 | 3.9246 | 4.5173 | 4.7321 | 4.4432 | 3.8722 | 3.8722 | 3.8722 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 11 | 8579 | 3.2 | 3.2 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.69719 | 16.8868 | 11.4268 | 156.9798 | 0 | 0 | 0.40854 | 0.68398 | 0.55875 | 0.10621 | 0 | 0 | 0.11321 | 8.0423 | 8.0423 | 8.0423 | 8.0423 | 8.0423 | 8.0423 | 8.0423 | 8.0423 | 16.8868 | 8.0423 | 8.0423 | 8.4509 | 8.7263 | 8.6011 | 8.1485 | 8.0423 | 8.0423 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 12 | 8580 | 3.7 | 3.7 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.79495 | 24.8222 | 13.9816 | 170.8383 | 0 | 0 | 0.30471 | 0.72256 | 0.71715 | 0.29164 | 0 | 0 | 0.17778 | 11.8236 | 11.8236 | 11.8236 | 11.8236 | 11.8236 | 11.8236 | 11.8236 | 11.8236 | 24.8222 | 11.8236 | 11.8236 | 12.1283 | 12.5461 | 12.5407 | 12.1152 | 11.8236 | 11.8236 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 13 | 8581 | 3.9 | 3.9 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.37243 | 18.9075 | 14.3146 | 185.0222 | 0 | 0 | 0.057542 | 0.29298 | 0.35679 | 0.2116 | 0 | 0 | 0.092478 | 8.9078 | 8.9078 | 8.9078 | 8.9078 | 8.9078 | 8.9078 | 8.9078 | 8.9078 | 18.9075 | 8.9078 | 8.9078 | 8.9653 | 9.2007 | 9.2645 | 9.1194 | 8.9078 | 8.9078 | 19 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 14 | 8582 | 4.3 | 4.3 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.13969 | 10.9672 | 12.3943 | 199.0244 | 0 | 0 | 0 | 0.086964 | 0.13484 | 0.10372 | 0.011849 | 0 | 0.03279 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 5.1193 | 10.9672 | 5.1193 | 5.1193 | 5.1193 | 5.2063 | 5.2541 | 5.223 | 5.1312 | 5.1193 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 15 | 8583 | 4.6 | 4.6 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.54403 | 16.9 | 8.3958 | 212.4096 | 0 | 0 | 0 | 0.23273 | 0.50233 | 0.47768 | 0.17321 | 0 | 0.10001 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 7.9553 | 16.9 | 7.9553 | 7.9553 | 7.9553 | 8.188 | 8.4576 | 8.433 | 8.1285 | 7.9553 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 16 | 8584 | 4.9 | 4.9 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0.41487 | 7.9589 | 2.6387 | 224.9664 | 0 | 0 | 0 | 0.089464 | 0.34649 | 0.40055 | 0.21997 | 0 | 0.041097 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 3.7103 | 7.9589 | 3.7103 | 3.7103 | 3.7103 | 3.7997 | 4.0568 | 4.1108 | 3.9302 | 3.7103 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 17 | 8585 | 5.1 | 5.1 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -4.5003 | 236.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 24 | 18 | 8586 | 5.3 | 5.3 | 1.2833 | 3.1225 | 15 | 99 | 99 | 0 | 0 | -12.651 | 247.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 19 | 8587 | 5.3 | 5.3 | 1.2833 | 3.1225 | 15 | 98 | 98 | 0 | 0 | -21.4709 | 259.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 20 | 8588 | 5.6 | 5.6 | 1.2833 | 3.1225 | 15 | 97 | 97 | 0 | 0 | -30.6301 | 270.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 21 | 8589 | 5.8 | 5.8 | 1.2833 | 3.1225 | 15 | 97 | 97 | 0 | 0 | -39.7643 | 283.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 22 | 8590 | 5.9 | 5.9 | 1.2833 | 3.1225 | 15 | 97 | 97 | 0 | 0 | -48.3805 | 298.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 23 | 8591 | 6 | 6 | 1.2833 | 3.1225 | 15 | 97 | 97 | 0 | 0 | -55.686 | 317.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 24 | 24 | 8592 | 6.1 | 6.1 | 3.8958 | 3.3621 | 15 | 96 | 96 | 0 | 0 | -60.3953 | 341.7747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 1 | 8593 | 6.1 | 6.1 | 3.8958 | 3.3621 | 15 | 97 | 97 | 0 | 0 | -61.0556 | 10.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 2 | 8594 | 6.5 | 6.5 | 3.8958 | 3.3621 | 15 | 97 | 97 | 0 | 0 | -57.4279 | 36.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 3 | 8595 | 6.7 | 6.7 | 3.8958 | 3.3621 | 15 | 96 | 96 | 0 | 0 | -50.7459 | 56.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 4 | 8596 | 6.9 | 6.9 | 3.8958 | 3.3621 | 15 | 95 | 95 | 0 | 0 | -42.422 | 72.7068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 5 | 8597 | 7.1 | 7.1 | 3.8958 | 3.3621 | 15 | 95 | 95 | 0 | 0 | -33.3827 | 85.9006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 6 | 8598 | 7.2 | 7.2 | 3.8958 | 3.3621 | 15 | 95 | 95 | 0 | 0 | -24.1891 | 97.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 7 | 8599 | 7.5 | 7.5 | 3.8958 | 3.3621 | 15 | 93 | 93 | 0 | 0 | -15.2317 | 108.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 25 | 8 | 8600 | 7.6 | 7.6 | 3.8958 | 3.3621 | 15 | 93 | 93 | 0 | 0 | -6.8441 | 119.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 9 | 8601 | 7.9 | 7.9 | 3.8958 | 3.3621 | 15 | 93 | 93 | 0 | 0 | 0.63779 | 131.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 10 | 8602 | 8.1 | 8.1 | 3.8958 | 3.3621 | 15 | 90 | 90 | 0.12293 | 2.9916 | 6.8515 | 143.7173 | 0 | 0.0076963 | 0.092191 | 0.12268 | 0.081307 | 0 | 0 | 0 | 0.0083888 | 1.4009 | 1.4009 | 1.4009 | 1.4009 | 1.4009 | 1.4009 | 1.4009 | 1.4009 | 2.9916 | 1.4009 | 1.4086 | 1.4931 | 1.5236 | 1.4822 | 1.4009 | 1.4009 | 1.4009 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 11 | 8603 | 8.4 | 8.4 | 3.8958 | 3.3621 | 15 | 87 | 87 | 0.47435 | 13.9231 | 11.4175 | 156.8665 | 0 | 0 | 0.2787 | 0.46552 | 0.37964 | 0.071378 | 0 | 0 | 0.076899 | 6.5879 | 6.5879 | 6.5879 | 6.5879 | 6.5879 | 6.5879 | 6.5879 | 6.5879 | 13.9231 | 6.5879 | 6.5879 | 6.8666 | 7.0534 | 6.9675 | 6.6592 | 6.5879 | 6.5879 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 12 | 8604 | 8.5 | 8.5 | 3.8958 | 3.3621 | 15 | 87 | 87 | 0.36754 | 16.9178 | 13.9899 | 170.7237 | 0 | 0 | 0.14154 | 0.33435 | 0.3313 | 0.13418 | 0 | 0 | 0.082196 | 7.9702 | 7.9702 | 7.9702 | 7.9702 | 7.9702 | 7.9702 | 7.9702 | 7.9702 | 16.9178 | 7.9702 | 7.9702 | 8.1118 | 8.3046 | 8.3015 | 8.1044 | 7.9702 | 7.9702 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 13 | 8605 | 8.8 | 8.8 | 3.8958 | 3.3621 | 15 | 87 | 87 | 0.98902 | 30.7541 | 14.341 | 184.9105 | 0 | 0 | 0.1547 | 0.77911 | 0.94713 | 0.56034 | 0 | 0 | 0.24587 | 14.6879 | 14.6879 | 14.6879 | 14.6879 | 14.6879 | 14.6879 | 14.6879 | 14.6879 | 30.7541 | 14.6879 | 14.6879 | 14.8426 | 15.467 | 15.6351 | 15.2483 | 14.6879 | 14.6879 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 14 | 8606 | 9.1 | 9.1 | 3.8958 | 3.3621 | 15 | 83 | 83 | 3.8643 | 57.0907 | 12.4378 | 198.9193 | 0 | 0 | 0 | 2.411 | 3.7302 | 2.8642 | 0.32047 | 0 | 0.90931 | 28.0604 | 28.0604 | 28.0604 | 28.0604 | 28.0604 | 28.0604 | 28.0604 | 28.0604 | 57.0907 | 28.0604 | 28.0604 | 28.0604 | 30.4714 | 31.7906 | 30.9246 | 28.3809 | 28.0604 | 58 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 15 | 8607 | 9.1 | 9.1 | 3.8958 | 3.3621 | 15 | 88 | 88 | 3.2903 | 41.3924 | 8.4539 | 212.3135 | 0 | 0 | 0 | 1.4126 | 3.0395 | 2.8859 | 1.0418 | 0 | 0.60759 | 20.1102 | 20.1102 | 20.1102 | 20.1102 | 20.1102 | 20.1102 | 20.1102 | 20.1102 | 41.3924 | 20.1102 | 20.1102 | 20.1102 | 21.5228 | 23.1497 | 22.9961 | 21.152 | 20.1102 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 16 | 8608 | 9.1 | 9.1 | 3.8958 | 3.3621 | 15 | 88 | 88 | 1.8337 | 16.8164 | 2.7083 | 224.8792 | 0 | 0 | 0 | 0.39833 | 1.5329 | 1.7695 | 0.96953 | 0 | 0.18359 | 7.9737 | 7.9737 | 7.9737 | 7.9737 | 7.9737 | 7.9737 | 7.9737 | 7.9737 | 16.8164 | 7.9737 | 7.9737 | 7.9737 | 8.372 | 9.5065 | 9.7431 | 8.9432 | 7.9737 | 17 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 17 | 8609 | 9 | 9 | 3.8958 | 3.3621 | 15 | 88 | 88 | 0 | 0 | -4.4222 | 236.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 25 | 18 | 8610 | 8.8 | 8.8 | 3.8958 | 3.3621 | 15 | 90 | 90 | 0 | 0 | -12.5672 | 247.8749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 19 | 8611 | 8.9 | 8.9 | 3.8958 | 3.3621 | 15 | 91 | 91 | 0 | 0 | -21.3837 | 258.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 20 | 8612 | 9 | 9 | 3.8958 | 3.3621 | 15 | 90 | 90 | 0 | 0 | -30.5418 | 270.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 21 | 8613 | 9 | 9 | 3.8958 | 3.3621 | 15 | 92 | 92 | 0 | 0 | -39.6775 | 282.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 22 | 8614 | 8.9 | 8.9 | 3.8958 | 3.3621 | 15 | 92 | 92 | 0 | 0 | -48.2995 | 297.9682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 23 | 8615 | 8.9 | 8.9 | 3.8958 | 3.3621 | 15 | 92 | 92 | 0 | 0 | -55.6181 | 317.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 25 | 24 | 8616 | 8.9 | 8.9 | 8.1667 | 4.7018 | 15 | 92 | 92 | 0 | 0 | -60.3525 | 341.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 1 | 8617 | 8.8 | 8.8 | 8.1667 | 4.7018 | 15 | 92 | 92 | 0 | 0 | -61.0483 | 9.8646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 2 | 8618 | 8.9 | 8.9 | 8.1667 | 4.7018 | 15 | 91 | 91 | 0 | 0 | -57.4452 | 35.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 3 | 8619 | 8.8 | 8.8 | 8.1667 | 4.7018 | 15 | 90 | 90 | 0 | 0 | -50.784 | 56.5117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 4 | 8620 | 8.6 | 8.6 | 8.1667 | 4.7018 | 15 | 90 | 90 | 0 | 0 | -42.4705 | 72.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 5 | 8621 | 8.4 | 8.4 | 8.1667 | 4.7018 | 15 | 90 | 90 | 0 | 0 | -33.435 | 85.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 6 | 8622 | 8 | 8 | 8.1667 | 4.7018 | 15 | 92 | 92 | 0 | 0 | -24.2409 | 97.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 7 | 8623 | 7.9 | 7.9 | 8.1667 | 4.7018 | 15 | 91 | 91 | 0 | 0 | -15.2796 | 108.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 26 | 8 | 8624 | 7.6 | 7.6 | 8.1667 | 4.7018 | 15 | 91 | 91 | 0 | 0 | -6.885 | 119.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 9 | 8625 | 7.3 | 7.3 | 8.1667 | 4.7018 | 15 | 91 | 91 | 0 | 0 | 0.60691 | 131.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 10 | 8626 | 7 | 7 | 8.1667 | 4.7018 | 15 | 90 | 90 | 0.12431 | 2.9916 | 6.8337 | 143.6051 | 0 | 0.0080179 | 0.093382 | 0.12404 | 0.082043 | 0 | 0 | 0 | 0.0084355 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 1.4012 | 2.9916 | 1.4012 | 1.4092 | 1.4946 | 1.5253 | 1.4833 | 1.4012 | 1.4012 | 1.4012 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 11 | 8627 | 7 | 7 | 8.1667 | 4.7018 | 15 | 86 | 86 | 0.29333 | 10.9525 | 11.4155 | 156.7513 | 0 | 0 | 0.17281 | 0.28797 | 0.23444 | 0.043577 | 0 | 0 | 0.047512 | 5.1481 | 5.1481 | 5.1481 | 5.1481 | 5.1481 | 5.1481 | 5.1481 | 5.1481 | 10.9525 | 5.1481 | 5.1481 | 5.3209 | 5.436 | 5.3825 | 5.1916 | 5.1481 | 5.1481 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 12 | 8628 | 7.1 | 7.1 | 8.1667 | 4.7018 | 15 | 86 | 86 | 0.79386 | 24.8224 | 14.0057 | 170.6085 | 0 | 0 | 0.30716 | 0.72275 | 0.71497 | 0.28837 | 0 | 0 | 0.17764 | 11.8238 | 11.8238 | 11.8238 | 11.8238 | 11.8238 | 11.8238 | 11.8238 | 11.8238 | 24.8224 | 11.8238 | 11.8238 | 12.131 | 12.5466 | 12.5388 | 12.1122 | 11.8238 | 11.8238 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 13 | 8629 | 7.1 | 7.1 | 8.1667 | 4.7018 | 15 | 86 | 86 | 1.3292 | 35.669 | 14.3751 | 184.7994 | 0 | 0 | 0.21045 | 1.0485 | 1.2724 | 0.75091 | 0 | 0 | 0.331 | 17.1305 | 17.1305 | 17.1305 | 17.1305 | 17.1305 | 17.1305 | 17.1305 | 17.1305 | 35.669 | 17.1305 | 17.1305 | 17.3409 | 18.179 | 18.4028 | 17.8814 | 17.1305 | 17.1305 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 14 | 8630 | 7.1 | 7.1 | 8.1667 | 4.7018 | 15 | 84 | 84 | 1.0973 | 30.741 | 12.4887 | 198.8161 | 0 | 0 | 0 | 0.68607 | 1.0592 | 0.81184 | 0.08893 | 0 | 0.25897 | 14.6741 | 14.6741 | 14.6741 | 14.6741 | 14.6741 | 14.6741 | 14.6741 | 14.6741 | 30.741 | 14.6741 | 14.6741 | 14.6741 | 15.3601 | 15.7333 | 15.4859 | 14.763 | 14.6741 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 15 | 8631 | 7 | 7 | 8.1667 | 4.7018 | 15 | 83 | 83 | 1.1536 | 24.7859 | 8.519 | 212.2202 | 0 | 0 | 0 | 0.49699 | 1.0661 | 1.0107 | 0.36327 | 0 | 0.21414 | 11.7865 | 11.7865 | 11.7865 | 11.7865 | 11.7865 | 11.7865 | 11.7865 | 11.7865 | 24.7859 | 11.7865 | 11.7865 | 11.7865 | 12.2835 | 12.8526 | 12.7972 | 12.1497 | 11.7865 | 25 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 16 | 8632 | 6.9 | 6.9 | 8.1667 | 4.7018 | 15 | 83 | 83 | 0.74984 | 10.924 | 2.7845 | 224.7958 | 0 | 0 | 0 | 0.16404 | 0.62737 | 0.7232 | 0.39539 | 0 | 0.075965 | 5.1209 | 5.1209 | 5.1209 | 5.1209 | 5.1209 | 5.1209 | 5.1209 | 5.1209 | 10.924 | 5.1209 | 5.1209 | 5.1209 | 5.285 | 5.7483 | 5.8441 | 5.5163 | 5.1209 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 17 | 8633 | 6.5 | 6.5 | 8.1667 | 4.7018 | 15 | 82 | 82 | 0 | 0 | -4.338 | 236.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 26 | 18 | 8634 | 6.1 | 6.1 | 8.1667 | 4.7018 | 15 | 83 | 83 | 0 | 0 | -12.4775 | 247.8046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 19 | 8635 | 6.2 | 6.2 | 8.1667 | 4.7018 | 15 | 83 | 83 | 0 | 0 | -21.2908 | 258.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 20 | 8636 | 6.4 | 6.4 | 8.1667 | 4.7018 | 15 | 85 | 85 | 0 | 0 | -30.4478 | 270.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 21 | 8637 | 7 | 7 | 8.1667 | 4.7018 | 15 | 85 | 85 | 0 | 0 | -39.5851 | 282.9087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 22 | 8638 | 7.5 | 7.5 | 8.1667 | 4.7018 | 15 | 85 | 85 | 0 | 0 | -48.2123 | 297.8604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 23 | 8639 | 7.8 | 7.8 | 8.1667 | 4.7018 | 15 | 87 | 87 | 0 | 0 | -55.5433 | 316.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 26 | 24 | 8640 | 8.7 | 8.7 | 7.4875 | 5.4567 | 15 | 85 | 85 | 0 | 0 | -60.302 | 341.3625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 1 | 8641 | 9 | 9 | 7.4875 | 5.4567 | 15 | 85 | 85 | 0 | 0 | -61.033 | 9.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 2 | 8642 | 8.7 | 8.7 | 7.4875 | 5.4567 | 15 | 91 | 91 | 0 | 0 | -57.4551 | 35.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 3 | 8643 | 8.9 | 8.9 | 7.4875 | 5.4567 | 15 | 90 | 90 | 0 | 0 | -50.8153 | 56.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 4 | 8644 | 8.5 | 8.5 | 7.4875 | 5.4567 | 15 | 90 | 90 | 0 | 0 | -42.5128 | 72.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 5 | 8645 | 8.4 | 8.4 | 7.4875 | 5.4567 | 15 | 84 | 84 | 0 | 0 | -33.4813 | 85.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 6 | 8646 | 8.2 | 8.2 | 7.4875 | 5.4567 | 15 | 82 | 82 | 0 | 0 | -24.2867 | 97.3819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 7 | 8647 | 8 | 8 | 7.4875 | 5.4567 | 15 | 81 | 81 | 0 | 0 | -15.3213 | 108.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 27 | 8 | 8648 | 7.4 | 7.4 | 7.4875 | 5.4567 | 15 | 80 | 80 | 0 | 0 | -6.9195 | 119.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 9 | 8649 | 6.8 | 6.8 | 7.4875 | 5.4567 | 15 | 84 | 84 | 0 | 0 | 0.58275 | 131.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 10 | 8650 | 6.5 | 6.5 | 7.4875 | 5.4567 | 15 | 84 | 84 | 2.7283 | 13.8156 | 6.823 | 143.49 | 0 | 0.1813 | 2.053 | 2.7221 | 1.7966 | 0 | 0 | 0 | 0.18442 | 6.2225 | 7.5303 | 21.0323 | 25.8588 | 19.1827 | 6.2225 | 6.2225 | 6.2225 | 13.8156 | 6.2225 | 7.7116 | 23.0853 | 28.5809 | 20.9793 | 6.2225 | 6.2225 | 6.2225 | 14 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 11 | 8651 | 7 | 7 | 7.4875 | 5.4567 | 15 | 77 | 77 | 188.5922 | 77.4559 | 11.421 | 156.6344 | 0 | 0 | 111.4108 | 185.2045 | 150.508 | 27.6459 | 0 | 0 | 30.5441 | 40.0461 | 40.0461 | 99.3626 | 138.6513 | 120.1785 | 54.7652 | 40.0461 | 40.0461 | 77.4559 | 40.0461 | 40.0461 | 210.7734 | 323.8559 | 270.6865 | 82.4111 | 40.0461 | 40.0461 | 108 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 12 | 8652 | 7.5 | 7.5 | 7.4875 | 5.4567 | 15 | 75 | 75 | 465.7245 | 84.6633 | 14.0291 | 170.4927 | 0 | 0 | 181.0477 | 424.3445 | 419.0661 | 168.3044 | 0 | 0 | 104.3367 | 52.3632 | 52.3632 | 90.6891 | 142.1925 | 141.0751 | 87.9915 | 52.3632 | 52.3632 | 84.6633 | 52.3632 | 52.3632 | 271.7368 | 566.537 | 560.1411 | 256.2958 | 52.3632 | 52.3632 | 189 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 13 | 8653 | 7 | 7 | 7.4875 | 5.4567 | 15 | 75 | 75 | 278.1147 | 113.5891 | 14.4166 | 184.6889 | 0 | 0 | 44.5669 | 219.6841 | 266.1133 | 156.6569 | 0 | 0 | 69.4109 | 61.9269 | 61.9269 | 80.2515 | 152.2543 | 171.3446 | 126.3395 | 61.9269 | 61.9269 | 113.5891 | 61.9269 | 61.9269 | 124.8184 | 371.9384 | 437.4579 | 282.9964 | 61.9269 | 61.9269 | 183 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 14 | 8654 | 7.7 | 7.7 | 7.4875 | 5.4567 | 15 | 73 | 73 | 443.6548 | 91.9202 | 12.5469 | 198.7148 | 0 | 0 | 0 | 277.9789 | 428.2465 | 327.6531 | 35.1249 | 0 | 105.0798 | 56.1826 | 56.1826 | 56.1826 | 121.0751 | 156.1542 | 132.6713 | 64.3823 | 56.1826 | 91.9202 | 56.1826 | 56.1826 | 56.1826 | 399.0541 | 584.4007 | 460.3243 | 99.5072 | 56.1826 | 197 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 15 | 8655 | 7.1 | 7.1 | 7.4875 | 5.4567 | 15 | 77 | 77 | 91.8171 | 88.8558 | 8.5911 | 212.1299 | 0 | 0 | 0 | 39.6893 | 84.8857 | 80.3573 | 28.7566 | 0 | 17.1442 | 44.4995 | 44.4995 | 44.4995 | 79.9949 | 120.4156 | 116.3656 | 70.2175 | 44.4995 | 88.8558 | 44.4995 | 44.4995 | 44.4995 | 119.6842 | 205.3013 | 196.7229 | 98.9741 | 44.4995 | 106 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 16 | 8656 | 7.1 | 7.1 | 7.4875 | 5.4567 | 15 | 74 | 74 | 18.1975 | 40.1327 | 2.8673 | 224.7162 | 0 | 0 | 0 | 4.0079 | 15.2376 | 17.5413 | 9.5696 | 0 | 1.8673 | 20.2833 | 20.2833 | 20.2833 | 24.7732 | 37.3535 | 39.9344 | 31.0039 | 20.2833 | 40.1327 | 20.2833 | 20.2833 | 20.2833 | 28.781 | 52.5911 | 57.4757 | 40.5735 | 20.2833 | 42 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 17 | 8657 | 6.5 | 6.5 | 7.4875 | 5.4567 | 15 | 79 | 79 | 0 | 3 | -4.2475 | 236.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 3 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 1.3899 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 27 | 18 | 8658 | 5.7 | 5.7 | 7.4875 | 5.4567 | 15 | 80 | 80 | 0 | 0 | -12.382 | 247.7395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 19 | 8659 | 5.7 | 5.7 | 7.4875 | 5.4567 | 15 | 83 | 83 | 0 | 0 | -21.1923 | 258.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 20 | 8660 | 5.4 | 5.4 | 7.4875 | 5.4567 | 15 | 82 | 82 | 0 | 0 | -30.3484 | 270.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 21 | 8661 | 5.4 | 5.4 | 7.4875 | 5.4567 | 15 | 83 | 83 | 0 | 0 | -39.4869 | 282.8316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 22 | 8662 | 5.4 | 5.4 | 7.4875 | 5.4567 | 15 | 84 | 84 | 0 | 0 | -48.119 | 297.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 23 | 8663 | 5.3 | 5.3 | 7.4875 | 5.4567 | 15 | 86 | 86 | 0 | 0 | -55.4617 | 316.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 27 | 24 | 8664 | 5.7 | 5.7 | 7.0375 | 5.7694 | 15 | 86 | 86 | 0 | 0 | -60.2438 | 341.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 1 | 8665 | 5.6 | 5.6 | 7.0375 | 5.7694 | 15 | 89 | 89 | 0 | 0 | -61.0097 | 9.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 2 | 8666 | 5.3 | 5.3 | 7.0375 | 5.7694 | 15 | 93 | 93 | 0 | 0 | -57.4575 | 35.3873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 3 | 8667 | 5.3 | 5.3 | 7.0375 | 5.7694 | 15 | 95 | 95 | 0 | 0 | -50.8398 | 56.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 4 | 8668 | 5.4 | 5.4 | 7.0375 | 5.7694 | 15 | 95 | 95 | 0 | 0 | -42.5487 | 72.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 5 | 8669 | 5.6 | 5.6 | 7.0375 | 5.7694 | 15 | 97 | 97 | 0 | 0 | -33.5216 | 85.5231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 6 | 8670 | 6.3 | 6.3 | 7.0375 | 5.7694 | 15 | 97 | 97 | 0 | 0 | -24.3264 | 97.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 7 | 8671 | 7.6 | 7.6 | 7.0375 | 5.7694 | 15 | 97 | 97 | 0 | 0 | -15.3568 | 108.3848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 28 | 8 | 8672 | 8.3 | 8.3 | 7.0375 | 5.7694 | 15 | 92 | 92 | 0 | 0 | -6.9476 | 119.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 9 | 8673 | 8.4 | 8.4 | 7.0375 | 5.7694 | 15 | 89 | 89 | 0 | 0 | 0.56535 | 131.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 10 | 8674 | 8.7 | 8.7 | 7.0375 | 5.7694 | 15 | 87 | 87 | 0 | 0 | 6.8193 | 143.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 11 | 8675 | 7.7 | 7.7 | 7.0375 | 5.7694 | 15 | 93 | 93 | 0.021793 | 2.9965 | 11.4337 | 156.5157 | 0 | 0 | 0.01291 | 0.021408 | 0.017366 | 0.0031507 | 0 | 0 | 0.0035318 | 1.3832 | 1.3832 | 1.3832 | 1.3832 | 1.3832 | 1.3832 | 1.3832 | 1.3832 | 2.9965 | 1.3832 | 1.3832 | 1.3961 | 1.4046 | 1.4005 | 1.3863 | 1.3832 | 1.3832 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 12 | 8676 | 3.4 | 3.4 | 7.0375 | 5.7694 | 15 | 96 | 96 | 0.080818 | 7.9819 | 14.06 | 170.3764 | 0 | 0 | 0.031567 | 0.073695 | 0.072653 | 0.029052 | 0 | 0 | 0.018137 | 3.7132 | 3.7132 | 3.7132 | 3.7132 | 3.7132 | 3.7132 | 3.7132 | 3.7132 | 7.9819 | 3.7132 | 3.7132 | 3.7448 | 3.7869 | 3.7859 | 3.7423 | 3.7132 | 3.7132 | 8 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 13 | 8677 | 3.4 | 3.4 | 7.0375 | 5.7694 | 15 | 96 | 96 | 1.1059 | 32.7233 | 14.4657 | 184.5793 | 0 | 0 | 0.17934 | 0.87468 | 1.0576 | 0.62106 | 0 | 0 | 0.27675 | 15.6614 | 15.6614 | 15.6614 | 15.6614 | 15.6614 | 15.6614 | 15.6614 | 15.6614 | 32.7233 | 15.6614 | 15.6614 | 15.8408 | 16.5361 | 16.7191 | 16.2825 | 15.6614 | 15.6614 | 33 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 14 | 8678 | 4 | 4 | 7.0375 | 5.7694 | 15 | 97 | 97 | 0.54428 | 21.8706 | 12.6124 | 198.6155 | 0 | 0 | 0 | 0.34172 | 0.52534 | 0.40123 | 0.042077 | 0 | 0.12944 | 10.3352 | 10.3352 | 10.3352 | 10.3352 | 10.3352 | 10.3352 | 10.3352 | 10.3352 | 21.8706 | 10.3352 | 10.3352 | 10.3352 | 10.6769 | 10.8605 | 10.7364 | 10.3773 | 10.3352 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 15 | 8679 | 4.6 | 4.6 | 7.0375 | 5.7694 | 15 | 95 | 95 | 0.87149 | 21.8362 | 8.6702 | 212.0427 | 0 | 0 | 0 | 0.37794 | 0.80597 | 0.76187 | 0.27148 | 0 | 0.16378 | 10.3423 | 10.3423 | 10.3423 | 10.3423 | 10.3423 | 10.3423 | 10.3423 | 10.3423 | 21.8362 | 10.3423 | 10.3423 | 10.3423 | 10.7202 | 11.1482 | 11.1041 | 10.6138 | 10.3423 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 16 | 8680 | 4.3 | 4.3 | 7.0375 | 5.7694 | 15 | 93 | 93 | 2.8439 | 21.7041 | 2.9566 | 224.6406 | 0 | 0 | 0 | 0.63039 | 2.3831 | 2.7398 | 1.4916 | 0 | 0.29587 | 10.3784 | 10.3784 | 10.3784 | 10.3784 | 10.3784 | 10.3784 | 10.3784 | 10.3784 | 21.7041 | 10.3784 | 10.3784 | 10.3784 | 11.0088 | 12.7615 | 13.1182 | 11.87 | 10.3784 | 22 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 17 | 8681 | 3.6 | 3.6 | 7.0375 | 5.7694 | 15 | 94 | 94 | 0 | 3 | -4.151 | 236.4413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 3 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 1.3896 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 28 | 18 | 8682 | 5.1 | 5.1 | 7.0375 | 5.7694 | 15 | 87 | 87 | 0 | 0 | -12.2808 | 247.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 19 | 8683 | 4.6 | 4.6 | 7.0375 | 5.7694 | 15 | 82 | 82 | 0 | 0 | -21.0884 | 258.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 20 | 8684 | 4.3 | 4.3 | 7.0375 | 5.7694 | 15 | 86 | 86 | 0 | 0 | -30.2435 | 270.1775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 21 | 8685 | 5 | 5 | 7.0375 | 5.7694 | 15 | 86 | 86 | 0 | 0 | -39.3832 | 282.7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 22 | 8686 | 4.8 | 4.8 | 7.0375 | 5.7694 | 15 | 83 | 83 | 0 | 0 | -48.0198 | 297.6675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 23 | 8687 | 4.7 | 4.7 | 7.0375 | 5.7694 | 15 | 81 | 81 | 0 | 0 | -55.3733 | 316.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 28 | 24 | 8688 | 4.3 | 4.3 | 5.4292 | 5.7421 | 15 | 80 | 80 | 0 | 0 | -60.178 | 340.9684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 1 | 8689 | 4.5 | 4.5 | 5.4292 | 5.7421 | 15 | 81 | 81 | 0 | 0 | -60.9784 | 9.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 2 | 8690 | 4.7 | 4.7 | 5.4292 | 5.7421 | 15 | 81 | 81 | 0 | 0 | -57.4523 | 35.1652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 3 | 8691 | 4.4 | 4.4 | 5.4292 | 5.7421 | 15 | 86 | 86 | 0 | 0 | -50.8574 | 55.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 4 | 8692 | 5 | 5 | 5.4292 | 5.7421 | 15 | 81 | 81 | 0 | 0 | -42.5783 | 72.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 5 | 8693 | 4.8 | 4.8 | 5.4292 | 5.7421 | 15 | 82 | 82 | 0 | 0 | -33.5558 | 85.3857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 6 | 8694 | 4.8 | 4.8 | 5.4292 | 5.7421 | 15 | 81 | 81 | 0 | 0 | -24.3601 | 97.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 7 | 8695 | 4.9 | 4.9 | 5.4292 | 5.7421 | 15 | 79 | 79 | 0 | 0 | -15.3862 | 108.2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 29 | 8 | 8696 | 5 | 5 | 5.4292 | 5.7421 | 15 | 80 | 80 | 0 | 0 | -6.9692 | 119.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 9 | 8697 | 4.8 | 4.8 | 5.4292 | 5.7421 | 15 | 83 | 83 | 0 | 0 | 0.55474 | 130.9548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 10 | 8698 | 3.9 | 3.9 | 5.4292 | 5.7421 | 15 | 87 | 87 | 1.6931 | 10.8859 | 6.8228 | 143.2519 | 0 | 0.11943 | 1.2786 | 1.6888 | 1.1097 | 0 | 0 | 0 | 0.11414 | 5.1451 | 5.6433 | 10.4785 | 12.1894 | 9.7739 | 5.1451 | 5.1451 | 5.1451 | 10.8859 | 5.1451 | 5.7627 | 11.7571 | 13.8782 | 10.8836 | 5.1451 | 5.1451 | 5.1451 | 11 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 11 | 8699 | 4 | 4 | 5.4292 | 5.7421 | 15 | 86 | 86 | 33.4874 | 69.5654 | 11.4539 | 156.3955 | 0 | 0 | 19.8936 | 32.906 | 26.6426 | 4.7723 | 0 | 0 | 5.4346 | 31.978 | 31.978 | 94.5007 | 135.3969 | 115.7118 | 46.9765 | 31.978 | 31.978 | 69.5654 | 31.978 | 31.978 | 114.3943 | 168.303 | 142.3543 | 51.7487 | 31.978 | 31.978 | 75 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 12 | 8700 | 5.6 | 5.6 | 5.4292 | 5.7421 | 15 | 78 | 78 | 135.3842 | 108.5484 | 14.0984 | 170.2597 | 0 | 0 | 53.131 | 123.5437 | 121.5862 | 48.4051 | 0 | 0 | 30.4516 | 52.8219 | 52.8219 | 101.3714 | 165.7124 | 163.9237 | 97.053 | 52.8219 | 52.8219 | 108.5484 | 52.8219 | 52.8219 | 154.5024 | 289.2561 | 285.5098 | 145.4581 | 52.8219 | 52.8219 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 13 | 8701 | 4.6 | 4.6 | 5.4292 | 5.7421 | 15 | 81 | 81 | 26.7711 | 104.2789 | 14.5222 | 184.4705 | 0 | 0 | 4.3928 | 21.2013 | 25.5905 | 14.989 | 0 | 0 | 6.7211 | 49.5007 | 49.5007 | 60.233 | 101.2991 | 112.0224 | 86.1213 | 49.5007 | 49.5007 | 104.2789 | 49.5007 | 49.5007 | 64.6258 | 122.5004 | 137.6129 | 101.1104 | 49.5007 | 49.5007 | 111 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 14 | 8702 | 4.6 | 4.6 | 5.4292 | 5.7421 | 15 | 81 | 81 | 8.0089 | 79.0867 | 12.6852 | 198.5183 | 0 | 0 | 0 | 5.0382 | 7.7294 | 5.8929 | 0.60431 | 0 | 1.9133 | 38.3981 | 38.3981 | 38.3981 | 45.3669 | 49.0894 | 46.549 | 39.234 | 38.3981 | 79.0867 | 38.3981 | 38.3981 | 38.3981 | 50.4051 | 56.8188 | 52.4419 | 39.8383 | 38.3981 | 81 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 15 | 8703 | 4.1 | 4.1 | 5.4292 | 5.7421 | 15 | 85 | 85 | 3.9213 | 46.2578 | 8.7561 | 211.9587 | 0 | 0 | 0 | 1.7059 | 3.6275 | 3.4242 | 1.215 | 0 | 0.74222 | 22.5918 | 22.5918 | 22.5918 | 22.5918 | 22.5918 | 22.5918 | 22.5918 | 22.5918 | 46.2578 | 22.5918 | 22.5918 | 22.5918 | 24.2977 | 26.2193 | 26.016 | 23.8068 | 22.5918 | 47 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 16 | 8704 | 3.7 | 3.7 | 5.4292 | 5.7421 | 15 | 88 | 88 | 2.0596 | 18.7826 | 3.0524 | 224.5689 | 0 | 0 | 0 | 0.45933 | 1.727 | 1.9831 | 1.0774 | 0 | 0.21745 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 8.9304 | 18.7826 | 8.9304 | 8.9304 | 8.9304 | 9.3898 | 10.6575 | 10.9135 | 10.0079 | 8.9304 | 19 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 17 | 8705 | 3.2 | 3.2 | 5.4292 | 5.7421 | 15 | 92 | 92 | 0 | 0 | -4.0485 | 236.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 18 | 8706 | 3.2 | 3.2 | 5.4292 | 5.7421 | 15 | 92 | 92 | 0 | 0 | -12.1738 | 247.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 19 | 8707 | 3.3 | 3.3 | 5.4292 | 5.7421 | 15 | 93 | 93 | 0 | 0 | -20.979 | 258.6916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 20 | 8708 | 3 | 3 | 5.4292 | 5.7421 | 15 | 94 | 94 | 0 | 0 | -30.1333 | 270.1239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 21 | 8709 | 3.1 | 3.1 | 5.4292 | 5.7421 | 15 | 95 | 95 | 0 | 0 | -39.2741 | 282.6985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 22 | 8710 | 3.1 | 3.1 | 5.4292 | 5.7421 | 15 | 95 | 95 | 0 | 0 | -47.9147 | 297.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 23 | 8711 | 3.4 | 3.4 | 5.4292 | 5.7421 | 15 | 94 | 94 | 0 | 0 | -55.2783 | 316.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 29 | 24 | 8712 | 2.9 | 2.9 | 4.1083 | 5.5553 | 15 | 93 | 93 | 0 | 0 | -60.1046 | 340.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 1 | 8713 | 1.4 | 1.4 | 4.1083 | 5.5553 | 15 | 95 | 95 | 0 | 0 | -60.9392 | 8.9366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 2 | 8714 | 1.3 | 1.3 | 4.1083 | 5.5553 | 15 | 96 | 96 | 0 | 0 | -57.4395 | 34.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 3 | 8715 | 1.3 | 1.3 | 4.1083 | 5.5553 | 15 | 96 | 96 | 0 | 0 | -50.8681 | 55.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 4 | 8716 | 1.3 | 1.3 | 4.1083 | 5.5553 | 15 | 97 | 97 | 0 | 0 | -42.6015 | 71.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 5 | 8717 | 1.1 | 1.1 | 4.1083 | 5.5553 | 15 | 97 | 97 | 0 | 0 | -33.5837 | 85.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 6 | 8718 | 0.8 | 0.8 | 4.1083 | 5.5553 | 15 | 97 | 97 | 0 | 0 | -24.3876 | 97.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 7 | 8719 | 0.8 | 0.8 | 4.1083 | 5.5553 | 15 | 97 | 97 | 0 | 0 | -15.4092 | 108.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 30 | 8 | 8720 | 0.9 | 0.9 | 4.1083 | 5.5553 | 15 | 96 | 96 | 0 | 0 | -6.9842 | 119.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 9 | 8721 | 1.3 | 1.3 | 4.1083 | 5.5553 | 15 | 96 | 96 | 0 | 0 | 0.55095 | 130.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 10 | 8722 | 1.9 | 1.9 | 4.1083 | 5.5553 | 15 | 95 | 95 | 7.0508 | 21.5241 | 6.8334 | 143.129 | 0 | 0.51239 | 5.3346 | 7.0318 | 4.6099 | 0 | 0 | 0 | 0.47595 | 9.468 | 13.1202 | 47.4913 | 59.5889 | 42.3263 | 9.468 | 9.468 | 9.468 | 21.5241 | 9.468 | 13.6326 | 52.8259 | 66.6207 | 46.9363 | 9.468 | 9.468 | 9.468 | 22 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 11 | 8723 | 2.7 | 2.7 | 4.1083 | 5.5553 | 15 | 91 | 91 | 40.3634 | 71.4355 | 11.4815 | 156.2738 | 0 | 0 | 24.0466 | 39.674 | 32.0609 | 5.6669 | 0 | 0 | 6.5645 | 32.7635 | 32.7635 | 98.9266 | 141.9245 | 120.9774 | 48.3558 | 32.7635 | 32.7635 | 71.4355 | 32.7635 | 32.7635 | 122.9732 | 181.5985 | 153.0383 | 54.0228 | 32.7635 | 32.7635 | 78 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 12 | 8724 | 3.3 | 3.3 | 4.1083 | 5.5553 | 15 | 89 | 89 | 23.2749 | 91.7501 | 14.1444 | 170.1427 | 0 | 0 | 9.1776 | 21.2549 | 20.8813 | 8.2757 | 0 | 0 | 5.2499 | 43.2408 | 43.2408 | 71.5079 | 108.7056 | 107.5549 | 68.7299 | 43.2408 | 43.2408 | 91.7501 | 43.2408 | 43.2408 | 80.6855 | 129.9604 | 128.4362 | 77.0057 | 43.2408 | 43.2408 | 97 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 13 | 8725 | 4.1 | 4.1 | 4.1083 | 5.5553 | 15 | 88 | 88 | 80.1429 | 118.8048 | 14.5863 | 184.3626 | 0 | 0 | 13.3042 | 63.5478 | 76.566 | 44.7328 | 0 | 0 | 20.1952 | 56.4897 | 56.4897 | 70.5329 | 123.5674 | 137.3088 | 103.7074 | 56.4897 | 56.4897 | 118.8048 | 56.4897 | 56.4897 | 83.837 | 187.1152 | 213.8747 | 148.4402 | 56.4897 | 56.4897 | 139 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 14 | 8726 | 4.5 | 4.5 | 4.1083 | 5.5553 | 15 | 89 | 89 | 3.4592 | 55.1694 | 12.7653 | 198.4233 | 0 | 0 | 0 | 2.1803 | 3.338 | 2.5404 | 0.25466 | 0 | 0.83059 | 27.0368 | 27.0368 | 27.0368 | 27.0368 | 27.0368 | 27.0368 | 27.0368 | 27.0368 | 55.1694 | 27.0368 | 27.0368 | 27.0368 | 29.217 | 30.3748 | 29.5772 | 27.2914 | 27.0368 | 56 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 15 | 8727 | 5 | 5 | 4.1083 | 5.5553 | 15 | 89 | 89 | 6.6839 | 59.7251 | 8.8489 | 211.8778 | 0 | 0 | 0 | 2.9165 | 6.1846 | 5.8299 | 2.0601 | 0 | 1.2749 | 29.6457 | 29.6457 | 29.6457 | 29.6606 | 29.6772 | 29.6754 | 29.6562 | 29.6457 | 59.7251 | 29.6457 | 29.6457 | 29.6457 | 32.577 | 35.8618 | 35.5053 | 31.7164 | 29.6457 | 61 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 16 | 8728 | 5.1 | 5.1 | 4.1083 | 5.5553 | 15 | 89 | 89 | 1.598 | 16.8286 | 3.1545 | 224.5013 | 0 | 0 | 0 | 0.35848 | 1.3409 | 1.5378 | 0.83389 | 0 | 0.17138 | 7.9706 | 7.9706 | 7.9706 | 7.9706 | 7.9706 | 7.9706 | 7.9706 | 7.9706 | 16.8286 | 7.9706 | 7.9706 | 7.9706 | 8.3291 | 9.3115 | 9.5084 | 8.8045 | 7.9706 | 17 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 17 | 8729 | 4.6 | 4.6 | 4.1083 | 5.5553 | 15 | 91 | 91 | 0 | 0 | -3.94 | 236.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 18 | 8730 | 4.2 | 4.2 | 4.1083 | 5.5553 | 15 | 93 | 93 | 0 | 0 | -12.0613 | 247.5754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 19 | 8731 | 4 | 4 | 4.1083 | 5.5553 | 15 | 92 | 92 | 0 | 0 | -20.8642 | 258.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 20 | 8732 | 3.7 | 3.7 | 4.1083 | 5.5553 | 15 | 92 | 92 | 0 | 0 | -30.0179 | 270.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 21 | 8733 | 3.3 | 3.3 | 4.1083 | 5.5553 | 15 | 93 | 93 | 0 | 0 | -39.1595 | 282.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 22 | 8734 | 3.2 | 3.2 | 4.1083 | 5.5553 | 15 | 93 | 93 | 0 | 0 | -47.8038 | 297.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 23 | 8735 | 2.9 | 2.9 | 4.1083 | 5.5553 | 15 | 94 | 94 | 0 | 0 | -55.1768 | 316.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 30 | 24 | 8736 | 2.4 | 2.4 | 2.7125 | 4.9999 | 15 | 95 | 95 | 0 | 0 | -60.0237 | 340.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 1 | 8737 | 1.9 | 1.9 | 2.7125 | 4.9999 | 15 | 96 | 96 | 0 | 0 | -60.8919 | 8.7042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 2 | 8738 | 1.6 | 1.6 | 2.7125 | 4.9999 | 15 | 97 | 97 | 0 | 0 | -57.419 | 34.7086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 3 | 8739 | 1.4 | 1.4 | 2.7125 | 4.9999 | 15 | 98 | 98 | 0 | 0 | -50.8719 | 55.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 4 | 8740 | 1.5 | 1.5 | 2.7125 | 4.9999 | 15 | 98 | 98 | 0 | 0 | -42.6182 | 71.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 5 | 8741 | 1.2 | 1.2 | 2.7125 | 4.9999 | 15 | 99 | 99 | 0 | 0 | -33.6054 | 85.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 6 | 8742 | 1.1 | 1.1 | 2.7125 | 4.9999 | 15 | 98 | 98 | 0 | 0 | -24.4089 | 96.8683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 7 | 8743 | 0.8 | 0.8 | 2.7125 | 4.9999 | 15 | 99 | 99 | 0 | 0 | -15.4259 | 108.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0.5 | 0.5 | 0.5 | 0.1 | 0.5 | 0.5
2003 | 12 | 31 | 8 | 8744 | 0.9 | 0.9 | 2.7125 | 4.9999 | 15 | 99 | 99 | 0 | 0 | -6.9928 | 119.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 9 | 8745 | 0.6 | 0.6 | 2.7125 | 4.9999 | 15 | 99 | 99 | 0 | 0 | 0.554 | 130.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 10 | 8746 | 0.9 | 0.9 | 2.7125 | 4.9999 | 15 | 99 | 99 | 0.49946 | 5.9662 | 6.8511 | 143.0037 | 0 | 0.037389 | 0.3786 | 0.49803 | 0.32572 | 0 | 0 | 0 | 0.033815 | 2.8682 | 2.8682 | 2.8682 | 2.8682 | 2.8682 | 2.8682 | 2.8682 | 2.8682 | 5.9662 | 2.8682 | 2.9056 | 3.2468 | 3.3662 | 3.1939 | 2.8682 | 2.8682 | 2.8682 | 6 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 11 | 8747 | 1.3 | 1.3 | 2.7125 | 4.9999 | 15 | 99 | 99 | 2.2973 | 30.6253 | 11.5165 | 156.1506 | 0 | 0 | 1.3726 | 2.2587 | 1.8217 | 0.31759 | 0 | 0 | 0.3747 | 15.0321 | 15.0321 | 15.0321 | 15.0321 | 15.0321 | 15.0321 | 15.0321 | 15.0321 | 30.6253 | 15.0321 | 15.0321 | 16.4046 | 17.2908 | 16.8538 | 15.3497 | 15.0321 | 15.0321 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 12 | 8748 | 1.2 | 1.2 | 2.7125 | 4.9999 | 15 | 99 | 99 | 2.7426 | 46.3793 | 14.1978 | 170.0254 | 0 | 0 | 1.0866 | 2.5064 | 2.4579 | 0.96966 | 0 | 0 | 0.62071 | 22.7428 | 22.7428 | 22.7428 | 22.7428 | 22.7428 | 22.7428 | 22.7428 | 22.7428 | 46.3793 | 22.7428 | 22.7428 | 23.8294 | 25.2491 | 25.2007 | 23.7124 | 22.7428 | 22.7428 | 47 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 13 | 8749 | 1.1 | 1.1 | 2.7125 | 4.9999 | 15 | 98 | 98 | 2.4829 | 49.3717 | 14.6578 | 184.2558 | 0 | 0 | 0.41694 | 1.9712 | 2.3707 | 1.3815 | 0 | 0 | 0.62829 | 24.0665 | 24.0665 | 24.0665 | 24.0665 | 24.0665 | 24.0665 | 24.0665 | 24.0665 | 49.3717 | 24.0665 | 24.0665 | 24.4834 | 26.0376 | 26.4372 | 25.448 | 24.0665 | 24.0665 | 50 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 14 | 8750 | 1.4 | 1.4 | 2.7125 | 4.9999 | 15 | 95 | 95 | 1.4138 | 35.6586 | 12.8525 | 198.3305 | 0 | 0 | 0 | 0.8927 | 1.364 | 1.0362 | 0.1015 | 0 | 0.34135 | 17.1058 | 17.1058 | 17.1058 | 17.1058 | 17.1058 | 17.1058 | 17.1058 | 17.1058 | 35.6586 | 17.1058 | 17.1058 | 17.1058 | 17.9985 | 18.4698 | 18.1421 | 17.2073 | 17.1058 | 36 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 15 | 8751 | 1.1 | 1.1 | 2.7125 | 4.9999 | 15 | 94 | 94 | 1.6523 | 30.6822 | 8.9485 | 211.8003 | 0 | 0 | 0 | 0.72302 | 1.5291 | 1.4395 | 0.50661 | 0 | 0.31777 | 14.6894 | 14.6894 | 14.6894 | 14.6894 | 14.6894 | 14.6894 | 14.6894 | 14.6894 | 30.6822 | 14.6894 | 14.6894 | 14.6894 | 15.4124 | 16.2185 | 16.1289 | 15.196 | 14.6894 | 31 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 16 | 8752 | 1.3 | 1.3 | 2.7125 | 4.9999 | 15 | 94 | 94 | 0.64737 | 10.9294 | 3.263 | 224.4378 | 0 | 0 | 0 | 0.14603 | 0.5435 | 0.6226 | 0.33699 | 0 | 0.07058 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 5.12 | 10.9294 | 5.12 | 5.12 | 5.12 | 5.266 | 5.6635 | 5.7426 | 5.457 | 5.12 | 11 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 17 | 8753 | 1.3 | 1.3 | 2.7125 | 4.9999 | 15 | 91 | 91 | 0 | 3 | -3.8255 | 236.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 3 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 1.3887 | 3 | 0.2 | 0.2 | 1 | 0.2 | 0.2 | 0.2 | 1 | 0.2
2003 | 12 | 31 | 18 | 8754 | 0.9 | 0.9 | 2.7125 | 4.9999 | 15 | 91 | 91 | 0 | 0 | -11.9433 | 247.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 19 | 8755 | 0.8 | 0.8 | 2.7125 | 4.9999 | 15 | 92 | 92 | 0 | 0 | -20.7443 | 258.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 20 | 8756 | 0.5 | 0.5 | 2.7125 | 4.9999 | 15 | 94 | 94 | 0 | 0 | -29.8972 | 270.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 21 | 8757 | 0.8 | 0.8 | 2.7125 | 4.9999 | 15 | 94 | 94 | 0 | 0 | -39.0397 | 282.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 22 | 8758 | 1.1 | 1.1 | 2.7125 | 4.9999 | 15 | 92 | 92 | 0 | 0 | -47.6871 | 297.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 23 | 8759 | 1.1 | 1.1 | 2.7125 | 4.9999 | 15 | 87 | 87 | 0 | 0 | -55.0687 | 316.2171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
2003 | 12 | 31 | 24 | 8760 | 0.1 | 0.1 |  |  | 15 | 88 | 88 | 0 | 0 | -59.9353 | 340.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 1 | 0.5
[14 empty] | -60.8367 | 8.4723
[31 empty] | Total sun radiation (kWh/m2) |  |  | 319.6607 | 439.17 | 657.2602 | 816.078 | 823.5553 | 726.3024 | 559.4323 | 390.5959 | 996.643
Note on N7630: Willem van der Spoel - BK: hier staat origineel 99, maar dat geeft een vreemd resultaat. Met de hand aangepast

## Calc
© TU Delft, Faculty of Architecture | [11 empty] | Heating mode | Cooling mode | Heating mode | Cooling mode | [27 empty] | Free floating |  | Free floating | [15 empty] | heating and cooling sorted |  |  | summer comfort
contact: dr.ir. W.H. van der Spoel | [11 empty] | Ventilation | Ventilation | Total Coupling | Total Coupling | Ground | [25 empty] | Max heating | with H_heat | Max cooling | with H_cool | Indoor temperature |  | Q_heat (kWh) | Q_cool (kWh) | Q_heat+cool (kWh) | T_set | T_set | T_set | condition logic | [7 empty] | heating | cooling | T_i | cat 1 | cat 2 | cat 3
version 1.4 | [6 empty] | Transmission coupling (W/K) |  |  |  | Infiltration coupling (W/K) | Coupling (W/K) | Coupling (W/K) | (W/K) | (W/K) | coupling (W/K) | Solar radiation through glazing (Wh) | [9 empty] | Solar radiation opaque parts (Wh) | [9 empty] | Internal heat gains (Wh) |  |  |  |  | T_i | T_i | T_i | T_i | T_i | sum: | 83610.961 | 34115.3187 |  | heating | cooling | vent.cool | 1 | 2 | 3 | 4 | 5 | 6 | 7 |  | sorted | sorted | counting
|  | Year | Month | Day | Hours | Hour | Window | Wall | Roof | Total | [6 empty] | North | N-E | East | S-E | South | S-W | West | N-W | Roof | Total | North | N-E | East | S-E | South | S-W | West | N-W | Roof | Total | People | Lighting | Appliances | Fans | Total | 20 | 20 | 20 |  | 20 |  | 0 | 0 | 0 | [11 empty] | kWh | kWh | hours | 0 | 0 | 0
|  | 2001 | 1 | 1 | 1 | 1 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5441 | 19.8471 | 16.6468 | 19.3036 | 19.8471 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8760 | 0 | 122.2952 | 19.8471 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 2 | 2 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3926 | 19.6957 | 16.4999 | 19.1567 | 19.6957 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8759 | 0 | 121.1042 | 19.6957 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 3 | 3 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2445 | 19.5476 | 16.3621 | 19.0189 | 19.5476 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8758 | 0 | 119.6182 | 19.5476 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 4 | 4 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.096 | 19.399 | 16.212 | 18.8689 | 19.399 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8757 | 0 | 119.4524 | 19.399 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 5 | 5 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9462 | 19.2492 | 16.0577 | 18.7146 | 19.2492 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8756 | 0 | 113.7542 | 19.2492 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 6 | 6 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7969 | 19.0999 | 15.9099 | 18.5667 | 19.0999 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8755 | 0 | 112.8369 | 19.0999 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 7 | 7 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.649 | 18.952 | 15.7664 | 18.4233 | 18.952 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8754 | 0 | 111.1006 | 18.952 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 8 | 8 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.526 | 18.8281 | 15.6512 | 18.309 | 20 |  | 434.3772 | 0 | 434.3772 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8753 | 0 | 110.9673 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 9 | 9 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5663 | 19.8684 | 16.6666 | 19.3244 | 20 |  | 48.7886 | 0 | 48.7886 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8752 | 0 | 110.5132 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 10 | 10 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5688 | 19.8709 | 16.6779 | 19.3357 | 20 |  | 47.8534 | 0 | 47.8534 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8751 | 0 | 110.1318 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 11 | 11 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 301.4145 | 0 | 177.0407 | 0 | 403.5622 | 0 | 171.8591 | 0 | 1053.8765 | 0 | 22.292 | 0 | 9.8324 | 0 | 19.6252 | 0 | 9.5446 | 26.1983 | 87.4926 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5753 | 19.8773 | 16.6961 | 19.3539 | 20 |  | 45.4652 | 0 | 45.4652 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8750 | 0 | 107.4401 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 12 | 12 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 967.1324 | 0 | 576.5407 | 0 | 1312.0766 | 0 | 551.4352 | 0 | 3407.185 | 0 | 71.5272 | 0 | 32.0197 | 0 | 63.8062 | 0 | 30.6254 | 82.9613 | 280.9398 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5855 | 19.8876 | 16.718 | 19.3758 | 20 |  | 41.6716 | 0 | 41.6716 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8749 | 0 | 107.1947 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 13 | 13 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2015.1076 | 0 | 1222.4399 | 0 | 2806.7077 | 0 | 1148.9648 | 0 | 7193.22 | 0 | 149.0334 | 0 | 67.8914 | 0 | 136.49 | 0 | 63.8107 | 170.289 | 587.5145 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6033 | 19.9053 | 16.7591 | 19.4169 | 20 |  | 35.0852 | 0 | 35.0852 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8748 | 0 | 106.971 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 14 | 14 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1853.1743 | 0 | 1111.242 | 0 | 2618.5781 | 0 | 1056.6345 | 0 | 6639.6289 | 0 | 137.0571 | 0 | 61.7157 | 0 | 127.3413 | 0 | 58.6829 | 157.1898 | 541.9868 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6067 | 19.9088 | 16.7802 | 19.438 | 20 |  | 33.814 | 0 | 33.814 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8747 | 0 | 106.9213 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 15 | 15 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 964.8764 | 0 | 566.6998 | 0 | 1363.2556 | 0 | 550.1489 | 0 | 3444.9807 | 0 | 71.3604 | 0 | 31.4731 | 0 | 66.295 | 0 | 30.5539 | 82.9613 | 282.6438 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6007 | 19.9028 | 16.7861 | 19.4439 | 20 |  | 36.0211 | 0 | 36.0211 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8746 | 0 | 106.7531 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 16 | 16 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 401.9563 | 0 | 233.8341 | 0 | 582.0203 | 0 | 229.1856 | 0 | 1446.9964 | 0 | 29.7279 | 0 | 12.9866 | 0 | 28.3036 | 0 | 12.7284 | 34.9311 | 118.6776 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5949 | 19.897 | 16.7804 | 19.4382 | 20 |  | 38.183 | 0 | 38.183 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8745 | 0 | 106.0978 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 17 | 17 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 150.4257 | 0 | 85.7691 | 0 | 200.5676 | 0 | 85.7691 | 0 | 522.5315 | 0 | 11.1252 | 0 | 4.7634 | 0 | 9.7536 | 0 | 4.7634 | 13.0992 | 43.5047 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.593 | 19.8951 | 16.7815 | 19.4393 | 20 |  | 38.871 | 0 | 38.871 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8744 | 0 | 105.7903 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 18 | 18 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6201 | 19.9232 | 16.8132 | 19.47 | 20 |  | 28.4875 | 0 | 28.4875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8743 | 0 | 105.5409 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 19 | 19 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6219 | 19.925 | 16.8209 | 19.4777 | 20 |  | 27.8107 | 0 | 27.8107 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8742 | 0 | 105.3134 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 20 | 20 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6238 | 19.9268 | 16.8286 | 19.4854 | 20 |  | 27.134 | 0 | 27.134 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8741 | 0 | 104.8474 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 21 | 21 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8740 | 0 | 103.5523 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 22 | 22 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6311 | 19.9341 | 16.8594 | 19.5162 | 20 |  | 24.4271 | 0 | 24.4271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8739 | 0 | 103.4226 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 23 | 23 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6338 | 19.9369 | 16.8709 | 19.5278 | 20 |  | 23.412 | 0 | 23.412 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8738 | 0 | 103.2115 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 1 | 24 | 24 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6338 | 19.9369 | 16.8709 | 19.5278 | 20 |  | 23.412 | 0 | 23.412 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8737 | 0 | 103.1462 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 1 | 25 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.587 | 19.89 | 16.8277 | 19.4845 | 19.89 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8736 | 0 | 103.0575 | 19.89 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 2 | 26 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4771 | 19.7802 | 16.7181 | 19.375 | 19.7802 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8735 | 0 | 102.9623 | 19.7802 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 3 | 27 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3683 | 19.6714 | 16.6126 | 19.2694 | 19.6714 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8734 | 0 | 102.5738 | 19.6714 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 4 | 28 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2578 | 19.5609 | 16.4965 | 19.1533 | 19.5609 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8733 | 0 | 102.3707 | 19.5609 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 5 | 29 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1557 | 19.4588 | 16.4211 | 19.0779 | 19.4588 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8732 | 0 | 102.3077 | 19.4588 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 6 | 30 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0564 | 19.3595 | 16.3307 | 18.9875 | 19.3595 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8731 | 0 | 102.1938 | 19.3595 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 7 | 31 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9635 | 19.2666 | 16.2583 | 18.9152 | 19.2666 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8730 | 0 | 102.0677 | 19.2666 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 8 | 32 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8874 | 19.1894 | 16.1767 | 18.8345 | 20 |  | 300.4378 | 0 | 300.4378 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8729 | 0 | 101.945 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 9 | 33 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.61 | 19.9121 | 16.8631 | 19.5209 | 20 |  | 32.5792 | 0 | 32.5792 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8728 | 0 | 101.5697 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 10 | 34 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 630.8842 | 0 | 837.3973 | 0 | 744.5087 | 0 | 318.3754 | 0 | 2531.1655 | 0 | 46.6589 | 0 | 46.507 | 0 | 36.2054 | 0 | 17.6818 | 48.0302 | 195.0834 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6241 | 19.9262 | 16.9006 | 19.5584 | 20 |  | 27.3592 | 0 | 27.3592 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8727 | 0 | 101.3259 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 11 | 35 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4393.7839 | 0 | 19323.1183 | 0 | 11208.0006 | 0 | 2505.2277 | 0 | 37430.1305 | 0 | 324.9556 | 0 | 1073.1594 | 0 | 545.0443 | 0 | 139.1343 | 471.5695 | 2553.8631 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7347 | 20.0368 | 17.045 | 19.7028 | 20.0368 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8726 | 0 | 101.2288 | 20.0368 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 12 | 36 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5778.705 | 0 | 17479.357 | 0 | 20371.4589 | 0 | 3294.8757 | 0 | 46924.3967 | 0 | 427.3816 | 0 | 970.7614 | 0 | 990.6626 | 0 | 182.9895 | 606.9274 | 3178.7225 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8086 | 20.1107 | 17.1526 | 19.8104 | 20.1107 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8725 | 0 | 101.1431 | 20.1107 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 13 | 37 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6027.3757 | 0 | 10394.2128 | 0 | 19340.3607 | 0 | 3436.6616 | 0 | 39198.6108 | 0 | 445.7728 | 0 | 577.2695 | 0 | 940.5204 | 0 | 190.8639 | 580.7291 | 2735.1557 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8597 | 20.1618 | 17.202 | 19.8597 | 20.1618 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8724 | 0 | 101.1397 | 20.1618 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 14 | 38 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5554.8653 | 0 | 7225.1317 | 0 | 18340.128 | 0 | 3167.2477 | 0 | 34287.3727 | 0 | 410.8268 | 0 | 401.2664 | 0 | 891.8792 | 0 | 175.9013 | 510.8669 | 2390.7407 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9022 | 20.2042 | 17.2636 | 19.9214 | 20.2042 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8723 | 0 | 101.0491 | 20.2042 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 15 | 39 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4977.5176 | 0 | 7275.2402 | 0 | 27135.3147 | 0 | 2838.0583 | 0 | 42226.1307 | 0 | 368.1273 | 0 | 404.0493 | 0 | 1319.5885 | 0 | 157.6189 | 471.5695 | 2720.9535 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9665 | 20.2686 | 17.3264 | 19.9842 | 20.2686 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8722 | 0 | 101.0438 | 20.2686 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 16 | 40 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 863.3181 | 0 | 512.5945 | 0 | 1351.7188 | 0 | 492.2428 | 0 | 3219.8742 | 0 | 63.8493 | 0 | 28.4683 | 0 | 65.734 | 0 | 27.338 | 74.2285 | 259.6181 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9159 | 20.218 | 17.2667 | 19.9245 | 20.218 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8721 | 0 | 100.9287 | 20.218 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 17 | 41 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 60.225 | 0 | 39.4866 | 0 | 1099.68 | 0 | 34.3388 | 0 | 1233.7305 | 0 | 4.4541 | 0 | 2.193 | 0 | 53.4774 | 0 | 1.9071 | 13.0992 | 75.1307 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.859 | 20.1611 | 17.2085 | 19.8663 | 20.1611 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8720 | 0 | 100.7791 | 20.1611 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 18 | 42 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8271 | 20.1301 | 17.1681 | 19.825 | 20.1301 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8719 | 0 | 100.552 | 20.1301 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 19 | 43 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7965 | 20.0995 | 17.1384 | 19.7952 | 20.0995 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8718 | 0 | 99.7315 | 20.0995 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 20 | 44 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7634 | 20.0664 | 17.0974 | 19.7543 | 20.0664 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8717 | 0 | 99.4203 | 20.0664 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 21 | 45 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7316 | 20.0346 | 17.0695 | 19.7263 | 20.0346 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8716 | 0 | 99.2623 | 20.0346 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 22 | 46 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7018 | 20.0049 | 17.0466 | 19.7034 | 20.0049 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8715 | 0 | 99.1849 | 20.0049 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 23 | 47 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6742 | 19.9773 | 17.0257 | 19.6826 | 20 |  | 8.4186 | 0 | 8.4186 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8714 | 0 | 99.1844 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 2 | 24 | 48 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6712 | 19.9743 | 17.0287 | 19.6856 | 20 |  | 9.5389 | 0 | 9.5389 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8713 | 0 | 98.6452 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 1 | 49 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6198 | 19.9229 | 16.9663 | 19.6231 | 19.9229 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8712 | 0 | 98.5787 | 19.9229 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 2 | 50 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5398 | 19.8428 | 16.8767 | 19.5336 | 19.8428 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8711 | 0 | 98.3513 | 19.8428 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 3 | 51 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.455 | 19.758 | 16.7767 | 19.4336 | 19.758 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8710 | 0 | 98.3153 | 19.758 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 4 | 52 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3628 | 19.6659 | 16.6606 | 19.3175 | 19.6659 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8709 | 0 | 98.2798 | 19.6659 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 5 | 53 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2707 | 19.5737 | 16.5682 | 19.2251 | 19.5737 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8708 | 0 | 98.2792 | 19.5737 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 6 | 54 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1785 | 19.4815 | 16.4758 | 19.1326 | 19.4815 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8707 | 0 | 98.2164 | 19.4815 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 7 | 55 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0862 | 19.3893 | 16.3833 | 19.0402 | 19.3893 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8706 | 0 | 98.1516 | 19.3893 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 8 | 56 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.0107 | 19.3127 | 16.3023 | 18.9601 | 20 |  | 254.7382 | 0 | 254.7382 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8705 | 0 | 98.1334 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 9 | 57 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6134 | 19.9155 | 16.8783 | 19.536 | 20 |  | 31.3323 | 0 | 31.3323 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8704 | 0 | 97.4353 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 10 | 58 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1638.5565 | 0 | 5568.6526 | 0 | 1216.4908 | 0 | 520.2099 | 0 | 8943.9097 | 0 | 121.1844 | 0 | 309.2696 | 0 | 59.1579 | 0 | 28.8912 | 96.0605 | 614.5635 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6375 | 19.9396 | 16.8961 | 19.5539 | 20 |  | 22.3973 | 0 | 22.3973 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8703 | 0 | 97.3326 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 11 | 59 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3701.2064 | 0 | 12366.4993 | 0 | 8141.0445 | 0 | 2110.337 | 0 | 26319.0872 | 0 | 273.7339 | 0 | 686.8056 | 0 | 395.8984 | 0 | 117.203 | 362.4099 | 1836.0508 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6893 | 19.9914 | 16.9531 | 19.6109 | 20 |  | 3.1771 | 0 | 3.1771 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8702 | 0 | 96.5041 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 12 | 60 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5978.0033 | 0 | 30655.2714 | 0 | 32139.9381 | 0 | 3408.5107 | 0 | 72181.7234 | 0 | 442.1213 | 0 | 1702.5199 | 0 | 1562.963 | 0 | 189.3005 | 799.0483 | 4695.953 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.825 | 20.1271 | 17.1015 | 19.7593 | 20.1271 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8701 | 0 | 96.3862 | 20.1271 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 13 | 61 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4676.4894 | 0 | 4532.2411 | 0 | 9253.4452 | 0 | 2666.4194 | 0 | 21128.595 | 0 | 345.8639 | 0 | 251.7098 | 0 | 449.9944 | 0 | 148.0865 | 410.4401 | 1606.0947 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8007 | 20.1028 | 17.0609 | 19.7187 | 20.1028 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8700 | 0 | 96.3555 | 20.1028 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 14 | 62 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6341.6024 | 0 | 24645.1765 | 0 | 64911.4828 | 0 | 3615.826 | 0 | 99514.0877 | 0 | 469.0124 | 0 | 1368.7337 | 0 | 3156.6409 | 0 | 200.8143 | 886.376 | 6081.5773 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.001 | 20.303 | 17.2615 | 19.9193 | 20.303 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8699 | 0 | 96.065 | 20.303 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 15 | 63 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4595.1833 | 0 | 22736.3921 | 0 | 98715.6171 | 0 | 2620.0606 | 0 | 128667.2532 | 0 | 339.8507 | 0 | 1262.7245 | 0 | 4800.5336 | 0 | 145.5119 | 812.1475 | 7360.768 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2832 | 20.5853 | 17.5426 | 20.2003 | 20.5853 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8698 | 0 | 95.9732 | 20.5853 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 16 | 64 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3145.5866 | 0 | 8468.8804 | 0 | 69657.6561 | 0 | 1793.5362 | 0 | 83065.6593 | 0 | 232.6414 | 0 | 470.3412 | 0 | 3387.447 | 0 | 99.6087 | 401.7073 | 4591.7456 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4291 | 20.7312 | 17.6703 | 20.3281 | 20.7312 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8697 | 0 | 95.9466 | 20.7312 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 17 | 65 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 270.3239 | 0 | 166.1852 | 0 | 2580.6377 | 0 | 154.132 | 0 | 3171.2788 | 0 | 19.9926 | 0 | 9.2295 | 0 | 125.4962 | 0 | 8.5601 | 61.1294 | 224.4079 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.338 | 20.6401 | 17.5489 | 20.2067 | 20.6401 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8696 | 0 | 95.8983 | 20.6401 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 18 | 66 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2613 | 20.5644 | 17.4591 | 20.1159 | 20.5644 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8695 | 0 | 95.7039 | 20.5644 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 19 | 67 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1809 | 20.4839 | 17.3632 | 20.0201 | 20.4839 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8694 | 0 | 95.3838 | 20.4839 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 20 | 68 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0994 | 20.4024 | 17.2782 | 19.9351 | 20.4024 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8693 | 0 | 95.3621 | 20.4024 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 21 | 69 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0187 | 20.3217 | 17.1999 | 19.8568 | 20.3217 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8692 | 0 | 95.0728 | 20.3217 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 22 | 70 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9424 | 20.2454 | 17.1378 | 19.7946 | 20.2454 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8691 | 0 | 94.9743 | 20.2454 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 23 | 71 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8705 | 20.1736 | 17.0798 | 19.7367 | 20.1736 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8690 | 0 | 94.4212 | 20.1736 | 0 | 0 | 0
|  | 2001 | 1 | 3 | 24 | 72 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7975 | 20.1005 | 17.0031 | 19.6599 | 20.1005 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8689 | 0 | 94.2108 | 20.1005 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 1 | 73 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6829 | 19.9859 | 16.9089 | 19.5658 | 19.9859 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8688 | 0 | 94.1955 | 19.9859 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 2 | 74 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5757 | 19.8788 | 16.8257 | 19.4826 | 19.8788 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8687 | 0 | 93.9593 | 19.8788 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 3 | 75 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4742 | 19.7773 | 16.742 | 19.3989 | 19.7773 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8686 | 0 | 93.8841 | 19.7773 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 4 | 76 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3718 | 19.6749 | 16.6367 | 19.2936 | 19.6749 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8685 | 0 | 93.8666 | 19.6749 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 5 | 77 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2723 | 19.5753 | 16.5461 | 19.2029 | 19.5753 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8684 | 0 | 93.7861 | 19.5753 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 6 | 78 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1746 | 19.4776 | 16.4542 | 19.1111 | 19.4776 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8683 | 0 | 93.7582 | 19.4776 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 7 | 79 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.076 | 19.3791 | 16.3526 | 19.0095 | 19.3791 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8682 | 0 | 93.72 | 19.3791 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 8 | 80 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.9971 | 19.2992 | 16.2773 | 18.9351 | 20 |  | 259.7471 | 0 | 259.7471 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8681 | 0 | 93.6492 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 9 | 81 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6142 | 19.9163 | 16.882 | 19.5398 | 20 |  | 31.0206 | 0 | 31.0206 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8680 | 0 | 93.5103 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 10 | 82 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 152.8614 | 0 | 93.7584 | 0 | 202.3917 | 0 | 86.5491 | 0 | 535.5606 | 0 | 11.3053 | 0 | 5.2071 | 0 | 9.8423 | 0 | 4.8067 | 13.0992 | 44.2606 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6192 | 19.9212 | 16.8987 | 19.5565 | 20 |  | 29.1939 | 0 | 29.1939 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8679 | 0 | 93.3835 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 11 | 83 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 713.52 | 0 | 434.2152 | 0 | 959.7677 | 0 | 406.8316 | 0 | 2514.3345 | 0 | 52.7705 | 0 | 24.1153 | 0 | 46.6734 | 0 | 22.5944 | 61.1294 | 207.2831 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6283 | 19.9304 | 16.9195 | 19.5773 | 20 |  | 25.8052 | 0 | 25.8052 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8678 | 0 | 93.1903 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 12 | 84 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2189.4111 | 0 | 1367.6634 | 0 | 3024.3404 | 0 | 1248.3484 | 0 | 7829.7632 | 0 | 161.9245 | 0 | 75.9567 | 0 | 147.0735 | 0 | 69.3303 | 183.3881 | 637.6731 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.648 | 19.9501 | 16.9537 | 19.6115 | 20 |  | 18.5008 | 0 | 18.5008 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8677 | 0 | 93.0769 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 13 | 85 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1276.2075 | 0 | 756.9562 | 0 | 1748.7883 | 0 | 727.6622 | 0 | 4509.6141 | 0 | 94.3858 | 0 | 42.0395 | 0 | 85.0435 | 0 | 40.4126 | 109.1596 | 371.041 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6409 | 19.9429 | 16.9555 | 19.6133 | 20 |  | 21.1524 | 0 | 21.1524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8676 | 0 | 93.0397 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 14 | 86 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 861.5391 | 0 | 502.9664 | 0 | 1180.1179 | 0 | 491.2285 | 0 | 3035.8519 | 0 | 63.7177 | 0 | 27.9335 | 0 | 57.3891 | 0 | 27.2816 | 74.2285 | 250.5505 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6382 | 19.9403 | 16.9588 | 19.6166 | 20 |  | 22.1232 | 0 | 22.1232 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8675 | 0 | 92.8934 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 15 | 87 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 402.1717 | 0 | 232.0951 | 0 | 549.0092 | 0 | 229.3084 | 0 | 1412.5845 | 0 | 29.7438 | 0 | 12.89 | 0 | 26.6983 | 0 | 12.7352 | 34.9311 | 116.9984 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6318 | 19.9339 | 16.9466 | 19.6044 | 20 |  | 24.5035 | 0 | 24.5035 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8674 | 0 | 92.7408 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 16 | 88 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 300.7416 | 0 | 173.8466 | 0 | 424.1275 | 0 | 171.4755 | 0 | 1070.1912 | 0 | 22.2423 | 0 | 9.655 | 0 | 20.6253 | 0 | 9.5233 | 26.1983 | 88.2442 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6308 | 19.9329 | 16.9456 | 19.6034 | 20 |  | 24.8746 | 0 | 24.8746 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8673 | 0 | 92.7065 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 17 | 89 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6277 | 19.9298 | 16.9425 | 19.6003 | 20 |  | 26.033 | 0 | 26.033 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8672 | 0 | 92.6775 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 18 | 90 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6566 | 19.9597 | 16.9671 | 19.624 | 20 |  | 14.9528 | 0 | 14.9528 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8671 | 0 | 92.5607 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 19 | 91 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6521 | 19.9551 | 16.9479 | 19.6047 | 20 |  | 16.6446 | 0 | 16.6446 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8670 | 0 | 92.2185 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 20 | 92 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6502 | 19.9533 | 16.9402 | 19.597 | 20 |  | 17.3214 | 0 | 17.3214 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8669 | 0 | 91.935 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 21 | 93 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6511 | 19.9542 | 16.944 | 19.6009 | 20 |  | 16.983 | 0 | 16.983 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8668 | 0 | 91.9245 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 22 | 94 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.653 | 19.956 | 16.9517 | 19.6086 | 20 |  | 16.3062 | 0 | 16.3062 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8667 | 0 | 91.9119 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 23 | 95 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6521 | 19.9551 | 16.9479 | 19.6047 | 20 |  | 16.6446 | 0 | 16.6446 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8666 | 0 | 91.8769 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 4 | 24 | 96 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6493 | 19.9524 | 16.9363 | 19.5932 | 20 |  | 17.6597 | 0 | 17.6597 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8665 | 0 | 91.6423 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 1 | 97 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5979 | 19.901 | 16.8739 | 19.5307 | 19.901 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8664 | 0 | 91.5934 | 19.901 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 2 | 98 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5007 | 19.8038 | 16.7826 | 19.4394 | 19.8038 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8663 | 0 | 91.5918 | 19.8038 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 3 | 99 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4027 | 19.7057 | 16.6815 | 19.3383 | 19.7057 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8662 | 0 | 91.2096 | 19.7057 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 4 | 100 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2973 | 19.6004 | 16.5526 | 19.2094 | 19.6004 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8661 | 0 | 90.9441 | 19.6004 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 5 | 101 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1957 | 19.4988 | 16.4629 | 19.1197 | 19.4988 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8660 | 0 | 90.6103 | 19.4988 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 6 | 102 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.096 | 19.3991 | 16.3691 | 19.026 | 19.3991 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8659 | 0 | 90.281 | 19.3991 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 7 | 103 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9982 | 19.3013 | 16.2772 | 18.934 | 19.3013 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8658 | 0 | 90.1568 | 19.3013 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 8 | 104 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.9217 | 19.2238 | 16.2101 | 18.8679 | 20 |  | 287.6944 | 0 | 287.6944 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8657 | 0 | 90.1247 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 9 | 105 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6142 | 19.9163 | 16.882 | 19.5398 | 20 |  | 31.0206 | 0 | 31.0206 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8656 | 0 | 90.0097 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 10 | 106 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6125 | 19.9146 | 16.8745 | 19.5323 | 20 |  | 31.644 | 0 | 31.644 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8655 | 0 | 89.8264 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 11 | 107 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6134 | 19.9155 | 16.8783 | 19.536 | 20 |  | 31.3323 | 0 | 31.3323 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8654 | 0 | 89.6782 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 12 | 108 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 301.0729 | 0 | 174.072 | 0 | 403.5373 | 0 | 171.6643 | 0 | 1050.3466 | 0 | 22.2668 | 0 | 9.6675 | 0 | 19.624 | 0 | 9.5338 | 26.1983 | 87.2904 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.619 | 19.9211 | 16.8926 | 19.5504 | 20 |  | 29.2595 | 0 | 29.2595 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8653 | 0 | 89.5175 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 13 | 109 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 402.4113 | 0 | 232.4093 | 0 | 541.3015 | 0 | 229.4451 | 0 | 1405.5672 | 0 | 29.7615 | 0 | 12.9075 | 0 | 26.3235 | 0 | 12.7428 | 34.9311 | 116.6664 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6284 | 19.9305 | 16.9314 | 19.5892 | 20 |  | 25.7577 | 0 | 25.7577 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8652 | 0 | 89.306 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 14 | 110 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 402.423 | 0 | 232.0146 | 0 | 543.3955 | 0 | 229.4517 | 0 | 1407.2847 | 0 | 29.7624 | 0 | 12.8855 | 0 | 26.4253 | 0 | 12.7432 | 34.9311 | 116.7475 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6368 | 19.9389 | 16.9692 | 19.627 | 20 |  | 22.6387 | 0 | 22.6387 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8651 | 0 | 88.1215 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 15 | 111 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 861.6036 | 0 | 503.6064 | 0 | 1205.208 | 0 | 491.2652 | 0 | 3061.6832 | 0 | 63.7225 | 0 | 27.9691 | 0 | 58.6092 | 0 | 27.2837 | 74.2285 | 251.813 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6518 | 19.9538 | 17.0193 | 19.6771 | 20 |  | 17.1086 | 0 | 17.1086 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8650 | 0 | 88.002 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 16 | 112 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 300.7471 | 0 | 173.7663 | 0 | 423.2186 | 0 | 171.4786 | 0 | 1069.2106 | 0 | 22.2427 | 0 | 9.6506 | 0 | 20.5811 | 0 | 9.5235 | 26.1983 | 88.1961 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.635 | 19.9371 | 16.9645 | 19.6223 | 20 |  | 23.317 | 0 | 23.317 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8649 | 0 | 87.8841 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 17 | 113 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6226 | 19.9247 | 16.9198 | 19.5776 | 20 |  | 27.9034 | 0 | 27.9034 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8648 | 0 | 87.8829 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 18 | 114 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6521 | 19.9551 | 16.9479 | 19.6047 | 20 |  | 16.6446 | 0 | 16.6446 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8647 | 0 | 87.8555 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 19 | 115 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6484 | 19.9515 | 16.9325 | 19.5893 | 20 |  | 17.9981 | 0 | 17.9981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8646 | 0 | 87.7716 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 20 | 116 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6457 | 19.9487 | 16.921 | 19.5778 | 20 |  | 19.0132 | 0 | 19.0132 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8645 | 0 | 87.037 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 21 | 117 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6448 | 19.9478 | 16.9171 | 19.5739 | 20 |  | 19.3516 | 0 | 19.3516 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8644 | 0 | 86.7768 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 22 | 118 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6457 | 19.9487 | 16.921 | 19.5778 | 20 |  | 19.0132 | 0 | 19.0132 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8643 | 0 | 86.7622 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 23 | 119 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6448 | 19.9478 | 16.9171 | 19.5739 | 20 |  | 19.3516 | 0 | 19.3516 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8642 | 0 | 86.7573 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 5 | 24 | 120 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6429 | 19.946 | 16.9094 | 19.5662 | 20 |  | 20.0283 | 0 | 20.0283 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8641 | 0 | 86.6624 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 1 | 121 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5952 | 19.8982 | 16.8623 | 19.5192 | 19.8982 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8640 | 0 | 86.6246 | 19.8982 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 2 | 122 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4934 | 19.7965 | 16.7607 | 19.4175 | 19.7965 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8639 | 0 | 86.204 | 19.7965 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 3 | 123 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3909 | 19.6939 | 16.6552 | 19.3121 | 19.6939 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8638 | 0 | 85.9921 | 19.6939 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 4 | 124 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2902 | 19.5933 | 16.5605 | 19.2174 | 19.5933 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8637 | 0 | 85.9761 | 19.5933 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 5 | 125 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1832 | 19.4863 | 16.433 | 19.0898 | 19.4863 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8636 | 0 | 85.9675 | 19.4863 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 6 | 126 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0773 | 19.3803 | 16.3302 | 18.987 | 19.3803 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8635 | 0 | 85.8654 | 19.3803 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 7 | 127 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9678 | 19.2708 | 16.2091 | 18.8659 | 19.2708 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8634 | 0 | 85.5792 | 19.2708 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 8 | 128 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.8989 | 19.2019 | 16.1163 | 18.7731 | 20 |  | 295.911 | 0 | 295.911 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8633 | 0 | 85.5536 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 9 | 129 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6229 | 19.9259 | 16.8247 | 19.4816 | 20 |  | 27.4724 | 0 | 27.4724 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8632 | 0 | 85.4979 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 10 | 130 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 426.9704 | 0 | 287.9418 | 0 | 559.076 | 0 | 239.0786 | 0 | 1513.0668 | 0 | 31.5779 | 0 | 15.9916 | 0 | 27.1878 | 0 | 13.2778 | 34.9311 | 122.9662 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6346 | 19.9376 | 16.8599 | 19.5167 | 20 |  | 23.1294 | 0 | 23.1294 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8631 | 0 | 85.3098 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 11 | 131 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2766.415 | 0 | 5730.7529 | 0 | 4916.5236 | 0 | 1577.3419 | 0 | 14991.0333 | 0 | 204.5986 | 0 | 318.2722 | 0 | 239.0902 | 0 | 87.6018 | 253.2503 | 1102.813 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6772 | 19.9803 | 16.9137 | 19.5705 | 20 |  | 7.3181 | 0 | 7.3181 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8630 | 0 | 85.1313 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 12 | 132 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1864.5343 | 0 | 1148.7323 | 0 | 2560.4517 | 0 | 1063.1116 | 0 | 6636.8299 | 0 | 137.8973 | 0 | 63.7978 | 0 | 124.5146 | 0 | 59.0427 | 157.1898 | 542.4422 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6577 | 19.9608 | 16.9092 | 19.5661 | 20 |  | 14.5409 | 0 | 14.5409 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8629 | 0 | 84.8218 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 13 | 133 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2605.0968 | 0 | 1599.6835 | 0 | 3655.9695 | 0 | 1485.3622 | 0 | 9346.1121 | 0 | 192.6678 | 0 | 88.8426 | 0 | 177.7895 | 0 | 82.4934 | 218.3192 | 760.1126 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6693 | 19.9723 | 16.9324 | 19.5892 | 20 |  | 10.2604 | 0 | 10.2604 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8628 | 0 | 84.5977 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 14 | 134 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5843.5369 | 0 | 7874.9665 | 0 | 19859.2043 | 0 | 3331.8412 | 0 | 36909.549 | 0 | 432.1764 | 0 | 437.3567 | 0 | 965.7517 | 0 | 185.0424 | 545.798 | 2566.1253 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7521 | 20.0552 | 17.0258 | 19.6827 | 20.0552 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8627 | 0 | 84.5586 | 20.0552 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 15 | 135 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3839.8952 | 0 | 2758.5774 | 0 | 7712.4456 | 0 | 2189.4139 | 0 | 16500.3321 | 0 | 283.991 | 0 | 153.2047 | 0 | 375.0557 | 0 | 121.5948 | 327.4788 | 1261.3251 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7446 | 20.0476 | 17.0058 | 19.6626 | 20.0476 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8626 | 0 | 84.4883 | 20.0476 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 16 | 136 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3495.7554 | 0 | 6674.4905 | 0 | 49938.1466 | 0 | 1993.1939 | 0 | 62101.5864 | 0 | 258.5391 | 0 | 370.6851 | 0 | 2428.4886 | 0 | 110.6972 | 375.509 | 3543.9191 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8635 | 20.1665 | 17.1142 | 19.771 | 20.1665 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8625 | 0 | 84.3938 | 20.1665 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 17 | 137 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 369.2871 | 0 | 237.1438 | 0 | 4667.1674 | 0 | 210.5584 | 0 | 5484.1567 | 0 | 27.3117 | 0 | 13.1704 | 0 | 226.964 | 0 | 11.6939 | 82.9613 | 362.1014 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8136 | 20.1167 | 17.0427 | 19.6995 | 20.1167 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8624 | 0 | 84.3659 | 20.1167 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 18 | 138 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7439 | 20.0469 | 16.9599 | 19.6168 | 20.0469 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8623 | 0 | 84.0978 | 20.0469 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 19 | 139 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6675 | 19.9705 | 16.8621 | 19.519 | 20 |  | 10.9211 | 0 | 10.9211 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8622 | 0 | 83.9862 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 20 | 140 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6183 | 19.9213 | 16.8055 | 19.4623 | 20 |  | 29.1642 | 0 | 29.1642 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8621 | 0 | 83.6725 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 21 | 141 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6192 | 19.9223 | 16.8093 | 19.4662 | 20 |  | 28.8258 | 0 | 28.8258 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8620 | 0 | 83.6065 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 22 | 142 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8619 | 0 | 83.4356 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 23 | 143 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8618 | 0 | 83.3108 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 6 | 24 | 144 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6311 | 19.9341 | 16.8594 | 19.5162 | 20 |  | 24.4271 | 0 | 24.4271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8617 | 0 | 83.1179 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 1 | 145 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5842 | 19.8873 | 16.8162 | 19.473 | 19.8873 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8616 | 0 | 83.0347 | 19.8873 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 2 | 146 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4616 | 19.7647 | 16.6616 | 19.3185 | 19.7647 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8615 | 0 | 82.9372 | 19.7647 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 3 | 147 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3356 | 19.6387 | 16.5246 | 19.1814 | 19.6387 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8614 | 0 | 82.8512 | 19.6387 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 4 | 148 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.209 | 19.5121 | 16.3958 | 19.0526 | 19.5121 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8613 | 0 | 82.1245 | 19.5121 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 5 | 149 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.091 | 19.394 | 16.3049 | 18.9618 | 19.394 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8612 | 0 | 81.9703 | 19.394 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 6 | 150 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9759 | 19.2789 | 16.1992 | 18.856 | 19.2789 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8611 | 0 | 81.7973 | 19.2789 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 7 | 151 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8619 | 19.1649 | 16.0886 | 18.7454 | 19.1649 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8610 | 0 | 81.2939 | 19.1649 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 8 | 152 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.7931 | 19.0961 | 16.0107 | 18.6675 | 20 |  | 335.1425 | 0 | 335.1425 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8609 | 0 | 81.2779 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 9 | 153 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6201 | 19.9232 | 16.8132 | 19.47 | 20 |  | 28.4875 | 0 | 28.4875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8608 | 0 | 81.2016 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 10 | 154 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 314.1891 | 0 | 203.4072 | 0 | 413.1707 | 0 | 176.6848 | 0 | 1107.4518 | 0 | 23.2368 | 0 | 11.2967 | 0 | 20.0925 | 0 | 9.8127 | 26.1983 | 90.637 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6261 | 19.9291 | 16.8279 | 19.4848 | 20 |  | 26.2743 | 0 | 26.2743 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8607 | 0 | 81.1785 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 11 | 155 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1735.9967 | 0 | 1135.7425 | 0 | 2356.9579 | 0 | 989.8227 | 0 | 6218.5198 | 0 | 128.3909 | 0 | 63.0764 | 0 | 114.6187 | 0 | 54.9724 | 144.0907 | 505.149 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6437 | 19.9468 | 16.8541 | 19.511 | 20 |  | 19.7336 | 0 | 19.7336 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8606 | 0 | 81.1101 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 12 | 156 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3659.5531 | 0 | 3440.4843 | 0 | 6047.7451 | 0 | 2086.5873 | 0 | 15234.3698 | 0 | 270.6533 | 0 | 191.0762 | 0 | 294.1014 | 0 | 115.884 | 314.3797 | 1186.0946 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6754 | 19.9784 | 16.903 | 19.5598 | 20 |  | 8.0066 | 0 | 8.0066 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8605 | 0 | 80.8473 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 13 | 157 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1695.509 | 0 | 1015.862 | 0 | 2338.7601 | 0 | 966.7376 | 0 | 6016.8688 | 0 | 125.3965 | 0 | 56.4185 | 0 | 113.7337 | 0 | 53.6903 | 144.0907 | 493.3297 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6523 | 19.9553 | 16.8921 | 19.5489 | 20 |  | 16.5634 | 0 | 16.5634 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8604 | 0 | 80.7549 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 14 | 158 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1588.5504 | 0 | 943.0623 | 0 | 2216.8336 | 0 | 905.7524 | 0 | 5654.1987 | 0 | 117.486 | 0 | 52.3754 | 0 | 107.8045 | 0 | 50.3033 | 135.3579 | 463.3271 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.654 | 19.957 | 16.9026 | 19.5594 | 20 |  | 15.941 | 0 | 15.941 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8603 | 0 | 80.5839 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 15 | 159 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1275.7998 | 0 | 753.0202 | 0 | 1817.259 | 0 | 727.4297 | 0 | 4573.5087 | 0 | 94.3556 | 0 | 41.8209 | 0 | 88.3732 | 0 | 40.3997 | 109.1596 | 374.109 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6526 | 19.9557 | 16.9072 | 19.564 | 20 |  | 16.4341 | 0 | 16.4341 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8602 | 0 | 80.3121 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 16 | 160 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1438.214 | 0 | 866.2213 | 0 | 2362.548 | 0 | 820.0343 | 0 | 5487.0176 | 0 | 106.3675 | 0 | 48.1078 | 0 | 114.8905 | 0 | 45.5427 | 122.2588 | 437.1673 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6553 | 19.9583 | 16.9097 | 19.5666 | 20 |  | 15.4576 | 0 | 15.4576 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8601 | 0 | 80.2106 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 17 | 161 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 412.2825 | 0 | 276.6122 | 0 | 6830.2137 | 0 | 235.0734 | 0 | 7754.1817 | 0 | 30.4916 | 0 | 15.3624 | 0 | 332.1528 | 0 | 13.0554 | 34.9311 | 425.9933 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6595 | 19.9626 | 16.908 | 19.5649 | 20 |  | 13.8783 | 0 | 13.8783 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8600 | 0 | 79.7537 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 18 | 162 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6292 | 19.9323 | 16.8517 | 19.5085 | 20 |  | 25.1038 | 0 | 25.1038 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8599 | 0 | 79.671 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 19 | 163 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6265 | 19.9296 | 16.8401 | 19.497 | 20 |  | 26.1189 | 0 | 26.1189 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8598 | 0 | 79.4105 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 20 | 164 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6311 | 19.9341 | 16.8594 | 19.5162 | 20 |  | 24.4271 | 0 | 24.4271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8597 | 0 | 79.27 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 21 | 165 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6311 | 19.9341 | 16.8594 | 19.5162 | 20 |  | 24.4271 | 0 | 24.4271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8596 | 0 | 79.2562 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 22 | 166 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8595 | 0 | 79.0093 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 23 | 167 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6219 | 19.925 | 16.8209 | 19.4777 | 20 |  | 27.8107 | 0 | 27.8107 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8594 | 0 | 78.991 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 7 | 24 | 168 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6146 | 19.9177 | 16.7901 | 19.4469 | 20 |  | 30.5177 | 0 | 30.5177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8593 | 0 | 78.9142 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 1 | 169 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5641 | 19.8672 | 16.7315 | 19.3883 | 19.8672 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8592 | 0 | 78.9094 | 19.8672 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 2 | 170 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4244 | 19.7274 | 16.5692 | 19.2261 | 19.7274 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8591 | 0 | 78.7812 | 19.7274 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 3 | 171 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2796 | 19.5827 | 16.408 | 19.0648 | 19.5827 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8590 | 0 | 78.7028 | 19.5827 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 4 | 172 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1353 | 19.4384 | 16.265 | 18.9218 | 19.4384 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8589 | 0 | 78.622 | 19.4384 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 5 | 173 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9897 | 19.2927 | 16.1148 | 18.7716 | 19.2927 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8588 | 0 | 78.5744 | 19.2927 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 6 | 174 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8454 | 19.1485 | 15.9748 | 18.6316 | 19.1485 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8587 | 0 | 78.3883 | 19.1485 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 7 | 175 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7016 | 19.0047 | 15.8323 | 18.4892 | 19.0047 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8586 | 0 | 78.1504 | 19.0047 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 8 | 176 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.579 | 18.8811 | 15.7056 | 18.3634 | 20 |  | 414.7245 | 0 | 414.7245 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8585 | 0 | 78.1032 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 9 | 177 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5705 | 19.8726 | 16.6855 | 19.3433 | 20 |  | 47.23 | 0 | 47.23 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8584 | 0 | 77.9878 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 10 | 178 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2679.5555 | 0 | 8693.9043 | 0 | 1821.9414 | 0 | 779.1197 | 0 | 13974.5208 | 0 | 198.1746 | 0 | 482.8385 | 0 | 88.6009 | 0 | 43.2704 | 144.0907 | 956.9751 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6184 | 19.9204 | 16.7592 | 19.417 | 20 |  | 29.493 | 0 | 29.493 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8583 | 0 | 77.912 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 11 | 179 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4591.0689 | 0 | 23870.3225 | 0 | 12156.9329 | 0 | 2617.7147 | 0 | 43236.0391 | 0 | 339.5464 | 0 | 1325.7002 | 0 | 591.1908 | 0 | 145.3816 | 532.6989 | 2934.5178 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7161 | 20.0182 | 16.9027 | 19.5605 | 20.0182 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8582 | 0 | 77.658 | 20.0182 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 12 | 180 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2187.4804 | 0 | 1360.6464 | 0 | 3013.8061 | 0 | 1247.2476 | 0 | 7809.1805 | 0 | 161.7817 | 0 | 75.567 | 0 | 146.5612 | 0 | 69.2691 | 183.3881 | 636.5672 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6306 | 19.9327 | 16.8123 | 19.4701 | 20 |  | 24.9412 | 0 | 24.9412 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8581 | 0 | 77.5361 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 13 | 181 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1275.8758 | 0 | 755.262 | 0 | 1745.1445 | 0 | 727.473 | 0 | 4503.7554 | 0 | 94.3612 | 0 | 41.9454 | 0 | 84.8663 | 0 | 40.4021 | 109.1596 | 370.7346 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6072 | 19.9093 | 16.8043 | 19.4621 | 20 |  | 33.6274 | 0 | 33.6274 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8580 | 0 | 77.5281 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 14 | 182 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2277.1089 | 0 | 1372.2647 | 0 | 3231.1493 | 0 | 1298.3516 | 0 | 8178.8745 | 0 | 168.4105 | 0 | 76.2123 | 0 | 157.1306 | 0 | 72.1073 | 192.1209 | 665.9815 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.623 | 19.925 | 16.8375 | 19.4953 | 20 |  | 27.7867 | 0 | 27.7867 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8579 | 0 | 77.4921 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 15 | 183 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2280.9986 | 0 | 1378.0742 | 0 | 3392.1529 | 0 | 1300.5694 | 0 | 8351.795 | 0 | 168.6981 | 0 | 76.5349 | 0 | 164.9602 | 0 | 72.2305 | 192.1209 | 674.5446 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6234 | 19.9255 | 16.838 | 19.4958 | 20 |  | 27.6052 | 0 | 27.6052 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8578 | 0 | 77.4696 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 16 | 184 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1122.5699 | 0 | 667.4631 | 0 | 1759.7463 | 0 | 640.0618 | 0 | 4189.8411 | 0 | 83.023 | 0 | 37.0693 | 0 | 85.5763 | 0 | 35.5475 | 96.0605 | 337.2766 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6113 | 19.9134 | 16.826 | 19.4838 | 20 |  | 32.1044 | 0 | 32.1044 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8577 | 0 | 77.283 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 17 | 185 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 351.2191 | 0 | 217.238 | 0 | 2956.24 | 0 | 200.2565 | 0 | 3724.9536 | 0 | 25.9755 | 0 | 12.0649 | 0 | 143.7617 | 0 | 11.1218 | 26.1983 | 219.1222 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6081 | 19.9101 | 16.8169 | 19.4747 | 20 |  | 33.3109 | 0 | 33.3109 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8576 | 0 | 77.2053 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 18 | 186 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6274 | 19.9305 | 16.844 | 19.5008 | 20 |  | 25.7805 | 0 | 25.7805 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8575 | 0 | 77.0511 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 19 | 187 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6265 | 19.9296 | 16.8401 | 19.497 | 20 |  | 26.1189 | 0 | 26.1189 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8574 | 0 | 76.9793 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 20 | 188 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6238 | 19.9268 | 16.8286 | 19.4854 | 20 |  | 27.134 | 0 | 27.134 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8573 | 0 | 76.8853 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 21 | 189 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8572 | 0 | 76.8249 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 22 | 190 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6274 | 19.9305 | 16.844 | 19.5008 | 20 |  | 25.7805 | 0 | 25.7805 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8571 | 0 | 76.4703 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 23 | 191 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6283 | 19.9314 | 16.8478 | 19.5047 | 20 |  | 25.4422 | 0 | 25.4422 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8570 | 0 | 76.4287 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 8 | 24 | 192 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6229 | 19.9259 | 16.8247 | 19.4816 | 20 |  | 27.4724 | 0 | 27.4724 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8569 | 0 | 75.9588 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 1 | 193 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5714 | 19.8745 | 16.7623 | 19.4191 | 19.8745 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8568 | 0 | 75.8302 | 19.8745 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 2 | 194 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4499 | 19.7529 | 16.6532 | 19.31 | 19.7529 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8567 | 0 | 75.733 | 19.7529 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 3 | 195 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3313 | 19.6344 | 16.5441 | 19.2009 | 19.6344 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8566 | 0 | 75.4706 | 19.6344 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 4 | 196 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2057 | 19.5087 | 16.3955 | 19.0523 | 19.5087 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8565 | 0 | 75.1353 | 19.5087 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 5 | 197 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.073 | 19.3761 | 16.2401 | 18.897 | 19.3761 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8564 | 0 | 75.0778 | 19.3761 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 6 | 198 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9481 | 19.2511 | 16.1396 | 18.7964 | 19.2511 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8563 | 0 | 75.0221 | 19.2511 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 7 | 199 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8133 | 19.1164 | 15.9733 | 18.6301 | 19.1164 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8562 | 0 | 74.9188 | 19.1164 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 8 | 200 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6956 | 18.9977 | 15.8395 | 18.4973 | 20 |  | 371.5105 | 0 | 371.5105 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8561 | 0 | 74.8701 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 9 | 201 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5739 | 19.8759 | 16.7006 | 19.3584 | 20 |  | 45.9831 | 0 | 45.9831 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8560 | 0 | 74.8273 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 10 | 202 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2465.3487 | 0 | 7408.6521 | 0 | 1774.9502 | 0 | 759.0248 | 0 | 12407.9758 | 0 | 182.3323 | 0 | 411.4587 | 0 | 86.3157 | 0 | 42.1544 | 135.3579 | 857.619 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6189 | 19.921 | 16.7774 | 19.4352 | 20 |  | 29.2886 | 0 | 29.2886 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8559 | 0 | 74.8134 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 11 | 203 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4314.0996 | 0 | 20199.6319 | 0 | 10684.8489 | 0 | 2459.7936 | 0 | 37658.3741 | 0 | 319.0623 | 0 | 1121.8389 | 0 | 519.6035 | 0 | 136.611 | 471.5695 | 2568.6851 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7026 | 20.0047 | 16.8982 | 19.556 | 20.0047 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8558 | 0 | 74.7059 | 20.0047 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 12 | 204 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5300.897 | 0 | 10076.471 | 0 | 13068.9277 | 0 | 3022.4413 | 0 | 31468.737 | 0 | 392.0438 | 0 | 559.6229 | 0 | 635.541 | 0 | 167.8591 | 497.7678 | 2252.8347 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6888 | 19.9909 | 16.8816 | 19.5394 | 20 |  | 3.3822 | 0 | 3.3822 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8557 | 0 | 74.6122 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 13 | 205 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5420.1904 | 0 | 6507.7559 | 0 | 12611.3517 | 0 | 3090.4594 | 0 | 27629.7575 | 0 | 400.8665 | 0 | 361.4251 | 0 | 613.2892 | 0 | 171.6367 | 497.7678 | 2044.9853 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6766 | 19.9787 | 16.8815 | 19.5393 | 20 |  | 7.8919 | 0 | 7.8919 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8556 | 0 | 74.4987 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 14 | 206 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6065.2562 | 0 | 8310.292 | 0 | 20845.8149 | 0 | 3458.2601 | 0 | 38679.6232 | 0 | 448.5743 | 0 | 461.5336 | 0 | 1013.7305 | 0 | 192.0634 | 571.9963 | 2687.8982 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7082 | 20.0103 | 16.9126 | 19.5704 | 20.0103 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8555 | 0 | 74.2497 | 20.0103 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 15 | 207 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5012.6922 | 0 | 5770.8523 | 0 | 19828.9872 | 0 | 2858.114 | 0 | 33470.6457 | 0 | 370.7288 | 0 | 320.4992 | 0 | 964.2823 | 0 | 158.7328 | 462.8367 | 2277.0798 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7065 | 20.0086 | 16.9227 | 19.5804 | 20.0086 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8554 | 0 | 74.1666 | 20.0086 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 16 | 208 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3292.458 | 0 | 3558.2583 | 0 | 20468.5632 | 0 | 1877.2787 | 0 | 29196.5582 | 0 | 243.5037 | 0 | 197.6171 | 0 | 995.3848 | 0 | 104.2595 | 292.5477 | 1833.3129 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6888 | 19.9909 | 16.8934 | 19.5512 | 20 |  | 3.3705 | 0 | 3.3705 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8553 | 0 | 73.766 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 17 | 209 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 598.5117 | 0 | 480.7824 | 0 | 20723.6069 | 0 | 341.2567 | 0 | 22144.1576 | 0 | 44.2647 | 0 | 26.7015 | 0 | 1007.7876 | 0 | 18.9526 | 48.0302 | 1145.7366 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6544 | 19.9564 | 16.8419 | 19.4997 | 20 |  | 16.1471 | 0 | 16.1471 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8552 | 0 | 73.4542 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 18 | 210 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8551 | 0 | 73.433 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 19 | 211 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6174 | 19.9204 | 16.8016 | 19.4585 | 20 |  | 29.5026 | 0 | 29.5026 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8550 | 0 | 73.3805 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 20 | 212 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8549 | 0 | 73.3261 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 21 | 213 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8548 | 0 | 73.2671 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 22 | 214 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8547 | 0 | 73.263 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 23 | 215 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8546 | 0 | 73.2119 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 9 | 24 | 216 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6028 | 19.9058 | 16.7401 | 19.3969 | 20 |  | 34.9165 | 0 | 34.9165 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8545 | 0 | 73.008 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 1 | 217 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5413 | 19.8444 | 16.6353 | 19.2921 | 19.8444 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8544 | 0 | 72.9874 | 19.8444 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 2 | 218 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3835 | 19.6866 | 16.4703 | 19.1271 | 19.6866 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8543 | 0 | 72.5525 | 19.6866 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 3 | 219 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2319 | 19.5349 | 16.3379 | 18.9948 | 19.5349 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8542 | 0 | 72.5294 | 19.5349 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 4 | 220 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0798 | 19.3829 | 16.1845 | 18.8413 | 19.3829 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8541 | 0 | 72.2947 | 19.3829 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 5 | 221 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9246 | 19.2277 | 16.0191 | 18.6759 | 19.2277 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8540 | 0 | 72.1333 | 19.2277 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 6 | 222 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7746 | 19.0777 | 15.8854 | 18.5422 | 19.0777 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8539 | 0 | 72.0118 | 19.0777 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 7 | 223 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6243 | 18.9273 | 15.7335 | 18.3904 | 18.9273 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8538 | 0 | 71.9557 | 18.9273 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 8 | 224 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.499 | 18.801 | 15.6161 | 18.2739 | 20 |  | 444.3999 | 0 | 444.3999 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8537 | 0 | 71.8756 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 9 | 225 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5629 | 19.865 | 16.6515 | 19.3093 | 20 |  | 50.0355 | 0 | 50.0355 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8536 | 0 | 71.787 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 10 | 226 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2049.825 | 0 | 6403.9647 | 0 | 1373.7318 | 0 | 587.4511 | 0 | 10414.9726 | 0 | 151.601 | 0 | 355.6608 | 0 | 66.8045 | 0 | 32.6256 | 109.1596 | 715.8515 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5955 | 19.8976 | 16.6924 | 19.3502 | 20 |  | 37.9695 | 0 | 37.9695 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8535 | 0 | 71.7567 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 11 | 227 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4007.7638 | 0 | 13705.1064 | 0 | 8450.6947 | 0 | 2285.1285 | 0 | 28448.6934 | 0 | 296.4063 | 0 | 761.1486 | 0 | 410.9567 | 0 | 126.9105 | 401.7073 | 1997.1294 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6577 | 19.9598 | 16.7891 | 19.4469 | 20 |  | 14.9139 | 0 | 14.9139 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8534 | 0 | 71.6465 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 12 | 228 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4432.1 | 0 | 5917.7377 | 0 | 8773.1939 | 0 | 2527.0746 | 0 | 21650.1062 | 0 | 327.7893 | 0 | 328.6569 | 0 | 426.6398 | 0 | 140.3476 | 401.7073 | 1625.141 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6442 | 19.9463 | 16.7965 | 19.4543 | 20 |  | 19.9024 | 0 | 19.9024 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8533 | 0 | 71.6115 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 13 | 229 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5339.9316 | 0 | 6053.333 | 0 | 11839.8713 | 0 | 3044.6979 | 0 | 26277.8338 | 0 | 394.9308 | 0 | 336.1875 | 0 | 575.7721 | 0 | 169.0952 | 484.6686 | 1960.6543 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.661 | 19.9631 | 16.8248 | 19.4826 | 20 |  | 13.6923 | 0 | 13.6923 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8532 | 0 | 71.6083 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 14 | 230 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5095.7744 | 0 | 4555.7456 | 0 | 11119.812 | 0 | 2905.4854 | 0 | 23676.8174 | 0 | 376.8734 | 0 | 253.0151 | 0 | 540.7557 | 0 | 161.3637 | 449.7376 | 1781.7454 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.656 | 19.9581 | 16.8288 | 19.4865 | 20 |  | 15.537 | 0 | 15.537 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8531 | 0 | 71.5147 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 15 | 231 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3621.3381 | 0 | 2298.2466 | 0 | 5879.0469 | 0 | 2064.798 | 0 | 13863.4296 | 0 | 267.827 | 0 | 127.6391 | 0 | 285.8976 | 0 | 114.6739 | 301.2805 | 1097.3181 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.626 | 19.9281 | 16.7933 | 19.4511 | 20 |  | 26.6583 | 0 | 26.6583 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8530 | 0 | 71.4097 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 16 | 232 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2449.7145 | 0 | 1532.4068 | 0 | 4559.6826 | 0 | 1396.767 | 0 | 9938.571 | 0 | 181.176 | 0 | 85.1062 | 0 | 221.7371 | 0 | 77.5731 | 205.2201 | 770.8124 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6095 | 19.9116 | 16.7593 | 19.4171 | 20 |  | 32.78 | 0 | 32.78 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8529 | 0 | 71.0686 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 17 | 233 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 621.3734 | 0 | 443.717 | 0 | 13345.7651 | 0 | 354.2919 | 0 | 14765.1474 | 0 | 45.9555 | 0 | 24.643 | 0 | 649.0036 | 0 | 19.6765 | 48.0302 | 787.3089 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6192 | 19.9213 | 16.7571 | 19.4149 | 20 |  | 29.1838 | 0 | 29.1838 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8528 | 0 | 71.0224 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 18 | 234 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6055 | 19.9086 | 16.7516 | 19.4084 | 20 |  | 33.9014 | 0 | 33.9014 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8527 | 0 | 70.9322 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 19 | 235 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6064 | 19.9095 | 16.7554 | 19.4123 | 20 |  | 33.563 | 0 | 33.563 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8526 | 0 | 70.489 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 20 | 236 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6073 | 19.9104 | 16.7593 | 19.4161 | 20 |  | 33.2246 | 0 | 33.2246 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8525 | 0 | 70.3945 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 21 | 237 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6064 | 19.9095 | 16.7554 | 19.4123 | 20 |  | 33.563 | 0 | 33.563 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8524 | 0 | 70.2799 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 22 | 238 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6055 | 19.9086 | 16.7516 | 19.4084 | 20 |  | 33.9014 | 0 | 33.9014 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8523 | 0 | 70.116 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 23 | 239 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6064 | 19.9095 | 16.7554 | 19.4123 | 20 |  | 33.563 | 0 | 33.563 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8522 | 0 | 70.115 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 10 | 24 | 240 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6046 | 19.9077 | 16.7477 | 19.4046 | 20 |  | 34.2397 | 0 | 34.2397 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8521 | 0 | 69.4751 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 1 | 241 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.555 | 19.8581 | 16.693 | 19.3498 | 19.8581 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8520 | 0 | 69.3526 | 19.8581 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 2 | 242 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4163 | 19.7193 | 16.5643 | 19.2211 | 19.7193 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8519 | 0 | 69.3282 | 19.7193 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 3 | 243 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2816 | 19.5847 | 16.4425 | 19.0993 | 19.5847 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8518 | 0 | 69.0224 | 19.5847 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 4 | 244 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1473 | 19.4504 | 16.3092 | 18.9661 | 19.4504 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8517 | 0 | 68.9219 | 19.4504 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 5 | 245 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0089 | 19.3119 | 16.1571 | 18.8139 | 19.3119 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8516 | 0 | 68.7206 | 19.3119 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 6 | 246 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8653 | 19.1684 | 15.9971 | 18.6539 | 19.1684 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8515 | 0 | 68.5028 | 19.1684 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 7 | 247 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7195 | 19.0226 | 15.8438 | 18.5006 | 19.0226 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8514 | 0 | 68.4963 | 19.0226 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 8 | 248 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.59 | 18.8921 | 15.6926 | 18.3504 | 20 |  | 410.6407 | 0 | 410.6407 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8513 | 0 | 68.3491 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 9 | 249 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5596 | 19.8616 | 16.6364 | 19.2942 | 20 |  | 51.2824 | 0 | 51.2824 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8512 | 0 | 68.2407 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 10 | 250 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2479.4574 | 0 | 7015.4554 | 0 | 1807.0561 | 0 | 772.7543 | 0 | 12074.7232 | 0 | 183.3758 | 0 | 389.6215 | 0 | 87.877 | 0 | 42.9169 | 135.3579 | 839.1491 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.591 | 19.8931 | 16.6556 | 19.3134 | 20 |  | 39.6154 | 0 | 39.6154 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8511 | 0 | 68.2398 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 11 | 251 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4623.1553 | 0 | 27884.8726 | 0 | 12880.9221 | 0 | 2636.0096 | 0 | 48024.9596 | 0 | 341.9194 | 0 | 1548.6587 | 0 | 626.3984 | 0 | 146.3976 | 593.8282 | 3257.2023 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7063 | 20.0084 | 16.8105 | 19.4683 | 20.0084 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8510 | 0 | 68.2043 | 20.0084 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 12 | 252 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5558.463 | 0 | 43995.4866 | 0 | 41641.6903 | 0 | 3169.2991 | 0 | 94364.939 | 0 | 411.0929 | 0 | 2443.4034 | 0 | 2025.0325 | 0 | 176.0152 | 982.4364 | 6037.9805 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8556 | 20.1577 | 16.9869 | 19.6447 | 20.1577 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8509 | 0 | 68.0919 | 20.1577 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 13 | 253 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5936.9376 | 0 | 45470.4305 | 0 | 73654.2945 | 0 | 3385.096 | 0 | 128446.7586 | 0 | 439.0841 | 0 | 2525.3182 | 0 | 3581.8032 | 0 | 188.0001 | 1200.7556 | 7934.9613 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1082 | 20.4103 | 17.2601 | 19.9179 | 20.4103 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8508 | 0 | 68.0534 | 20.4103 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 14 | 254 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5794.9818 | 0 | 35421.7032 | 0 | 91642.1263 | 0 | 3304.1563 | 0 | 136162.9676 | 0 | 428.5854 | 0 | 1967.2361 | 0 | 4456.5503 | 0 | 183.5049 | 1126.5271 | 8162.4037 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3833 | 20.6854 | 17.5392 | 20.197 | 20.6854 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8507 | 0 | 67.6472 | 20.6854 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 15 | 255 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5061.5955 | 0 | 23007.4857 | 0 | 97058.6775 | 0 | 2885.9974 | 0 | 128013.7561 | 0 | 374.3456 | 0 | 1277.7803 | 0 | 4719.9568 | 0 | 160.2813 | 886.376 | 7418.74 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6294 | 20.9315 | 17.7688 | 20.4266 | 20.9315 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8506 | 0 | 67.5638 | 20.9315 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 16 | 256 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3844.1277 | 0 | 7595.5092 | 0 | 56509.4876 | 0 | 2191.8272 | 0 | 70140.9517 | 0 | 284.3041 | 0 | 421.8363 | 0 | 2748.0525 | 0 | 121.7288 | 436.6384 | 4012.5601 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7013 | 21.0034 | 17.8124 | 20.4702 | 21.0034 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8505 | 0 | 67.5065 | 21.0034 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 17 | 257 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 749.664 | 0 | 560.7713 | 0 | 19388.7149 | 0 | 427.44 | 0 | 21126.5901 | 0 | 55.4437 | 0 | 31.1439 | 0 | 942.8719 | 0 | 23.739 | 61.1294 | 1114.3278 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6199 | 20.922 | 17.6869 | 20.3447 | 20.922 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8504 | 0 | 67.407 | 20.922 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 18 | 258 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.494 | 20.797 | 17.5337 | 20.1906 | 20.797 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8503 | 0 | 67.3017 | 20.797 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 19 | 259 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3611 | 20.6642 | 17.3751 | 20.032 | 20.6642 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8502 | 0 | 67.2183 | 20.6642 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 20 | 260 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2304 | 20.5335 | 17.2513 | 19.9081 | 20.5335 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8501 | 0 | 67.1622 | 20.5335 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 21 | 261 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0974 | 20.4004 | 17.1103 | 19.7672 | 20.4004 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8500 | 0 | 66.9798 | 20.4004 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 22 | 262 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9656 | 20.2686 | 16.9824 | 19.6393 | 20.2686 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8499 | 0 | 66.9784 | 20.2686 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 23 | 263 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8332 | 20.1363 | 16.8481 | 19.5049 | 20.1363 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8498 | 0 | 66.9562 | 20.1363 | 0 | 0 | 0
|  | 2001 | 1 | 11 | 24 | 264 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6994 | 20.0025 | 16.7093 | 19.3662 | 20.0025 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8497 | 0 | 66.8574 | 20.0025 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 1 | 265 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5191 | 19.8222 | 16.5337 | 19.1905 | 19.8222 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8496 | 0 | 66.8004 | 19.8222 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 2 | 266 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3397 | 19.6427 | 16.3566 | 19.0134 | 19.6427 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8495 | 0 | 66.6708 | 19.6427 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 3 | 267 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1519 | 19.4549 | 16.1418 | 18.7986 | 19.4549 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8494 | 0 | 66.6687 | 19.4549 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 4 | 268 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9577 | 19.2608 | 15.9267 | 18.5835 | 19.2608 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8493 | 0 | 66.638 | 19.2608 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 5 | 269 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7791 | 19.0821 | 15.7978 | 18.4547 | 19.0821 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8492 | 0 | 66.5752 | 19.0821 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 6 | 270 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6113 | 18.9144 | 15.6647 | 18.3215 | 18.9144 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8491 | 0 | 66.4871 | 18.9144 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 7 | 271 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.4434 | 18.7464 | 15.4957 | 18.1526 | 18.7464 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8490 | 0 | 66.2824 | 18.7464 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 8 | 272 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.302 | 18.6041 | 15.3627 | 18.0205 | 20 |  | 517.4011 | 0 | 517.4011 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8489 | 0 | 65.6091 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 9 | 273 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5537 | 19.8558 | 16.6099 | 19.2677 | 20 |  | 53.4644 | 0 | 53.4644 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8488 | 0 | 65.5415 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 10 | 274 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 854.8719 | 0 | 1230.7455 | 0 | 934.9309 | 0 | 399.806 | 0 | 3420.3543 | 0 | 63.2246 | 0 | 68.3526 | 0 | 45.4656 | 0 | 22.2043 | 61.1294 | 260.3765 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.567 | 19.8691 | 16.6348 | 19.2926 | 20 |  | 48.5368 | 0 | 48.5368 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8487 | 0 | 65.2949 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 11 | 275 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3178.6544 | 0 | 7716.2176 | 0 | 5772.7295 | 0 | 1812.3907 | 0 | 18479.9922 | 0 | 235.087 | 0 | 428.5401 | 0 | 280.7274 | 0 | 100.6558 | 301.2805 | 1346.2909 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6215 | 19.9235 | 16.7269 | 19.3846 | 20 |  | 28.3389 | 0 | 28.3389 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8486 | 0 | 65.2287 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 12 | 276 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4053.086 | 0 | 4229.4833 | 0 | 7000.8614 | 0 | 2310.9701 | 0 | 17594.4007 | 0 | 299.7582 | 0 | 234.8953 | 0 | 340.4514 | 0 | 128.3457 | 353.6771 | 1357.1278 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6275 | 19.9296 | 16.7623 | 19.4201 | 20 |  | 26.0964 | 0 | 26.0964 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8485 | 0 | 65.219 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 13 | 277 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4082.4729 | 0 | 2794.8895 | 0 | 6169.88 | 0 | 2327.7258 | 0 | 15374.9682 | 0 | 301.9316 | 0 | 155.2214 | 0 | 300.0408 | 0 | 129.2763 | 340.578 | 1227.0481 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6262 | 19.9283 | 16.7788 | 19.4365 | 20 |  | 26.5756 | 0 | 26.5756 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8484 | 0 | 64.7529 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 14 | 278 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3965.2425 | 0 | 2460.1208 | 0 | 5805.9347 | 0 | 2260.8839 | 0 | 14492.1819 | 0 | 293.2615 | 0 | 136.6292 | 0 | 282.3422 | 0 | 125.564 | 327.4788 | 1165.2757 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6254 | 19.9274 | 16.7838 | 19.4416 | 20 |  | 26.8967 | 0 | 26.8967 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8483 | 0 | 64.7368 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 15 | 279 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5377.7711 | 0 | 6590.2363 | 0 | 22946.3534 | 0 | 3066.273 | 0 | 37980.6339 | 0 | 397.7293 | 0 | 366.0059 | 0 | 1115.8796 | 0 | 170.2934 | 510.8669 | 2560.7751 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6975 | 19.9996 | 16.8726 | 19.5304 | 20 |  | 0.14247 | 0 | 0.14247 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8482 | 0 | 64.415 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 16 | 280 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3920.449 | 0 | 7764.4599 | 0 | 57674.5506 | 0 | 2235.3437 | 0 | 71594.8031 | 0 | 289.9486 | 0 | 431.2194 | 0 | 2804.7094 | 0 | 124.1456 | 449.7376 | 4099.7606 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7991 | 20.1012 | 16.9963 | 19.6541 | 20.1012 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8481 | 0 | 64.1924 | 20.1012 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 17 | 281 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 900.683 | 0 | 773.0629 | 0 | 36648.2358 | 0 | 513.5473 | 0 | 38835.5291 | 0 | 66.6127 | 0 | 42.9341 | 0 | 1782.2012 | 0 | 28.5212 | 82.9613 | 2003.2304 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7969 | 20.099 | 16.9632 | 19.621 | 20.099 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8480 | 0 | 63.9363 | 20.099 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 18 | 282 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6999 | 20.003 | 16.8314 | 19.4882 | 20.003 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8479 | 0 | 63.8263 | 20.003 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 19 | 283 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5984 | 19.9015 | 16.7121 | 19.369 | 20 |  | 36.5282 | 0 | 36.5282 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8478 | 0 | 63.7449 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 20 | 284 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.59 | 19.8931 | 16.6862 | 19.343 | 20 |  | 39.6536 | 0 | 39.6536 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8477 | 0 | 63.4471 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 21 | 285 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5818 | 19.8848 | 16.6515 | 19.3084 | 20 |  | 42.6989 | 0 | 42.6989 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8476 | 0 | 63.4368 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 22 | 286 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.58 | 19.883 | 16.6438 | 19.3007 | 20 |  | 43.3757 | 0 | 43.3757 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8475 | 0 | 63.1451 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 23 | 287 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5781 | 19.8812 | 16.6361 | 19.293 | 20 |  | 44.0524 | 0 | 44.0524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8474 | 0 | 62.8863 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 12 | 24 | 288 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.58 | 19.883 | 16.6438 | 19.3007 | 20 |  | 43.3757 | 0 | 43.3757 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8473 | 0 | 62.5805 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 1 | 289 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5304 | 19.8334 | 16.5891 | 19.2459 | 19.8334 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8472 | 0 | 62.209 | 19.8334 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 2 | 290 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3545 | 19.6575 | 16.3828 | 19.0396 | 19.6575 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8471 | 0 | 62.0398 | 19.6575 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 3 | 291 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1748 | 19.4778 | 16.1907 | 18.8475 | 19.4778 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8470 | 0 | 61.9251 | 19.4778 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 4 | 292 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9931 | 19.2962 | 16.0026 | 18.6594 | 19.2962 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8469 | 0 | 61.774 | 19.2962 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 5 | 293 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8114 | 19.1145 | 15.8203 | 18.4772 | 19.1145 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8468 | 0 | 61.6313 | 19.1145 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 6 | 294 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6306 | 18.9336 | 15.6419 | 18.2987 | 18.9336 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8467 | 0 | 61.4391 | 18.9336 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 7 | 295 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.4469 | 18.75 | 15.4488 | 18.1057 | 18.75 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8466 | 0 | 61.1231 | 18.75 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 8 | 296 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.3109 | 18.614 | 15.3117 | 17.9685 | 20 |  | 513.9156 | 0 | 513.9156 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8465 | 0 | 60.8768 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 9 | 297 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5526 | 19.8556 | 16.5284 | 19.1852 | 20 |  | 53.5267 | 0 | 53.5267 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8464 | 0 | 60.6946 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 10 | 298 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7408.5199 | 0 | 31176.58 | 0 | 2226.5038 | 0 | 952.1233 | 0 | 41763.727 | 0 | 547.9195 | 0 | 1731.4722 | 0 | 108.2747 | 0 | 52.8786 | 340.578 | 2781.1229 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6818 | 19.9849 | 16.6852 | 19.342 | 20 |  | 5.5982 | 0 | 5.5982 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8463 | 0 | 60.4047 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 11 | 299 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3721.3077 | 0 | 57321.8562 | 0 | 18969.8971 | 0 | 2121.7982 | 0 | 82134.8592 | 0 | 275.2205 | 0 | 3183.5178 | 0 | 922.5048 | 0 | 117.8396 | 847.0785 | 5346.1612 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8113 | 20.1144 | 16.857 | 19.5138 | 20.1144 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8462 | 0 | 60.3694 | 20.1144 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 12 | 300 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5420.816 | 0 | 50473.4933 | 0 | 46371.489 | 0 | 3090.8162 | 0 | 105356.6145 | 0 | 400.9128 | 0 | 2803.1762 | 0 | 2255.0423 | 0 | 171.6565 | 1078.4969 | 6709.2847 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9955 | 20.2985 | 17.0515 | 19.7083 | 20.2985 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8461 | 0 | 60.3302 | 20.2985 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 13 | 301 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6111.3565 | 0 | 43090.8946 | 0 | 69484.9206 | 0 | 3484.5454 | 0 | 122171.717 | 0 | 451.9838 | 0 | 2393.1645 | 0 | 3379.0469 | 0 | 193.5233 | 1174.5573 | 7592.2758 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2384 | 20.5414 | 17.3294 | 19.9862 | 20.5414 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8460 | 0 | 59.9446 | 20.5414 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 14 | 302 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6378.3514 | 0 | 30093.2024 | 0 | 77205.8122 | 0 | 3636.7793 | 0 | 117314.1454 | 0 | 471.7302 | 0 | 1671.304 | 0 | 3754.5133 | 0 | 201.978 | 1056.665 | 7156.1905 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4701 | 20.7732 | 17.5718 | 20.2287 | 20.7732 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8459 | 0 | 59.3866 | 20.7732 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 15 | 303 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5092.8143 | 0 | 24939.4775 | 0 | 105201.1104 | 0 | 2903.7977 | 0 | 138137.1999 | 0 | 376.6545 | 0 | 1385.0785 | 0 | 5115.9227 | 0 | 161.2699 | 956.2381 | 7995.1637 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7635 | 21.0666 | 17.8752 | 20.532 | 21.0666 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8458 | 0 | 59.2898 | 21.0666 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 16 | 304 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4024.2634 | 0 | 7484.1635 | 0 | 54486.9703 | 0 | 2294.5361 | 0 | 68289.9333 | 0 | 297.6266 | 0 | 415.6524 | 0 | 2649.6976 | 0 | 127.433 | 449.7376 | 3940.1471 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8447 | 21.1478 | 17.9184 | 20.5753 | 21.1478 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8457 | 0 | 59.0971 | 21.1478 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 17 | 305 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 788.7446 | 0 | 681.4544 | 0 | 32555.3477 | 0 | 449.7228 | 0 | 34475.2695 | 0 | 58.334 | 0 | 37.8463 | 0 | 1583.1643 | 0 | 24.9765 | 157.1898 | 1861.511 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.822 | 21.1251 | 17.8742 | 20.531 | 21.1251 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8456 | 0 | 59.063 | 21.1251 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 18 | 306 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6914 | 20.9945 | 17.7135 | 20.3703 | 20.9945 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8455 | 0 | 58.6031 | 20.9945 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 19 | 307 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5567 | 20.8597 | 17.5649 | 20.2217 | 20.8597 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8454 | 0 | 58.2129 | 20.8597 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 20 | 308 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4177 | 20.7208 | 17.4123 | 20.0691 | 20.7208 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8453 | 0 | 57.8635 | 20.7208 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 21 | 309 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2764 | 20.5795 | 17.2634 | 19.9202 | 20.5795 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8452 | 0 | 57.7609 | 20.5795 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 22 | 310 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.132 | 20.435 | 17.1083 | 19.7652 | 20.435 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8451 | 0 | 57.6318 | 20.435 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 23 | 311 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9852 | 20.2883 | 16.9541 | 19.611 | 20.2883 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8450 | 0 | 57.2698 | 20.2883 | 0 | 0 | 0
|  | 2001 | 1 | 13 | 24 | 312 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8399 | 20.143 | 16.8131 | 19.47 | 20.143 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8449 | 0 | 56.7105 | 20.143 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 1 | 313 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6428 | 19.9458 | 16.6033 | 19.2602 | 19.9458 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8448 | 0 | 56.6836 | 19.9458 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 2 | 314 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4448 | 19.7478 | 16.4023 | 19.0591 | 19.7478 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8447 | 0 | 56.482 | 19.7478 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 3 | 315 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2478 | 19.5508 | 16.2082 | 18.865 | 19.5508 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8446 | 0 | 56.385 | 19.5508 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 4 | 316 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0509 | 19.3539 | 16.0112 | 18.668 | 19.3539 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8445 | 0 | 56.2552 | 19.3539 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 5 | 317 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8476 | 19.1507 | 15.7873 | 18.4441 | 19.1507 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8444 | 0 | 56.2116 | 19.1507 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 6 | 318 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6463 | 18.9494 | 15.592 | 18.2488 | 18.9494 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8443 | 0 | 55.9556 | 18.9494 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 7 | 319 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.447 | 18.7501 | 15.3985 | 18.0554 | 18.7501 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8442 | 0 | 55.855 | 18.7501 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 8 | 320 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.2946 | 18.5977 | 15.2425 | 17.8993 | 20 |  | 519.9708 | 0 | 519.9708 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8441 | 0 | 55.721 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 9 | 321 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5398 | 19.8429 | 16.4745 | 19.1313 | 20 |  | 58.2638 | 0 | 58.2638 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8440 | 0 | 55.6916 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 10 | 322 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1321.5062 | 0 | 2688.7738 | 0 | 1196.3581 | 0 | 511.6005 | 0 | 5718.2386 | 0 | 97.736 | 0 | 149.328 | 0 | 58.1788 | 0 | 28.4131 | 82.9613 | 416.6172 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.57 | 19.8731 | 16.5485 | 19.2053 | 20 |  | 47.0535 | 0 | 47.0535 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8439 | 0 | 55.4495 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 11 | 323 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2054.0906 | 0 | 1414.3163 | 0 | 2798.9792 | 0 | 1171.192 | 0 | 7438.5781 | 0 | 151.9165 | 0 | 78.5477 | 0 | 136.1142 | 0 | 65.0452 | 170.289 | 601.9125 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5898 | 19.8928 | 16.6152 | 19.272 | 20 |  | 39.7339 | 0 | 39.7339 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8438 | 0 | 55.1612 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 12 | 324 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2455.1193 | 0 | 1528.0499 | 0 | 3378.6114 | 0 | 1399.8487 | 0 | 8761.6293 | 0 | 181.5758 | 0 | 84.8642 | 0 | 164.3016 | 0 | 77.7442 | 205.2201 | 713.7059 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6019 | 19.9049 | 16.6536 | 19.3104 | 20 |  | 35.2538 | 0 | 35.2538 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8437 | 0 | 55.0853 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 13 | 325 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2171.1008 | 0 | 1308.6914 | 0 | 3003.9532 | 0 | 1237.9084 | 0 | 7721.6538 | 0 | 160.5703 | 0 | 72.6816 | 0 | 146.082 | 0 | 68.7504 | 183.3881 | 631.4725 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6052 | 19.9083 | 16.6776 | 19.3344 | 20 |  | 34.0074 | 0 | 34.0074 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8436 | 0 | 55.064 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 14 | 326 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2595.9443 | 0 | 1565.0677 | 0 | 3681.136 | 0 | 1480.1437 | 0 | 9322.2916 | 0 | 191.9909 | 0 | 86.9201 | 0 | 179.0134 | 0 | 82.2036 | 218.3192 | 758.4472 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6108 | 19.9139 | 16.686 | 19.3428 | 20 |  | 31.9414 | 0 | 31.9414 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8435 | 0 | 54.9672 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 15 | 327 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1274.9283 | 0 | 748.3981 | 0 | 1795.5498 | 0 | 726.9328 | 0 | 4545.8091 | 0 | 94.2912 | 0 | 41.5642 | 0 | 87.3175 | 0 | 40.3721 | 109.1596 | 372.7046 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5941 | 19.8972 | 16.6607 | 19.3176 | 20 |  | 38.1188 | 0 | 38.1188 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8434 | 0 | 54.7546 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 16 | 328 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 965.5514 | 0 | 566.2924 | 0 | 1436.2891 | 0 | 550.5337 | 0 | 3518.6665 | 0 | 71.4103 | 0 | 31.4505 | 0 | 69.8466 | 0 | 30.5753 | 82.9613 | 286.244 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5911 | 19.8942 | 16.6578 | 19.3146 | 20 |  | 39.2324 | 0 | 39.2324 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8433 | 0 | 54.7411 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 17 | 329 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 343.8998 | 0 | 198.0415 | 0 | 724.8276 | 0 | 196.0832 | 0 | 1462.8521 | 0 | 25.4341 | 0 | 10.9987 | 0 | 35.2483 | 0 | 10.89 | 26.1983 | 108.7695 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5842 | 19.8873 | 16.648 | 19.3048 | 20 |  | 41.804 | 0 | 41.804 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8432 | 0 | 54.7175 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 18 | 330 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8431 | 0 | 54.5163 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 19 | 331 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5772 | 19.8803 | 16.6323 | 19.2891 | 20 |  | 44.3908 | 0 | 44.3908 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8430 | 0 | 54.454 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 20 | 332 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5745 | 19.8775 | 16.6207 | 19.2776 | 20 |  | 45.4059 | 0 | 45.4059 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8429 | 0 | 54.312 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 21 | 333 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5699 | 19.873 | 16.6015 | 19.2583 | 20 |  | 47.0977 | 0 | 47.0977 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8428 | 0 | 54.0181 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 22 | 334 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5645 | 19.8675 | 16.5784 | 19.2352 | 20 |  | 49.1279 | 0 | 49.1279 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8427 | 0 | 53.7762 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 23 | 335 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5617 | 19.8648 | 16.5668 | 19.2237 | 20 |  | 50.143 | 0 | 50.143 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8426 | 0 | 53.1379 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 14 | 24 | 336 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5562 | 19.8593 | 16.5438 | 19.2006 | 20 |  | 52.1732 | 0 | 52.1732 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8425 | 0 | 52.8562 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 1 | 337 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5057 | 19.8088 | 16.4852 | 19.142 | 19.8088 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8424 | 0 | 52.7115 | 19.8088 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 2 | 338 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3164 | 19.6194 | 16.3014 | 18.9582 | 19.6194 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8423 | 0 | 52.6019 | 19.6194 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 3 | 339 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1279 | 19.431 | 16.1156 | 18.7724 | 19.431 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8422 | 0 | 52.5753 | 19.431 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 4 | 340 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9413 | 19.2443 | 15.9344 | 18.5913 | 19.2443 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8421 | 0 | 52.4233 | 19.2443 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 5 | 341 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7509 | 19.054 | 15.732 | 18.3888 | 19.054 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8420 | 0 | 52.3051 | 19.054 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 6 | 342 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5615 | 18.8646 | 15.5452 | 18.2021 | 18.8646 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8419 | 0 | 52.1883 | 18.8646 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 7 | 343 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.3703 | 18.6734 | 15.3478 | 18.0047 | 18.6734 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8418 | 0 | 51.9731 | 18.6734 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 8 | 344 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.2052 | 18.5073 | 15.1829 | 17.8407 | 20 |  | 553.2694 | 0 | 553.2694 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8417 | 0 | 51.4057 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 9 | 345 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.52 | 19.8221 | 16.4587 | 19.1165 | 20 |  | 65.9332 | 0 | 65.9332 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8416 | 0 | 51.0262 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 10 | 346 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4375.102 | 0 | 13946.8153 | 0 | 2388.2927 | 0 | 1021.3094 | 0 | 21731.5194 | 0 | 323.5739 | 0 | 774.5725 | 0 | 116.1425 | 0 | 56.7211 | 205.2201 | 1476.23 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5885 | 19.8906 | 16.5469 | 19.2047 | 20 |  | 40.5434 | 0 | 40.5434 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8415 | 0 | 50.5923 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 11 | 347 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4812.711 | 0 | 29209.2153 | 0 | 12804.0081 | 0 | 2744.0896 | 0 | 49570.024 | 0 | 355.9386 | 0 | 1622.2095 | 0 | 622.658 | 0 | 152.4001 | 628.7593 | 3381.9655 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.678 | 19.9801 | 16.6675 | 19.3253 | 20 |  | 7.3702 | 0 | 7.3702 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8414 | 0 | 50.5762 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 12 | 348 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5773.6283 | 0 | 43938.4357 | 0 | 40775.8113 | 0 | 3291.981 | 0 | 93779.8563 | 0 | 427.0061 | 0 | 2440.2349 | 0 | 1982.9249 | 0 | 182.8287 | 1017.3675 | 6050.3621 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8146 | 20.1167 | 16.8374 | 19.4952 | 20.1167 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8413 | 0 | 50.4218 | 20.1167 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 13 | 349 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6086.9846 | 0 | 45150.1335 | 0 | 72116.9723 | 0 | 3470.6491 | 0 | 126824.7395 | 0 | 450.1813 | 0 | 2507.5297 | 0 | 3507.0434 | 0 | 192.7515 | 1226.954 | 7884.4598 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0344 | 20.3365 | 17.0877 | 19.7455 | 20.3365 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8412 | 0 | 50.394 | 20.3365 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 14 | 350 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6017.2696 | 0 | 37113.8449 | 0 | 94980.7543 | 0 | 3430.8993 | 0 | 141542.7682 | 0 | 445.0253 | 0 | 2061.2136 | 0 | 4618.9075 | 0 | 190.5439 | 1213.8548 | 8529.5451 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2988 | 20.6009 | 17.3626 | 20.0204 | 20.6009 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8411 | 0 | 50.0798 | 20.6009 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 15 | 351 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5066.5549 | 0 | 26532.8404 | 0 | 111884.5828 | 0 | 2888.8252 | 0 | 146372.8033 | 0 | 374.7124 | 0 | 1473.57 | 0 | 5440.9395 | 0 | 160.4384 | 1017.3675 | 8467.0278 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5779 | 20.88 | 17.6484 | 20.3062 | 20.88 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8410 | 0 | 50.0511 | 20.88 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 16 | 352 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3550.8709 | 0 | 13128.3696 | 0 | 109483.7299 | 0 | 2024.6194 | 0 | 128187.5899 | 0 | 262.6154 | 0 | 729.118 | 0 | 5324.1862 | 0 | 112.4425 | 628.7593 | 7057.1214 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7974 | 21.0995 | 17.8459 | 20.5036 | 21.0995 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8409 | 0 | 50.0325 | 21.0995 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 17 | 353 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1017.8957 | 0 | 896.1983 | 0 | 44530.0441 | 0 | 580.3791 | 0 | 47024.5172 | 0 | 75.2815 | 0 | 49.7727 | 0 | 2165.493 | 0 | 32.2329 | 205.2201 | 2528.0001 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7762 | 21.0783 | 17.7952 | 20.453 | 21.0783 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8408 | 0 | 49.9976 | 21.0783 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 18 | 354 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6387 | 20.9418 | 17.6416 | 20.2984 | 20.9418 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8407 | 0 | 49.4814 | 20.9418 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 19 | 355 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4981 | 20.8011 | 17.4873 | 20.1441 | 20.8011 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8406 | 0 | 49.3151 | 20.8011 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 20 | 356 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3542 | 20.6572 | 17.3329 | 19.9897 | 20.6572 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8405 | 0 | 49.2384 | 20.6572 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 21 | 357 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2099 | 20.5129 | 17.1869 | 19.8438 | 20.5129 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8404 | 0 | 49.2107 | 20.5129 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 22 | 358 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0624 | 20.3655 | 17.029 | 19.6858 | 20.3655 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8403 | 0 | 49.2026 | 20.3655 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 23 | 359 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9127 | 20.2158 | 16.8719 | 19.5287 | 20.2158 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8402 | 0 | 48.875 | 20.2158 | 0 | 0 | 0
|  | 2001 | 1 | 15 | 24 | 360 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7535 | 20.0565 | 16.6818 | 19.3387 | 20.0565 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8401 | 0 | 48.8657 | 20.0565 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 1 | 361 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.549 | 19.852 | 16.4856 | 19.1424 | 19.852 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8400 | 0 | 48.6407 | 19.852 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 2 | 362 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3446 | 19.6476 | 16.2813 | 18.9382 | 19.6476 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8399 | 0 | 48.6075 | 19.6476 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 3 | 363 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1421 | 19.4452 | 16.0849 | 18.7418 | 19.4452 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8398 | 0 | 48.4875 | 19.4452 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 4 | 364 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.938 | 19.2411 | 15.875 | 18.5318 | 19.2411 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8397 | 0 | 48.3882 | 19.2411 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 5 | 365 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.734 | 19.0371 | 15.6711 | 18.328 | 19.0371 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8396 | 0 | 47.7229 | 19.0371 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 6 | 366 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.532 | 18.8351 | 15.4751 | 18.132 | 18.8351 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8395 | 0 | 47.6838 | 18.8351 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 7 | 367 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.332 | 18.635 | 15.281 | 17.9378 | 18.635 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8394 | 0 | 47.52 | 18.635 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 8 | 368 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.1563 | 18.4584 | 15.0969 | 17.7547 | 20 |  | 571.4074 | 0 | 571.4074 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8393 | 0 | 47.4663 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 9 | 369 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5015 | 19.8036 | 16.3756 | 19.0334 | 20 |  | 72.791 | 0 | 72.791 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8392 | 0 | 47.3742 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 10 | 370 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4403.4533 | 0 | 12285.4012 | 0 | 2845.7332 | 0 | 1216.9254 | 0 | 20751.5131 | 0 | 325.6707 | 0 | 682.3016 | 0 | 138.3878 | 0 | 67.5851 | 244.5175 | 1458.4627 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5766 | 19.8787 | 16.5026 | 19.1604 | 20 |  | 44.9701 | 0 | 44.9701 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8391 | 0 | 47.2742 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 11 | 371 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4392.089 | 0 | 39700.871 | 0 | 14599.691 | 0 | 2504.2613 | 0 | 61196.9123 | 0 | 324.8302 | 0 | 2204.8908 | 0 | 709.982 | 0 | 139.0806 | 716.087 | 4094.8706 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7096 | 20.0117 | 16.6927 | 19.3505 | 20.0117 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8390 | 0 | 46.4036 | 20.0117 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 12 | 372 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5696.2052 | 0 | 46699.5211 | 0 | 42687.8578 | 0 | 3247.8363 | 0 | 98331.4204 | 0 | 421.2801 | 0 | 2593.5789 | 0 | 2075.9076 | 0 | 180.377 | 1056.665 | 6327.8085 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8435 | 20.1455 | 16.8804 | 19.5382 | 20.1455 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8389 | 0 | 46.2328 | 20.1455 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 13 | 373 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6266.3009 | 0 | 43527.7852 | 0 | 69450.645 | 0 | 3572.8909 | 0 | 122817.622 | 0 | 463.4432 | 0 | 2417.4283 | 0 | 3377.3801 | 0 | 198.4298 | 1213.8548 | 7670.5362 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0558 | 20.3579 | 17.1231 | 19.7809 | 20.3579 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8388 | 0 | 45.7945 | 20.3579 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 14 | 374 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6046.1201 | 0 | 36335.8741 | 0 | 92730.7575 | 0 | 3447.3492 | 0 | 138560.1008 | 0 | 447.1591 | 0 | 2018.0069 | 0 | 4509.4903 | 0 | 191.4575 | 1200.7556 | 8366.8694 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3166 | 20.6187 | 17.3975 | 20.0553 | 20.6187 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8387 | 0 | 45.7735 | 20.6187 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 15 | 375 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5317.7861 | 0 | 24988.5748 | 0 | 104522.6494 | 0 | 3032.071 | 0 | 137861.0812 | 0 | 393.2929 | 0 | 1387.8053 | 0 | 5082.9292 | 0 | 168.3939 | 995.5356 | 8027.9569 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5756 | 20.8776 | 17.6607 | 20.3184 | 20.8776 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8386 | 0 | 45.2119 | 20.8776 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 16 | 376 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3723.4445 | 0 | 12639.9303 | 0 | 104059.9126 | 0 | 2123.0166 | 0 | 122546.304 | 0 | 275.3786 | 0 | 701.9913 | 0 | 5060.4263 | 0 | 117.9072 | 628.7593 | 6784.4628 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7842 | 21.0863 | 17.8506 | 20.5084 | 21.0863 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8385 | 0 | 45.0197 | 21.0863 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 17 | 377 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1039.8111 | 0 | 1021.5009 | 0 | 60591.919 | 0 | 592.8748 | 0 | 63246.1058 | 0 | 76.9024 | 0 | 56.7317 | 0 | 2946.5808 | 0 | 32.9268 | 192.1209 | 3305.2626 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8081 | 21.1102 | 17.8239 | 20.4817 | 21.1102 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8384 | 0 | 44.9387 | 21.1102 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 18 | 378 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6658 | 20.9688 | 17.653 | 20.3098 | 20.9688 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8383 | 0 | 44.9353 | 20.9688 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 19 | 379 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.513 | 20.816 | 17.4633 | 20.1201 | 20.816 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8382 | 0 | 44.7077 | 20.816 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 20 | 380 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.348 | 20.651 | 17.2587 | 19.9155 | 20.651 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8381 | 0 | 44.3031 | 20.651 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 21 | 381 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1855 | 20.4885 | 17.104 | 19.7608 | 20.4885 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8380 | 0 | 44.0955 | 20.4885 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 22 | 382 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0173 | 20.3203 | 16.917 | 19.5739 | 20.3203 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8379 | 0 | 43.9056 | 20.3203 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 23 | 383 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.857 | 20.1601 | 16.7823 | 19.4391 | 20.1601 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8378 | 0 | 43.7636 | 20.1601 | 0 | 0 | 0
|  | 2001 | 1 | 16 | 24 | 384 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6883 | 19.9914 | 16.586 | 19.2428 | 20 |  | 3.1956 | 0 | 3.1956 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8377 | 0 | 42.9953 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 1 | 385 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4729 | 19.7759 | 16.3466 | 19.0034 | 19.7759 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8376 | 0 | 42.991 | 19.7759 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 2 | 386 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2473 | 19.5504 | 16.1159 | 18.7727 | 19.5504 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8375 | 0 | 42.8543 | 19.5504 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 3 | 387 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0267 | 19.3297 | 15.9106 | 18.5675 | 19.3297 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8374 | 0 | 42.651 | 19.3297 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 4 | 388 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8045 | 19.1076 | 15.6832 | 18.3401 | 19.1076 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8373 | 0 | 42.6166 | 19.1076 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 5 | 389 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.579 | 18.8821 | 15.4466 | 18.1035 | 18.8821 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8372 | 0 | 42.5505 | 18.8821 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 6 | 390 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.3529 | 18.656 | 15.2184 | 17.8752 | 18.656 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8371 | 0 | 42.4188 | 18.656 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 7 | 391 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.1217 | 18.4248 | 14.9703 | 17.6271 | 18.4248 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8370 | 0 | 42.263 | 18.4248 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 8 | 392 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 20.9194 | 18.2214 | 14.7662 | 17.424 | 20 |  | 659.2337 | 0 | 659.2337 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8369 | 0 | 41.9234 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 9 | 393 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.4797 | 19.7817 | 16.2773 | 18.9351 | 20 |  | 80.8957 | 0 | 80.8957 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8368 | 0 | 41.8744 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 10 | 394 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3864.3993 | 0 | 9406.1721 | 0 | 2859.3329 | 0 | 1222.741 | 0 | 17352.6452 | 0 | 285.8033 | 0 | 522.3961 | 0 | 139.0492 | 0 | 67.9081 | 231.4184 | 1246.5751 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5467 | 19.8487 | 16.4023 | 19.0601 | 20 |  | 56.0621 | 0 | 56.0621 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8367 | 0 | 41.6156 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 11 | 395 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4434.6262 | 0 | 40375.0443 | 0 | 14570.3819 | 0 | 2528.515 | 0 | 61908.5674 | 0 | 327.9762 | 0 | 2242.3327 | 0 | 708.5567 | 0 | 140.4276 | 729.1862 | 4148.4793 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6898 | 19.9919 | 16.5965 | 19.2543 | 20 |  | 2.9933 | 0 | 2.9933 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8366 | 0 | 41.4369 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 12 | 396 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5765.0404 | 0 | 46526.9266 | 0 | 42342.666 | 0 | 3287.0845 | 0 | 97921.7175 | 0 | 426.371 | 0 | 2583.9934 | 0 | 2059.1209 | 0 | 182.5568 | 1065.3977 | 6317.4398 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8114 | 20.1134 | 16.7811 | 19.4389 | 20.1134 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8365 | 0 | 41.3291 | 20.1134 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 13 | 397 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6817.3834 | 0 | 59675.1633 | 0 | 94041.4487 | 0 | 3887.1046 | 0 | 164421.0999 | 0 | 504.2002 | 0 | 3314.2148 | 0 | 4573.2291 | 0 | 215.8804 | 1589.3638 | 10196.8884 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1338 | 20.4359 | 17.168 | 19.8258 | 20.4359 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8364 | 0 | 41.3138 | 20.4359 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 14 | 398 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6763.1674 | 0 | 48713.0545 | 0 | 124184.8357 | 0 | 3856.1919 | 0 | 183517.2495 | 0 | 500.1905 | 0 | 2705.4057 | 0 | 6039.1 | 0 | 214.1636 | 1563.1655 | 11022.0253 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5106 | 20.8126 | 17.5462 | 20.204 | 20.8126 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8363 | 0 | 41.0514 | 20.8126 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 15 | 399 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5401.4667 | 0 | 24963.4476 | 0 | 104132.6938 | 0 | 3079.7836 | 0 | 137577.3917 | 0 | 399.4818 | 0 | 1386.4098 | 0 | 5063.9657 | 0 | 171.0438 | 1008.6347 | 8029.5357 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7586 | 21.0607 | 17.8087 | 20.4665 | 21.0607 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8362 | 0 | 40.6003 | 21.0607 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 16 | 400 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4131.6175 | 0 | 9776.5566 | 0 | 75370.8722 | 0 | 2355.7468 | 0 | 91634.7931 | 0 | 305.5662 | 0 | 542.9664 | 0 | 3665.2803 | 0 | 130.8325 | 558.8972 | 5203.5426 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8704 | 21.1725 | 17.9063 | 20.5641 | 21.1725 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8361 | 0 | 40.566 | 21.1725 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 17 | 401 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1413.2588 | 0 | 1077.4128 | 0 | 39995.2346 | 0 | 805.8054 | 0 | 43291.7116 | 0 | 104.5218 | 0 | 59.8369 | 0 | 1944.9655 | 0 | 44.7525 | 135.3579 | 2289.4346 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8319 | 21.134 | 17.8284 | 20.4862 | 21.134 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8360 | 0 | 40.5015 | 21.134 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 18 | 402 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6848 | 20.9879 | 17.6567 | 20.3135 | 20.9879 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8359 | 0 | 40.0913 | 20.9879 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 19 | 403 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5328 | 20.8358 | 17.4854 | 20.1422 | 20.8358 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8358 | 0 | 39.9525 | 20.8358 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 20 | 404 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3703 | 20.6734 | 17.2892 | 19.9461 | 20.6734 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8357 | 0 | 39.7811 | 20.6734 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 21 | 405 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.203 | 20.5061 | 17.1062 | 19.763 | 20.5061 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8356 | 0 | 39.5647 | 20.5061 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 22 | 406 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.031 | 20.334 | 16.9185 | 19.5753 | 20.334 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8355 | 0 | 39.3986 | 20.334 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 23 | 407 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8515 | 20.1545 | 16.7147 | 19.3715 | 20.1545 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8354 | 0 | 39.3978 | 20.1545 | 0 | 0 | 0
|  | 2001 | 1 | 17 | 24 | 408 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6645 | 19.9676 | 16.5036 | 19.1605 | 20 |  | 12.0136 | 0 | 12.0136 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8353 | 0 | 39.2888 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 1 | 409 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4619 | 19.765 | 16.3004 | 18.9572 | 19.765 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8352 | 0 | 39.277 | 19.765 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 2 | 410 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2255 | 19.5286 | 16.0592 | 18.716 | 19.5286 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8351 | 0 | 38.8285 | 19.5286 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 3 | 411 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9887 | 19.2917 | 15.8204 | 18.4773 | 19.2917 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8350 | 0 | 38.6785 | 19.2917 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 4 | 412 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7504 | 19.0535 | 15.5774 | 18.2342 | 19.0535 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8349 | 0 | 38.6465 | 19.0535 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 5 | 413 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5255 | 18.8285 | 15.3946 | 18.0515 | 18.8285 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8348 | 0 | 38.5939 | 18.8285 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 6 | 414 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.3017 | 18.6048 | 15.1746 | 17.8314 | 18.6048 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8347 | 0 | 38.5607 | 18.6048 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 7 | 415 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.0865 | 18.3896 | 14.9865 | 17.6434 | 18.3896 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8346 | 0 | 38.5386 | 18.3896 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 8 | 416 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 20.9055 | 18.2076 | 14.8269 | 17.4846 | 20 |  | 664.3723 | 0 | 664.3723 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8345 | 0 | 37.6169 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 9 | 417 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5041 | 19.8061 | 16.3869 | 19.0447 | 20 |  | 71.8559 | 0 | 71.8559 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8344 | 0 | 37.4776 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 10 | 418 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1263.1839 | 0 | 2082.5289 | 0 | 1238.2695 | 0 | 529.5232 | 0 | 5113.5056 | 0 | 93.4226 | 0 | 115.6586 | 0 | 60.217 | 0 | 29.4084 | 82.9613 | 381.6679 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5248 | 19.8269 | 16.428 | 19.0858 | 20 |  | 64.1787 | 0 | 64.1787 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8343 | 0 | 37.4231 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 11 | 419 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 972.7702 | 0 | 592.7844 | 0 | 1305.5086 | 0 | 554.6497 | 0 | 3425.7129 | 0 | 71.9442 | 0 | 32.9218 | 0 | 63.4868 | 0 | 30.8039 | 82.9613 | 282.118 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.53 | 19.8321 | 16.4686 | 19.1264 | 20 |  | 62.2254 | 0 | 62.2254 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8342 | 0 | 37.3433 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 12 | 420 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1435.3181 | 0 | 860.2774 | 0 | 1947.0779 | 0 | 818.3831 | 0 | 5061.0565 | 0 | 106.1533 | 0 | 47.7777 | 0 | 94.6863 | 0 | 45.451 | 122.2588 | 416.3271 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5399 | 19.8419 | 16.496 | 19.1538 | 20 |  | 58.5855 | 0 | 58.5855 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8341 | 0 | 37.2342 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 13 | 421 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1851.1861 | 0 | 1103.4369 | 0 | 2540.9424 | 0 | 1055.5009 | 0 | 6551.0663 | 0 | 136.9101 | 0 | 61.2822 | 0 | 123.5659 | 0 | 58.62 | 157.1898 | 537.5679 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5493 | 19.8513 | 16.5229 | 19.1807 | 20 |  | 55.1039 | 0 | 55.1039 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8340 | 0 | 37.0651 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 14 | 422 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1691.5731 | 0 | 998.2684 | 0 | 2341.9176 | 0 | 964.4934 | 0 | 5996.2525 | 0 | 125.1054 | 0 | 55.4414 | 0 | 113.8873 | 0 | 53.5656 | 144.0907 | 492.0904 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5527 | 19.8548 | 16.544 | 19.2018 | 20 |  | 53.8339 | 0 | 53.8339 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8339 | 0 | 36.8812 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 15 | 423 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 964.1132 | 0 | 560.7483 | 0 | 1334.2783 | 0 | 549.7137 | 0 | 3408.8534 | 0 | 71.3039 | 0 | 31.1426 | 0 | 64.8859 | 0 | 30.5298 | 82.9613 | 280.8234 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5468 | 19.8489 | 16.5441 | 19.2019 | 20 |  | 56.0091 | 0 | 56.0091 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8338 | 0 | 35.8053 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 16 | 424 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 554.3924 | 0 | 320.477 | 0 | 780.3657 | 0 | 316.1009 | 0 | 1971.3361 | 0 | 41.0018 | 0 | 17.7985 | 0 | 37.9491 | 0 | 17.5555 | 48.0302 | 162.3351 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5451 | 19.8472 | 16.5513 | 19.2091 | 20 |  | 56.63 | 0 | 56.63 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8337 | 0 | 35.7748 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 17 | 425 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5419 | 19.844 | 16.557 | 19.2148 | 20 |  | 57.8285 | 0 | 57.8285 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8336 | 0 | 35.635 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 18 | 426 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5672 | 19.8702 | 16.5899 | 19.2468 | 20 |  | 48.1128 | 0 | 48.1128 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8335 | 0 | 35.5428 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 19 | 427 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5681 | 19.8712 | 16.5938 | 19.2506 | 20 |  | 47.7744 | 0 | 47.7744 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8334 | 0 | 34.711 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 20 | 428 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.569 | 19.8721 | 16.5976 | 19.2545 | 20 |  | 47.4361 | 0 | 47.4361 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8333 | 0 | 34.0172 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 21 | 429 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5699 | 19.873 | 16.6015 | 19.2583 | 20 |  | 47.0977 | 0 | 47.0977 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8332 | 0 | 34.0066 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 22 | 430 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5708 | 19.8739 | 16.6053 | 19.2622 | 20 |  | 46.7593 | 0 | 46.7593 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8331 | 0 | 33.8118 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 23 | 431 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5718 | 19.8748 | 16.6092 | 19.266 | 20 |  | 46.421 | 0 | 46.421 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8330 | 0 | 33.6389 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 18 | 24 | 432 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5727 | 19.8757 | 16.613 | 19.2699 | 20 |  | 46.0826 | 0 | 46.0826 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8329 | 0 | 33.3466 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 1 | 433 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5249 | 19.8279 | 16.566 | 19.2228 | 19.8279 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8328 | 0 | 33.0107 | 19.8279 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 2 | 434 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3554 | 19.6585 | 16.4045 | 19.0613 | 19.6585 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8327 | 0 | 32.6919 | 19.6585 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 3 | 435 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1876 | 19.4906 | 16.2416 | 18.8985 | 19.4906 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8326 | 0 | 32.4237 | 19.4906 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 4 | 436 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0204 | 19.3235 | 16.0765 | 18.7333 | 19.3235 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8325 | 0 | 32.0466 | 19.3235 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 5 | 437 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8558 | 19.1589 | 15.9197 | 18.5765 | 19.1589 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8324 | 0 | 31.9458 | 19.1589 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 6 | 438 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.691 | 18.994 | 15.7538 | 18.4106 | 18.994 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8323 | 0 | 31.5595 | 18.994 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 7 | 439 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5268 | 18.8298 | 15.5915 | 18.2484 | 18.8298 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8322 | 0 | 31.3942 | 18.8298 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 8 | 440 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.3864 | 18.6885 | 15.4505 | 18.1083 | 20 |  | 486.133 | 0 | 486.133 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8321 | 0 | 31.0976 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 9 | 441 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5436 | 19.8457 | 16.5646 | 19.2223 | 20 |  | 57.205 | 0 | 57.205 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8320 | 0 | 31.0906 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 10 | 442 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 587.416 | 0 | 382.7706 | 0 | 767.1226 | 0 | 328.0458 | 0 | 2065.355 | 0 | 43.4441 | 0 | 21.2582 | 0 | 37.3051 | 0 | 18.2189 | 48.0302 | 168.2565 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5496 | 19.8517 | 16.5705 | 19.2283 | 20 |  | 54.9714 | 0 | 54.9714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8319 | 0 | 30.8088 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 11 | 443 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2433.3664 | 0 | 2135.3237 | 0 | 3406.064 | 0 | 1387.4458 | 0 | 9362.1999 | 0 | 179.967 | 0 | 118.5907 | 0 | 165.6367 | 0 | 77.0554 | 205.2201 | 746.4698 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5717 | 19.8738 | 16.5952 | 19.253 | 20 |  | 46.7846 | 0 | 46.7846 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8318 | 0 | 30.5045 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 12 | 444 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4935.7798 | 0 | 6450.6162 | 0 | 9450.9454 | 0 | 2814.2604 | 0 | 23651.6018 | 0 | 365.0405 | 0 | 358.2517 | 0 | 459.5988 | 0 | 156.2972 | 449.7376 | 1788.9258 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6139 | 19.916 | 16.6397 | 19.2975 | 20 |  | 31.1411 | 0 | 31.1411 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8317 | 0 | 30.5012 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 13 | 445 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6912.1826 | 0 | 11083.9231 | 0 | 20003.9328 | 0 | 3941.1568 | 0 | 41941.1954 | 0 | 511.2113 | 0 | 615.5744 | 0 | 972.7899 | 0 | 218.8824 | 668.0568 | 2986.5147 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6707 | 19.9728 | 16.7104 | 19.3682 | 20 |  | 10.0953 | 0 | 10.0953 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8316 | 0 | 30.3969 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 14 | 446 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3350.3289 | 0 | 2034.2845 | 0 | 4783.8451 | 0 | 1910.2752 | 0 | 12078.7338 | 0 | 247.7837 | 0 | 112.9793 | 0 | 232.6381 | 0 | 106.0921 | 279.4486 | 978.9417 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5813 | 19.8834 | 16.6106 | 19.2684 | 20 |  | 43.2122 | 0 | 43.2122 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8315 | 0 | 29.818 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 15 | 447 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1430.5384 | 0 | 838.9009 | 0 | 2010.0053 | 0 | 815.6578 | 0 | 5095.1024 | 0 | 105.7998 | 0 | 46.5905 | 0 | 97.7464 | 0 | 45.2997 | 122.2588 | 417.6952 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.561 | 19.8631 | 16.5905 | 19.2483 | 20 |  | 50.7571 | 0 | 50.7571 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8314 | 0 | 29.5117 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 16 | 448 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1592.0561 | 0 | 940.8674 | 0 | 2434.279 | 0 | 907.7513 | 0 | 5874.9537 | 0 | 117.7453 | 0 | 52.2535 | 0 | 118.3788 | 0 | 50.4143 | 135.3579 | 474.1499 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5632 | 19.8653 | 16.5928 | 19.2506 | 20 |  | 49.9208 | 0 | 49.9208 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8313 | 0 | 29.4569 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 17 | 449 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 401.638 | 0 | 230.3749 | 0 | 737.4537 | 0 | 229.0041 | 0 | 1598.4707 | 0 | 29.7044 | 0 | 12.7945 | 0 | 35.8623 | 0 | 12.7183 | 34.9311 | 126.0106 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5533 | 19.8554 | 16.5918 | 19.2496 | 20 |  | 53.6102 | 0 | 53.6102 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8312 | 0 | 29.2599 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 18 | 450 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5763 | 19.8794 | 16.6284 | 19.2853 | 20 |  | 44.7291 | 0 | 44.7291 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8311 | 0 | 28.8753 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 19 | 451 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8310 | 0 | 28.7733 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 20 | 452 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.58 | 19.883 | 16.6438 | 19.3007 | 20 |  | 43.3757 | 0 | 43.3757 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8309 | 0 | 28.5497 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 21 | 453 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5809 | 19.8839 | 16.6477 | 19.3045 | 20 |  | 43.0373 | 0 | 43.0373 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8308 | 0 | 28.5062 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 22 | 454 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5809 | 19.8839 | 16.6477 | 19.3045 | 20 |  | 43.0373 | 0 | 43.0373 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8307 | 0 | 28.4859 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 23 | 455 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5781 | 19.8812 | 16.6361 | 19.293 | 20 |  | 44.0524 | 0 | 44.0524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8306 | 0 | 28.3844 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 19 | 24 | 456 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5763 | 19.8794 | 16.6284 | 19.2853 | 20 |  | 44.7291 | 0 | 44.7291 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8305 | 0 | 28.2664 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 1 | 457 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5304 | 19.8334 | 16.5891 | 19.2459 | 19.8334 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8304 | 0 | 28.2601 | 19.8334 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 2 | 458 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3654 | 19.6685 | 16.429 | 19.0858 | 19.6685 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8303 | 0 | 28.2057 | 19.6685 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 3 | 459 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.202 | 19.5051 | 16.2705 | 18.9273 | 19.5051 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8302 | 0 | 28.1064 | 19.5051 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 4 | 460 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0375 | 19.3405 | 16.1019 | 18.7587 | 19.3405 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8301 | 0 | 27.9783 | 19.3405 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 5 | 461 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.869 | 19.1721 | 15.9207 | 18.5775 | 19.1721 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8300 | 0 | 27.6045 | 19.1721 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 6 | 462 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7041 | 19.0071 | 15.7665 | 18.4234 | 19.0071 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8299 | 0 | 27.2715 | 19.0071 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 7 | 463 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5388 | 18.8419 | 15.6003 | 18.2571 | 18.8419 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8298 | 0 | 27.1777 | 18.8419 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 8 | 464 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.4294 | 18.7324 | 15.5155 | 18.1723 | 20 |  | 470.0047 | 0 | 470.0047 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8297 | 0 | 27.0976 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 9 | 465 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5772 | 19.8803 | 16.6323 | 19.2891 | 20 |  | 44.3908 | 0 | 44.3908 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8296 | 0 | 26.5847 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 10 | 466 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 417.9945 | 0 | 262.3195 | 0 | 549.0308 | 0 | 234.7829 | 0 | 1464.1277 | 0 | 30.914 | 0 | 14.5686 | 0 | 26.6993 | 0 | 13.0393 | 34.9311 | 120.1523 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5842 | 19.8873 | 16.648 | 19.3049 | 20 |  | 41.7914 | 0 | 41.7914 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8295 | 0 | 26.2145 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 11 | 467 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1130.3811 | 0 | 692.9453 | 0 | 1517.3282 | 0 | 644.5155 | 0 | 3985.1702 | 0 | 83.6007 | 0 | 38.4845 | 0 | 73.7876 | 0 | 35.7948 | 96.0605 | 327.7281 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5943 | 19.8974 | 16.6668 | 19.3237 | 20 |  | 38.0477 | 0 | 38.0477 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8294 | 0 | 26.1501 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 12 | 468 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1858.0313 | 0 | 1125.6229 | 0 | 2529.233 | 0 | 1059.4038 | 0 | 6572.2911 | 0 | 137.4163 | 0 | 62.5144 | 0 | 122.9964 | 0 | 58.8367 | 157.1898 | 538.9537 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6028 | 19.9058 | 16.6781 | 19.335 | 20 |  | 34.9109 | 0 | 34.9109 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8293 | 0 | 25.9515 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 13 | 469 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3028.9644 | 0 | 1846.118 | 0 | 4217.7347 | 0 | 1727.0411 | 0 | 10819.8582 | 0 | 224.0162 | 0 | 102.5289 | 0 | 205.1081 | 0 | 95.9157 | 253.2503 | 880.8193 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6161 | 19.9191 | 16.6942 | 19.351 | 20 |  | 29.9831 | 0 | 29.9831 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8292 | 0 | 25.9246 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 14 | 470 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2431.8988 | 0 | 1451.8629 | 0 | 3408.7915 | 0 | 1386.609 | 0 | 8679.1622 | 0 | 179.8584 | 0 | 80.633 | 0 | 165.7693 | 0 | 77.0089 | 205.2201 | 708.4897 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6089 | 19.912 | 16.6842 | 19.341 | 20 |  | 32.6345 | 0 | 32.6345 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8291 | 0 | 25.6701 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 15 | 471 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3355.2214 | 0 | 2030.7839 | 0 | 4992.6542 | 0 | 1913.0648 | 0 | 12291.7244 | 0 | 248.1455 | 0 | 112.7848 | 0 | 242.7924 | 0 | 106.247 | 279.4486 | 989.4184 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.624 | 19.927 | 16.7138 | 19.3706 | 20 |  | 27.0492 | 0 | 27.0492 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8290 | 0 | 25.6271 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 16 | 472 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2447.3392 | 0 | 1467.9153 | 0 | 3945.2721 | 0 | 1395.4127 | 0 | 9255.9393 | 0 | 181.0004 | 0 | 81.5245 | 0 | 191.8583 | 0 | 77.4979 | 205.2201 | 737.1011 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6078 | 19.9109 | 16.6742 | 19.3311 | 20 |  | 33.0442 | 0 | 33.0442 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8289 | 0 | 25.4531 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 17 | 473 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8288 | 0 | 25.4244 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 18 | 474 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.58 | 19.883 | 16.6438 | 19.3007 | 20 |  | 43.3757 | 0 | 43.3757 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8287 | 0 | 24.9933 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 19 | 475 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8286 | 0 | 24.9743 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 20 | 476 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.58 | 19.883 | 16.6438 | 19.3007 | 20 |  | 43.3757 | 0 | 43.3757 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8285 | 0 | 24.8289 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 21 | 477 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8284 | 0 | 24.3452 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 22 | 478 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5781 | 19.8812 | 16.6361 | 19.293 | 20 |  | 44.0524 | 0 | 44.0524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8283 | 0 | 23.8986 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 23 | 479 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5763 | 19.8794 | 16.6284 | 19.2853 | 20 |  | 44.7291 | 0 | 44.7291 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8282 | 0 | 23.6987 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 20 | 24 | 480 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5781 | 19.8812 | 16.6361 | 19.293 | 20 |  | 44.0524 | 0 | 44.0524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8281 | 0 | 23.4823 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 1 | 481 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5304 | 19.8334 | 16.5891 | 19.2459 | 19.8334 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8280 | 0 | 23.44 | 19.8334 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 2 | 482 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3663 | 19.6694 | 16.4328 | 19.0897 | 19.6694 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8279 | 0 | 23.1745 | 19.6694 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 3 | 483 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2038 | 19.5069 | 16.2752 | 18.932 | 19.5069 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8278 | 0 | 23.0286 | 19.5069 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 4 | 484 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0429 | 19.346 | 16.119 | 18.7759 | 19.346 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8277 | 0 | 22.6531 | 19.346 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 5 | 485 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8817 | 19.1848 | 15.9567 | 18.6135 | 19.1848 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8276 | 0 | 22.6092 | 19.1848 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 6 | 486 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7203 | 19.0233 | 15.7941 | 18.4509 | 19.0233 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8275 | 0 | 22.3759 | 19.0233 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 7 | 487 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5595 | 18.8625 | 15.6351 | 18.2919 | 18.8625 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8274 | 0 | 22.1638 | 18.8625 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 8 | 488 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.448 | 18.751 | 15.5276 | 18.1845 | 20 |  | 463.1053 | 0 | 463.1053 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8273 | 0 | 22.1343 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 9 | 489 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5699 | 19.873 | 16.6015 | 19.2583 | 20 |  | 47.0977 | 0 | 47.0977 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8272 | 0 | 22.0547 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 10 | 490 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3377.9507 | 0 | 8043.4457 | 0 | 2330.9602 | 0 | 996.7922 | 0 | 14749.1488 | 0 | 249.8265 | 0 | 446.7136 | 0 | 113.3544 | 0 | 55.3594 | 170.289 | 1035.543 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6052 | 19.9082 | 16.6126 | 19.2695 | 20 |  | 34.0199 | 0 | 34.0199 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8271 | 0 | 21.8506 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 11 | 491 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4971.1856 | 0 | 21817.3541 | 0 | 10486.3379 | 0 | 2834.4479 | 0 | 40109.3255 | 0 | 367.659 | 0 | 1211.6833 | 0 | 509.9499 | 0 | 157.4184 | 558.8972 | 2805.6078 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6793 | 19.9823 | 16.6886 | 19.3454 | 20 |  | 6.5513 | 0 | 6.5513 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8270 | 0 | 21.8469 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 12 | 492 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6805.4497 | 0 | 33958.1844 | 0 | 32445.9063 | 0 | 3880.3002 | 0 | 77089.8406 | 0 | 503.3176 | 0 | 1885.9558 | 0 | 1577.8422 | 0 | 215.5025 | 956.2381 | 5138.8562 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7917 | 20.0947 | 16.82 | 19.4768 | 20.0947 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8269 | 0 | 21.6276 | 20.0947 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 13 | 493 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7387.0966 | 0 | 34896.0679 | 0 | 55820.391 | 0 | 4211.941 | 0 | 102315.4965 | 0 | 546.335 | 0 | 1938.0436 | 0 | 2714.5417 | 0 | 233.9211 | 1139.6263 | 6572.4677 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9629 | 20.266 | 17.0049 | 19.6618 | 20.266 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8268 | 0 | 21.4085 | 20.266 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 14 | 494 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7646.971 | 0 | 14511.7344 | 0 | 35999.9329 | 0 | 4360.115 | 0 | 62518.7533 | 0 | 565.5548 | 0 | 805.9468 | 0 | 1750.6742 | 0 | 242.1503 | 812.1475 | 4176.4736 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0241 | 20.3272 | 17.0805 | 19.7373 | 20.3272 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8267 | 0 | 21.363 | 20.3272 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 15 | 495 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6245.0268 | 0 | 7593.198 | 0 | 26084.0379 | 0 | 3560.7609 | 0 | 43483.0235 | 0 | 461.8698 | 0 | 421.7079 | 0 | 1268.465 | 0 | 197.7561 | 606.9274 | 2956.7262 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0338 | 20.3369 | 17.1009 | 19.7577 | 20.3369 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8266 | 0 | 21.2572 | 20.3369 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 16 | 496 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3672.7746 | 0 | 2858.3697 | 0 | 12090.9461 | 0 | 2094.1259 | 0 | 20716.2162 | 0 | 271.6311 | 0 | 158.747 | 0 | 587.9819 | 0 | 116.3027 | 314.3797 | 1449.0423 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.977 | 20.2801 | 17.0418 | 19.6987 | 20.2801 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8265 | 0 | 20.9502 | 20.2801 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 17 | 497 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1057.1692 | 0 | 611.5956 | 0 | 2810.684 | 0 | 602.7719 | 0 | 5082.2207 | 0 | 78.1861 | 0 | 33.9665 | 0 | 136.6834 | 0 | 33.4765 | 82.9613 | 365.2739 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8766 | 20.1796 | 16.9467 | 19.6035 | 20.1796 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8264 | 0 | 20.9099 | 20.1796 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 18 | 498 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7624 | 20.0655 | 16.8357 | 19.4926 | 20.0655 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8263 | 0 | 20.5584 | 20.0655 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 19 | 499 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.643 | 19.9461 | 16.6991 | 19.3559 | 20 |  | 20.0026 | 0 | 20.0026 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8262 | 0 | 20.5171 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 20 | 500 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5763 | 19.8794 | 16.6284 | 19.2853 | 20 |  | 44.7291 | 0 | 44.7291 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8261 | 0 | 20.4048 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 21 | 501 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5763 | 19.8794 | 16.6284 | 19.2853 | 20 |  | 44.7291 | 0 | 44.7291 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8260 | 0 | 20.3359 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 22 | 502 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5772 | 19.8803 | 16.6323 | 19.2891 | 20 |  | 44.3908 | 0 | 44.3908 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8259 | 0 | 20.297 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 23 | 503 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5791 | 19.8821 | 16.64 | 19.2968 | 20 |  | 43.714 | 0 | 43.714 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8258 | 0 | 20.2206 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 21 | 24 | 504 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5818 | 19.8848 | 16.6515 | 19.3084 | 20 |  | 42.6989 | 0 | 42.6989 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8257 | 0 | 20.1574 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 1 | 505 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5358 | 19.8389 | 16.6122 | 19.269 | 19.8389 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8256 | 0 | 20.1501 | 19.8389 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 2 | 506 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3772 | 19.6803 | 16.4612 | 19.118 | 19.6803 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8255 | 0 | 20.0929 | 19.6803 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 3 | 507 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2201 | 19.5232 | 16.3087 | 18.9656 | 19.5232 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8254 | 0 | 20.0909 | 19.5232 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 4 | 508 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0645 | 19.3676 | 16.1578 | 18.8146 | 19.3676 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8253 | 0 | 19.9191 | 19.3676 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 5 | 509 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9113 | 19.2144 | 16.0121 | 18.6689 | 19.2144 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8252 | 0 | 19.8278 | 19.2144 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 6 | 510 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7596 | 19.0627 | 15.8649 | 18.5217 | 19.0627 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8251 | 0 | 19.5624 | 19.0627 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 7 | 511 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6094 | 18.9124 | 15.7191 | 18.3759 | 18.9124 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8250 | 0 | 19.4499 | 18.9124 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 8 | 512 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.4825 | 18.7846 | 15.5942 | 18.252 | 20 |  | 450.4844 | 0 | 450.4844 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8249 | 0 | 19.1452 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 9 | 513 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5612 | 19.8633 | 16.6439 | 19.3017 | 20 |  | 50.6589 | 0 | 50.6589 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8248 | 0 | 19.0854 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 10 | 514 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 756.5336 | 0 | 502.4413 | 0 | 982.7823 | 0 | 420.2687 | 0 | 2662.0259 | 0 | 55.9517 | 0 | 27.9044 | 0 | 47.7926 | 0 | 23.3407 | 61.1294 | 216.1188 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5707 | 19.8728 | 16.6591 | 19.3169 | 20 |  | 47.1573 | 0 | 47.1573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8247 | 0 | 19.0349 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 11 | 515 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2584.5459 | 0 | 2281.0814 | 0 | 3604.973 | 0 | 1473.6446 | 0 | 9944.2449 | 0 | 191.1479 | 0 | 126.6858 | 0 | 175.3096 | 0 | 81.8427 | 218.3192 | 793.3051 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5961 | 19.8982 | 16.6989 | 19.3567 | 20 |  | 37.7393 | 0 | 37.7393 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8246 | 0 | 18.8198 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 12 | 516 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3765.0517 | 0 | 2672.9871 | 0 | 5425.8042 | 0 | 2146.74 | 0 | 14010.583 | 0 | 278.4558 | 0 | 148.4513 | 0 | 263.8565 | 0 | 119.2248 | 314.3797 | 1124.3679 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6096 | 19.9117 | 16.7182 | 19.376 | 20 |  | 32.7185 | 0 | 32.7185 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8245 | 0 | 18.436 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 13 | 517 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3793.5962 | 0 | 2338.8435 | 0 | 5320.5158 | 0 | 2163.0154 | 0 | 13615.9709 | 0 | 280.5669 | 0 | 129.8937 | 0 | 258.7363 | 0 | 120.1287 | 314.3797 | 1103.7052 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6144 | 19.9165 | 16.7435 | 19.4013 | 20 |  | 30.9517 | 0 | 30.9517 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8244 | 0 | 18.2568 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 14 | 518 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3021.6521 | 0 | 1816.8545 | 0 | 4267.2169 | 0 | 1722.8718 | 0 | 10828.5953 | 0 | 223.4754 | 0 | 100.9037 | 0 | 207.5145 | 0 | 95.6842 | 253.2503 | 880.828 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6088 | 19.9109 | 16.7469 | 19.4046 | 20 |  | 33.0268 | 0 | 33.0268 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8243 | 0 | 17.6283 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 15 | 519 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1586.8642 | 0 | 930.313 | 0 | 2228.0886 | 0 | 904.791 | 0 | 5650.0569 | 0 | 117.3613 | 0 | 51.6673 | 0 | 108.3518 | 0 | 50.2499 | 135.3579 | 462.9883 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5954 | 19.8975 | 16.7395 | 19.3973 | 20 |  | 37.9998 | 0 | 37.9998 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8242 | 0 | 17.4617 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 16 | 520 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1120.1078 | 0 | 652.5668 | 0 | 1624.5093 | 0 | 638.658 | 0 | 4035.8419 | 0 | 82.841 | 0 | 36.242 | 0 | 78.9998 | 0 | 35.4695 | 96.0605 | 329.6127 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5966 | 19.8987 | 16.7614 | 19.4191 | 20 |  | 37.5653 | 0 | 37.5653 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8241 | 0 | 17.1929 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 17 | 521 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 554.8773 | 0 | 317.7252 | 0 | 964.6623 | 0 | 316.3774 | 0 | 2153.6422 | 0 | 41.0376 | 0 | 17.6457 | 0 | 46.9115 | 0 | 17.5708 | 48.0302 | 171.1958 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5978 | 19.8999 | 16.7862 | 19.444 | 20 |  | 37.1122 | 0 | 37.1122 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8240 | 0 | 17.0679 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 18 | 522 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6247 | 19.9277 | 16.8324 | 19.4893 | 20 |  | 26.7956 | 0 | 26.7956 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8239 | 0 | 17.0428 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 19 | 523 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6265 | 19.9296 | 16.8401 | 19.497 | 20 |  | 26.1189 | 0 | 26.1189 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8238 | 0 | 16.8499 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 20 | 524 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6265 | 19.9296 | 16.8401 | 19.497 | 20 |  | 26.1189 | 0 | 26.1189 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8237 | 0 | 16.8089 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 21 | 525 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6256 | 19.9286 | 16.8363 | 19.4931 | 20 |  | 26.4573 | 0 | 26.4573 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8236 | 0 | 16.6637 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 22 | 526 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6238 | 19.9268 | 16.8286 | 19.4854 | 20 |  | 27.134 | 0 | 27.134 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8235 | 0 | 16.3354 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 23 | 527 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6247 | 19.9277 | 16.8324 | 19.4893 | 20 |  | 26.7956 | 0 | 26.7956 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8234 | 0 | 16.2107 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 22 | 24 | 528 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6219 | 19.925 | 16.8209 | 19.4777 | 20 |  | 27.8107 | 0 | 27.8107 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8233 | 0 | 16.1752 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 1 | 529 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5751 | 19.8781 | 16.7777 | 19.4345 | 19.8781 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8232 | 0 | 15.487 | 19.8781 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 2 | 530 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4571 | 19.7602 | 16.6721 | 19.3289 | 19.7602 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8231 | 0 | 15.4483 | 19.7602 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 3 | 531 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3394 | 19.6425 | 16.5549 | 19.2118 | 19.6425 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8230 | 0 | 15.3658 | 19.6425 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 4 | 532 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2237 | 19.5268 | 16.4456 | 19.1025 | 19.5268 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8229 | 0 | 14.815 | 19.5268 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 5 | 533 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1064 | 19.4095 | 16.3229 | 18.9798 | 19.4095 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8228 | 0 | 14.7783 | 19.4095 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 6 | 534 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9921 | 19.2951 | 16.2179 | 18.8747 | 19.2951 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8227 | 0 | 14.3779 | 19.2951 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 7 | 535 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8898 | 19.1929 | 16.1542 | 18.811 | 19.1929 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8226 | 0 | 14.1628 | 19.1929 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 8 | 536 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8 | 19.1021 | 16.0415 | 18.6993 | 20 |  | 332.8231 | 0 | 332.8231 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8225 | 0 | 13.7729 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 9 | 537 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5974 | 19.8995 | 16.8064 | 19.4642 | 20 |  | 37.255 | 0 | 37.255 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8224 | 0 | 13.638 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 10 | 538 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1797.8589 | 0 | 3160.1826 | 0 | 1597.6477 | 0 | 683.2046 | 0 | 7238.8939 | 0 | 132.9661 | 0 | 175.5089 | 0 | 77.6935 | 0 | 37.9435 | 109.1596 | 533.2717 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6243 | 19.9263 | 16.8536 | 19.5113 | 20 |  | 27.3008 | 0 | 27.3008 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8223 | 0 | 13.4212 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 11 | 539 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3047.0313 | 0 | 3792.1858 | 0 | 4453.8813 | 0 | 1737.3424 | 0 | 13030.4408 | 0 | 225.3524 | 0 | 210.6089 | 0 | 216.5919 | 0 | 96.4878 | 266.3494 | 1015.3905 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.642 | 19.9441 | 16.874 | 19.5318 | 20 |  | 20.7154 | 0 | 20.7154 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8222 | 0 | 13.0828 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 12 | 540 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3378.4907 | 0 | 2123.162 | 0 | 4655.2242 | 0 | 1926.3324 | 0 | 12083.2093 | 0 | 249.8665 | 0 | 117.9153 | 0 | 226.3832 | 0 | 106.9839 | 279.4486 | 980.5975 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6427 | 19.9448 | 16.8865 | 19.5443 | 20 |  | 20.4505 | 0 | 20.4505 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8221 | 0 | 13.0795 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 13 | 541 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7877.6425 | 0 | 17746.9336 | 0 | 30207.4294 | 0 | 4491.6383 | 0 | 60323.6438 | 0 | 582.6148 | 0 | 985.6219 | 0 | 1468.9852 | 0 | 249.4548 | 847.0785 | 4133.7553 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7949 | 20.0969 | 17.0836 | 19.7414 | 20.0969 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8220 | 0 | 13.0547 | 20.0969 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 14 | 542 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7479.1598 | 0 | 11128.1005 | 0 | 27341.103 | 0 | 4264.4332 | 0 | 50212.7965 | 0 | 553.1438 | 0 | 618.0279 | 0 | 1329.5959 | 0 | 236.8363 | 751.0181 | 3488.6221 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8585 | 20.1606 | 17.1331 | 19.7909 | 20.1606 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8219 | 0 | 12.7041 | 20.1606 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 15 | 543 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5149.8916 | 0 | 3917.9062 | 0 | 11180.4506 | 0 | 2936.3417 | 0 | 23184.5901 | 0 | 380.8758 | 0 | 217.5911 | 0 | 543.7045 | 0 | 163.0773 | 449.7376 | 1754.9863 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8458 | 20.1478 | 17.1255 | 19.7833 | 20.1478 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8218 | 0 | 12.4414 | 20.1478 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 16 | 544 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2770.3645 | 0 | 1657.0564 | 0 | 4424.4256 | 0 | 1579.5938 | 0 | 10431.4404 | 0 | 204.8907 | 0 | 92.0289 | 0 | 215.1595 | 0 | 87.7268 | 231.4184 | 831.2243 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7962 | 20.0983 | 17.0768 | 19.7346 | 20.0983 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8217 | 0 | 12.1309 | 20.0983 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 17 | 545 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 554.8113 | 0 | 317.4952 | 0 | 944.1193 | 0 | 316.3398 | 0 | 2132.7656 | 0 | 41.0327 | 0 | 17.6329 | 0 | 45.9125 | 0 | 17.5688 | 48.0302 | 170.1771 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7195 | 20.0216 | 16.9902 | 19.648 | 20.0216 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8216 | 0 | 12.0516 | 20.0216 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 18 | 546 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6634 | 19.9664 | 16.9263 | 19.5831 | 20 |  | 12.4405 | 0 | 12.4405 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8215 | 0 | 11.4733 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 19 | 547 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6438 | 19.9469 | 16.9133 | 19.5701 | 20 |  | 19.6899 | 0 | 19.6899 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8214 | 0 | 11.4057 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 20 | 548 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6493 | 19.9524 | 16.9363 | 19.5932 | 20 |  | 17.6597 | 0 | 17.6597 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8213 | 0 | 11.1878 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 21 | 549 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6521 | 19.9551 | 16.9479 | 19.6047 | 20 |  | 16.6446 | 0 | 16.6446 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8212 | 0 | 11.1345 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 22 | 550 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6584 | 19.9615 | 16.9748 | 19.6317 | 20 |  | 14.276 | 0 | 14.276 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8211 | 0 | 10.8303 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 23 | 551 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6648 | 19.9679 | 17.0018 | 19.6586 | 20 |  | 11.9075 | 0 | 11.9075 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8210 | 0 | 10.8232 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 23 | 24 | 552 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6712 | 19.9743 | 17.0287 | 19.6856 | 20 |  | 9.5389 | 0 | 9.5389 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8209 | 0 | 10.0319 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 1 | 553 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6262 | 19.9292 | 16.9932 | 19.6501 | 19.9292 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8208 | 0 | 9.8244 | 19.9292 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 2 | 554 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5552 | 19.8583 | 16.9214 | 19.5782 | 19.8583 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8207 | 0 | 9.8099 | 19.8583 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 3 | 555 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4876 | 19.7907 | 16.8647 | 19.5215 | 19.7907 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8206 | 0 | 9.511 | 19.7907 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 4 | 556 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4244 | 19.7274 | 16.8152 | 19.472 | 19.7274 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8205 | 0 | 9.368 | 19.7274 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 5 | 557 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3681 | 19.6712 | 16.7813 | 19.4381 | 19.6712 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8204 | 0 | 9.1759 | 19.6712 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 6 | 558 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.296 | 19.599 | 16.6579 | 19.3148 | 19.599 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8203 | 0 | 9.1497 | 19.599 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 7 | 559 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2291 | 19.5321 | 16.6079 | 19.2647 | 19.5321 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8202 | 0 | 8.901 | 19.5321 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 8 | 560 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.164 | 19.4661 | 16.4925 | 19.1503 | 20 |  | 197.9092 | 0 | 197.9092 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8201 | 0 | 8.8478 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 9 | 561 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6268 | 19.9289 | 16.9387 | 19.5965 | 20 |  | 26.3448 | 0 | 26.3448 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8200 | 0 | 8.8277 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 10 | 562 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 751.452 | 0 | 489.7708 | 0 | 978.3755 | 0 | 418.3843 | 0 | 2637.9826 | 0 | 55.5759 | 0 | 27.2007 | 0 | 47.5783 | 0 | 23.2361 | 61.1294 | 214.7204 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6387 | 19.9408 | 16.9652 | 19.623 | 20 |  | 21.9335 | 0 | 21.9335 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8199 | 0 | 8.4867 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 11 | 563 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2855.8103 | 0 | 2894.6927 | 0 | 4040.6489 | 0 | 1628.3129 | 0 | 11419.4647 | 0 | 211.2101 | 0 | 160.7643 | 0 | 196.4965 | 0 | 90.4326 | 244.5175 | 903.4209 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6643 | 19.9664 | 16.9904 | 19.6482 | 20 |  | 12.4633 | 0 | 12.4633 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8198 | 0 | 8.3771 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 12 | 564 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6521.0207 | 0 | 12869.8462 | 0 | 15640.7338 | 0 | 3718.1258 | 0 | 38749.7264 | 0 | 482.2818 | 0 | 714.7603 | 0 | 760.6078 | 0 | 206.4958 | 641.8585 | 2806.0041 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7516 | 20.0537 | 17.1059 | 19.7637 | 20.0537 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8197 | 0 | 8.33 | 20.0537 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 13 | 565 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8285.064 | 0 | 23175.1479 | 0 | 38369.2061 | 0 | 4723.94 | 0 | 74553.3581 | 0 | 612.7469 | 0 | 1287.0919 | 0 | 1865.8918 | 0 | 262.3562 | 969.3373 | 4997.4242 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.903 | 20.2051 | 17.2395 | 19.8973 | 20.2051 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8196 | 0 | 8.126 | 20.2051 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 14 | 566 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7583.8399 | 0 | 11294.0207 | 0 | 27712.8069 | 0 | 4324.1192 | 0 | 50914.7866 | 0 | 560.8858 | 0 | 627.2427 | 0 | 1347.6719 | 0 | 240.1512 | 764.1172 | 3540.0688 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9905 | 20.2926 | 17.3412 | 19.999 | 20.2926 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8195 | 0 | 8.1158 | 20.2926 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 15 | 567 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5981.1582 | 0 | 6089.8449 | 0 | 19742.563 | 0 | 3410.3095 | 0 | 35223.8756 | 0 | 442.3546 | 0 | 338.2153 | 0 | 960.0795 | 0 | 189.4004 | 545.798 | 2475.8478 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0269 | 20.329 | 17.3581 | 20.0159 | 20.329 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8194 | 0 | 7.9373 | 20.329 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 16 | 568 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3833.5394 | 0 | 2924.161 | 0 | 12086.0402 | 0 | 2185.79 | 0 | 21029.5306 | 0 | 283.521 | 0 | 162.4009 | 0 | 587.7433 | 0 | 121.3935 | 327.4788 | 1482.5375 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0196 | 20.3216 | 17.3414 | 19.9992 | 20.3216 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8193 | 0 | 7.8695 | 20.3216 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 17 | 569 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2180.0797 | 0 | 1368.4449 | 0 | 26690.2651 | 0 | 1243.0279 | 0 | 31481.8176 | 0 | 161.2344 | 0 | 76.0001 | 0 | 1297.9457 | 0 | 69.0348 | 192.1209 | 1796.3359 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0362 | 20.3383 | 17.3403 | 19.9981 | 20.3383 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8192 | 0 | 7.5323 | 20.3383 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 18 | 570 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 152.3312 | 0 | 86.8555 | 0 | 203.1083 | 0 | 86.8555 | 0 | 529.1506 | 0 | 11.2661 | 0 | 4.8237 | 0 | 9.8771 | 0 | 4.8237 | 13.0992 | 43.8899 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9841 | 20.2871 | 17.2553 | 19.9121 | 20.2871 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8191 | 0 | 7.3213 | 20.2871 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 19 | 571 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9218 | 20.2249 | 17.1623 | 19.8191 | 20.2249 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8190 | 0 | 7.0513 | 20.2249 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 20 | 572 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8593 | 20.1623 | 17.0986 | 19.7554 | 20.1623 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8189 | 0 | 6.9744 | 20.1623 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 21 | 573 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7946 | 20.0976 | 17.0269 | 19.6837 | 20.0976 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8188 | 0 | 6.9271 | 20.0976 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 22 | 574 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7204 | 20.0235 | 16.9224 | 19.5792 | 20.0235 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8187 | 0 | 6.891 | 20.0235 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 23 | 575 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6434 | 19.9464 | 16.8358 | 19.4926 | 20 |  | 19.8592 | 0 | 19.8592 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8186 | 0 | 6.4131 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 24 | 24 | 576 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6146 | 19.9177 | 16.7901 | 19.4469 | 20 |  | 30.5177 | 0 | 30.5177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8185 | 0 | 5.7172 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 1 | 577 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5577 | 19.8608 | 16.7045 | 19.3614 | 19.8608 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8184 | 0 | 5.6986 | 19.8608 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 2 | 578 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4226 | 19.7257 | 16.5823 | 19.2392 | 19.7257 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8183 | 0 | 5.5756 | 19.7257 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 3 | 579 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2879 | 19.591 | 16.4486 | 19.1055 | 19.591 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8182 | 0 | 5.444 | 19.591 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 4 | 580 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1572 | 19.4603 | 16.3307 | 18.9875 | 19.4603 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8181 | 0 | 5.114 | 19.4603 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 5 | 581 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0332 | 19.3363 | 16.2282 | 18.885 | 19.3363 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8180 | 0 | 5.11 | 19.3363 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 6 | 582 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9223 | 19.2254 | 16.1591 | 18.8159 | 19.2254 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8179 | 0 | 4.7431 | 19.2254 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 7 | 583 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8162 | 19.1192 | 16.0679 | 18.7248 | 19.1192 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8178 | 0 | 4.6284 | 19.1192 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 8 | 584 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.7321 | 19.0341 | 15.9934 | 18.6512 | 20 |  | 358.0045 | 0 | 358.0045 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8177 | 0 | 4.4676 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 9 | 585 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6075 | 19.9096 | 16.8518 | 19.5096 | 20 |  | 33.5143 | 0 | 33.5143 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8176 | 0 | 4.3999 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 10 | 586 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 749.0548 | 0 | 484.086 | 0 | 976.2715 | 0 | 417.4845 | 0 | 2626.8968 | 0 | 55.3986 | 0 | 26.885 | 0 | 47.476 | 0 | 23.1861 | 61.1294 | 214.0751 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6211 | 19.9231 | 16.8858 | 19.5436 | 20 |  | 28.4913 | 0 | 28.4913 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8175 | 0 | 4.1766 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 11 | 587 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3941.2637 | 0 | 8307.601 | 0 | 6330.4308 | 0 | 2247.2118 | 0 | 20826.5072 | 0 | 291.4881 | 0 | 461.3842 | 0 | 307.8484 | 0 | 124.8047 | 375.509 | 1561.0344 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6797 | 19.9818 | 16.9642 | 19.622 | 20 |  | 6.7627 | 0 | 6.7627 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8174 | 0 | 4.0842 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 12 | 588 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4266.9387 | 0 | 3469.0413 | 0 | 6469.4984 | 0 | 2432.9036 | 0 | 16638.3819 | 0 | 315.5743 | 0 | 192.6622 | 0 | 314.6113 | 0 | 135.1176 | 362.4099 | 1320.3753 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6677 | 19.9698 | 16.9524 | 19.6102 | 20 |  | 11.1915 | 0 | 11.1915 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8173 | 0 | 4.0349 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 13 | 589 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4670.061 | 0 | 3106.2697 | 0 | 6881.0239 | 0 | 2662.7541 | 0 | 17320.1086 | 0 | 345.3885 | 0 | 172.5147 | 0 | 334.6237 | 0 | 147.8829 | 388.6082 | 1389.0181 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6714 | 19.9735 | 16.962 | 19.6198 | 20 |  | 9.8177 | 0 | 9.8177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8172 | 0 | 4.0297 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 14 | 590 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2589.5256 | 0 | 1541.2773 | 0 | 3615.9988 | 0 | 1476.4839 | 0 | 9223.2856 | 0 | 191.5162 | 0 | 85.5988 | 0 | 175.8458 | 0 | 82.0004 | 218.3192 | 753.2804 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6428 | 19.9449 | 16.9161 | 19.5739 | 20 |  | 20.4206 | 0 | 20.4206 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8171 | 0 | 3.3304 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 15 | 591 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2271.7761 | 0 | 1342.4294 | 0 | 3235.8451 | 0 | 1295.3109 | 0 | 8145.3615 | 0 | 168.0161 | 0 | 74.5553 | 0 | 157.3589 | 0 | 71.9384 | 192.1209 | 663.9896 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.638 | 19.9401 | 16.9054 | 19.5632 | 20 |  | 22.2112 | 0 | 22.2112 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8170 | 0 | 2.8861 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 16 | 592 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1432.2648 | 0 | 836.5166 | 0 | 2097.7711 | 0 | 816.6422 | 0 | 5183.1948 | 0 | 105.9275 | 0 | 46.4581 | 0 | 102.0145 | 0 | 45.3543 | 122.2588 | 422.0132 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6285 | 19.9306 | 16.8931 | 19.5509 | 20 |  | 25.7271 | 0 | 25.7271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8169 | 0 | 2.8056 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 17 | 593 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1282.3106 | 0 | 735.4011 | 0 | 2587.1437 | 0 | 731.142 | 0 | 5335.9974 | 0 | 94.8372 | 0 | 40.8424 | 0 | 125.8126 | 0 | 40.6059 | 109.1596 | 411.2576 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6264 | 19.9285 | 16.8822 | 19.54 | 20 |  | 26.5202 | 0 | 26.5202 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8168 | 0 | 2.7629 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 18 | 594 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 311.5811 | 0 | 177.6559 | 0 | 415.4414 | 0 | 177.6559 | 0 | 1082.3343 | 0 | 23.0439 | 0 | 9.8666 | 0 | 20.2029 | 0 | 9.8666 | 26.1983 | 89.1783 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6333 | 19.9364 | 16.8586 | 19.5155 | 20 |  | 23.5939 | 0 | 23.5939 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8167 | 0 | 2.6933 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 19 | 595 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6283 | 19.9314 | 16.8478 | 19.5047 | 20 |  | 25.4422 | 0 | 25.4422 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8166 | 0 | 2.6864 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 20 | 596 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6229 | 19.9259 | 16.8247 | 19.4816 | 20 |  | 27.4724 | 0 | 27.4724 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8165 | 0 | 2.581 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 21 | 597 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6174 | 19.9204 | 16.8016 | 19.4585 | 20 |  | 29.5026 | 0 | 29.5026 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8164 | 0 | 1.7936 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 22 | 598 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6146 | 19.9177 | 16.7901 | 19.4469 | 20 |  | 30.5177 | 0 | 30.5177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8163 | 0 | 1.7644 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 23 | 599 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8162 | 0 | 1.6835 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 25 | 24 | 600 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8161 | 0 | 1.4371 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 1 | 601 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5596 | 19.8626 | 16.7122 | 19.3691 | 19.8626 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8160 | 0 | 1.0611 | 19.8626 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 2 | 602 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4253 | 19.7284 | 16.5879 | 19.2448 | 19.7284 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8159 | 0 | 0.93886 | 19.7284 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 3 | 603 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2924 | 19.5955 | 16.4589 | 19.1158 | 19.5955 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8158 | 0 | 0 | 19.5955 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 4 | 604 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1589 | 19.462 | 16.3235 | 18.9803 | 19.462 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8157 | 0 | 0 | 19.462 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 5 | 605 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0231 | 19.3262 | 16.1798 | 18.8367 | 19.3262 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8156 | 0 | 0 | 19.3262 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 6 | 606 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8904 | 19.1935 | 16.057 | 18.7138 | 19.1935 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8155 | 0 | 0 | 19.1935 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 7 | 607 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7699 | 19.073 | 15.9756 | 18.6325 | 19.073 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8154 | 0 | 0 | 19.073 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 8 | 608 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6728 | 18.9749 | 15.8885 | 18.5463 | 20 |  | 379.9778 | 0 | 379.9778 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8153 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 9 | 609 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5924 | 19.8944 | 16.7838 | 19.4416 | 20 |  | 39.1253 | 0 | 39.1253 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8152 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 10 | 610 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 920.4356 | 0 | 602.9801 | 0 | 1195.6432 | 0 | 511.2948 | 0 | 3230.3537 | 0 | 68.0736 | 0 | 33.4881 | 0 | 58.144 | 0 | 28.3961 | 74.2285 | 262.3303 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6052 | 19.9072 | 16.8082 | 19.466 | 20 |  | 34.3857 | 0 | 34.3857 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8151 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 11 | 611 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2317.4755 | 0 | 1484.2249 | 0 | 3117.8131 | 0 | 1321.3676 | 0 | 8240.8811 | 0 | 171.3959 | 0 | 82.4303 | 0 | 151.619 | 0 | 73.3856 | 192.1209 | 670.9517 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6231 | 19.9252 | 16.8377 | 19.4955 | 20 |  | 27.7197 | 0 | 27.7197 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8150 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 12 | 612 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4844.7115 | 0 | 4794.8529 | 0 | 7978.1478 | 0 | 2762.3355 | 0 | 20380.0477 | 0 | 358.3053 | 0 | 266.2946 | 0 | 387.9768 | 0 | 153.4135 | 423.5393 | 1589.5293 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6617 | 19.9638 | 16.8875 | 19.5453 | 20 |  | 13.4151 | 0 | 13.4151 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8149 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 13 | 613 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2165.9536 | 0 | 1289.1603 | 0 | 2967.5776 | 0 | 1234.9736 | 0 | 7657.665 | 0 | 160.1896 | 0 | 71.5969 | 0 | 144.3131 | 0 | 68.5875 | 183.3881 | 628.0752 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.624 | 19.926 | 16.8474 | 19.5052 | 20 |  | 27.4106 | 0 | 27.4106 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8148 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 14 | 614 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1429.4741 | 0 | 834.8531 | 0 | 1955.7786 | 0 | 815.051 | 0 | 5035.1568 | 0 | 105.7211 | 0 | 46.3657 | 0 | 95.1094 | 0 | 45.266 | 122.2588 | 414.7209 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6104 | 19.9125 | 16.8134 | 19.4712 | 20 |  | 32.4285 | 0 | 32.4285 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8147 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 15 | 615 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2006.3656 | 0 | 1179.9056 | 0 | 2832.7703 | 0 | 1143.9804 | 0 | 7163.0218 | 0 | 148.3868 | 0 | 65.5291 | 0 | 137.7574 | 0 | 63.5339 | 170.289 | 585.4963 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6225 | 19.9246 | 16.8459 | 19.5037 | 20 |  | 27.9478 | 0 | 27.9478 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8146 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 16 | 616 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2279.8958 | 0 | 1346.9586 | 0 | 3485.8143 | 0 | 1299.9406 | 0 | 8412.6093 | 0 | 168.6166 | 0 | 74.8068 | 0 | 169.5149 | 0 | 72.1956 | 192.1209 | 677.2548 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6295 | 19.9316 | 16.8646 | 19.5224 | 20 |  | 25.3596 | 0 | 25.3596 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8145 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 17 | 617 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1761.6421 | 0 | 1022.1995 | 0 | 6387.44 | 0 | 1004.4451 | 0 | 10175.7267 | 0 | 130.2876 | 0 | 56.7705 | 0 | 310.6208 | 0 | 55.7845 | 144.0907 | 697.554 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6335 | 19.9356 | 16.8656 | 19.5234 | 20 |  | 23.8879 | 0 | 23.8879 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8144 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 18 | 618 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6311 | 19.9341 | 16.8594 | 19.5162 | 20 |  | 24.4271 | 0 | 24.4271 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8143 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 19 | 619 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6302 | 19.9332 | 16.8555 | 19.5124 | 20 |  | 24.7654 | 0 | 24.7654 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8142 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 20 | 620 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6183 | 19.9213 | 16.8055 | 19.4623 | 20 |  | 29.1642 | 0 | 29.1642 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8141 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 21 | 621 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8140 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 22 | 622 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6073 | 19.9104 | 16.7593 | 19.4161 | 20 |  | 33.2246 | 0 | 33.2246 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8139 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 23 | 623 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.611 | 19.914 | 16.7747 | 19.4315 | 20 |  | 31.8712 | 0 | 31.8712 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8138 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 26 | 24 | 624 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6073 | 19.9104 | 16.7593 | 19.4161 | 20 |  | 33.2246 | 0 | 33.2246 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8137 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 1 | 625 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5623 | 19.8654 | 16.7238 | 19.3806 | 19.8654 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8136 | 0 | 0 | 19.8654 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 2 | 626 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4308 | 19.7339 | 16.6021 | 19.2589 | 19.7339 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8135 | 0 | 0 | 19.7339 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 3 | 627 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3015 | 19.6045 | 16.4796 | 19.1364 | 19.6045 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8134 | 0 | 0 | 19.6045 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 4 | 628 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1734 | 19.4764 | 16.3553 | 19.0121 | 19.4764 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8133 | 0 | 0 | 19.4764 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 5 | 629 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0447 | 19.3478 | 16.2245 | 18.8813 | 19.3478 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8132 | 0 | 0 | 19.3478 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 6 | 630 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9182 | 19.2212 | 16.1047 | 18.7615 | 19.2212 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8131 | 0 | 0 | 19.2212 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 7 | 631 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7938 | 19.0968 | 15.9869 | 18.6438 | 19.0968 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8130 | 0 | 0 | 19.0968 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 8 | 632 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.7184 | 19.0214 | 15.9144 | 18.5713 | 20 |  | 362.851 | 0 | 362.851 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8129 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 9 | 633 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.611 | 19.914 | 16.7747 | 19.4315 | 20 |  | 31.8712 | 0 | 31.8712 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8128 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 10 | 634 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 306.6679 | 0 | 183.9188 | 0 | 405.1335 | 0 | 173.2479 | 0 | 1068.968 | 0 | 22.6806 | 0 | 10.2144 | 0 | 19.7016 | 0 | 9.6218 | 26.1983 | 88.4166 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6114 | 19.9144 | 16.7662 | 19.4231 | 20 |  | 31.7289 | 0 | 31.7289 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8127 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 11 | 635 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1126.9259 | 0 | 681.7905 | 0 | 1509.0243 | 0 | 642.5455 | 0 | 3960.2862 | 0 | 83.3452 | 0 | 37.865 | 0 | 73.3837 | 0 | 35.6854 | 96.0605 | 326.3398 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6189 | 19.922 | 16.7707 | 19.4275 | 20 |  | 28.938 | 0 | 28.938 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8126 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 12 | 636 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2174.082 | 0 | 1315.4389 | 0 | 2954.9852 | 0 | 1239.6082 | 0 | 7684.1142 | 0 | 160.7908 | 0 | 73.0563 | 0 | 143.7007 | 0 | 68.8449 | 183.3881 | 629.7808 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6307 | 19.9337 | 16.7852 | 19.4421 | 20 |  | 24.5724 | 0 | 24.5724 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8125 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 13 | 637 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3511.6864 | 0 | 2136.6875 | 0 | 4879.0727 | 0 | 2002.2774 | 0 | 12529.7239 | 0 | 259.7174 | 0 | 118.6665 | 0 | 237.269 | 0 | 111.2017 | 292.5477 | 1019.4022 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6539 | 19.957 | 16.8376 | 19.4945 | 20 |  | 15.9535 | 0 | 15.9535 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8124 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 14 | 638 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2269.267 | 0 | 1341.5189 | 0 | 3145.3135 | 0 | 1293.8803 | 0 | 8049.9796 | 0 | 167.8305 | 0 | 74.5047 | 0 | 152.9564 | 0 | 71.859 | 192.1209 | 659.2715 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6409 | 19.9439 | 16.8248 | 19.4816 | 20 |  | 20.7933 | 0 | 20.7933 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8123 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 15 | 639 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5852.9526 | 0 | 5455.9649 | 0 | 17097.3889 | 0 | 3337.2098 | 0 | 31743.5161 | 0 | 432.8728 | 0 | 303.0111 | 0 | 831.4448 | 0 | 185.3406 | 519.5997 | 2272.2691 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.721 | 20.024 | 16.942 | 19.5989 | 20.024 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8122 | 0 | 0 | 20.024 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 16 | 640 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3963.3469 | 0 | 2622.0463 | 0 | 8729.1567 | 0 | 2259.8031 | 0 | 17574.353 | 0 | 293.1213 | 0 | 145.6221 | 0 | 424.4983 | 0 | 125.504 | 340.578 | 1329.3237 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6995 | 20.0025 | 16.9057 | 19.5626 | 20.0025 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8121 | 0 | 0 | 20.0025 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 17 | 641 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1679.0736 | 0 | 968.8199 | 0 | 5176.2913 | 0 | 957.3665 | 0 | 8781.5513 | 0 | 124.181 | 0 | 53.8059 | 0 | 251.7227 | 0 | 53.1698 | 135.3579 | 618.2373 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6516 | 19.9547 | 16.856 | 19.5128 | 20 |  | 16.8091 | 0 | 16.8091 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8120 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 18 | 642 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 309.624 | 0 | 176.54 | 0 | 412.832 | 0 | 176.54 | 0 | 1075.536 | 0 | 22.8992 | 0 | 9.8046 | 0 | 20.076 | 0 | 9.8046 | 26.1983 | 88.7827 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6223 | 19.9254 | 16.8124 | 19.4693 | 20 |  | 27.6615 | 0 | 27.6615 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8119 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 19 | 643 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6174 | 19.9204 | 16.8016 | 19.4585 | 20 |  | 29.5026 | 0 | 29.5026 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8118 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 20 | 644 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8117 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 21 | 645 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6137 | 19.9168 | 16.7862 | 19.4431 | 20 |  | 30.8561 | 0 | 30.8561 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8116 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 22 | 646 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6219 | 19.925 | 16.8209 | 19.4777 | 20 |  | 27.8107 | 0 | 27.8107 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8115 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 23 | 647 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6192 | 19.9223 | 16.8093 | 19.4662 | 20 |  | 28.8258 | 0 | 28.8258 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8114 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 27 | 24 | 648 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6201 | 19.9232 | 16.8132 | 19.47 | 20 |  | 28.4875 | 0 | 28.4875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8113 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 1 | 649 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.576 | 19.8791 | 16.7815 | 19.4384 | 19.8791 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8112 | 0 | 0 | 19.8791 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 2 | 650 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4489 | 19.752 | 16.6345 | 19.2913 | 19.752 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8111 | 0 | 0 | 19.752 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 3 | 651 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3121 | 19.6152 | 16.4662 | 19.123 | 19.6152 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8110 | 0 | 0 | 19.6152 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 4 | 652 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1711 | 19.4742 | 16.3116 | 18.9685 | 19.4742 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8109 | 0 | 0 | 19.4742 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 5 | 653 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0315 | 19.3346 | 16.1761 | 18.833 | 19.3346 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8108 | 0 | 0 | 19.3346 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 6 | 654 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8924 | 19.1954 | 16.0381 | 18.695 | 19.1954 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8107 | 0 | 0 | 19.1954 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 7 | 655 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7509 | 19.0539 | 15.889 | 18.5458 | 19.0539 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8106 | 0 | 0 | 19.0539 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 8 | 656 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.6549 | 18.9579 | 15.7847 | 18.4415 | 20 |  | 386.3879 | 0 | 386.3879 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8105 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 9 | 657 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5918 | 19.8949 | 16.6939 | 19.3507 | 20 |  | 38.9769 | 0 | 38.9769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8104 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 10 | 658 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4927.7979 | 0 | 10928.9276 | 0 | 3121.2379 | 0 | 1334.7399 | 0 | 20312.7033 | 0 | 364.4502 | 0 | 606.9663 | 0 | 151.7856 | 0 | 74.1282 | 231.4184 | 1428.7487 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6614 | 19.9645 | 16.7978 | 19.4547 | 20 |  | 13.175 | 0 | 13.175 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8103 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 11 | 659 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5631.498 | 0 | 22778.7812 | 0 | 10601.3308 | 0 | 3210.9419 | 0 | 42222.5519 | 0 | 416.4944 | 0 | 1265.0786 | 0 | 515.542 | 0 | 178.328 | 641.8585 | 3017.3015 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7449 | 20.0479 | 16.9449 | 19.6018 | 20.0479 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8102 | 0 | 0 | 20.0479 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 12 | 660 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7508.9014 | 0 | 32864.9208 | 0 | 31032.646 | 0 | 4281.3911 | 0 | 75687.8594 | 0 | 555.3435 | 0 | 1825.2385 | 0 | 1509.1154 | 0 | 237.7782 | 1030.4667 | 5157.9423 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8966 | 20.1996 | 17.1202 | 19.7771 | 20.1996 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8101 | 0 | 0 | 20.1996 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 13 | 661 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7579.8004 | 0 | 11246.1317 | 0 | 20209.6854 | 0 | 4321.816 | 0 | 43357.4336 | 0 | 560.587 | 0 | 624.5831 | 0 | 982.7956 | 0 | 240.0233 | 729.1862 | 3137.1751 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9569 | 20.2599 | 17.1863 | 19.8431 | 20.2599 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8100 | 0 | 0 | 20.2599 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 14 | 662 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6782.5905 | 0 | 6520.2988 | 0 | 15694.2904 | 0 | 3867.2665 | 0 | 32864.4462 | 0 | 501.627 | 0 | 362.1217 | 0 | 763.2123 | 0 | 214.7787 | 620.0266 | 2461.7661 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.992 | 20.295 | 17.2377 | 19.8945 | 20.295 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8099 | 0 | 0 | 20.295 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 15 | 663 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6841.2031 | 0 | 21515.4833 | 0 | 86379.43 | 0 | 3900.686 | 0 | 118636.8024 | 0 | 505.9618 | 0 | 1194.9181 | 0 | 4200.6257 | 0 | 216.6347 | 1078.4969 | 7196.6373 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2663 | 20.5693 | 17.4926 | 20.1495 | 20.5693 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8098 | 0 | 0 | 20.5693 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 16 | 664 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1852.1873 | 0 | 1084.9204 | 0 | 2744.7274 | 0 | 1056.0717 | 0 | 6737.9068 | 0 | 136.9841 | 0 | 60.2539 | 0 | 133.4759 | 0 | 58.6517 | 157.1898 | 546.5554 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2109 | 20.514 | 17.4105 | 20.0673 | 20.514 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8097 | 0 | 0 | 20.514 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 17 | 665 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1685.0353 | 0 | 969.7423 | 0 | 4916.254 | 0 | 960.7657 | 0 | 8531.7972 | 0 | 124.6219 | 0 | 53.8571 | 0 | 239.0771 | 0 | 53.3586 | 135.3579 | 606.2726 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.162 | 20.465 | 17.366 | 20.0229 | 20.465 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8096 | 0 | 0 | 20.465 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 18 | 666 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0843 | 20.3874 | 17.2755 | 19.9323 | 20.3874 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8095 | 0 | 0 | 20.3874 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 19 | 667 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9965 | 20.2995 | 17.1547 | 19.8115 | 20.2995 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8094 | 0 | 0 | 20.2995 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 20 | 668 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9076 | 20.2107 | 17.0625 | 19.7194 | 20.2107 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8093 | 0 | 0 | 20.2107 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 21 | 669 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8178 | 20.1209 | 16.9695 | 19.6263 | 20.1209 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8092 | 0 | 0 | 20.1209 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 22 | 670 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7362 | 20.0392 | 16.9139 | 19.5708 | 20.0392 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8091 | 0 | 0 | 20.0392 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 23 | 671 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6535 | 19.9565 | 16.8278 | 19.4846 | 20 |  | 16.113 | 0 | 16.113 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8090 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 28 | 24 | 672 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8089 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 1 | 673 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5678 | 19.8708 | 16.7469 | 19.4037 | 19.8708 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8088 | 0 | 0 | 19.8708 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 2 | 674 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4371 | 19.7402 | 16.6112 | 19.268 | 19.7402 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8087 | 0 | 0 | 19.7402 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 3 | 675 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3041 | 19.6071 | 16.4703 | 19.1271 | 19.6071 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8086 | 0 | 0 | 19.6071 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 4 | 676 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1751 | 19.4781 | 16.3539 | 19.0108 | 19.4781 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8085 | 0 | 0 | 19.4781 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 5 | 677 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0464 | 19.3494 | 16.2261 | 18.8829 | 19.3494 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8084 | 0 | 0 | 19.3494 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 6 | 678 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9134 | 19.2165 | 16.0793 | 18.7362 | 19.2165 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8083 | 0 | 0 | 19.2165 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 7 | 679 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7654 | 19.0684 | 15.8823 | 18.5391 | 19.0684 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8082 | 0 | 0 | 19.0684 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 8 | 680 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6304 | 18.9325 | 15.714 | 18.3718 | 20 |  | 395.6793 | 0 | 395.6793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8081 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 9 | 681 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 158.0924 | 0 | 90.1404 | 0 | 210.7898 | 0 | 90.1404 | 0 | 549.1629 | 0 | 11.6922 | 0 | 5.0062 | 0 | 10.2507 | 0 | 5.0062 | 13.0992 | 45.0544 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5469 | 19.849 | 16.5737 | 19.2315 | 20 |  | 55.9874 | 0 | 55.9874 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8080 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 10 | 682 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6400.6364 | 0 | 15039.2369 | 0 | 3576.8136 | 0 | 1529.5585 | 0 | 26546.2454 | 0 | 473.3784 | 0 | 835.243 | 0 | 173.9402 | 0 | 84.948 | 279.4486 | 1846.9582 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6328 | 19.9349 | 16.6967 | 19.3545 | 20 |  | 24.136 | 0 | 24.136 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8079 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 11 | 683 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5749.9178 | 0 | 23827.0893 | 0 | 10781.4511 | 0 | 3278.4619 | 0 | 43636.92 | 0 | 425.2525 | 0 | 1323.2991 | 0 | 524.3012 | 0 | 182.0779 | 668.0568 | 3122.9876 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7009 | 20.0029 | 16.8287 | 19.4865 | 20.0029 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8078 | 0 | 0 | 20.0029 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 12 | 684 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6826.3889 | 0 | 43460.7001 | 0 | 37972.2933 | 0 | 3892.2393 | 0 | 92151.6216 | 0 | 504.8662 | 0 | 2413.7026 | 0 | 1846.59 | 0 | 216.1656 | 1187.6565 | 6168.9809 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8656 | 20.1677 | 17.0706 | 19.7284 | 20.1677 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8077 | 0 | 0 | 20.1677 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 13 | 685 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8064.2302 | 0 | 35688.1253 | 0 | 55956.3221 | 0 | 4598.026 | 0 | 104306.7036 | 0 | 596.4145 | 0 | 1982.0325 | 0 | 2721.1521 | 0 | 255.3633 | 1261.885 | 6816.8474 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0659 | 20.368 | 17.2744 | 19.9322 | 20.368 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8076 | 0 | 0 | 20.368 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 14 | 686 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7889.0614 | 0 | 30142.6662 | 0 | 74705.9352 | 0 | 4498.149 | 0 | 117235.8119 | 0 | 583.4594 | 0 | 1674.0511 | 0 | 3632.9445 | 0 | 249.8164 | 1261.885 | 7402.1563 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3026 | 20.6047 | 17.5105 | 20.1683 | 20.6047 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8075 | 0 | 0 | 20.6047 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 15 | 687 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7281.8754 | 0 | 10067.1304 | 0 | 35655.5271 | 0 | 4151.9465 | 0 | 57156.4794 | 0 | 538.5531 | 0 | 559.1042 | 0 | 1733.9258 | 0 | 230.5891 | 737.9189 | 3800.0911 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3662 | 20.6683 | 17.5726 | 20.2304 | 20.6683 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8074 | 0 | 0 | 20.6683 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 16 | 688 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4451.9136 | 0 | 3458.4675 | 0 | 14740.6107 | 0 | 2538.3718 | 0 | 25189.3635 | 0 | 329.2547 | 0 | 192.075 | 0 | 716.8349 | 0 | 140.9751 | 388.6082 | 1767.7478 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3349 | 20.637 | 17.5321 | 20.1899 | 20.637 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8073 | 0 | 0 | 20.637 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 17 | 689 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2056.3145 | 0 | 1186.1888 | 0 | 7668.021 | 0 | 1172.46 | 0 | 12082.9843 | 0 | 152.0809 | 0 | 65.8781 | 0 | 372.8953 | 0 | 65.1156 | 170.289 | 826.2589 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2543 | 20.5564 | 17.4118 | 20.0696 | 20.5564 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8072 | 0 | 0 | 20.5564 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 18 | 690 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 151.2231 | 0 | 86.2237 | 0 | 201.6307 | 0 | 86.2237 | 0 | 525.3012 | 0 | 11.1842 | 0 | 4.7887 | 0 | 9.8053 | 0 | 4.7887 | 13.0992 | 43.6659 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.149 | 20.452 | 17.2493 | 19.9062 | 20.452 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8071 | 0 | 0 | 20.452 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 19 | 691 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0258 | 20.3289 | 17.0705 | 19.7274 | 20.3289 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8070 | 0 | 0 | 20.3289 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 20 | 692 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8984 | 20.2014 | 16.9291 | 19.5859 | 20.2014 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8069 | 0 | 0 | 20.2014 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 21 | 693 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7785 | 20.0816 | 16.8335 | 19.4904 | 20.0816 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8068 | 0 | 0 | 20.0816 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 22 | 694 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6571 | 19.9602 | 16.7068 | 19.3637 | 20 |  | 14.7723 | 0 | 14.7723 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8067 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 23 | 695 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5772 | 19.8803 | 16.6323 | 19.2891 | 20 |  | 44.3908 | 0 | 44.3908 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8066 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 29 | 24 | 696 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5854 | 19.8885 | 16.6669 | 19.3238 | 20 |  | 41.3454 | 0 | 41.3454 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8065 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 1 | 697 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5486 | 19.8517 | 16.6661 | 19.3229 | 19.8517 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8064 | 0 | 0 | 19.8517 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 2 | 698 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3963 | 19.6993 | 16.5004 | 19.1573 | 19.6993 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8063 | 0 | 0 | 19.6993 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 3 | 699 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2344 | 19.5375 | 16.3078 | 18.9646 | 19.5375 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8062 | 0 | 0 | 19.5375 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 4 | 700 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0604 | 19.3635 | 16.0945 | 18.7514 | 19.3635 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8061 | 0 | 0 | 19.3635 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 5 | 701 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8836 | 19.1866 | 15.9081 | 18.5649 | 19.1866 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8060 | 0 | 0 | 19.1866 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 6 | 702 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7029 | 19.006 | 15.715 | 18.3719 | 19.006 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8059 | 0 | 0 | 19.006 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 7 | 703 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5231 | 18.8262 | 15.5376 | 18.1944 | 18.8262 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8058 | 0 | 0 | 18.8262 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 8 | 704 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.371 | 18.673 | 15.3941 | 18.0519 | 20 |  | 491.844 | 0 | 491.844 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8057 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 9 | 705 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 158.0924 | 0 | 90.1404 | 0 | 210.7899 | 0 | 90.1404 | 0 | 549.1631 | 0 | 11.6922 | 0 | 5.0062 | 0 | 10.2507 | 0 | 5.0062 | 13.0992 | 45.0544 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5343 | 19.8363 | 16.517 | 19.1748 | 20 |  | 60.6632 | 0 | 60.6632 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8056 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 10 | 706 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3710.4808 | 0 | 7580.9312 | 0 | 2510.8939 | 0 | 1073.7375 | 0 | 14876.0435 | 0 | 274.4198 | 0 | 421.0267 | 0 | 122.1046 | 0 | 59.6328 | 183.3881 | 1060.572 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5874 | 19.8895 | 16.6107 | 19.2685 | 20 |  | 40.9567 | 0 | 40.9567 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8055 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 11 | 707 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4321.2678 | 0 | 8349.0646 | 0 | 6615.8172 | 0 | 2463.8808 | 0 | 21750.0303 | 0 | 319.5924 | 0 | 463.6869 | 0 | 321.7267 | 0 | 136.838 | 410.4401 | 1652.2842 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6126 | 19.9147 | 16.6532 | 19.311 | 20 |  | 31.6207 | 0 | 31.6207 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8054 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 12 | 708 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5256.2871 | 0 | 5311.2881 | 0 | 8683.6887 | 0 | 2997.0058 | 0 | 22248.2696 | 0 | 388.7446 | 0 | 294.9761 | 0 | 422.2872 | 0 | 166.4465 | 462.8367 | 1735.2911 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6251 | 19.9272 | 16.7039 | 19.3617 | 20 |  | 26.9871 | 0 | 26.9871 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8053 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 13 | 709 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5666.1079 | 0 | 4415.3612 | 0 | 9271.3666 | 0 | 3230.6756 | 0 | 22583.5113 | 0 | 419.0541 | 0 | 245.2185 | 0 | 450.8659 | 0 | 179.4239 | 484.6686 | 1779.2312 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6354 | 19.9375 | 16.7465 | 19.4043 | 20 |  | 23.179 | 0 | 23.179 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8052 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 14 | 710 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3610.3905 | 0 | 2166.6884 | 0 | 5084.1111 | 0 | 2058.556 | 0 | 12919.746 | 0 | 267.0173 | 0 | 120.3327 | 0 | 247.24 | 0 | 114.3272 | 301.2805 | 1050.1977 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6116 | 19.9136 | 16.7377 | 19.3955 | 20 |  | 32.0132 | 0 | 32.0132 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8051 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 15 | 711 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6802.8117 | 0 | 7217.7968 | 0 | 23720.6203 | 0 | 3878.7961 | 0 | 41620.0249 | 0 | 503.1225 | 0 | 400.859 | 0 | 1153.5321 | 0 | 215.419 | 641.8585 | 2914.7911 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7041 | 20.0062 | 16.8643 | 19.5221 | 20.0062 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8050 | 0 | 0 | 20.0062 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 16 | 712 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5739.7116 | 0 | 8855.9071 | 0 | 61279.9315 | 0 | 3272.6426 | 0 | 79148.1927 | 0 | 424.4977 | 0 | 491.8357 | 0 | 2980.0388 | 0 | 181.7547 | 681.1559 | 4759.2829 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8207 | 20.1227 | 16.9938 | 19.6516 | 20.1227 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8049 | 0 | 0 | 20.1227 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 17 | 713 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1279.8984 | 0 | 731.0063 | 0 | 2277.3567 | 0 | 729.7666 | 0 | 5018.0281 | 0 | 94.6587 | 0 | 40.5983 | 0 | 110.7477 | 0 | 40.5295 | 109.1596 | 395.6939 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7118 | 20.0139 | 16.8406 | 19.4984 | 20.0139 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8048 | 0 | 0 | 20.0139 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 18 | 714 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6147 | 19.9178 | 16.7457 | 19.4025 | 20 |  | 30.4973 | 0 | 30.4973 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8047 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 19 | 715 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5991 | 19.9022 | 16.7247 | 19.3815 | 20 |  | 36.2699 | 0 | 36.2699 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8046 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 20 | 716 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6 | 19.9031 | 16.7285 | 19.3853 | 20 |  | 35.9316 | 0 | 35.9316 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8045 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 21 | 717 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.601 | 19.904 | 16.7324 | 19.3892 | 20 |  | 35.5932 | 0 | 35.5932 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8044 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 22 | 718 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5955 | 19.8985 | 16.7093 | 19.3661 | 20 |  | 37.6234 | 0 | 37.6234 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8043 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 23 | 719 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5927 | 19.8958 | 16.6977 | 19.3546 | 20 |  | 38.6385 | 0 | 38.6385 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8042 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 30 | 24 | 720 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5827 | 19.8858 | 16.6554 | 19.3122 | 20 |  | 42.3606 | 0 | 42.3606 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8041 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 1 | 721 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5404 | 19.8435 | 16.6314 | 19.2883 | 19.8435 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8040 | 0 | 0 | 19.8435 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 2 | 722 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3836 | 19.6866 | 16.4733 | 19.1301 | 19.6866 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8039 | 0 | 0 | 19.6866 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 3 | 723 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2264 | 19.5294 | 16.3148 | 18.9717 | 19.5294 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8038 | 0 | 0 | 19.5294 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 4 | 724 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0707 | 19.3738 | 16.1638 | 18.8206 | 19.3738 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8037 | 0 | 0 | 19.3738 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 5 | 725 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9193 | 19.2224 | 16.0258 | 18.6826 | 19.2224 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8036 | 0 | 0 | 19.2224 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 6 | 726 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7675 | 19.0706 | 15.8726 | 18.5294 | 19.0706 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8035 | 0 | 0 | 19.0706 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 7 | 727 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6145 | 18.9175 | 15.7152 | 18.372 | 18.9175 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8034 | 0 | 0 | 18.9175 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 8 | 728 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.4834 | 18.7855 | 15.5802 | 18.238 | 20 |  | 450.1708 | 0 | 450.1708 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8033 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 9 | 729 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.557 | 19.8591 | 16.625 | 19.2828 | 20 |  | 52.2175 | 0 | 52.2175 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8032 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 10 | 730 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1020.3803 | 0 | 650.5634 | 0 | 1329.1176 | 0 | 568.3727 | 0 | 3568.4339 | 0 | 75.4653 | 0 | 36.1307 | 0 | 64.6349 | 0 | 31.566 | 82.9613 | 290.7583 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5691 | 19.8712 | 16.6428 | 19.3006 | 20 |  | 47.7349 | 0 | 47.7349 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8031 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 11 | 731 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3391.1195 | 0 | 3495.2553 | 0 | 4738.0829 | 0 | 1933.533 | 0 | 13557.9908 | 0 | 250.8005 | 0 | 194.1181 | 0 | 230.4126 | 0 | 107.3838 | 292.5477 | 1075.2627 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6024 | 19.9045 | 16.6904 | 19.3482 | 20 |  | 35.4022 | 0 | 35.4022 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8030 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 12 | 732 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4801.2999 | 0 | 4006.5375 | 0 | 7313.1168 | 0 | 2737.5833 | 0 | 18858.5374 | 0 | 355.0946 | 0 | 222.5134 | 0 | 355.6364 | 0 | 152.0388 | 410.4401 | 1495.7233 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6204 | 19.9224 | 16.7169 | 19.3747 | 20 |  | 28.7461 | 0 | 28.7461 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8029 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 13 | 733 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5803.3198 | 0 | 4576.2988 | 0 | 9567.9505 | 0 | 3308.9104 | 0 | 23256.4795 | 0 | 429.202 | 0 | 254.1566 | 0 | 465.2888 | 0 | 183.7689 | 497.7678 | 1830.1841 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.634 | 19.9361 | 16.7333 | 19.3911 | 20 |  | 23.7019 | 0 | 23.7019 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8028 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 14 | 734 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6048.5394 | 0 | 4510.3159 | 0 | 10714.3936 | 0 | 3448.7286 | 0 | 24721.9775 | 0 | 447.338 | 0 | 250.4921 | 0 | 521.0402 | 0 | 191.5341 | 519.5997 | 1930.0041 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6441 | 19.9462 | 16.7639 | 19.4217 | 20 |  | 19.9546 | 0 | 19.9546 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8027 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 15 | 735 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6995.6671 | 0 | 7575.2741 | 0 | 25070.8444 | 0 | 3988.7575 | 0 | 43630.543 | 0 | 517.3857 | 0 | 420.7125 | 0 | 1219.1934 | 0 | 221.526 | 668.0568 | 3046.8743 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7006 | 20.0027 | 16.8285 | 19.4862 | 20.0027 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8026 | 0 | 0 | 20.0027 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 16 | 736 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5115.8482 | 0 | 4367.8193 | 0 | 20814.0636 | 0 | 2916.931 | 0 | 33214.6621 | 0 | 378.358 | 0 | 242.5782 | 0 | 1012.1865 | 0 | 161.9993 | 471.5695 | 2266.6915 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6807 | 19.9828 | 16.8353 | 19.4931 | 20 |  | 6.3875 | 0 | 6.3875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8025 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 17 | 737 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2080.6975 | 0 | 1192.3384 | 0 | 6712.6683 | 0 | 1186.3626 | 0 | 11172.0667 | 0 | 153.8843 | 0 | 66.2196 | 0 | 326.4366 | 0 | 65.8877 | 170.289 | 782.7172 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6078 | 19.9099 | 16.7399 | 19.3977 | 20 |  | 33.4049 | 0 | 33.4049 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8024 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 18 | 738 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.9179 | 0 | 86.0497 | 0 | 201.2238 | 0 | 86.0497 | 0 | 524.241 | 0 | 11.1616 | 0 | 4.779 | 0 | 9.7855 | 0 | 4.779 | 13.0992 | 43.6042 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5934 | 19.8964 | 16.6954 | 19.3522 | 20 |  | 38.409 | 0 | 38.409 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8023 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 19 | 739 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5982 | 19.9013 | 16.7208 | 19.3776 | 20 |  | 36.6083 | 0 | 36.6083 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8022 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 20 | 740 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6101 | 19.9131 | 16.7708 | 19.4277 | 20 |  | 32.2095 | 0 | 32.2095 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8021 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 21 | 741 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6146 | 19.9177 | 16.7901 | 19.4469 | 20 |  | 30.5177 | 0 | 30.5177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8020 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 22 | 742 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8019 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 23 | 743 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6192 | 19.9223 | 16.8093 | 19.4662 | 20 |  | 28.8258 | 0 | 28.8258 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8018 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2001 | 1 | 31 | 24 | 744 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.621 | 19.9241 | 16.817 | 19.4739 | 20 |  | 28.1491 | 0 | 28.1491 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8017 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 1 | 745 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5842 | 19.8873 | 16.8162 | 19.473 | 19.8873 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8016 | 0 | 0 | 19.8873 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 2 | 746 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4689 | 19.772 | 16.6924 | 19.3493 | 19.772 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8015 | 0 | 0 | 19.772 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 3 | 747 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3584 | 19.6614 | 16.597 | 19.2539 | 19.6614 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8014 | 0 | 0 | 19.6614 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 4 | 748 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2526 | 19.5556 | 16.5062 | 19.163 | 19.5556 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8013 | 0 | 0 | 19.5556 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 5 | 749 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1532 | 19.4563 | 16.4276 | 19.0844 | 19.4563 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8012 | 0 | 0 | 19.4563 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 6 | 750 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0567 | 19.3597 | 16.3398 | 18.9967 | 19.3597 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8011 | 0 | 0 | 19.3597 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 7 | 751 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9656 | 19.2687 | 16.2663 | 18.9231 | 19.2687 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8010 | 0 | 0 | 19.2687 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 8 | 752 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8953 | 19.1974 | 16.2052 | 18.863 | 20 |  | 297.4849 | 0 | 297.4849 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8009 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 9 | 753 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6268 | 19.9289 | 16.9387 | 19.5965 | 20 |  | 26.3448 | 0 | 26.3448 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8008 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 10 | 754 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1191.3679 | 0 | 765.4483 | 0 | 1548.2346 | 0 | 662.074 | 0 | 4167.1248 | 0 | 88.1112 | 0 | 42.5112 | 0 | 75.2905 | 0 | 36.77 | 96.0605 | 338.7434 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6508 | 19.9529 | 17.0036 | 19.6614 | 20 |  | 17.4748 | 0 | 17.4748 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8007 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 11 | 755 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3606.6077 | 0 | 4022.2076 | 0 | 5068.797 | 0 | 2056.3991 | 0 | 14754.0113 | 0 | 266.7376 | 0 | 223.3837 | 0 | 246.4952 | 0 | 114.2075 | 314.3797 | 1165.2036 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6858 | 19.9879 | 17.0528 | 19.7106 | 20 |  | 4.5029 | 0 | 4.5029 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8006 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 12 | 756 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8121.9709 | 0 | 29634.5097 | 0 | 28646.5244 | 0 | 4630.9483 | 0 | 71033.9533 | 0 | 600.6849 | 0 | 1645.8293 | 0 | 1393.0785 | 0 | 257.1917 | 1030.4667 | 4927.2511 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8553 | 20.1574 | 17.2464 | 19.9042 | 20.1574 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8005 | 0 | 0 | 20.1574 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 13 | 757 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8420.167 | 0 | 35061.0216 | 0 | 54780.1741 | 0 | 4800.9724 | 0 | 103062.335 | 0 | 622.7389 | 0 | 1947.2047 | 0 | 2663.9561 | 0 | 266.6344 | 1296.8161 | 6797.3502 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1053 | 20.4074 | 17.4993 | 20.157 | 20.4074 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8004 | 0 | 0 | 20.4074 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 14 | 758 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8964.8423 | 0 | 21142.7144 | 0 | 51916.9158 | 0 | 5111.5329 | 0 | 87136.0054 | 0 | 663.022 | 0 | 1174.2154 | 0 | 2524.716 | 0 | 283.8822 | 1091.596 | 5737.4317 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3098 | 20.6118 | 17.7059 | 20.3636 | 20.6118 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8003 | 0 | 0 | 20.6118 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 15 | 759 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7351.5176 | 0 | 8593.8304 | 0 | 29137.8438 | 0 | 4191.6548 | 0 | 49274.8465 | 0 | 543.7037 | 0 | 477.2806 | 0 | 1416.9713 | 0 | 232.7944 | 729.1862 | 3399.9362 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3955 | 20.6976 | 17.7578 | 20.4156 | 20.6976 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8002 | 0 | 0 | 20.6976 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 16 | 760 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5684.2117 | 0 | 5904.6832 | 0 | 33384.1463 | 0 | 3240.9979 | 0 | 48214.0392 | 0 | 420.393 | 0 | 327.9319 | 0 | 1623.4687 | 0 | 179.9972 | 558.8972 | 3110.688 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4727 | 20.7748 | 17.8178 | 20.4756 | 20.7748 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8001 | 0 | 0 | 20.7748 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 17 | 761 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1595.7931 | 0 | 910.498 | 0 | 2875.8205 | 0 | 909.882 | 0 | 6291.9936 | 0 | 118.0217 | 0 | 50.5669 | 0 | 139.851 | 0 | 50.5327 | 135.3579 | 494.3301 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4197 | 20.7218 | 17.7321 | 20.3899 | 20.7218 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8000 | 0 | 0 | 20.7218 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 18 | 762 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3769 | 20.68 | 17.6839 | 20.3407 | 20.68 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7999 | 0 | 0 | 20.68 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 19 | 763 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3383 | 20.6413 | 17.6553 | 20.3121 | 20.6413 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7998 | 0 | 0 | 20.6413 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 20 | 764 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3055 | 20.6085 | 17.6412 | 20.298 | 20.6085 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7997 | 0 | 0 | 20.6085 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 21 | 765 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2693 | 20.5724 | 17.5943 | 20.2511 | 20.5724 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7996 | 0 | 0 | 20.5724 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 22 | 766 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2362 | 20.5393 | 17.5711 | 20.2279 | 20.5393 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7995 | 0 | 0 | 20.5393 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 23 | 767 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2026 | 20.5056 | 17.5354 | 20.1923 | 20.5056 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7994 | 0 | 0 | 20.5056 | 0 | 0 | 0
|  | 2004 | 2 | 1 | 24 | 768 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1765 | 20.4796 | 17.5339 | 20.1907 | 20.4796 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7993 | 0 | 0 | 20.4796 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 1 | 769 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1075 | 20.4106 | 17.481 | 20.1379 | 20.4106 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7992 | 0 | 0 | 20.4106 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 2 | 770 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0356 | 20.3386 | 17.3993 | 20.0562 | 20.3386 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7991 | 0 | 0 | 20.3386 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 3 | 771 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9643 | 20.2673 | 17.3302 | 19.987 | 20.2673 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7990 | 0 | 0 | 20.2673 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 4 | 772 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8937 | 20.1967 | 17.2617 | 19.9185 | 20.1967 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7989 | 0 | 0 | 20.1967 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 5 | 773 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8238 | 20.1268 | 17.1938 | 19.8507 | 20.1268 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7988 | 0 | 0 | 20.1268 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 6 | 774 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7527 | 20.0558 | 17.1189 | 19.7758 | 20.0558 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7987 | 0 | 0 | 20.0558 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 7 | 775 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6814 | 19.9845 | 17.0468 | 19.7036 | 19.9845 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7986 | 0 | 0 | 19.9845 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 8 | 776 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6232 | 19.9253 | 16.9767 | 19.6345 | 20 |  | 27.6851 | 0 | 27.6851 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7985 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 9 | 777 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6378 | 19.9399 | 16.9879 | 19.6457 | 20 |  | 22.2924 | 0 | 22.2924 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7984 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 10 | 778 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 304.7618 | 0 | 179.7615 | 0 | 403.4834 | 0 | 172.5423 | 0 | 1060.549 | 0 | 22.5396 | 0 | 9.9835 | 0 | 19.6214 | 0 | 9.5826 | 26.1983 | 87.9254 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6392 | 19.9413 | 16.9834 | 19.6411 | 20 |  | 21.7674 | 0 | 21.7674 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7983 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 11 | 779 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 555.2184 | 0 | 324.4269 | 0 | 741.2796 | 0 | 316.5719 | 0 | 1937.4968 | 0 | 41.0629 | 0 | 18.0179 | 0 | 36.0484 | 0 | 17.5816 | 48.0302 | 160.741 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6401 | 19.9422 | 16.9783 | 19.6361 | 20 |  | 21.4411 | 0 | 21.4411 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7982 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 12 | 780 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1431.5597 | 0 | 844.5633 | 0 | 1928.7712 | 0 | 816.2402 | 0 | 5021.1344 | 0 | 105.8753 | 0 | 46.905 | 0 | 93.796 | 0 | 45.332 | 122.2588 | 414.1671 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6499 | 19.952 | 16.991 | 19.6488 | 20 |  | 17.7923 | 0 | 17.7923 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7981 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 13 | 781 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1118.9929 | 0 | 650.3897 | 0 | 1509.7337 | 0 | 638.0223 | 0 | 3917.1386 | 0 | 82.7585 | 0 | 36.1211 | 0 | 73.4182 | 0 | 35.4342 | 96.0605 | 323.7925 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6484 | 19.9505 | 16.9953 | 19.6531 | 20 |  | 18.3632 | 0 | 18.3632 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7980 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 14 | 782 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1429.1704 | 0 | 831.2773 | 0 | 1946.3966 | 0 | 814.8779 | 0 | 5021.7222 | 0 | 105.6986 | 0 | 46.1671 | 0 | 94.6531 | 0 | 45.2564 | 122.2588 | 414.034 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6566 | 19.9587 | 17.0212 | 19.679 | 20 |  | 15.2981 | 0 | 15.2981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7979 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 15 | 783 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1585.1176 | 0 | 922.0252 | 0 | 2193.6274 | 0 | 903.7951 | 0 | 5604.5654 | 0 | 117.2322 | 0 | 51.2071 | 0 | 106.6759 | 0 | 50.1946 | 135.3579 | 460.6677 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6676 | 19.9697 | 17.0644 | 19.7222 | 20 |  | 11.2397 | 0 | 11.2397 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7978 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 16 | 784 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1849.7601 | 0 | 1077.7375 | 0 | 2690.7408 | 0 | 1054.6878 | 0 | 6672.9262 | 0 | 136.8046 | 0 | 59.8549 | 0 | 130.8505 | 0 | 58.5748 | 157.1898 | 543.2747 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6715 | 19.9736 | 17.0713 | 19.7291 | 20 |  | 9.777 | 0 | 9.777 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7977 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 17 | 785 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1278.5853 | 0 | 729.0585 | 0 | 2155.0601 | 0 | 729.0179 | 0 | 4891.7219 | 0 | 94.5616 | 0 | 40.4902 | 0 | 104.8004 | 0 | 40.4879 | 109.1596 | 389.4997 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.663 | 19.965 | 17.051 | 19.7088 | 20 |  | 12.9588 | 0 | 12.9588 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7976 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 18 | 786 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.6766 | 0 | 85.9121 | 0 | 200.9022 | 0 | 85.9121 | 0 | 523.403 | 0 | 11.1437 | 0 | 4.7714 | 0 | 9.7699 | 0 | 4.7714 | 13.0992 | 43.5555 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6773 | 19.9804 | 17.0495 | 19.7063 | 20 |  | 7.2801 | 0 | 7.2801 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7975 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 19 | 787 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.673 | 19.9761 | 17.0364 | 19.6933 | 20 |  | 8.8622 | 0 | 8.8622 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7974 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 20 | 788 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6758 | 19.9788 | 17.048 | 19.7048 | 20 |  | 7.8471 | 0 | 7.8471 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7973 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 21 | 789 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6785 | 19.9816 | 17.0595 | 19.7164 | 20 |  | 6.832 | 0 | 6.832 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7972 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 22 | 790 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6785 | 19.9816 | 17.0595 | 19.7164 | 20 |  | 6.832 | 0 | 6.832 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7971 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 23 | 791 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6785 | 19.9816 | 17.0595 | 19.7164 | 20 |  | 6.832 | 0 | 6.832 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7970 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 2 | 24 | 792 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6813 | 19.9843 | 17.0711 | 19.7279 | 20 |  | 5.8169 | 0 | 5.8169 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7969 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 1 | 793 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6344 | 19.9375 | 17.0279 | 19.6847 | 19.9375 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7968 | 0 | 0 | 19.9375 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 2 | 794 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5725 | 19.8755 | 16.9677 | 19.6246 | 19.8755 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7967 | 0 | 0 | 19.8755 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 3 | 795 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5111 | 19.8142 | 16.9082 | 19.5651 | 19.8142 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7966 | 0 | 0 | 19.8142 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 4 | 796 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4476 | 19.7507 | 16.8377 | 19.4946 | 19.7507 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7965 | 0 | 0 | 19.7507 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 5 | 797 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3857 | 19.6887 | 16.7806 | 19.4374 | 19.6887 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7964 | 0 | 0 | 19.6887 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 6 | 798 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3261 | 19.6292 | 16.7287 | 19.3855 | 19.6292 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7963 | 0 | 0 | 19.6292 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 7 | 799 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2699 | 19.5729 | 16.683 | 19.3399 | 19.5729 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7962 | 0 | 0 | 19.5729 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 8 | 800 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.2638 | 19.5668 | 16.6837 | 19.3406 | 20 |  | 160.6102 | 0 | 160.6102 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7961 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 9 | 801 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6904 | 19.9934 | 17.1095 | 19.7664 | 20 |  | 2.4332 | 0 | 2.4332 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7960 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 10 | 802 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 731.9588 | 0 | 447.8911 | 0 | 961.0056 | 0 | 410.9563 | 0 | 2551.8118 | 0 | 54.1342 | 0 | 24.8748 | 0 | 46.7336 | 0 | 22.8235 | 61.1294 | 209.6956 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7024 | 20.0054 | 17.1361 | 19.793 | 20.0054 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7959 | 0 | 0 | 20.0054 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 11 | 803 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2632.0541 | 0 | 1657.1168 | 0 | 3528.0835 | 0 | 1500.7326 | 0 | 9317.9871 | 0 | 194.6615 | 0 | 92.0323 | 0 | 171.5705 | 0 | 83.3471 | 218.3192 | 759.9305 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.733 | 20.0361 | 17.1839 | 19.8407 | 20.0361 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7958 | 0 | 0 | 20.0361 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 12 | 804 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6021.322 | 0 | 6894.8827 | 0 | 10456.7949 | 0 | 3433.2099 | 0 | 26806.2096 | 0 | 445.3251 | 0 | 382.9252 | 0 | 508.5132 | 0 | 190.6722 | 545.798 | 2073.2337 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8222 | 20.1253 | 17.2979 | 19.9547 | 20.1253 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7957 | 0 | 0 | 20.1253 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 13 | 805 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9112.1074 | 0 | 22360.1728 | 0 | 36697.6175 | 0 | 5195.4998 | 0 | 73365.3975 | 0 | 673.9134 | 0 | 1241.8301 | 0 | 1784.6026 | 0 | 288.5455 | 1078.4969 | 5067.3886 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0543 | 20.3573 | 17.5576 | 20.2145 | 20.3573 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7956 | 0 | 0 | 20.3573 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 14 | 806 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8308.1297 | 0 | 10650.6748 | 0 | 25788.0858 | 0 | 4737.0915 | 0 | 49483.9818 | 0 | 614.4528 | 0 | 591.5128 | 0 | 1254.0728 | 0 | 263.0867 | 812.1475 | 3535.2726 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2165 | 20.5195 | 17.717 | 20.3738 | 20.5195 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7955 | 0 | 0 | 20.5195 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 15 | 807 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7501.4004 | 0 | 8471.2014 | 0 | 28456.8027 | 0 | 4277.1143 | 0 | 48706.5188 | 0 | 554.7887 | 0 | 470.4701 | 0 | 1383.8523 | 0 | 237.5406 | 737.9189 | 3384.5707 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3764 | 20.6795 | 17.8781 | 20.5349 | 20.6795 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7954 | 0 | 0 | 20.6795 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 16 | 808 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3791.2432 | 0 | 2251.754 | 0 | 5936.5945 | 0 | 2161.6738 | 0 | 14141.2655 | 0 | 280.3928 | 0 | 125.057 | 0 | 288.6962 | 0 | 120.0542 | 314.3797 | 1128.5798 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4337 | 20.7367 | 17.9263 | 20.5831 | 20.7367 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7953 | 0 | 0 | 20.7367 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 17 | 809 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1121.3783 | 0 | 639.3824 | 0 | 1818.3933 | 0 | 639.603 | 0 | 4218.7571 | 0 | 82.9349 | 0 | 35.5098 | 0 | 88.4283 | 0 | 35.522 | 96.0605 | 338.4555 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4588 | 20.7618 | 17.9413 | 20.5981 | 20.7618 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7952 | 0 | 0 | 20.7618 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 18 | 810 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4677 | 20.7707 | 17.9379 | 20.5947 | 20.7707 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7951 | 0 | 0 | 20.7707 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 19 | 811 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4738 | 20.7768 | 17.9349 | 20.5917 | 20.7768 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7950 | 0 | 0 | 20.7768 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 20 | 812 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4789 | 20.7819 | 17.9369 | 20.5937 | 20.7819 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7949 | 0 | 0 | 20.7819 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 21 | 813 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.483 | 20.7861 | 17.938 | 20.5948 | 20.7861 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7948 | 0 | 0 | 20.7861 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 22 | 814 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4835 | 20.7866 | 17.9266 | 20.5834 | 20.7866 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7947 | 0 | 0 | 20.7866 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 23 | 815 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.483 | 20.7861 | 17.9232 | 20.58 | 20.7861 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7946 | 0 | 0 | 20.7861 | 0 | 0 | 0
|  | 2004 | 2 | 3 | 24 | 816 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4835 | 20.7866 | 17.9266 | 20.5834 | 20.7866 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7945 | 0 | 0 | 20.7866 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 1 | 817 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4389 | 20.742 | 17.8915 | 20.5484 | 20.742 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7944 | 0 | 0 | 20.742 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 2 | 818 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.393 | 20.696 | 17.841 | 20.4978 | 20.696 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7943 | 0 | 0 | 20.696 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 3 | 819 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3438 | 20.6469 | 17.7814 | 20.4383 | 20.6469 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7942 | 0 | 0 | 20.6469 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 4 | 820 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.296 | 20.5991 | 17.738 | 20.3948 | 20.5991 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7941 | 0 | 0 | 20.5991 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 5 | 821 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2459 | 20.549 | 17.6805 | 20.3374 | 20.549 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7940 | 0 | 0 | 20.549 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 6 | 822 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1818 | 20.4848 | 17.5708 | 20.2277 | 20.4848 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7939 | 0 | 0 | 20.4848 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 7 | 823 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.12 | 20.4231 | 17.5169 | 20.1737 | 20.4231 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7938 | 0 | 0 | 20.4231 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 8 | 824 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.113 | 20.4161 | 17.5315 | 20.1884 | 20.4161 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7937 | 0 | 0 | 20.4161 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 9 | 825 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 299.574 | 0 | 323.5054 | 0 | 158.8699 | 0 | 67.9378 | 0 | 849.8871 | 0 | 22.1559 | 0 | 17.9667 | 0 | 7.7258 | 0 | 3.7731 | 13.0992 | 64.7207 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0985 | 20.4016 | 17.4849 | 20.1417 | 20.4016 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7936 | 0 | 0 | 20.4016 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 10 | 826 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2516.9275 | 0 | 3391.2983 | 0 | 2377.4947 | 0 | 1016.6918 | 0 | 9302.4124 | 0 | 186.147 | 0 | 188.3445 | 0 | 115.6174 | 0 | 56.4646 | 157.1898 | 703.7634 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1224 | 20.4254 | 17.5529 | 20.2097 | 20.4254 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7935 | 0 | 0 | 20.4254 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 11 | 827 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4836.3081 | 0 | 8991.0961 | 0 | 7153.1525 | 0 | 2757.5441 | 0 | 23738.1008 | 0 | 357.6838 | 0 | 499.3438 | 0 | 347.8573 | 0 | 153.1474 | 462.8367 | 1820.869 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.198 | 20.5011 | 17.6594 | 20.3163 | 20.5011 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7934 | 0 | 0 | 20.5011 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 12 | 828 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4855.8861 | 0 | 3693.7359 | 0 | 7118.3777 | 0 | 2768.707 | 0 | 18436.7067 | 0 | 359.1317 | 0 | 205.1412 | 0 | 346.1662 | 0 | 153.7673 | 410.4401 | 1474.6466 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2649 | 20.568 | 17.7479 | 20.4047 | 20.568 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7933 | 0 | 0 | 20.568 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 13 | 829 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3015.6049 | 0 | 1800.8451 | 0 | 4136.8952 | 0 | 1719.4239 | 0 | 10672.7691 | 0 | 223.0282 | 0 | 100.0146 | 0 | 201.1769 | 0 | 95.4927 | 253.2503 | 872.9626 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2996 | 20.6026 | 17.7515 | 20.4083 | 20.6026 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7932 | 0 | 0 | 20.6026 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 14 | 830 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4867.0301 | 0 | 2942.4983 | 0 | 6905.5197 | 0 | 2775.061 | 0 | 17490.1091 | 0 | 359.9559 | 0 | 163.4193 | 0 | 335.8149 | 0 | 154.1202 | 401.7073 | 1415.0177 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3674 | 20.6704 | 17.8621 | 20.5189 | 20.6704 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7931 | 0 | 0 | 20.6704 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 15 | 831 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4707.4274 | 0 | 2824.874 | 0 | 6896.9121 | 0 | 2684.0595 | 0 | 17113.273 | 0 | 348.152 | 0 | 156.8867 | 0 | 335.3964 | 0 | 149.0662 | 388.6082 | 1378.1095 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.438 | 20.741 | 17.9454 | 20.6022 | 20.741 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7930 | 0 | 0 | 20.741 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 16 | 832 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3789.7186 | 0 | 2246.0692 | 0 | 5892.2044 | 0 | 2160.8045 | 0 | 14088.7967 | 0 | 280.2801 | 0 | 124.7413 | 0 | 286.5375 | 0 | 120.0059 | 314.3797 | 1125.9444 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5027 | 20.8058 | 18.0199 | 20.6768 | 20.8058 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7929 | 0 | 0 | 20.8058 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 17 | 833 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 861.9222 | 0 | 491.4469 | 0 | 1328.4036 | 0 | 491.7147 | 0 | 3173.4874 | 0 | 63.7461 | 0 | 27.2938 | 0 | 64.6002 | 0 | 27.3086 | 74.2285 | 257.1772 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5323 | 20.8354 | 18.0393 | 20.6961 | 20.8354 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7928 | 0 | 0 | 20.8354 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 18 | 834 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.4883 | 0 | 85.8047 | 0 | 200.651 | 0 | 85.8047 | 0 | 522.7487 | 0 | 11.1298 | 0 | 4.7654 | 0 | 9.7576 | 0 | 4.7654 | 13.0992 | 43.5174 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5494 | 20.8524 | 18.0409 | 20.6977 | 20.8524 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7927 | 0 | 0 | 20.8524 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 19 | 835 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5629 | 20.8659 | 18.048 | 20.7049 | 20.8659 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7926 | 0 | 0 | 20.8659 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 20 | 836 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5763 | 20.8793 | 18.061 | 20.7179 | 20.8793 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7925 | 0 | 0 | 20.8793 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 21 | 837 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5913 | 20.8944 | 18.0816 | 20.7384 | 20.8944 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7924 | 0 | 0 | 20.8944 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 22 | 838 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6099 | 20.913 | 18.1115 | 20.7683 | 20.913 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7923 | 0 | 0 | 20.913 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 23 | 839 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6238 | 20.9268 | 18.1101 | 20.7669 | 20.9268 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7922 | 0 | 0 | 20.9268 | 0 | 0 | 0
|  | 2004 | 2 | 4 | 24 | 840 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.632 | 20.9351 | 18.1003 | 20.7571 | 20.9351 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7921 | 0 | 0 | 20.9351 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 1 | 841 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.5887 | 20.8918 | 18.0458 | 20.7026 | 20.8918 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7920 | 0 | 0 | 20.8918 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 2 | 842 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.5422 | 20.8453 | 17.9888 | 20.6456 | 20.8453 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7919 | 0 | 0 | 20.8453 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 3 | 843 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4944 | 20.7974 | 17.9364 | 20.5932 | 20.7974 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7918 | 0 | 0 | 20.7974 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 4 | 844 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4433 | 20.7463 | 17.875 | 20.5318 | 20.7463 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7917 | 0 | 0 | 20.7463 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 5 | 845 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3809 | 20.6839 | 17.7759 | 20.4327 | 20.6839 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7916 | 0 | 0 | 20.6839 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 6 | 846 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3136 | 20.6166 | 17.6928 | 20.3496 | 20.6166 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7915 | 0 | 0 | 20.6166 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 7 | 847 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.246 | 20.549 | 17.6243 | 20.2811 | 20.549 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7914 | 0 | 0 | 20.549 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 8 | 848 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1937 | 20.4958 | 17.5688 | 20.2266 | 20.4958 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7913 | 0 | 0 | 20.4958 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 9 | 849 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.14 | 20.4421 | 17.5138 | 20.1716 | 20.4421 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7912 | 0 | 0 | 20.4421 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 10 | 850 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 894.3457 | 0 | 549.4978 | 0 | 1172.2306 | 0 | 501.2828 | 0 | 3117.3568 | 0 | 66.144 | 0 | 30.5178 | 0 | 57.0055 | 0 | 27.84 | 74.2285 | 255.7359 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.096 | 20.3981 | 17.4712 | 20.1289 | 20.3981 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7911 | 0 | 0 | 20.3981 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 11 | 851 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2627.4419 | 0 | 1643.3353 | 0 | 3518.7518 | 0 | 1498.1028 | 0 | 9287.6317 | 0 | 194.3204 | 0 | 91.2669 | 0 | 171.1167 | 0 | 83.201 | 218.3192 | 758.2242 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0745 | 20.3766 | 17.4654 | 20.1232 | 20.3766 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7910 | 0 | 0 | 20.3766 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 12 | 852 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3355.4565 | 0 | 2048.6299 | 0 | 4567.4779 | 0 | 1913.1989 | 0 | 11884.7632 | 0 | 248.1629 | 0 | 113.776 | 0 | 222.1161 | 0 | 106.2545 | 279.4486 | 969.7581 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0625 | 20.3646 | 17.4598 | 20.1176 | 20.3646 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7909 | 0 | 0 | 20.3646 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 13 | 853 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3014.8613 | 0 | 1798.2292 | 0 | 4132.4425 | 0 | 1718.9999 | 0 | 10664.5329 | 0 | 222.9732 | 0 | 99.8693 | 0 | 200.9604 | 0 | 95.4691 | 253.2503 | 872.5223 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0488 | 20.3509 | 17.4523 | 20.1101 | 20.3509 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7908 | 0 | 0 | 20.3509 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 14 | 854 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3172.1792 | 0 | 1880.267 | 0 | 4407.3104 | 0 | 1808.6987 | 0 | 11268.4553 | 0 | 234.6081 | 0 | 104.4255 | 0 | 214.3272 | 0 | 100.4508 | 266.3494 | 920.161 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0402 | 20.3423 | 17.4559 | 20.1137 | 20.3423 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7907 | 0 | 0 | 20.3423 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 15 | 855 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2161.464 | 0 | 1262.7629 | 0 | 3015.8335 | 0 | 1232.4137 | 0 | 7672.4742 | 0 | 159.8576 | 0 | 70.1308 | 0 | 146.6598 | 0 | 68.4453 | 183.3881 | 628.4816 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0179 | 20.32 | 17.4223 | 20.0801 | 20.32 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7906 | 0 | 0 | 20.32 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 16 | 856 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 963.7978 | 0 | 555.1255 | 0 | 1340.4398 | 0 | 549.5338 | 0 | 3408.8969 | 0 | 71.2806 | 0 | 30.8303 | 0 | 65.1855 | 0 | 30.5198 | 82.9613 | 280.7775 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9826 | 20.2846 | 17.3848 | 20.0426 | 20.2846 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7905 | 0 | 0 | 20.2846 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 17 | 857 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 300.7462 | 0 | 171.4781 | 0 | 421.7465 | 0 | 171.5268 | 0 | 1065.4976 | 0 | 22.2426 | 0 | 9.5235 | 0 | 20.5095 | 0 | 9.5262 | 26.1983 | 88.0001 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9398 | 20.2419 | 17.3403 | 19.998 | 20.2419 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7904 | 0 | 0 | 20.2419 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 18 | 858 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9263 | 20.2293 | 17.3266 | 19.9835 | 20.2293 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7903 | 0 | 0 | 20.2293 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 19 | 859 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9157 | 20.2188 | 17.3223 | 19.9791 | 20.2188 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7902 | 0 | 0 | 20.2188 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 20 | 860 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9034 | 20.2064 | 17.3044 | 19.9612 | 20.2064 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7901 | 0 | 0 | 20.2064 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 21 | 861 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.893 | 20.1961 | 17.3002 | 19.9571 | 20.1961 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7900 | 0 | 0 | 20.1961 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 22 | 862 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8782 | 20.1812 | 17.271 | 19.9279 | 20.1812 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7899 | 0 | 0 | 20.1812 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 23 | 863 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.858 | 20.161 | 17.2337 | 19.8905 | 20.161 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7898 | 0 | 0 | 20.161 | 0 | 0 | 0
|  | 2004 | 2 | 5 | 24 | 864 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8371 | 20.1402 | 17.2104 | 19.8673 | 20.1402 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7897 | 0 | 0 | 20.1402 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 1 | 865 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7659 | 20.069 | 17.1317 | 19.7886 | 20.069 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7896 | 0 | 0 | 20.069 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 2 | 866 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6945 | 19.9975 | 17.0595 | 19.7163 | 19.9975 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7895 | 0 | 0 | 19.9975 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 3 | 867 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6201 | 19.9232 | 16.9754 | 19.6323 | 19.9232 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7894 | 0 | 0 | 19.9232 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 4 | 868 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5483 | 19.8513 | 16.9117 | 19.5685 | 19.8513 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7893 | 0 | 0 | 19.8513 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 5 | 869 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.478 | 19.7811 | 16.8465 | 19.5033 | 19.7811 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7892 | 0 | 0 | 19.7811 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 6 | 870 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4085 | 19.7115 | 16.779 | 19.4358 | 19.7115 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7891 | 0 | 0 | 19.7115 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 7 | 871 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3414 | 19.6445 | 16.7198 | 19.3767 | 19.6445 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7890 | 0 | 0 | 19.6445 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 8 | 872 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.2921 | 19.5942 | 16.6762 | 19.334 | 20 |  | 150.408 | 0 | 150.408 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7889 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 9 | 873 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 586.7997 | 0 | 620.6426 | 0 | 316.4927 | 0 | 135.3423 | 0 | 1659.2774 | 0 | 43.3985 | 0 | 34.469 | 0 | 15.391 | 0 | 7.5166 | 26.1983 | 126.9735 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6502 | 19.9522 | 17.0266 | 19.6844 | 20 |  | 17.7007 | 0 | 17.7007 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7888 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 10 | 874 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1345.7478 | 0 | 847.6055 | 0 | 1752.3688 | 0 | 749.3682 | 0 | 4695.0904 | 0 | 99.5288 | 0 | 47.074 | 0 | 85.2176 | 0 | 41.6181 | 109.1596 | 382.5981 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6599 | 19.962 | 17.0391 | 19.6969 | 20 |  | 14.0975 | 0 | 14.0975 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7887 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 11 | 875 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 863.2741 | 0 | 508.3993 | 0 | 1152.6562 | 0 | 492.2177 | 0 | 3016.5473 | 0 | 63.846 | 0 | 28.2353 | 0 | 56.0536 | 0 | 27.3366 | 74.2285 | 249.7 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6567 | 19.9588 | 17.0419 | 19.6997 | 20 |  | 15.2855 | 0 | 15.2855 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7886 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 12 | 876 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1850.2431 | 0 | 1096.5636 | 0 | 2495.5007 | 0 | 1054.9632 | 0 | 6497.2706 | 0 | 136.8403 | 0 | 60.9005 | 0 | 121.356 | 0 | 58.5901 | 157.1898 | 534.8768 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6694 | 19.9714 | 17.0632 | 19.721 | 20 |  | 10.5845 | 0 | 10.5845 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7885 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 13 | 877 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1846.7956 | 0 | 1082.6967 | 0 | 2504.4906 | 0 | 1052.9975 | 0 | 6486.9804 | 0 | 136.5853 | 0 | 60.1304 | 0 | 121.7932 | 0 | 58.4809 | 157.1898 | 534.1797 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6719 | 19.9739 | 17.0745 | 19.7323 | 20 |  | 9.6603 | 0 | 9.6603 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7884 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 14 | 878 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 862.2235 | 0 | 497.0223 | 0 | 1163.0425 | 0 | 491.6187 | 0 | 3013.907 | 0 | 63.7683 | 0 | 27.6034 | 0 | 56.5587 | 0 | 27.3033 | 74.2285 | 249.4623 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6668 | 19.9688 | 17.0872 | 19.745 | 20 |  | 11.5478 | 0 | 11.5478 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7883 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 15 | 879 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1273.4653 | 0 | 736.5036 | 0 | 1743.9247 | 0 | 726.0986 | 0 | 4479.9923 | 0 | 94.183 | 0 | 40.9036 | 0 | 84.8069 | 0 | 40.3258 | 109.1596 | 369.3789 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6744 | 19.9765 | 17.1066 | 19.7644 | 20 |  | 8.7149 | 0 | 8.7149 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7882 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 16 | 880 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 554.7514 | 0 | 318.0946 | 0 | 757.5015 | 0 | 316.3056 | 0 | 1946.6531 | 0 | 41.0283 | 0 | 17.6662 | 0 | 36.8372 | 0 | 17.5669 | 48.0302 | 161.1288 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.667 | 19.9691 | 17.0993 | 19.7571 | 20 |  | 11.4565 | 0 | 11.4565 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7881 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 17 | 881 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 300.7686 | 0 | 171.4909 | 0 | 420.3471 | 0 | 171.5534 | 0 | 1064.16 | 0 | 22.2443 | 0 | 9.5242 | 0 | 20.4415 | 0 | 9.5277 | 26.1983 | 87.9359 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.656 | 19.9581 | 17.059 | 19.7167 | 20 |  | 15.5294 | 0 | 15.5294 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7880 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 18 | 882 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6803 | 19.9834 | 17.0672 | 19.7241 | 20 |  | 6.1552 | 0 | 6.1552 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7879 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 19 | 883 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6776 | 19.9807 | 17.0557 | 19.7125 | 20 |  | 7.1703 | 0 | 7.1703 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7878 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 20 | 884 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6785 | 19.9816 | 17.0595 | 19.7164 | 20 |  | 6.832 | 0 | 6.832 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7877 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 21 | 885 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6803 | 19.9834 | 17.0672 | 19.7241 | 20 |  | 6.1552 | 0 | 6.1552 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7876 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 22 | 886 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6785 | 19.9816 | 17.0595 | 19.7164 | 20 |  | 6.832 | 0 | 6.832 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7875 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 23 | 887 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6767 | 19.9797 | 17.0518 | 19.7087 | 20 |  | 7.5087 | 0 | 7.5087 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7874 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 6 | 24 | 888 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6676 | 19.9706 | 17.0133 | 19.6702 | 20 |  | 10.8924 | 0 | 10.8924 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7873 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 1 | 889 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6198 | 19.9229 | 16.9663 | 19.6231 | 19.9229 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7872 | 0 | 0 | 19.9229 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 2 | 890 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5379 | 19.841 | 16.869 | 19.5259 | 19.841 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7871 | 0 | 0 | 19.841 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 3 | 891 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4523 | 19.7553 | 16.7711 | 19.4279 | 19.7553 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7870 | 0 | 0 | 19.7553 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 4 | 892 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3665 | 19.6696 | 16.6849 | 19.3418 | 19.6696 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7869 | 0 | 0 | 19.6696 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 5 | 893 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2798 | 19.5829 | 16.5949 | 19.2517 | 19.5829 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7868 | 0 | 0 | 19.5829 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 6 | 894 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1802 | 19.4833 | 16.4538 | 19.1106 | 19.4833 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7867 | 0 | 0 | 19.4833 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 7 | 895 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0825 | 19.3856 | 16.3619 | 19.0188 | 19.3856 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7866 | 0 | 0 | 19.3856 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 8 | 896 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.0061 | 19.3082 | 16.2949 | 18.9527 | 20 |  | 256.4263 | 0 | 256.4263 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7865 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 9 | 897 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 207.1611 | 0 | 162.3957 | 0 | 202.8917 | 0 | 86.7629 | 0 | 659.2115 | 0 | 15.3212 | 0 | 9.0191 | 0 | 9.8666 | 0 | 4.8186 | 13.0992 | 52.1247 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6145 | 19.9165 | 16.8764 | 19.5342 | 20 |  | 30.9327 | 0 | 30.9327 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7864 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 10 | 898 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 726.7115 | 0 | 438.0024 | 0 | 956.3206 | 0 | 408.9529 | 0 | 2529.9874 | 0 | 53.7461 | 0 | 24.3256 | 0 | 46.5058 | 0 | 22.7123 | 61.1294 | 208.4192 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6157 | 19.9178 | 16.8629 | 19.5206 | 20 |  | 30.4642 | 0 | 30.4642 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7863 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 11 | 899 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 966.647 | 0 | 570.6426 | 0 | 1290.6952 | 0 | 551.1584 | 0 | 3379.1431 | 0 | 71.4913 | 0 | 31.6921 | 0 | 62.7664 | 0 | 30.61 | 82.9613 | 279.5211 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.614 | 19.9161 | 16.8464 | 19.5042 | 20 |  | 31.1025 | 0 | 31.1025 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7862 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 12 | 900 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2167.2576 | 0 | 1290.686 | 0 | 2927.059 | 0 | 1235.7171 | 0 | 7620.7197 | 0 | 160.2861 | 0 | 71.6816 | 0 | 142.3427 | 0 | 68.6287 | 183.3881 | 626.3272 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.639 | 19.9411 | 16.9153 | 19.5731 | 20 |  | 21.8384 | 0 | 21.8384 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7861 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 13 | 901 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8075.2895 | 0 | 10129.157 | 0 | 18576.1441 | 0 | 4604.3318 | 0 | 41384.9224 | 0 | 597.2324 | 0 | 562.549 | 0 | 903.3566 | 0 | 255.7135 | 751.0181 | 3069.8696 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7443 | 20.0463 | 17.0455 | 19.7033 | 20.0463 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7860 | 0 | 0 | 20.0463 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 14 | 902 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9133.0922 | 0 | 12968.4572 | 0 | 31429.0131 | 0 | 5207.4648 | 0 | 58738.0274 | 0 | 675.4654 | 0 | 720.2369 | 0 | 1528.3907 | 0 | 289.2101 | 947.5054 | 4160.8084 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8425 | 20.1445 | 17.1505 | 19.8083 | 20.1445 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7859 | 0 | 0 | 20.1445 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 15 | 903 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8397.5619 | 0 | 11764.2192 | 0 | 42071.8418 | 0 | 4788.0836 | 0 | 67021.7065 | 0 | 621.0671 | 0 | 653.3564 | 0 | 2045.9508 | 0 | 265.9186 | 899.4751 | 4485.768 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.963 | 20.2651 | 17.2678 | 19.9256 | 20.2651 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7858 | 0 | 0 | 20.2651 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 16 | 904 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6428.0777 | 0 | 6589.6987 | 0 | 37927.8214 | 0 | 3665.132 | 0 | 54610.7298 | 0 | 475.4079 | 0 | 365.976 | 0 | 1844.4273 | 0 | 203.5526 | 654.9576 | 3544.3214 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0431 | 20.3452 | 17.3331 | 19.9909 | 20.3452 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7857 | 0 | 0 | 20.3452 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 17 | 905 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2974.4572 | 0 | 1695.9624 | 0 | 10980.8849 | 0 | 1725.1918 | 0 | 17376.4963 | 0 | 219.985 | 0 | 94.1897 | 0 | 533.9997 | 0 | 95.813 | 253.2503 | 1197.2376 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0115 | 20.3136 | 17.286 | 19.9438 | 20.3136 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7856 | 0 | 0 | 20.3136 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 18 | 906 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 303.7367 | 0 | 173.1832 | 0 | 404.9822 | 0 | 173.1832 | 0 | 1055.0853 | 0 | 22.4638 | 0 | 9.6182 | 0 | 19.6943 | 0 | 9.6182 | 26.1983 | 87.5927 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9593 | 20.2624 | 17.2253 | 19.8822 | 20.2624 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7855 | 0 | 0 | 20.2624 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 19 | 907 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9046 | 20.2076 | 17.1692 | 19.8261 | 20.2076 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7854 | 0 | 0 | 20.2076 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 20 | 908 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8294 | 20.1325 | 17.0281 | 19.685 | 20.1325 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7853 | 0 | 0 | 20.1325 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 21 | 909 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7623 | 20.0653 | 16.9867 | 19.6435 | 20.0653 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7852 | 0 | 0 | 20.0653 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 22 | 910 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7003 | 20.0034 | 16.9414 | 19.5982 | 20.0034 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7851 | 0 | 0 | 20.0034 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 23 | 911 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6371 | 19.9402 | 16.8741 | 19.531 | 20 |  | 22.1779 | 0 | 22.1779 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7850 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 7 | 24 | 912 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6338 | 19.9369 | 16.8709 | 19.5278 | 20 |  | 23.412 | 0 | 23.412 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7849 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 1 | 913 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5842 | 19.8873 | 16.8162 | 19.473 | 19.8873 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7848 | 0 | 0 | 19.8873 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 2 | 914 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.468 | 19.7711 | 16.6886 | 19.3454 | 19.7711 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7847 | 0 | 0 | 19.7711 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 3 | 915 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.321 | 19.624 | 16.4422 | 19.099 | 19.624 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7846 | 0 | 0 | 19.624 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 4 | 916 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1836 | 19.4866 | 16.3355 | 18.9924 | 19.4866 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7845 | 0 | 0 | 19.4866 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 5 | 917 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0603 | 19.3633 | 16.2574 | 18.9142 | 19.3633 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7844 | 0 | 0 | 19.3633 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 6 | 918 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9245 | 19.2275 | 16.0811 | 18.738 | 19.2275 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7843 | 0 | 0 | 19.2275 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 7 | 919 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8055 | 19.1085 | 16.0161 | 18.6729 | 19.1085 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7842 | 0 | 0 | 19.1085 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 8 | 920 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6988 | 19.0008 | 15.8811 | 18.5389 | 20 |  | 370.3411 | 0 | 370.3411 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7841 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 9 | 921 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1797.6831 | 0 | 2031.907 | 0 | 701.5262 | 0 | 299.9947 | 0 | 4831.1111 | 0 | 132.9531 | 0 | 112.8472 | 0 | 34.1152 | 0 | 16.661 | 61.1294 | 357.7058 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5904 | 19.8925 | 16.7257 | 19.3835 | 20 |  | 39.8591 | 0 | 39.8591 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7840 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 10 | 922 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6799.3557 | 0 | 12239.2124 | 0 | 4504.7507 | 0 | 1926.3736 | 0 | 25469.6923 | 0 | 502.8669 | 0 | 679.7364 | 0 | 219.0657 | 0 | 106.9862 | 327.4788 | 1836.1339 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6669 | 19.969 | 16.8601 | 19.5179 | 20 |  | 11.5077 | 0 | 11.5077 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7839 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 11 | 923 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6450.5136 | 0 | 16135.7426 | 0 | 9694.1304 | 0 | 3677.9244 | 0 | 35958.311 | 0 | 477.0672 | 0 | 896.1403 | 0 | 471.4249 | 0 | 204.2631 | 668.0568 | 2716.9522 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7018 | 20.0038 | 16.9092 | 19.567 | 20.0038 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7838 | 0 | 0 | 20.0038 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 12 | 924 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7157.757 | 0 | 53217.7189 | 0 | 42704.144 | 0 | 4081.1773 | 0 | 107160.7972 | 0 | 529.3735 | 0 | 2955.5839 | 0 | 2076.6996 | 0 | 226.6588 | 1515.1353 | 7303.4511 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9235 | 20.2256 | 17.1748 | 19.8326 | 20.2256 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7837 | 0 | 0 | 20.2256 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 13 | 925 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6626.1984 | 0 | 5260.8639 | 0 | 10925.0716 | 0 | 3778.0956 | 0 | 26590.2294 | 0 | 490.0605 | 0 | 292.1757 | 0 | 531.2855 | 0 | 209.8263 | 571.9963 | 2095.3443 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8916 | 20.1937 | 17.0694 | 19.7272 | 20.1937 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7836 | 0 | 0 | 20.1937 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 14 | 926 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3331.4361 | 0 | 1971.8591 | 0 | 4621.3249 | 0 | 1899.503 | 0 | 11824.1231 | 0 | 246.3864 | 0 | 109.5123 | 0 | 224.7347 | 0 | 105.4938 | 279.4486 | 965.5758 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8037 | 20.1058 | 16.936 | 19.5938 | 20.1058 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7835 | 0 | 0 | 20.1058 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 15 | 927 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8614.4885 | 0 | 13599.8668 | 0 | 50011.7494 | 0 | 4911.7698 | 0 | 77137.8745 | 0 | 637.1105 | 0 | 755.3038 | 0 | 2432.0679 | 0 | 272.7879 | 995.5356 | 5092.8057 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9275 | 20.2295 | 17.1418 | 19.7996 | 20.2295 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7834 | 0 | 0 | 20.2295 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 16 | 928 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5566.0519 | 0 | 4245.3841 | 0 | 18259.9366 | 0 | 3173.6261 | 0 | 31244.9987 | 0 | 411.6542 | 0 | 235.7784 | 0 | 887.9795 | 0 | 176.2555 | 497.7678 | 2209.4354 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9168 | 20.2189 | 17.1237 | 19.7815 | 20.2189 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7833 | 0 | 0 | 20.2189 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 17 | 929 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2283.9899 | 0 | 1302.275 | 0 | 3971.819 | 0 | 1307.0331 | 0 | 8865.117 | 0 | 168.9194 | 0 | 72.3252 | 0 | 193.1493 | 0 | 72.5895 | 192.1209 | 699.1042 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8377 | 20.1397 | 17.0311 | 19.6889 | 20.1397 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7832 | 0 | 0 | 20.1397 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 18 | 930 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 120.0693 | 0 | 68.4606 | 0 | 2936.4099 | 0 | 349.9333 | 0 | 3474.873 | 0 | 8.8801 | 0 | 3.8021 | 0 | 142.7974 | 0 | 19.4345 | 26.1983 | 201.1124 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7666 | 20.0697 | 16.9495 | 19.6064 | 20.0697 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7831 | 0 | 0 | 20.0697 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 19 | 931 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6809 | 19.9839 | 16.8455 | 19.5023 | 20 |  | 5.9554 | 0 | 5.9554 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7830 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 20 | 932 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6046 | 19.9077 | 16.7477 | 19.4046 | 20 |  | 34.2397 | 0 | 34.2397 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7829 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 21 | 933 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6192 | 19.9223 | 16.8093 | 19.4662 | 20 |  | 28.8258 | 0 | 28.8258 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7828 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 22 | 934 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6201 | 19.9232 | 16.8132 | 19.47 | 20 |  | 28.4875 | 0 | 28.4875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7827 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 23 | 935 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6165 | 19.9195 | 16.7978 | 19.4546 | 20 |  | 29.841 | 0 | 29.841 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7826 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 8 | 24 | 936 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6083 | 19.9113 | 16.7631 | 19.42 | 20 |  | 32.8863 | 0 | 32.8863 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7825 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 1 | 937 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.565 | 19.8681 | 16.7353 | 19.3922 | 19.8681 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7824 | 0 | 0 | 19.8681 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 2 | 938 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4271 | 19.7302 | 16.5778 | 19.2346 | 19.7302 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7823 | 0 | 0 | 19.7302 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 3 | 939 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2942 | 19.5972 | 16.4606 | 19.1175 | 19.5972 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7822 | 0 | 0 | 19.5972 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 4 | 940 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1516 | 19.4546 | 16.2867 | 18.9435 | 19.4546 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7821 | 0 | 0 | 19.4546 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 5 | 941 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0167 | 19.3198 | 16.1766 | 18.8334 | 19.3198 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7820 | 0 | 0 | 19.3198 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 6 | 942 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8822 | 19.1853 | 16.0431 | 18.7 | 19.1853 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7819 | 0 | 0 | 19.1853 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 7 | 943 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7445 | 19.0476 | 15.8947 | 18.5515 | 19.0476 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7818 | 0 | 0 | 19.0476 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 8 | 944 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6308 | 18.9328 | 15.7884 | 18.4462 | 20 |  | 395.5528 | 0 | 395.5528 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7817 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 9 | 945 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7784.6576 | 0 | 9675.4204 | 0 | 1414.3278 | 0 | 604.8112 | 0 | 19479.217 | 0 | 575.7379 | 0 | 537.3495 | 0 | 68.7787 | 0 | 33.5898 | 109.1596 | 1324.6154 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6359 | 19.938 | 16.7824 | 19.4402 | 20 |  | 22.9972 | 0 | 22.9972 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7816 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 10 | 946 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8381.3775 | 0 | 15830.7236 | 0 | 5019.62 | 0 | 2146.548 | 0 | 31378.2691 | 0 | 619.8701 | 0 | 879.2003 | 0 | 244.1038 | 0 | 119.2141 | 388.6082 | 2250.9964 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6764 | 19.9784 | 16.8429 | 19.5007 | 20 |  | 7.9898 | 0 | 7.9898 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7815 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 11 | 947 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5833.2522 | 0 | 10720.4277 | 0 | 8380.4621 | 0 | 3325.9771 | 0 | 28260.1192 | 0 | 431.4158 | 0 | 595.3867 | 0 | 407.5413 | 0 | 184.7168 | 545.798 | 2164.8586 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6761 | 19.9782 | 16.8722 | 19.53 | 20 |  | 8.0769 | 0 | 8.0769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7814 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 12 | 948 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6394.9373 | 0 | 6591.617 | 0 | 10499.2062 | 0 | 3646.2362 | 0 | 27131.9967 | 0 | 472.9569 | 0 | 366.0825 | 0 | 510.5757 | 0 | 202.5032 | 571.9963 | 2124.1146 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6747 | 19.9767 | 16.8766 | 19.5344 | 20 |  | 8.6223 | 0 | 8.6223 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7813 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 13 | 949 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7554.7922 | 0 | 7187.4307 | 0 | 14121.9414 | 0 | 4307.5569 | 0 | 33171.7212 | 0 | 558.7375 | 0 | 399.1726 | 0 | 686.749 | 0 | 239.2313 | 681.1559 | 2565.0464 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6795 | 19.9816 | 16.8372 | 19.495 | 20 |  | 6.8174 | 0 | 6.8174 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7812 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 14 | 950 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9301.8408 | 0 | 12728.4978 | 0 | 30807.3964 | 0 | 5303.6811 | 0 | 58141.4161 | 0 | 687.9457 | 0 | 706.9101 | 0 | 1498.1616 | 0 | 294.5537 | 956.2381 | 4143.8092 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7697 | 20.0717 | 16.9909 | 19.6487 | 20.0717 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7811 | 0 | 0 | 20.0717 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 15 | 951 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7654.5287 | 0 | 7413.9955 | 0 | 23757.3525 | 0 | 4364.4243 | 0 | 43190.301 | 0 | 566.1138 | 0 | 411.7555 | 0 | 1155.3184 | 0 | 242.3896 | 716.087 | 3091.6643 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7967 | 20.0988 | 17.0136 | 19.6713 | 20.0988 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7810 | 0 | 0 | 20.0988 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 16 | 952 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5069.4838 | 0 | 3253.305 | 0 | 10457.3525 | 0 | 2890.4952 | 0 | 21670.6365 | 0 | 374.929 | 0 | 180.6807 | 0 | 508.5403 | 0 | 160.5311 | 436.6384 | 1661.3196 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7558 | 20.0578 | 16.9521 | 19.6099 | 20.0578 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7809 | 0 | 0 | 20.0578 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 17 | 953 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2176.255 | 0 | 1240.8472 | 0 | 3672.432 | 0 | 1245.5822 | 0 | 8335.1164 | 0 | 160.9515 | 0 | 68.9137 | 0 | 178.5901 | 0 | 69.1766 | 183.3881 | 661.0201 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6639 | 19.966 | 16.818 | 19.4757 | 20 |  | 12.6205 | 0 | 12.6205 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7808 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 18 | 954 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 219.4624 | 0 | 125.1321 | 0 | 4711.71 | 0 | 578.7539 | 0 | 5635.0583 | 0 | 16.231 | 0 | 6.9495 | 0 | 229.1301 | 0 | 32.1426 | 48.0302 | 332.4835 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6216 | 19.9247 | 16.7675 | 19.4243 | 20 |  | 27.9338 | 0 | 27.9338 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7807 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 19 | 955 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6037 | 19.9067 | 16.7439 | 19.4007 | 20 |  | 34.5781 | 0 | 34.5781 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7806 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 20 | 956 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6028 | 19.9058 | 16.7401 | 19.3969 | 20 |  | 34.9165 | 0 | 34.9165 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7805 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 21 | 957 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6028 | 19.9058 | 16.7401 | 19.3969 | 20 |  | 34.9165 | 0 | 34.9165 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7804 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 22 | 958 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6037 | 19.9067 | 16.7439 | 19.4007 | 20 |  | 34.5781 | 0 | 34.5781 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7803 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 23 | 959 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5991 | 19.9022 | 16.7247 | 19.3815 | 20 |  | 36.2699 | 0 | 36.2699 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7802 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 9 | 24 | 960 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5946 | 19.8976 | 16.7054 | 19.3623 | 20 |  | 37.9618 | 0 | 37.9618 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7801 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 1 | 961 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5459 | 19.8489 | 16.6545 | 19.3113 | 19.8489 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7800 | 0 | 0 | 19.8489 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 2 | 962 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4036 | 19.7066 | 16.5401 | 19.197 | 19.7066 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7799 | 0 | 0 | 19.7066 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 3 | 963 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2499 | 19.5529 | 16.3495 | 19.0063 | 19.5529 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7798 | 0 | 0 | 19.5529 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 4 | 964 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1022 | 19.4053 | 16.221 | 18.8779 | 19.4053 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7797 | 0 | 0 | 19.4053 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 5 | 965 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9496 | 19.2526 | 16.0522 | 18.709 | 19.2526 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7796 | 0 | 0 | 19.2526 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 6 | 966 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7929 | 19.096 | 15.8824 | 18.5392 | 19.096 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7795 | 0 | 0 | 19.096 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 7 | 967 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6415 | 18.9445 | 15.7473 | 18.4041 | 18.9445 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7794 | 0 | 0 | 18.9445 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 8 | 968 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.5401 | 18.8432 | 15.6526 | 18.3094 | 20 |  | 428.9366 | 0 | 428.9366 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7793 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 9 | 969 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 195.0849 | 0 | 143.9274 | 0 | 203.2032 | 0 | 86.8961 | 0 | 629.1115 | 0 | 14.4281 | 0 | 7.9934 | 0 | 9.8818 | 0 | 4.826 | 13.0992 | 50.2284 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5964 | 19.8995 | 16.7072 | 19.3641 | 20 |  | 37.2824 | 0 | 37.2824 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7792 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 10 | 970 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3224.3231 | 0 | 3978.872 | 0 | 3082.0438 | 0 | 1317.9793 | 0 | 11603.2182 | 0 | 238.4645 | 0 | 220.977 | 0 | 149.8796 | 0 | 73.1974 | 205.2201 | 887.7385 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6374 | 19.9404 | 16.7771 | 19.4339 | 20 |  | 22.0871 | 0 | 22.0871 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7791 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 11 | 971 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4114.297 | 0 | 3815.2356 | 0 | 5596.3698 | 0 | 2345.8711 | 0 | 15871.7736 | 0 | 304.2853 | 0 | 211.889 | 0 | 272.1511 | 0 | 130.284 | 353.6771 | 1272.2865 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6554 | 19.9585 | 16.8125 | 19.4694 | 20 |  | 15.4038 | 0 | 15.4038 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7790 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 12 | 972 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7220.01 | 0 | 9261.1654 | 0 | 13046.0931 | 0 | 4116.6724 | 0 | 33643.9408 | 0 | 533.9776 | 0 | 514.3428 | 0 | 634.4306 | 0 | 228.6301 | 681.1559 | 2592.5371 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7169 | 20.02 | 16.9056 | 19.5624 | 20.02 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7789 | 0 | 0 | 20.02 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 13 | 973 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7380.8247 | 0 | 6558.7155 | 0 | 13137.1574 | 0 | 4208.365 | 0 | 31285.0626 | 0 | 545.8712 | 0 | 364.2553 | 0 | 638.8591 | 0 | 233.7225 | 654.9576 | 2437.6656 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7318 | 20.0348 | 16.9258 | 19.5827 | 20.0348 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7788 | 0 | 0 | 20.0348 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 14 | 974 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3924.5873 | 0 | 2331.5514 | 0 | 5465.3803 | 0 | 2237.7033 | 0 | 13959.2222 | 0 | 290.2547 | 0 | 129.4887 | 0 | 265.7811 | 0 | 124.2766 | 327.4788 | 1137.28 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6971 | 20.0002 | 16.8945 | 19.5513 | 20.0002 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7787 | 0 | 0 | 20.0002 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 15 | 975 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3170.58 | 0 | 1862.0276 | 0 | 4469.0237 | 0 | 1807.7868 | 0 | 11309.4181 | 0 | 234.4898 | 0 | 103.4125 | 0 | 217.3283 | 0 | 100.4001 | 266.3494 | 921.9802 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.657 | 19.96 | 16.8613 | 19.5181 | 20 |  | 14.8292 | 0 | 14.8292 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7786 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 16 | 976 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3342.7197 | 0 | 1956.0989 | 0 | 4972.5304 | 0 | 1905.9367 | 0 | 12177.2857 | 0 | 247.2209 | 0 | 108.637 | 0 | 241.8138 | 0 | 105.8511 | 279.4486 | 982.9715 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6611 | 19.9641 | 16.8712 | 19.5281 | 20 |  | 13.297 | 0 | 13.297 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7785 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 17 | 977 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1695.9822 | 0 | 967.0074 | 0 | 2706.7931 | 0 | 970.2104 | 0 | 6339.9932 | 0 | 125.4315 | 0 | 53.7053 | 0 | 131.6312 | 0 | 53.8831 | 144.0907 | 508.7417 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6432 | 19.9462 | 16.8506 | 19.5075 | 20 |  | 19.9469 | 0 | 19.9469 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7784 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 18 | 978 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 179.8176 | 0 | 102.5276 | 0 | 1136.7862 | 0 | 195.7825 | 0 | 1614.9138 | 0 | 13.299 | 0 | 5.6941 | 0 | 55.2818 | 0 | 10.8733 | 13.0992 | 98.2474 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6275 | 19.9305 | 16.8293 | 19.4861 | 20 |  | 25.7592 | 0 | 25.7592 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7783 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 19 | 979 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6219 | 19.925 | 16.8209 | 19.4777 | 20 |  | 27.8107 | 0 | 27.8107 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7782 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 20 | 980 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6274 | 19.9305 | 16.844 | 19.5008 | 20 |  | 25.7805 | 0 | 25.7805 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7781 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 21 | 981 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6329 | 19.9359 | 16.8671 | 19.5239 | 20 |  | 23.7503 | 0 | 23.7503 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7780 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 22 | 982 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6393 | 19.9423 | 16.894 | 19.5508 | 20 |  | 21.3818 | 0 | 21.3818 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7779 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 23 | 983 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6448 | 19.9478 | 16.9171 | 19.5739 | 20 |  | 19.3516 | 0 | 19.3516 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7778 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 10 | 24 | 984 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6484 | 19.9515 | 16.9325 | 19.5893 | 20 |  | 17.9981 | 0 | 17.9981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7777 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 1 | 985 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6025 | 19.9055 | 16.8931 | 19.55 | 19.9055 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7776 | 0 | 0 | 19.9055 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 2 | 986 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5089 | 19.8119 | 16.8023 | 19.4592 | 19.8119 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7775 | 0 | 0 | 19.8119 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 3 | 987 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4162 | 19.7193 | 16.7124 | 19.3693 | 19.7193 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7774 | 0 | 0 | 19.7193 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 4 | 988 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3244 | 19.6275 | 16.6234 | 19.2802 | 19.6275 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7773 | 0 | 0 | 19.6275 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 5 | 989 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2336 | 19.5366 | 16.5352 | 19.192 | 19.5366 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7772 | 0 | 0 | 19.5366 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 6 | 990 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1417 | 19.4448 | 16.4401 | 19.097 | 19.4448 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7771 | 0 | 0 | 19.4448 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 7 | 991 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0498 | 19.3529 | 16.348 | 19.0048 | 19.3529 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7770 | 0 | 0 | 19.3529 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 8 | 992 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.0048 | 19.3078 | 16.2991 | 18.9559 | 20 |  | 256.6425 | 0 | 256.6425 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7769 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 9 | 993 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 193.1894 | 0 | 140.8427 | 0 | 203.2696 | 0 | 86.9245 | 0 | 624.2263 | 0 | 14.2879 | 0 | 7.8221 | 0 | 9.885 | 0 | 4.8276 | 13.0992 | 49.9217 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6448 | 19.9478 | 16.9112 | 19.568 | 20 |  | 19.3541 | 0 | 19.3541 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7768 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 10 | 994 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6317.3055 | 0 | 10895.9023 | 0 | 4190.3117 | 0 | 1791.9096 | 0 | 23195.4292 | 0 | 467.2154 | 0 | 605.1322 | 0 | 203.7746 | 0 | 99.5183 | 314.3797 | 1690.0202 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7146 | 20.0177 | 16.9948 | 19.6516 | 20.0177 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7767 | 0 | 0 | 20.0177 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 11 | 995 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3617.6856 | 0 | 2524.1698 | 0 | 4855.4715 | 0 | 2062.7155 | 0 | 13060.0425 | 0 | 267.5569 | 0 | 140.1863 | 0 | 236.1212 | 0 | 114.5583 | 301.2805 | 1059.7032 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.704 | 20.007 | 16.987 | 19.6438 | 20.007 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7766 | 0 | 0 | 20.007 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 12 | 996 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5676.2741 | 0 | 4513.0764 | 0 | 8410.5217 | 0 | 3236.4721 | 0 | 21836.3443 | 0 | 419.806 | 0 | 250.6454 | 0 | 409.0031 | 0 | 179.7459 | 484.6686 | 1743.869 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7208 | 20.0238 | 17.0096 | 19.6664 | 20.0238 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7765 | 0 | 0 | 20.0238 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 13 | 997 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6885.2421 | 0 | 5391.1767 | 0 | 11230.322 | 0 | 3925.7959 | 0 | 27432.5367 | 0 | 509.2189 | 0 | 299.413 | 0 | 546.1298 | 0 | 218.0293 | 593.8282 | 2166.6191 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7546 | 20.0576 | 17.0456 | 19.7024 | 20.0576 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7764 | 0 | 0 | 20.0576 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 14 | 998 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3760.9304 | 0 | 2228.4379 | 0 | 5222.8742 | 0 | 2144.3902 | 0 | 13356.6327 | 0 | 278.151 | 0 | 123.7621 | 0 | 253.988 | 0 | 119.0943 | 314.3797 | 1089.375 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.739 | 20.042 | 17.0032 | 19.66 | 20.042 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7763 | 0 | 0 | 20.042 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 15 | 999 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2423.9332 | 0 | 1413.2082 | 0 | 3370.9569 | 0 | 1382.0672 | 0 | 8590.1654 | 0 | 179.2693 | 0 | 78.4862 | 0 | 163.9294 | 0 | 76.7567 | 205.2201 | 703.6616 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7005 | 20.0035 | 16.936 | 19.5928 | 20.0035 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7762 | 0 | 0 | 20.0035 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 16 | 1000 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2428.0316 | 0 | 1410.1995 | 0 | 3504.8478 | 0 | 1384.404 | 0 | 8727.4829 | 0 | 179.5724 | 0 | 78.3191 | 0 | 170.4405 | 0 | 76.8865 | 205.2201 | 710.4385 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6536 | 19.9567 | 16.8609 | 19.5178 | 20 |  | 16.0547 | 0 | 16.0547 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7761 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 17 | 1001 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 554.2191 | 0 | 316.0021 | 0 | 785.3601 | 0 | 316.3861 | 0 | 1971.9674 | 0 | 40.9889 | 0 | 17.55 | 0 | 38.192 | 0 | 17.5713 | 48.0302 | 162.3325 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6259 | 19.9289 | 16.8189 | 19.4757 | 20 |  | 26.3532 | 0 | 26.3532 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7760 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 18 | 1002 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7759 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 19 | 1003 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6146 | 19.9177 | 16.7901 | 19.4469 | 20 |  | 30.5177 | 0 | 30.5177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7758 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 20 | 1004 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6156 | 19.9186 | 16.7939 | 19.4508 | 20 |  | 30.1793 | 0 | 30.1793 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7757 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 21 | 1005 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.611 | 19.914 | 16.7747 | 19.4315 | 20 |  | 31.8712 | 0 | 31.8712 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7756 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 22 | 1006 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6119 | 19.915 | 16.7785 | 19.4354 | 20 |  | 31.5328 | 0 | 31.5328 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7755 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 23 | 1007 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6119 | 19.915 | 16.7785 | 19.4354 | 20 |  | 31.5328 | 0 | 31.5328 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7754 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 11 | 24 | 1008 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.611 | 19.914 | 16.7747 | 19.4315 | 20 |  | 31.8712 | 0 | 31.8712 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7753 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 1 | 1009 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5596 | 19.8626 | 16.7122 | 19.3691 | 19.8626 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7752 | 0 | 0 | 19.8626 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 2 | 1010 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4162 | 19.7193 | 16.5494 | 19.2063 | 19.7193 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7751 | 0 | 0 | 19.7193 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 3 | 1011 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2697 | 19.5727 | 16.3924 | 19.0493 | 19.5727 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7750 | 0 | 0 | 19.5727 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 4 | 1012 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1282 | 19.4313 | 16.267 | 18.9238 | 19.4313 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7749 | 0 | 0 | 19.4313 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 5 | 1013 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9899 | 19.293 | 16.1387 | 18.7956 | 19.293 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7748 | 0 | 0 | 19.293 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 6 | 1014 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.853 | 19.156 | 16.0059 | 18.6627 | 19.156 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7747 | 0 | 0 | 19.156 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 7 | 1015 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7174 | 19.0204 | 15.8743 | 18.5311 | 19.0204 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7746 | 0 | 0 | 19.0204 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 8 | 1016 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6047 | 18.9068 | 15.7661 | 18.4239 | 20 |  | 405.2076 | 0 | 405.2076 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7745 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 9 | 1017 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 853.569 | 0 | 731.9412 | 0 | 696.7776 | 0 | 297.9641 | 0 | 2580.2519 | 0 | 63.1283 | 0 | 40.6503 | 0 | 33.8842 | 0 | 16.5482 | 48.0302 | 202.2412 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5906 | 19.8927 | 16.7496 | 19.4074 | 20 |  | 39.7717 | 0 | 39.7717 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7744 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 10 | 1018 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5027.1906 | 0 | 7532.5809 | 0 | 3940.0229 | 0 | 1684.8782 | 0 | 18184.6726 | 0 | 371.8011 | 0 | 418.3414 | 0 | 191.603 | 0 | 93.5741 | 279.4486 | 1354.7682 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6426 | 19.9446 | 16.8244 | 19.4822 | 20 |  | 20.521 | 0 | 20.521 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7743 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 11 | 1019 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6352.8497 | 0 | 11962.7953 | 0 | 8995.5347 | 0 | 3622.2389 | 0 | 30933.4186 | 0 | 469.8442 | 0 | 664.3848 | 0 | 437.4522 | 0 | 201.1704 | 606.9274 | 2379.7791 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6864 | 19.9885 | 16.8912 | 19.549 | 20 |  | 4.2535 | 0 | 4.2535 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7742 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 12 | 1020 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5693.0359 | 0 | 4430.7528 | 0 | 8366.4311 | 0 | 3246.0292 | 0 | 21736.2489 | 0 | 421.0457 | 0 | 246.0733 | 0 | 406.859 | 0 | 180.2766 | 484.6686 | 1738.9232 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6675 | 19.9696 | 16.8991 | 19.5569 | 20 |  | 11.286 | 0 | 11.286 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7741 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 13 | 1021 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6582.2149 | 0 | 4776.3631 | 0 | 10204.5495 | 0 | 3753.0173 | 0 | 25316.1449 | 0 | 486.8076 | 0 | 265.2677 | 0 | 496.2465 | 0 | 208.4335 | 558.8972 | 2015.6525 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6787 | 19.9808 | 16.9131 | 19.5709 | 20 |  | 7.1177 | 0 | 7.1177 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7740 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 14 | 1022 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6153.779 | 0 | 3885.746 | 0 | 9139.4933 | 0 | 3508.7337 | 0 | 22687.7519 | 0 | 455.1213 | 0 | 215.805 | 0 | 444.4529 | 0 | 194.8666 | 510.8669 | 1821.1128 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6761 | 19.9782 | 16.9283 | 19.5861 | 20 |  | 8.0703 | 0 | 8.0703 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7739 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 15 | 1023 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4691.7144 | 0 | 2783.0841 | 0 | 6739.0695 | 0 | 2675.1003 | 0 | 16888.9684 | 0 | 346.9899 | 0 | 154.5658 | 0 | 327.7205 | 0 | 148.5686 | 388.6082 | 1366.453 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6643 | 19.9664 | 16.9343 | 19.5921 | 20 |  | 12.4534 | 0 | 12.4534 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7738 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 16 | 1024 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3340.2201 | 0 | 1950.1106 | 0 | 4930.8512 | 0 | 1904.5115 | 0 | 12125.6934 | 0 | 247.0361 | 0 | 108.3044 | 0 | 239.787 | 0 | 105.772 | 279.4486 | 980.348 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6538 | 19.9559 | 16.9358 | 19.5936 | 20 |  | 16.3559 | 0 | 16.3559 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7737 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 17 | 1025 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2602.9755 | 0 | 1484.1527 | 0 | 4392.3033 | 0 | 1492.8151 | 0 | 9972.2468 | 0 | 192.5109 | 0 | 82.4263 | 0 | 213.5974 | 0 | 82.9074 | 218.3192 | 789.7612 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6475 | 19.9495 | 16.9295 | 19.5873 | 20 |  | 18.7 | 0 | 18.7 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7736 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 18 | 1026 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 342.0042 | 0 | 195.0024 | 0 | 1126.0079 | 0 | 266.4946 | 0 | 1929.5091 | 0 | 25.294 | 0 | 10.83 | 0 | 54.7577 | 0 | 14.8005 | 26.1983 | 131.8804 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6521 | 19.9552 | 16.9303 | 19.5871 | 20 |  | 16.6134 | 0 | 16.6134 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7735 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 19 | 1027 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6411 | 19.9442 | 16.9017 | 19.5585 | 20 |  | 20.705 | 0 | 20.705 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7734 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 20 | 1028 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6393 | 19.9423 | 16.894 | 19.5508 | 20 |  | 21.3818 | 0 | 21.3818 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7733 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 21 | 1029 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6393 | 19.9423 | 16.894 | 19.5508 | 20 |  | 21.3818 | 0 | 21.3818 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7732 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 22 | 1030 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6384 | 19.9414 | 16.8902 | 19.547 | 20 |  | 21.7201 | 0 | 21.7201 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7731 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 23 | 1031 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6384 | 19.9414 | 16.8902 | 19.547 | 20 |  | 21.7201 | 0 | 21.7201 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7730 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 12 | 24 | 1032 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6393 | 19.9423 | 16.894 | 19.5508 | 20 |  | 21.3818 | 0 | 21.3818 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7729 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 1 | 1033 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5915 | 19.8946 | 16.847 | 19.5038 | 19.8946 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7728 | 0 | 0 | 19.8946 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 2 | 1034 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4871 | 19.7901 | 16.7456 | 19.4025 | 19.7901 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7727 | 0 | 0 | 19.7901 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 3 | 1035 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3828 | 19.6858 | 16.6414 | 19.2983 | 19.6858 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7726 | 0 | 0 | 19.6858 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 4 | 1036 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2804 | 19.5834 | 16.545 | 19.2019 | 19.5834 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7725 | 0 | 0 | 19.5834 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 5 | 1037 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1799 | 19.4829 | 16.4505 | 19.1073 | 19.4829 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7724 | 0 | 0 | 19.4829 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 6 | 1038 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0812 | 19.3843 | 16.3577 | 19.0146 | 19.3843 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7723 | 0 | 0 | 19.3843 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 7 | 1039 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9826 | 19.2857 | 16.2591 | 18.9159 | 19.2857 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7722 | 0 | 0 | 19.2857 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 8 | 1040 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.9013 | 19.2033 | 16.1724 | 18.8302 | 20 |  | 295.2889 | 0 | 295.2889 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7721 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 9 | 1041 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 395.321 | 0 | 292.0045 | 0 | 405.2478 | 0 | 173.2968 | 0 | 1265.8701 | 0 | 29.2372 | 0 | 16.2172 | 0 | 19.7072 | 0 | 9.6245 | 26.1983 | 100.9844 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6146 | 19.9166 | 16.8705 | 19.5283 | 20 |  | 30.9006 | 0 | 30.9006 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7720 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 10 | 1042 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1778.9191 | 0 | 1106.0769 | 0 | 2316.4578 | 0 | 990.5905 | 0 | 6192.0443 | 0 | 131.5653 | 0 | 61.4288 | 0 | 112.6492 | 0 | 55.015 | 144.0907 | 504.749 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.634 | 19.9361 | 16.9074 | 19.5652 | 20 |  | 23.7003 | 0 | 23.7003 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7719 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 11 | 1043 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4034.8849 | 0 | 3167.1215 | 0 | 5429.0939 | 0 | 2300.5922 | 0 | 14931.6926 | 0 | 298.4121 | 0 | 175.8943 | 0 | 264.0165 | 0 | 127.7694 | 340.578 | 1206.6702 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6679 | 19.9699 | 16.9703 | 19.6281 | 20 |  | 11.1416 | 0 | 11.1416 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7718 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 12 | 1044 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5236.9423 | 0 | 3557.5707 | 0 | 7354.0801 | 0 | 2985.9759 | 0 | 19134.5689 | 0 | 387.3139 | 0 | 197.5789 | 0 | 357.6284 | 0 | 165.8339 | 436.6384 | 1544.9935 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6868 | 19.9889 | 17.0126 | 19.6704 | 20 |  | 4.1066 | 0 | 4.1066 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7717 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 13 | 1045 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5136.348 | 0 | 3106.4059 | 0 | 7096.0402 | 0 | 2928.6195 | 0 | 18267.4136 | 0 | 379.8741 | 0 | 172.5223 | 0 | 345.0799 | 0 | 162.6485 | 423.5393 | 1483.6641 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6869 | 19.9889 | 17.0215 | 19.6792 | 20 |  | 4.0999 | 0 | 4.0999 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7716 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 14 | 1046 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5737.9646 | 0 | 3450.2056 | 0 | 8093.2876 | 0 | 3271.6465 | 0 | 20553.1043 | 0 | 424.3685 | 0 | 191.6161 | 0 | 393.576 | 0 | 181.6994 | 471.5695 | 1662.8295 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6943 | 19.9964 | 17.0318 | 19.6896 | 20 |  | 1.3234 | 0 | 1.3234 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7715 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 15 | 1047 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5132.0803 | 0 | 3050.2193 | 0 | 7399.6827 | 0 | 2926.1861 | 0 | 18508.1685 | 0 | 379.5585 | 0 | 169.4018 | 0 | 359.8461 | 0 | 162.5133 | 423.5393 | 1494.859 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6884 | 19.9905 | 17.0259 | 19.6837 | 20 |  | 3.5363 | 0 | 3.5363 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7714 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 16 | 1048 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5273.4878 | 0 | 3289.593 | 0 | 10019.8575 | 0 | 3006.8132 | 0 | 21589.7515 | 0 | 390.0167 | 0 | 182.6961 | 0 | 487.265 | 0 | 166.9912 | 449.7376 | 1676.7065 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.698 | 20.0001 | 17.0384 | 19.6961 | 20.0001 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7713 | 0 | 0 | 20.0001 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 17 | 1049 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1589.0553 | 0 | 906.0403 | 0 | 2443.7978 | 0 | 909.473 | 0 | 5848.3663 | 0 | 117.5234 | 0 | 50.3193 | 0 | 118.8417 | 0 | 50.5099 | 135.3579 | 472.5522 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6465 | 19.9486 | 16.967 | 19.6248 | 20 |  | 19.0502 | 0 | 19.0502 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7712 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 18 | 1050 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 342.9788 | 0 | 195.5581 | 0 | 910.062 | 0 | 244.5189 | 0 | 1693.1178 | 0 | 25.366 | 0 | 10.8608 | 0 | 44.2563 | 0 | 13.58 | 26.1983 | 120.2614 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6606 | 19.9637 | 16.9681 | 19.6249 | 20 |  | 13.4778 | 0 | 13.4778 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7711 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 19 | 1051 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6511 | 19.9542 | 16.944 | 19.6009 | 20 |  | 16.983 | 0 | 16.983 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7710 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 20 | 1052 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6502 | 19.9533 | 16.9402 | 19.597 | 20 |  | 17.3214 | 0 | 17.3214 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7709 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 21 | 1053 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6511 | 19.9542 | 16.944 | 19.6009 | 20 |  | 16.983 | 0 | 16.983 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7708 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 22 | 1054 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6511 | 19.9542 | 16.944 | 19.6009 | 20 |  | 16.983 | 0 | 16.983 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7707 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 23 | 1055 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6484 | 19.9515 | 16.9325 | 19.5893 | 20 |  | 17.9981 | 0 | 17.9981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7706 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 13 | 24 | 1056 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6457 | 19.9487 | 16.921 | 19.5778 | 20 |  | 19.0132 | 0 | 19.0132 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7705 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 1 | 1057 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5943 | 19.8973 | 16.8585 | 19.5153 | 19.8973 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7704 | 0 | 0 | 19.8973 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 2 | 1058 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4916 | 19.7947 | 16.756 | 19.4128 | 19.7947 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7703 | 0 | 0 | 19.7947 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 3 | 1059 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3882 | 19.6912 | 16.6496 | 19.3065 | 19.6912 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7702 | 0 | 0 | 19.6912 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 4 | 1060 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2848 | 19.5879 | 16.5464 | 19.2032 | 19.5879 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7701 | 0 | 0 | 19.5879 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 5 | 1061 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1788 | 19.4818 | 16.4316 | 19.0885 | 19.4818 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7700 | 0 | 0 | 19.4818 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 6 | 1062 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0747 | 19.3777 | 16.3336 | 18.9904 | 19.3777 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7699 | 0 | 0 | 19.3777 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 7 | 1063 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.968 | 19.271 | 16.2182 | 18.875 | 19.271 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7698 | 0 | 0 | 19.271 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 8 | 1064 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8816 | 19.1837 | 16.1356 | 18.7934 | 20 |  | 302.5565 | 0 | 302.5565 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7697 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 9 | 1065 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 532.8601 | 0 | 395.8605 | 0 | 539.2894 | 0 | 230.6172 | 0 | 1698.6271 | 0 | 39.4093 | 0 | 21.9851 | 0 | 26.2256 | 0 | 12.8079 | 34.9311 | 135.359 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6124 | 19.9145 | 16.8567 | 19.5145 | 20 |  | 31.6803 | 0 | 31.6803 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7696 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 10 | 1066 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4034.5657 | 0 | 4953.3675 | 0 | 3745.3631 | 0 | 1601.6355 | 0 | 14334.9318 | 0 | 298.3885 | 0 | 275.0981 | 0 | 182.1367 | 0 | 88.951 | 253.2503 | 1097.8246 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6567 | 19.9588 | 16.9268 | 19.5846 | 20 |  | 15.2761 | 0 | 15.2761 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7695 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 11 | 1067 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5774.437 | 0 | 8858.0585 | 0 | 7981.6947 | 0 | 3292.4422 | 0 | 25906.6324 | 0 | 427.0659 | 0 | 491.9552 | 0 | 388.1493 | 0 | 182.8543 | 545.798 | 2035.8227 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6972 | 19.9993 | 16.9903 | 19.6481 | 20 |  | 0.27263 | 0 | 0.27263 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7694 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 12 | 1068 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8015.3915 | 0 | 11253.0511 | 0 | 14998.6092 | 0 | 4570.1794 | 0 | 38837.2312 | 0 | 592.8025 | 0 | 624.9674 | 0 | 729.3813 | 0 | 253.8168 | 751.0181 | 2951.986 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7404 | 20.0425 | 17.0536 | 19.7114 | 20.0425 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7693 | 0 | 0 | 20.0425 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 13 | 1069 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8340.9121 | 0 | 8186.5704 | 0 | 15888.4969 | 0 | 4755.7832 | 0 | 37171.7626 | 0 | 616.8773 | 0 | 454.6624 | 0 | 772.6565 | 0 | 264.1247 | 764.1172 | 2872.4382 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7779 | 20.0799 | 17.0898 | 19.7476 | 20.0799 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7692 | 0 | 0 | 20.0799 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 14 | 1070 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6533.0278 | 0 | 4226.9621 | 0 | 9955.6195 | 0 | 3724.972 | 0 | 24440.5813 | 0 | 483.1698 | 0 | 234.7553 | 0 | 484.1411 | 0 | 206.876 | 545.798 | 1954.7402 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7756 | 20.0777 | 17.0782 | 19.736 | 20.0777 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7691 | 0 | 0 | 20.0777 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 15 | 1071 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4086.3605 | 0 | 2407.4919 | 0 | 5797.7528 | 0 | 2329.9424 | 0 | 14621.5476 | 0 | 302.2191 | 0 | 133.7063 | 0 | 281.9443 | 0 | 129.3994 | 340.578 | 1187.8471 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7448 | 20.0469 | 17.0479 | 19.7057 | 20.0469 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7690 | 0 | 0 | 20.0469 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 16 | 1072 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2746.1825 | 0 | 1594.2106 | 0 | 3964.8726 | 0 | 1565.8058 | 0 | 9871.0715 | 0 | 203.1022 | 0 | 88.5386 | 0 | 192.8115 | 0 | 86.9611 | 231.4184 | 802.8318 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7013 | 20.0033 | 17.0084 | 19.6662 | 20.0033 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7689 | 0 | 0 | 20.0033 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 17 | 1073 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2171.5643 | 0 | 1238.1726 | 0 | 3456.8031 | 0 | 1244.7745 | 0 | 8111.3145 | 0 | 160.6046 | 0 | 68.7651 | 0 | 168.1041 | 0 | 69.1318 | 183.3881 | 649.9937 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6513 | 19.9533 | 16.9539 | 19.6117 | 20 |  | 17.2934 | 0 | 17.2934 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7688 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 18 | 1074 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 456.9421 | 0 | 260.5372 | 0 | 1187.1963 | 0 | 323.8886 | 0 | 2228.5642 | 0 | 33.7945 | 0 | 14.4696 | 0 | 57.7333 | 0 | 17.988 | 34.9311 | 158.9165 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6594 | 19.9625 | 16.9581 | 19.6149 | 20 |  | 13.9188 | 0 | 13.9188 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7687 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 19 | 1075 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6484 | 19.9515 | 16.9325 | 19.5893 | 20 |  | 17.9981 | 0 | 17.9981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7686 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 20 | 1076 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6484 | 19.9515 | 16.9325 | 19.5893 | 20 |  | 17.9981 | 0 | 17.9981 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7685 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 21 | 1077 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6448 | 19.9478 | 16.9171 | 19.5739 | 20 |  | 19.3516 | 0 | 19.3516 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7684 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 22 | 1078 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6411 | 19.9442 | 16.9017 | 19.5585 | 20 |  | 20.705 | 0 | 20.705 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7683 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 23 | 1079 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6238 | 19.9268 | 16.8286 | 19.4854 | 20 |  | 27.134 | 0 | 27.134 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7682 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 14 | 24 | 1080 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6101 | 19.9131 | 16.7708 | 19.4277 | 20 |  | 32.2095 | 0 | 32.2095 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7681 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 1 | 1081 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5541 | 19.8572 | 16.6891 | 19.346 | 19.8572 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7680 | 0 | 0 | 19.8572 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 2 | 1082 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4172 | 19.7202 | 16.5711 | 19.228 | 19.7202 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7679 | 0 | 0 | 19.7202 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 3 | 1083 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2898 | 19.5929 | 16.4742 | 19.131 | 19.5929 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7678 | 0 | 0 | 19.5929 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 4 | 1084 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1728 | 19.4758 | 16.3903 | 19.0471 | 19.4758 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7677 | 0 | 0 | 19.4758 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 5 | 1085 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.056 | 19.359 | 16.2739 | 18.9308 | 19.359 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7676 | 0 | 0 | 19.359 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 6 | 1086 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9394 | 19.2424 | 16.1578 | 18.8147 | 19.2424 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7675 | 0 | 0 | 19.2424 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 7 | 1087 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8239 | 19.127 | 16.0458 | 18.7026 | 19.127 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7674 | 0 | 0 | 19.127 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 8 | 1088 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.728 | 19.03 | 15.9479 | 18.6057 | 20 |  | 359.522 | 0 | 359.522 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7673 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 9 | 1089 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 744.3219 | 0 | 558.1935 | 0 | 739.4075 | 0 | 316.194 | 0 | 2358.1169 | 0 | 55.0486 | 0 | 31.0007 | 0 | 35.9573 | 0 | 17.5607 | 48.0302 | 187.5975 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6026 | 19.9047 | 16.8056 | 19.4634 | 20 |  | 35.3327 | 0 | 35.3327 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7672 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 10 | 1090 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2836.6812 | 0 | 2546.7823 | 0 | 3198.6223 | 0 | 1367.8319 | 0 | 9949.9177 | 0 | 209.7953 | 0 | 141.4422 | 0 | 155.5488 | 0 | 75.9661 | 205.2201 | 787.9724 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6331 | 19.9352 | 16.8652 | 19.523 | 20 |  | 24.0233 | 0 | 24.0233 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7671 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 11 | 1091 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5629.3353 | 0 | 7663.9942 | 0 | 7704.8882 | 0 | 3209.7087 | 0 | 24207.9265 | 0 | 416.3345 | 0 | 425.6398 | 0 | 374.6882 | 0 | 178.2595 | 519.5997 | 1914.5217 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.683 | 19.9851 | 16.9439 | 19.6017 | 20 |  | 5.5216 | 0 | 5.5216 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7670 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 12 | 1092 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6846.9211 | 0 | 6516.2632 | 0 | 10802.2701 | 0 | 3903.9462 | 0 | 28069.4006 | 0 | 506.3847 | 0 | 361.8976 | 0 | 525.3136 | 0 | 216.8158 | 606.9274 | 2217.3391 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7001 | 20.0022 | 16.9814 | 19.6392 | 20.0022 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7669 | 0 | 0 | 20.0022 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 13 | 1093 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8946.3195 | 0 | 10795.2971 | 0 | 19824.819 | 0 | 5100.9716 | 0 | 44667.4071 | 0 | 661.6521 | 0 | 599.5448 | 0 | 964.0796 | 0 | 283.2957 | 838.3458 | 3346.9179 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7535 | 20.0556 | 17.0458 | 19.7036 | 20.0556 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7668 | 0 | 0 | 20.0556 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 14 | 1094 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6282.6525 | 0 | 3899.0572 | 0 | 9162.9968 | 0 | 3582.2142 | 0 | 22926.9207 | 0 | 464.6525 | 0 | 216.5442 | 0 | 445.5959 | 0 | 198.9475 | 519.5997 | 1845.3399 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7421 | 20.0442 | 17.0278 | 19.6856 | 20.0442 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7667 | 0 | 0 | 20.0442 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 15 | 1095 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4686.839 | 0 | 2769.9428 | 0 | 6690.2409 | 0 | 2672.3205 | 0 | 16819.3432 | 0 | 346.6293 | 0 | 153.836 | 0 | 325.3459 | 0 | 148.4142 | 388.6082 | 1362.8337 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7129 | 20.015 | 16.9993 | 19.6571 | 20.015 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7666 | 0 | 0 | 20.015 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 16 | 1096 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3771.3433 | 0 | 2200.2732 | 0 | 5567.5477 | 0 | 2150.3273 | 0 | 13689.4915 | 0 | 278.9211 | 0 | 122.1979 | 0 | 270.7495 | 0 | 119.424 | 314.3797 | 1105.6721 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6749 | 19.977 | 16.9622 | 19.62 | 20 |  | 8.5289 | 0 | 8.5289 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7665 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 17 | 1097 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2010.9421 | 0 | 1146.5898 | 0 | 3137.2055 | 0 | 1152.5159 | 0 | 7447.2533 | 0 | 148.7253 | 0 | 63.6788 | 0 | 152.5621 | 0 | 64.008 | 170.289 | 599.2632 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6401 | 19.9422 | 16.9223 | 19.5801 | 20 |  | 21.4155 | 0 | 21.4155 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7664 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 18 | 1098 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 149.4019 | 0 | 85.1853 | 0 | 260.1854 | 0 | 91.9625 | 0 | 586.7351 | 0 | 11.0495 | 0 | 4.731 | 0 | 12.6528 | 0 | 5.1074 | 13.0992 | 46.6398 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6456 | 19.9486 | 16.9149 | 19.5718 | 20 |  | 19.0565 | 0 | 19.0565 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7663 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 19 | 1099 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6393 | 19.9423 | 16.894 | 19.5508 | 20 |  | 21.3818 | 0 | 21.3818 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7662 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 20 | 1100 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6356 | 19.9387 | 16.8786 | 19.5355 | 20 |  | 22.7352 | 0 | 22.7352 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7661 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 21 | 1101 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6347 | 19.9378 | 16.8748 | 19.5316 | 20 |  | 23.0736 | 0 | 23.0736 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7660 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 22 | 1102 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.632 | 19.935 | 16.8632 | 19.5201 | 20 |  | 24.0887 | 0 | 24.0887 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7659 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 23 | 1103 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6283 | 19.9314 | 16.8478 | 19.5047 | 20 |  | 25.4422 | 0 | 25.4422 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7658 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 15 | 24 | 1104 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6247 | 19.9277 | 16.8324 | 19.4893 | 20 |  | 26.7956 | 0 | 26.7956 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7657 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 1 | 1105 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5632 | 19.8663 | 16.7276 | 19.3845 | 19.8663 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7656 | 0 | 0 | 19.8663 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 2 | 1106 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4107 | 19.7138 | 16.5144 | 19.1713 | 19.7138 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7655 | 0 | 0 | 19.7138 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 3 | 1107 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2487 | 19.5518 | 16.3217 | 18.9785 | 19.5518 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7654 | 0 | 0 | 19.5518 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 4 | 1108 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0819 | 19.385 | 16.1391 | 18.7959 | 19.385 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7653 | 0 | 0 | 19.385 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 5 | 1109 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9167 | 19.2197 | 15.9788 | 18.6356 | 19.2197 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7652 | 0 | 0 | 19.2197 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 6 | 1110 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7576 | 19.0607 | 15.8392 | 18.4961 | 19.0607 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7651 | 0 | 0 | 19.0607 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 7 | 1111 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6038 | 18.9068 | 15.7018 | 18.3586 | 18.9068 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7650 | 0 | 0 | 18.9068 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 8 | 1112 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.4778 | 18.7799 | 15.5926 | 18.2504 | 20 |  | 452.2391 | 0 | 452.2391 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7649 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 9 | 1113 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1188.1772 | 0 | 910.5413 | 0 | 1136.141 | 0 | 485.8498 | 0 | 3720.7093 | 0 | 87.8752 | 0 | 50.5693 | 0 | 55.2505 | 0 | 26.9829 | 74.2285 | 294.9064 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5788 | 19.8809 | 16.6848 | 19.3426 | 20 |  | 44.1495 | 0 | 44.1495 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7648 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 10 | 1114 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4147.0923 | 0 | 4821.2093 | 0 | 3957.0246 | 0 | 1692.1487 | 0 | 14617.4748 | 0 | 306.7107 | 0 | 267.7584 | 0 | 192.4298 | 0 | 93.9779 | 266.3494 | 1127.2262 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6172 | 19.9193 | 16.7462 | 19.404 | 20 |  | 29.9267 | 0 | 29.9267 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7647 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 11 | 1115 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5213.0473 | 0 | 5728.4584 | 0 | 7057.3631 | 0 | 2972.3515 | 0 | 20971.2203 | 0 | 385.5467 | 0 | 318.1448 | 0 | 343.1991 | 0 | 165.0772 | 462.8367 | 1674.8045 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.64 | 19.9421 | 16.7835 | 19.4413 | 20 |  | 21.4668 | 0 | 21.4668 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7646 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 12 | 1116 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6095.5895 | 0 | 4718.7732 | 0 | 8917.9103 | 0 | 3475.5554 | 0 | 23207.8284 | 0 | 450.8177 | 0 | 262.0693 | 0 | 433.6774 | 0 | 193.024 | 519.5997 | 1859.1881 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6507 | 19.9528 | 16.8088 | 19.4666 | 20 |  | 17.4872 | 0 | 17.4872 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7645 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 13 | 1117 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6035.7475 | 0 | 3761.5904 | 0 | 8490.7614 | 0 | 3441.435 | 0 | 21729.5342 | 0 | 446.3919 | 0 | 208.9097 | 0 | 412.9051 | 0 | 191.129 | 497.7678 | 1757.1035 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6524 | 19.9544 | 16.8311 | 19.4889 | 20 |  | 16.8855 | 0 | 16.8855 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7644 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 14 | 1118 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6562.1107 | 0 | 4163.73 | 0 | 9797.5753 | 0 | 3741.5543 | 0 | 24264.9703 | 0 | 485.3207 | 0 | 231.2435 | 0 | 476.4554 | 0 | 207.7969 | 545.798 | 1946.6146 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6631 | 19.9652 | 16.8534 | 19.5112 | 20 |  | 12.9137 | 0 | 12.9137 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7643 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 15 | 1119 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7643.5995 | 0 | 5669.2504 | 0 | 16136.3436 | 0 | 4358.1927 | 0 | 33807.3862 | 0 | 565.3055 | 0 | 314.8565 | 0 | 784.7093 | 0 | 242.0435 | 681.1559 | 2588.0707 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6939 | 19.996 | 16.8956 | 19.5534 | 20 |  | 1.4829 | 0 | 1.4829 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7642 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 16 | 1120 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6616.3129 | 0 | 4968.6864 | 0 | 21880.2129 | 0 | 3772.4591 | 0 | 37237.6713 | 0 | 489.3294 | 0 | 275.9489 | 0 | 1064.0332 | 0 | 209.5133 | 606.9274 | 2645.7522 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7042 | 20.0063 | 16.9087 | 19.5665 | 20.0063 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7641 | 0 | 0 | 20.0063 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 17 | 1121 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3930.5462 | 0 | 2241.1009 | 0 | 13580.0405 | 0 | 2360.1219 | 0 | 22111.8094 | 0 | 290.6954 | 0 | 124.4653 | 0 | 660.3964 | 0 | 131.0755 | 340.578 | 1547.2106 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6649 | 19.967 | 16.864 | 19.5218 | 20 |  | 12.235 | 0 | 12.235 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7640 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 18 | 1122 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 783.8462 | 0 | 446.9299 | 0 | 2466.5611 | 0 | 607.1146 | 0 | 4304.4517 | 0 | 57.9717 | 0 | 24.8214 | 0 | 119.9487 | 0 | 33.7177 | 61.1294 | 297.5889 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6179 | 19.921 | 16.7638 | 19.4207 | 20 |  | 29.2993 | 0 | 29.2993 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7639 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 19 | 1123 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6019 | 19.9049 | 16.7362 | 19.393 | 20 |  | 35.2548 | 0 | 35.2548 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7638 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 20 | 1124 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6092 | 19.9122 | 16.767 | 19.4238 | 20 |  | 32.5479 | 0 | 32.5479 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7637 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 21 | 1125 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6073 | 19.9104 | 16.7593 | 19.4161 | 20 |  | 33.2246 | 0 | 33.2246 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7636 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 22 | 1126 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6037 | 19.9067 | 16.7439 | 19.4007 | 20 |  | 34.5781 | 0 | 34.5781 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7635 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 23 | 1127 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6019 | 19.9049 | 16.7362 | 19.393 | 20 |  | 35.2548 | 0 | 35.2548 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7634 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 16 | 24 | 1128 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6037 | 19.9067 | 16.7439 | 19.4007 | 20 |  | 34.5781 | 0 | 34.5781 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7633 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 1 | 1129 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5568 | 19.8599 | 16.7007 | 19.3575 | 19.8599 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7632 | 0 | 0 | 19.8599 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 2 | 1130 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4108 | 19.7138 | 16.5353 | 19.1921 | 19.7138 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7631 | 0 | 0 | 19.7138 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 3 | 1131 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2616 | 19.5646 | 16.3756 | 19.0325 | 19.5646 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7630 | 0 | 0 | 19.5646 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 4 | 1132 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1156 | 19.4187 | 16.2399 | 18.8968 | 19.4187 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7629 | 0 | 0 | 19.4187 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 5 | 1133 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9747 | 19.2778 | 16.1151 | 18.7719 | 19.2778 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7628 | 0 | 0 | 19.2778 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 6 | 1134 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.837 | 19.14 | 15.9874 | 18.6442 | 19.14 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7627 | 0 | 0 | 19.14 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 7 | 1135 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7024 | 19.0055 | 15.8627 | 18.5196 | 19.0055 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7626 | 0 | 0 | 19.0055 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 8 | 1136 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.6197 | 18.9227 | 15.792 | 18.4489 | 20 |  | 399.4414 | 0 | 399.4414 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7625 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 9 | 1137 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 329.8032 | 0 | 199.7056 | 0 | 416.9475 | 0 | 178.2999 | 0 | 1124.7562 | 0 | 24.3916 | 0 | 11.0912 | 0 | 20.2761 | 0 | 9.9023 | 26.1983 | 91.8595 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6115 | 19.9146 | 16.7664 | 19.4232 | 20 |  | 31.6696 | 0 | 31.6696 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7624 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 10 | 1138 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1148.0145 | 0 | 687.2045 | 0 | 1509.3998 | 0 | 645.467 | 0 | 3990.0857 | 0 | 84.9049 | 0 | 38.1657 | 0 | 73.402 | 0 | 35.8477 | 96.0605 | 328.3807 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6245 | 19.9275 | 16.7939 | 19.4507 | 20 |  | 26.876 | 0 | 26.876 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7623 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 11 | 1139 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2931.556 | 0 | 1789.9438 | 0 | 3912.6165 | 0 | 1671.5012 | 0 | 10305.6174 | 0 | 216.8121 | 0 | 99.4092 | 0 | 190.2703 | 0 | 92.8312 | 244.5175 | 843.8402 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6493 | 19.9523 | 16.839 | 19.4958 | 20 |  | 17.6764 | 0 | 17.6764 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7622 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 12 | 1140 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7558.0761 | 0 | 8066.2543 | 0 | 12448.975 | 0 | 4309.4294 | 0 | 32382.7348 | 0 | 558.9803 | 0 | 447.9803 | 0 | 605.3928 | 0 | 239.3353 | 689.8887 | 2541.5775 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7225 | 20.0256 | 16.9406 | 19.5975 | 20.0256 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7621 | 0 | 0 | 20.0256 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 13 | 1141 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10721.9795 | 0 | 21620.3211 | 0 | 35717.9834 | 0 | 6113.4093 | 0 | 74173.6933 | 0 | 792.9764 | 0 | 1200.7406 | 0 | 1736.9631 | 0 | 339.524 | 1235.6867 | 5305.8907 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.878 | 20.1811 | 17.1259 | 19.7827 | 20.1811 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7620 | 0 | 0 | 20.1811 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 14 | 1142 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8033.3255 | 0 | 6102.5772 | 0 | 14492.7836 | 0 | 4580.4049 | 0 | 33209.0912 | 0 | 594.1288 | 0 | 338.9224 | 0 | 704.7831 | 0 | 254.3847 | 702.9879 | 2595.2069 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9179 | 20.221 | 17.1747 | 19.8316 | 20.221 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7619 | 0 | 0 | 20.221 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 15 | 1143 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4519.4742 | 0 | 2662.1036 | 0 | 6413.7694 | 0 | 2576.8932 | 0 | 16172.2403 | 0 | 334.2514 | 0 | 147.8468 | 0 | 311.9012 | 0 | 143.1144 | 375.509 | 1312.6228 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9044 | 20.2074 | 17.149 | 19.8058 | 20.2074 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7618 | 0 | 0 | 20.2074 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 16 | 1144 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1584.5064 | 0 | 911.8467 | 0 | 2205.4671 | 0 | 903.4466 | 0 | 5605.2668 | 0 | 117.187 | 0 | 50.6418 | 0 | 107.2517 | 0 | 50.1753 | 135.3579 | 460.6136 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8583 | 20.1614 | 17.0979 | 19.7548 | 20.1614 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7617 | 0 | 0 | 20.1614 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 17 | 1145 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1850.7989 | 0 | 1055.2801 | 0 | 2813.5896 | 0 | 1060.67 | 0 | 6780.3386 | 0 | 136.8814 | 0 | 58.6077 | 0 | 136.8247 | 0 | 58.9071 | 157.1898 | 548.4107 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8171 | 20.1201 | 17.0609 | 19.7177 | 20.1201 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7616 | 0 | 0 | 20.1201 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 18 | 1146 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 149.5153 | 0 | 85.2499 | 0 | 237.0407 | 0 | 89.5572 | 0 | 561.3631 | 0 | 11.0579 | 0 | 4.7346 | 0 | 11.5273 | 0 | 4.9738 | 13.0992 | 45.3926 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7507 | 20.0538 | 16.9726 | 19.6294 | 20.0538 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7615 | 0 | 0 | 20.0538 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 19 | 1147 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6825 | 19.9856 | 16.9034 | 19.5602 | 20 |  | 5.3468 | 0 | 5.3468 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7614 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 20 | 1148 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6302 | 19.9332 | 16.8555 | 19.5124 | 20 |  | 24.7654 | 0 | 24.7654 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7613 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 21 | 1149 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.632 | 19.935 | 16.8632 | 19.5201 | 20 |  | 24.0887 | 0 | 24.0887 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7612 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 22 | 1150 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6201 | 19.9232 | 16.8132 | 19.47 | 20 |  | 28.4875 | 0 | 28.4875 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7611 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 23 | 1151 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6046 | 19.9077 | 16.7477 | 19.4046 | 20 |  | 34.2397 | 0 | 34.2397 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7610 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 17 | 24 | 1152 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6055 | 19.9086 | 16.7516 | 19.4084 | 20 |  | 33.9014 | 0 | 33.9014 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7609 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 1 | 1153 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.565 | 19.8681 | 16.7353 | 19.3922 | 19.8681 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7608 | 0 | 0 | 19.8681 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 2 | 1154 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4417 | 19.7448 | 16.6394 | 19.2962 | 19.7448 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7607 | 0 | 0 | 19.7448 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 3 | 1155 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3196 | 19.6226 | 16.5209 | 19.1777 | 19.6226 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7606 | 0 | 0 | 19.6226 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 4 | 1156 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1986 | 19.5017 | 16.4035 | 19.0603 | 19.5017 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7605 | 0 | 0 | 19.5017 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 5 | 1157 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0834 | 19.3864 | 16.3065 | 18.9633 | 19.3864 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7604 | 0 | 0 | 19.3864 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 6 | 1158 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.951 | 19.2541 | 16.1188 | 18.7756 | 19.2541 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7603 | 0 | 0 | 19.2541 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 7 | 1159 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8172 | 19.1202 | 15.98 | 18.6368 | 19.1202 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7602 | 0 | 0 | 19.1202 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 8 | 1160 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.7406 | 19.0437 | 15.9331 | 18.5899 | 20 |  | 354.5965 | 0 | 354.5965 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7601 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 9 | 1161 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10516.8472 | 0 | 12228.0232 | 0 | 1640.0287 | 0 | 701.3281 | 0 | 25086.2272 | 0 | 777.8052 | 0 | 679.115 | 0 | 79.7545 | 0 | 38.9501 | 244.5175 | 1820.1422 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7018 | 20.0049 | 16.9232 | 19.58 | 20.0049 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7600 | 0 | 0 | 20.0049 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 10 | 1162 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11997.3072 | 0 | 20460.0553 | 0 | 6946.1802 | 0 | 2970.406 | 0 | 42373.9488 | 0 | 887.2971 | 0 | 1136.3022 | 0 | 337.7923 | 0 | 164.9692 | 571.9963 | 3098.3571 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7631 | 20.0661 | 17.0041 | 19.6609 | 20.0661 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7599 | 0 | 0 | 20.0661 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 11 | 1163 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5929.2163 | 0 | 7702.3661 | 0 | 8021.3746 | 0 | 3380.6935 | 0 | 25033.6505 | 0 | 438.5131 | 0 | 427.7709 | 0 | 390.0789 | 0 | 187.7556 | 545.798 | 1989.9164 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7795 | 20.0825 | 17.0371 | 19.6939 | 20.0825 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7598 | 0 | 0 | 20.0825 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 12 | 1164 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8487.9097 | 0 | 11653.6743 | 0 | 15588.1493 | 0 | 4839.5976 | 0 | 40569.331 | 0 | 627.749 | 0 | 647.217 | 0 | 758.0506 | 0 | 268.7796 | 799.0483 | 3100.8445 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8461 | 20.1492 | 17.1201 | 19.777 | 20.1492 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7597 | 0 | 0 | 20.1492 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 13 | 1165 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9519.1719 | 0 | 11743.2 | 0 | 21401.6454 | 0 | 5427.598 | 0 | 48091.6154 | 0 | 704.0191 | 0 | 652.189 | 0 | 1040.7605 | 0 | 301.4357 | 908.2079 | 3606.6123 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9383 | 20.2413 | 17.2247 | 19.8816 | 20.2413 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7596 | 0 | 0 | 20.2413 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 14 | 1166 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7758.9174 | 0 | 5567.7885 | 0 | 13189.4073 | 0 | 4423.9441 | 0 | 30940.0573 | 0 | 573.8342 | 0 | 309.2216 | 0 | 641.4 | 0 | 245.6952 | 668.0568 | 2438.2077 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9765 | 20.2796 | 17.2493 | 19.9061 | 20.2796 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7595 | 0 | 0 | 20.2796 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 15 | 1167 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8539.8244 | 0 | 7771.1698 | 0 | 24645.0639 | 0 | 4869.1981 | 0 | 45825.2563 | 0 | 631.5885 | 0 | 431.5921 | 0 | 1198.4878 | 0 | 270.4235 | 799.0483 | 3331.1402 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0515 | 20.3545 | 17.3048 | 19.9617 | 20.3545 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7594 | 0 | 0 | 20.3545 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 16 | 1168 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3333.9157 | 0 | 1935.0077 | 0 | 4826.5167 | 0 | 1900.9169 | 0 | 11996.3571 | 0 | 246.5698 | 0 | 107.4657 | 0 | 234.7132 | 0 | 105.5723 | 279.4486 | 973.7696 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0181 | 20.3211 | 17.2384 | 19.8952 | 20.3211 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7593 | 0 | 0 | 20.3211 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 17 | 1169 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2275.1478 | 0 | 1297.2334 | 0 | 3521.7921 | 0 | 1305.5012 | 0 | 8399.6744 | 0 | 168.2654 | 0 | 72.0452 | 0 | 171.2645 | 0 | 72.5044 | 192.1209 | 676.2004 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9781 | 20.2812 | 17.2113 | 19.8682 | 20.2812 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7592 | 0 | 0 | 20.2812 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 18 | 1170 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 401.0789 | 0 | 228.6853 | 0 | 752.8132 | 0 | 253.9633 | 0 | 1636.5407 | 0 | 29.663 | 0 | 12.7006 | 0 | 36.6093 | 0 | 14.1045 | 34.9311 | 128.0085 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9134 | 20.2165 | 17.1304 | 19.7873 | 20.2165 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7591 | 0 | 0 | 20.2165 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 19 | 1171 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8464 | 20.1494 | 17.0712 | 19.7281 | 20.1494 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7590 | 0 | 0 | 20.1494 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 20 | 1172 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7626 | 20.0657 | 16.9337 | 19.5905 | 20.0657 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7589 | 0 | 0 | 20.0657 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 21 | 1173 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6861 | 19.9891 | 16.8801 | 19.537 | 20 |  | 4.0381 | 0 | 4.0381 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7588 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 22 | 1174 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6183 | 19.9213 | 16.8055 | 19.4623 | 20 |  | 29.1642 | 0 | 29.1642 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7587 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 23 | 1175 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6101 | 19.9131 | 16.7708 | 19.4277 | 20 |  | 32.2095 | 0 | 32.2095 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7586 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 18 | 24 | 1176 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6064 | 19.9095 | 16.7554 | 19.4123 | 20 |  | 33.563 | 0 | 33.563 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7585 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 1 | 1177 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5532 | 19.8562 | 16.6853 | 19.3421 | 19.8562 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7584 | 0 | 0 | 19.8562 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 2 | 1178 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4072 | 19.7102 | 16.5317 | 19.1886 | 19.7102 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7583 | 0 | 0 | 19.7102 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 3 | 1179 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.258 | 19.561 | 16.3722 | 19.029 | 19.561 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7582 | 0 | 0 | 19.561 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 4 | 1180 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1066 | 19.4096 | 16.2134 | 18.8702 | 19.4096 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7581 | 0 | 0 | 19.4096 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 5 | 1181 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.953 | 19.2561 | 16.0525 | 18.7094 | 19.2561 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7580 | 0 | 0 | 19.2561 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 6 | 1182 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7972 | 19.1003 | 15.8895 | 18.5464 | 19.1003 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7579 | 0 | 0 | 19.1003 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 7 | 1183 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.643 | 18.946 | 15.7398 | 18.3967 | 18.946 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7578 | 0 | 0 | 18.946 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 8 | 1184 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.5133 | 18.8154 | 15.6152 | 18.273 | 20 |  | 439.0767 | 0 | 439.0767 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7577 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 9 | 1185 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11837.4935 | 0 | 13483.0244 | 0 | 2181.2791 | 0 | 932.7838 | 0 | 28434.5809 | 0 | 875.4776 | 0 | 748.8147 | 0 | 106.0755 | 0 | 51.8046 | 205.2201 | 1987.3924 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6391 | 19.9412 | 16.7059 | 19.3637 | 20 |  | 21.7955 | 0 | 21.7955 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7576 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 10 | 1186 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 16414.3319 | 0 | 30685.5016 | 0 | 7451.3947 | 0 | 3186.4517 | 0 | 57737.6799 | 0 | 1213.9715 | 0 | 1704.1988 | 0 | 362.3608 | 0 | 176.9679 | 764.1172 | 4221.6162 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7326 | 20.0347 | 16.8275 | 19.4853 | 20.0347 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7575 | 0 | 0 | 20.0347 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 11 | 1187 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7614.8357 | 0 | 44887.0965 | 0 | 11000.1031 | 0 | 4341.7923 | 0 | 67843.8275 | 0 | 563.1782 | 0 | 2492.9212 | 0 | 534.9343 | 0 | 241.1327 | 1283.7169 | 5115.8833 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8068 | 20.1088 | 16.9355 | 19.5932 | 20.1088 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7574 | 0 | 0 | 20.1088 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 12 | 1188 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9187.4698 | 0 | 43843.7157 | 0 | 36276.8832 | 0 | 5238.4697 | 0 | 94546.5384 | 0 | 679.4871 | 0 | 2434.9744 | 0 | 1764.1423 | 0 | 290.932 | 1576.2647 | 6745.8004 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9617 | 20.2638 | 17.1047 | 19.7625 | 20.2638 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7573 | 0 | 0 | 20.2638 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 13 | 1189 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11011.9504 | 0 | 23813.7417 | 0 | 38824.0315 | 0 | 6278.7437 | 0 | 79928.4673 | 0 | 814.422 | 0 | 1322.5579 | 0 | 1888.01 | 0 | 348.7063 | 1336.1136 | 5709.8097 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0731 | 20.3752 | 17.2122 | 19.87 | 20.3752 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7572 | 0 | 0 | 20.3752 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 14 | 1190 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9334.0632 | 0 | 34502.1539 | 0 | 85073.1303 | 0 | 5322.0536 | 0 | 134231.401 | 0 | 690.3288 | 0 | 1916.1665 | 0 | 4137.1004 | 0 | 295.574 | 1781.4847 | 8820.6546 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3493 | 20.6514 | 17.521 | 20.1788 | 20.6514 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7571 | 0 | 0 | 20.6514 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 15 | 1191 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8341.2153 | 0 | 24920.6744 | 0 | 103627.975 | 0 | 4755.9561 | 0 | 141645.8207 | 0 | 616.8998 | 0 | 1384.0342 | 0 | 5039.4212 | 0 | 264.1343 | 1624.2949 | 8928.7845 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6425 | 20.9446 | 17.8028 | 20.4606 | 20.9446 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7570 | 0 | 0 | 20.9446 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 16 | 1192 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8119.5368 | 0 | 9019.8103 | 0 | 60571.7221 | 0 | 4629.5604 | 0 | 82340.6296 | 0 | 600.5049 | 0 | 500.9385 | 0 | 2945.5987 | 0 | 257.1146 | 956.2381 | 5260.3948 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7564 | 21.0585 | 17.8872 | 20.545 | 21.0585 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7569 | 0 | 0 | 21.0585 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 17 | 1193 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5344.9073 | 0 | 3047.5349 | 0 | 51528.0962 | 0 | 3860.9015 | 0 | 63781.4398 | 0 | 395.2988 | 0 | 169.2527 | 0 | 2505.8077 | 0 | 214.4252 | 580.7291 | 3865.5135 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8113 | 21.1134 | 17.9248 | 20.5826 | 21.1134 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7568 | 0 | 0 | 21.1134 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 18 | 1194 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1674.4642 | 0 | 954.7384 | 0 | 34039.3874 | 0 | 4695.5938 | 0 | 41364.1837 | 0 | 123.8401 | 0 | 53.0239 | 0 | 1655.3331 | 0 | 260.782 | 157.1898 | 2250.1688 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8194 | 21.1225 | 17.9105 | 20.5674 | 21.1225 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7567 | 0 | 0 | 21.1225 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 19 | 1195 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7026 | 21.0056 | 17.7687 | 20.4256 | 21.0056 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7566 | 0 | 0 | 21.0056 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 20 | 1196 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5814 | 20.8844 | 17.6333 | 20.2902 | 20.8844 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7565 | 0 | 0 | 20.8844 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 21 | 1197 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4586 | 20.7617 | 17.5053 | 20.1622 | 20.7617 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7564 | 0 | 0 | 20.7617 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 22 | 1198 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3343 | 20.6373 | 17.3758 | 20.0326 | 20.6373 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7563 | 0 | 0 | 20.6373 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 23 | 1199 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2057 | 20.5087 | 17.2332 | 19.8901 | 20.5087 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7562 | 0 | 0 | 20.5087 | 0 | 0 | 0
|  | 2004 | 2 | 19 | 24 | 1200 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0774 | 20.3805 | 17.1058 | 19.7626 | 20.3805 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7561 | 0 | 0 | 20.3805 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 1 | 1201 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8981 | 20.2011 | 16.9162 | 19.5731 | 20.2011 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7560 | 0 | 0 | 20.2011 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 2 | 1202 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7195 | 20.0226 | 16.74 | 19.3968 | 20.0226 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7559 | 0 | 0 | 20.0226 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 3 | 1203 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5408 | 19.8439 | 16.5607 | 19.2176 | 19.8439 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7558 | 0 | 0 | 19.8439 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 4 | 1204 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3612 | 19.6642 | 16.3775 | 19.0343 | 19.6642 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7557 | 0 | 0 | 19.6642 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 5 | 1205 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1796 | 19.4826 | 16.1894 | 18.8463 | 19.4826 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7556 | 0 | 0 | 19.4826 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 6 | 1206 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9997 | 19.3028 | 16.0149 | 18.6717 | 19.3028 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7555 | 0 | 0 | 19.3028 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 7 | 1207 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8189 | 19.122 | 15.8305 | 18.4874 | 19.122 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7554 | 0 | 0 | 19.122 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 8 | 1208 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6633 | 18.9654 | 15.6748 | 18.3326 | 20 |  | 383.4956 | 0 | 383.4956 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7553 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 9 | 1209 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11757.4005 | 0 | 13309.0335 | 0 | 2112.4979 | 0 | 903.3708 | 0 | 28082.3027 | 0 | 869.5541 | 0 | 739.1517 | 0 | 102.7306 | 0 | 50.171 | 279.4486 | 2041.056 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6215 | 19.9236 | 16.6295 | 19.2873 | 20 |  | 28.3286 | 0 | 28.3286 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7552 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 10 | 1210 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 20102.7242 | 0 | 39857.967 | 0 | 7232.48 | 0 | 3092.8368 | 0 | 70286.0081 | 0 | 1486.7577 | 0 | 2213.6155 | 0 | 351.715 | 0 | 171.7687 | 860.1777 | 5084.0346 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7553 | 20.0574 | 16.8027 | 19.4605 | 20.0574 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7551 | 0 | 0 | 20.0574 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 11 | 1211 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7056.2708 | 0 | 52678.7573 | 0 | 10139.8934 | 0 | 4023.3123 | 0 | 73898.2338 | 0 | 521.8678 | 0 | 2925.6513 | 0 | 493.1023 | 0 | 223.4451 | 1419.0749 | 5583.1414 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8334 | 20.1355 | 16.9142 | 19.572 | 20.1355 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7550 | 0 | 0 | 20.1355 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 12 | 1212 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8399.8904 | 0 | 53721.1848 | 0 | 41441.7042 | 0 | 4789.4112 | 0 | 108352.1907 | 0 | 621.2393 | 0 | 2983.5452 | 0 | 2015.3072 | 0 | 265.9924 | 1820.7822 | 7706.8662 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0188 | 20.3208 | 17.1281 | 19.7858 | 20.3208 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7549 | 0 | 0 | 20.3208 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 13 | 1213 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8982.0033 | 0 | 49195.7681 | 0 | 72561.8087 | 0 | 5121.3177 | 0 | 135860.8978 | 0 | 664.2912 | 0 | 2732.2145 | 0 | 3528.6757 | 0 | 284.4256 | 2026.0023 | 9235.6093 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.29 | 20.5921 | 17.425 | 20.0828 | 20.5921 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7548 | 0 | 0 | 20.5921 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 14 | 1214 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8883.8588 | 0 | 39898.3583 | 0 | 98638.5244 | 0 | 5065.3581 | 0 | 152486.0995 | 0 | 657.0326 | 0 | 2215.8587 | 0 | 4796.7846 | 0 | 281.3178 | 2012.9031 | 9963.8968 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6107 | 20.9128 | 17.7547 | 20.4125 | 20.9128 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7547 | 0 | 0 | 20.9128 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 15 | 1215 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8167.3263 | 0 | 26910.4305 | 0 | 113417.7267 | 0 | 4656.8088 | 0 | 153152.2923 | 0 | 604.0393 | 0 | 1494.5405 | 0 | 5515.4962 | 0 | 258.6279 | 1759.6528 | 9632.3567 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9371 | 21.2391 | 18.098 | 20.7558 | 21.2391 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7546 | 0 | 0 | 21.2391 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 16 | 1216 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6973.9088 | 0 | 12545.9541 | 0 | 107727.8165 | 0 | 3976.3515 | 0 | 131224.0308 | 0 | 515.7765 | 0 | 696.7721 | 0 | 5238.7963 | 0 | 220.837 | 1274.9842 | 7947.166 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.1934 | 21.4955 | 18.334 | 20.9918 | 21.4955 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7545 | 0 | 0 | 21.4955 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 17 | 1217 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5296.5068 | 0 | 3019.9381 | 0 | 72135.9229 | 0 | 4304.4925 | 0 | 84756.8602 | 0 | 391.7192 | 0 | 167.7201 | 0 | 3507.9649 | 0 | 239.0611 | 681.1559 | 4987.6212 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.3099 | 21.612 | 18.4302 | 21.088 | 21.612 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7544 | 0 | 0 | 21.612 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 18 | 1218 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1767.4904 | 0 | 1007.7796 | 0 | 26064.6089 | 0 | 3836.8935 | 0 | 32676.7724 | 0 | 130.7201 | 0 | 55.9697 | 0 | 1267.5201 | 0 | 213.0918 | 157.1898 | 1824.4915 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.2913 | 21.5944 | 18.377 | 21.0338 | 21.5944 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7543 | 0 | 0 | 21.5944 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 19 | 1219 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1718 | 21.4748 | 18.2299 | 20.8868 | 21.4748 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7542 | 0 | 0 | 21.4748 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 20 | 1220 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0461 | 21.3491 | 18.0842 | 20.7411 | 21.3491 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7541 | 0 | 0 | 21.3491 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 21 | 1221 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9161 | 21.2191 | 17.9403 | 20.5972 | 21.2191 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7540 | 0 | 0 | 21.2191 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 22 | 1222 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7828 | 21.0858 | 17.7962 | 20.453 | 21.0858 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7539 | 0 | 0 | 21.0858 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 23 | 1223 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6499 | 20.9529 | 17.6642 | 20.3211 | 20.9529 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7538 | 0 | 0 | 20.9529 | 0 | 0 | 0
|  | 2004 | 2 | 20 | 24 | 1224 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5173 | 20.8204 | 17.5326 | 20.1895 | 20.8204 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7537 | 0 | 0 | 20.8204 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 1 | 1225 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3328 | 20.6358 | 17.3351 | 19.9919 | 20.6358 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7536 | 0 | 0 | 20.6358 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 2 | 1226 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1455 | 20.4485 | 17.1385 | 19.7954 | 20.4485 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7535 | 0 | 0 | 20.4485 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 3 | 1227 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9636 | 20.2667 | 16.9739 | 19.6308 | 20.2667 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7534 | 0 | 0 | 20.2667 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 4 | 1228 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7835 | 20.0866 | 16.7992 | 19.456 | 20.0866 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7533 | 0 | 0 | 20.0866 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 5 | 1229 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6024 | 19.9055 | 16.6146 | 19.2714 | 19.9055 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7532 | 0 | 0 | 19.9055 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 6 | 1230 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4194 | 19.7225 | 16.4251 | 19.082 | 19.7225 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7531 | 0 | 0 | 19.7225 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 7 | 1231 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2336 | 19.5367 | 16.23 | 18.8868 | 19.5367 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7530 | 0 | 0 | 19.5367 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 8 | 1232 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.0743 | 19.3764 | 16.0736 | 18.7314 | 20 |  | 231.144 | 0 | 231.144 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7529 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 9 | 1233 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7474.4226 | 0 | 7646.4006 | 0 | 2900.3211 | 0 | 1240.2689 | 0 | 19261.4133 | 0 | 552.7935 | 0 | 424.6627 | 0 | 141.0424 | 0 | 68.8815 | 253.2503 | 1440.6304 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5952 | 19.8973 | 16.6007 | 19.2585 | 20 |  | 38.0616 | 0 | 38.0616 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7528 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 10 | 1234 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9730.3064 | 0 | 14230.0796 | 0 | 6881.5976 | 0 | 2942.7884 | 0 | 33784.772 | 0 | 719.6342 | 0 | 790.3043 | 0 | 334.6516 | 0 | 163.4354 | 519.5997 | 2527.6253 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6441 | 19.9462 | 16.6724 | 19.3302 | 20 |  | 19.9575 | 0 | 19.9575 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7527 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 11 | 1235 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7562.805 | 0 | 13439.5961 | 0 | 10167.8898 | 0 | 4312.1256 | 0 | 35482.4165 | 0 | 559.3301 | 0 | 746.4028 | 0 | 494.4638 | 0 | 239.4851 | 737.9189 | 2777.6006 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6586 | 19.9607 | 16.7192 | 19.3769 | 20 |  | 14.5809 | 0 | 14.5809 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7526 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 12 | 1236 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9088.1497 | 0 | 12827.2237 | 0 | 16810.1228 | 0 | 5181.8397 | 0 | 43907.3359 | 0 | 672.1416 | 0 | 712.3931 | 0 | 817.4751 | 0 | 287.7869 | 873.2768 | 3363.0735 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6863 | 19.9883 | 16.7582 | 19.416 | 20 |  | 4.3237 | 0 | 4.3237 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7525 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 13 | 1237 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7329.292 | 0 | 5131.2703 | 0 | 11079.531 | 0 | 4178.9823 | 0 | 27719.0756 | 0 | 542.0599 | 0 | 284.9784 | 0 | 538.7968 | 0 | 232.0906 | 620.0266 | 2217.9523 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6403 | 19.9424 | 16.7159 | 19.3737 | 20 |  | 21.3453 | 0 | 21.3453 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7524 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 14 | 1238 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6334.2813 | 0 | 3784.012 | 0 | 8875.7085 | 0 | 3611.6516 | 0 | 22605.6534 | 0 | 468.4709 | 0 | 210.1549 | 0 | 431.6251 | 0 | 200.5824 | 519.5997 | 1830.4331 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6297 | 19.9318 | 16.7202 | 19.378 | 20 |  | 25.2877 | 0 | 25.2877 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7523 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 15 | 1239 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8912.3457 | 0 | 8024.1399 | 0 | 25501.1725 | 0 | 5081.6006 | 0 | 47519.2587 | 0 | 659.1394 | 0 | 445.6414 | 0 | 1240.1203 | 0 | 282.2199 | 838.3458 | 3465.4667 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7038 | 20.0059 | 16.8021 | 19.4599 | 20.0059 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7522 | 0 | 0 | 20.0059 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 16 | 1240 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5875.6472 | 0 | 3571.0702 | 0 | 10407.9094 | 0 | 3350.1497 | 0 | 23204.7765 | 0 | 434.5512 | 0 | 198.3286 | 0 | 506.1359 | 0 | 186.0592 | 497.7678 | 1822.8428 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6405 | 19.9426 | 16.7426 | 19.4004 | 20 |  | 21.2727 | 0 | 21.2727 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7521 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 17 | 1241 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2007.4719 | 0 | 1144.6111 | 0 | 3002.3987 | 0 | 1151.5166 | 0 | 7305.9982 | 0 | 148.4686 | 0 | 63.5689 | 0 | 146.0064 | 0 | 63.9525 | 170.289 | 592.2855 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5868 | 19.8888 | 16.6838 | 19.3416 | 20 |  | 41.202 | 0 | 41.202 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7520 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 18 | 1242 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 300.3582 | 0 | 171.2569 | 0 | 473.0647 | 0 | 180.0466 | 0 | 1124.7264 | 0 | 22.2139 | 0 | 9.5112 | 0 | 23.0051 | 0 | 9.9994 | 26.1983 | 90.9279 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5933 | 19.8963 | 16.6894 | 19.3462 | 20 |  | 38.438 | 0 | 38.438 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7519 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 19 | 1243 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5891 | 19.8921 | 16.6823 | 19.3392 | 20 |  | 39.992 | 0 | 39.992 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7518 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 20 | 1244 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5882 | 19.8912 | 16.6785 | 19.3353 | 20 |  | 40.3303 | 0 | 40.3303 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7517 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 21 | 1245 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5873 | 19.8903 | 16.6746 | 19.3315 | 20 |  | 40.6687 | 0 | 40.6687 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7516 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 22 | 1246 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5882 | 19.8912 | 16.6785 | 19.3353 | 20 |  | 40.3303 | 0 | 40.3303 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7515 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 23 | 1247 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5873 | 19.8903 | 16.6746 | 19.3315 | 20 |  | 40.6687 | 0 | 40.6687 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7514 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 21 | 24 | 1248 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5873 | 19.8903 | 16.6746 | 19.3315 | 20 |  | 40.6687 | 0 | 40.6687 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7513 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 1 | 1249 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5404 | 19.8435 | 16.6314 | 19.2883 | 19.8435 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7512 | 0 | 0 | 19.8435 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 2 | 1250 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3854 | 19.6884 | 16.481 | 19.1378 | 19.6884 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7511 | 0 | 0 | 19.6884 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 3 | 1251 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2328 | 19.5358 | 16.3358 | 18.9927 | 19.5358 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7510 | 0 | 0 | 19.5358 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 4 | 1252 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0816 | 19.3847 | 16.1892 | 18.846 | 19.3847 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7509 | 0 | 0 | 19.3847 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 5 | 1253 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9301 | 19.2331 | 16.0362 | 18.6931 | 19.2331 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7508 | 0 | 0 | 19.2331 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 6 | 1254 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7864 | 19.0895 | 15.9175 | 18.5744 | 19.0895 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7507 | 0 | 0 | 19.0895 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 7 | 1255 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6487 | 18.9517 | 15.7987 | 18.4556 | 18.9517 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7506 | 0 | 0 | 18.9517 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 8 | 1256 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.5375 | 18.8396 | 15.7038 | 18.3616 | 20 |  | 430.1233 | 0 | 430.1233 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7505 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 9 | 1257 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2157.1135 | 0 | 2004.5531 | 0 | 1232.3737 | 0 | 527.0019 | 0 | 5921.0422 | 0 | 159.5358 | 0 | 111.3281 | 0 | 59.9302 | 0 | 29.2684 | 82.9613 | 443.0239 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5961 | 19.8982 | 16.7402 | 19.398 | 20 |  | 37.7487 | 0 | 37.7487 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7504 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 10 | 1258 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2766.6211 | 0 | 1840.9275 | 0 | 3500.6523 | 0 | 1496.9895 | 0 | 9605.1904 | 0 | 204.6138 | 0 | 102.2407 | 0 | 170.2365 | 0 | 83.1392 | 218.3192 | 778.5494 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6136 | 19.9157 | 16.7811 | 19.4389 | 20 |  | 31.2353 | 0 | 31.2353 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7503 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 11 | 1259 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8801.3584 | 0 | 31687.2298 | 0 | 11826.9721 | 0 | 5018.3184 | 0 | 57333.8786 | 0 | 650.931 | 0 | 1759.8324 | 0 | 575.1448 | 0 | 278.7053 | 1139.6263 | 4404.2399 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7631 | 20.0652 | 16.9667 | 19.6245 | 20.0652 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7502 | 0 | 0 | 20.0652 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 12 | 1260 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10527.2523 | 0 | 31884.753 | 0 | 29814.048 | 0 | 6002.3807 | 0 | 78228.434 | 0 | 778.5747 | 0 | 1770.8024 | 0 | 1449.8551 | 0 | 333.3578 | 1392.8766 | 5725.4665 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9003 | 20.2024 | 17.1452 | 19.803 | 20.2024 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7501 | 0 | 0 | 20.2024 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 13 | 1261 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9928.7163 | 0 | 11896.0252 | 0 | 21784.9966 | 0 | 5661.1102 | 0 | 49270.8483 | 0 | 734.3082 | 0 | 660.6766 | 0 | 1059.4029 | 0 | 314.4044 | 947.5054 | 3716.2974 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9426 | 20.2447 | 17.1495 | 19.8073 | 20.2447 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7500 | 0 | 0 | 20.2447 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 14 | 1262 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8684.6239 | 0 | 6599.3832 | 0 | 15695.5382 | 0 | 4951.7593 | 0 | 35931.3046 | 0 | 642.2976 | 0 | 366.5138 | 0 | 763.2729 | 0 | 275.0088 | 764.1172 | 2811.2104 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.952 | 20.2541 | 17.1788 | 19.8366 | 20.2541 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7499 | 0 | 0 | 20.2541 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 15 | 1263 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9007.7826 | 0 | 8051.0021 | 0 | 25564.4189 | 0 | 5136.0164 | 0 | 47759.2199 | 0 | 666.1978 | 0 | 447.1333 | 0 | 1243.1959 | 0 | 285.242 | 847.0785 | 3488.8475 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9926 | 20.2946 | 17.2097 | 19.8675 | 20.2946 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7498 | 0 | 0 | 20.2946 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 16 | 1264 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7296.5355 | 0 | 12165.6718 | 0 | 104382.3071 | 0 | 4160.3053 | 0 | 128004.8197 | 0 | 539.6373 | 0 | 675.6521 | 0 | 5076.1044 | 0 | 231.0533 | 1296.8161 | 7819.2632 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.255 | 20.5571 | 17.447 | 20.1048 | 20.5571 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7497 | 0 | 0 | 20.5571 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 17 | 1265 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4856.3498 | 0 | 2768.9714 | 0 | 18127.1292 | 0 | 3033.3543 | 0 | 28785.8047 | 0 | 359.166 | 0 | 153.782 | 0 | 881.521 | 0 | 168.4652 | 436.6384 | 1999.5727 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2217 | 20.5237 | 17.3749 | 20.0327 | 20.5237 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7496 | 0 | 0 | 20.5237 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 18 | 1266 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1509.8468 | 0 | 860.8776 | 0 | 5343.746 | 0 | 1270.1764 | 0 | 8984.6467 | 0 | 111.6653 | 0 | 47.8111 | 0 | 259.866 | 0 | 70.5425 | 122.2588 | 612.1436 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1474 | 20.4504 | 17.2689 | 19.9257 | 20.4504 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7495 | 0 | 0 | 20.4504 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 19 | 1267 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0306 | 20.3337 | 17.0959 | 19.7528 | 20.3337 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7494 | 0 | 0 | 20.3337 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 20 | 1268 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9113 | 20.2144 | 16.9683 | 19.6252 | 20.2144 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7493 | 0 | 0 | 20.2144 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 21 | 1269 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7859 | 20.0889 | 16.8229 | 19.4797 | 20.0889 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7492 | 0 | 0 | 20.0889 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 22 | 1270 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6525 | 19.9556 | 16.6639 | 19.3207 | 20 |  | 16.4691 | 0 | 16.4691 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7491 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 23 | 1271 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5745 | 19.8775 | 16.6207 | 19.2776 | 20 |  | 45.4059 | 0 | 45.4059 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7490 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 22 | 24 | 1272 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5635 | 19.8666 | 16.5745 | 19.2314 | 20 |  | 49.4663 | 0 | 49.4663 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7489 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 1 | 1273 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5285 | 19.8316 | 16.5814 | 19.2382 | 19.8316 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7488 | 0 | 0 | 19.8316 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 2 | 1274 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3581 | 19.6612 | 16.4041 | 19.061 | 19.6612 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7487 | 0 | 0 | 19.6612 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 3 | 1275 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1884 | 19.4915 | 16.2365 | 18.8934 | 19.4915 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7486 | 0 | 0 | 19.4915 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 4 | 1276 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0185 | 19.3216 | 16.0657 | 18.7226 | 19.3216 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7485 | 0 | 0 | 19.3216 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 5 | 1277 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.843 | 19.146 | 15.8717 | 18.5285 | 19.146 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7484 | 0 | 0 | 19.146 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 6 | 1278 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6737 | 18.9767 | 15.7222 | 18.3791 | 18.9767 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7483 | 0 | 0 | 18.9767 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 7 | 1279 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.496 | 18.799 | 15.5172 | 18.174 | 18.799 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7482 | 0 | 0 | 18.799 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 8 | 1280 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 158.0935 | 0 | 90.141 | 0 | 210.7913 | 0 | 90.141 | 0 | 549.1669 | 0 | 11.6923 | 0 | 5.0062 | 0 | 10.2508 | 0 | 5.0062 | 13.0992 | 45.0546 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.3667 | 18.6688 | 15.4641 | 18.1219 | 20 |  | 493.4198 | 0 | 493.4198 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7481 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 9 | 1281 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8165.8116 | 0 | 8577.1017 | 0 | 2429.456 | 0 | 1038.9121 | 0 | 20211.2814 | 0 | 603.9273 | 0 | 476.3516 | 0 | 118.1443 | 0 | 57.6987 | 183.3881 | 1439.5099 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6171 | 19.9192 | 16.6901 | 19.3479 | 20 |  | 29.9433 | 0 | 29.9433 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7480 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 10 | 1282 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 18074.4067 | 0 | 32305.5691 | 0 | 8108.9204 | 0 | 3467.6304 | 0 | 61956.5265 | 0 | 1336.7473 | 0 | 1794.1735 | 0 | 394.3362 | 0 | 192.5838 | 847.0785 | 4564.9194 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7542 | 20.0563 | 16.8812 | 19.539 | 20.0563 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7479 | 0 | 0 | 20.0563 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 11 | 1283 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7594.7321 | 0 | 50467.0813 | 0 | 10020.3816 | 0 | 4285.0316 | 0 | 72367.2266 | 0 | 561.6913 | 0 | 2802.8201 | 0 | 487.2905 | 0 | 237.9803 | 1454.0059 | 5543.7882 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8524 | 20.1545 | 17.0185 | 19.6763 | 20.1545 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7478 | 0 | 0 | 20.1545 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 12 | 1284 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10076.0558 | 0 | 39047.3832 | 0 | 33598.4947 | 0 | 5745.1196 | 0 | 88467.0533 | 0 | 745.2051 | 0 | 2168.5976 | 0 | 1633.8925 | 0 | 319.0701 | 1563.1655 | 6429.9309 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0049 | 20.307 | 17.1997 | 19.8575 | 20.307 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7477 | 0 | 0 | 20.307 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 13 | 1285 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11299.3993 | 0 | 31233.0765 | 0 | 49005.7218 | 0 | 6442.64 | 0 | 97980.8376 | 0 | 835.6812 | 0 | 1734.6098 | 0 | 2383.1449 | 0 | 357.8087 | 1589.3638 | 6900.6084 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1896 | 20.4917 | 17.4031 | 20.0609 | 20.4917 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7476 | 0 | 0 | 20.4917 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 14 | 1286 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9339.8692 | 0 | 37071.789 | 0 | 91878.9455 | 0 | 5325.364 | 0 | 143615.9678 | 0 | 690.7582 | 0 | 2058.8779 | 0 | 4468.0668 | 0 | 295.7579 | 1964.8729 | 9478.3336 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5079 | 20.8099 | 17.7316 | 20.3894 | 20.8099 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7475 | 0 | 0 | 20.8099 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 15 | 1287 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8820.9075 | 0 | 24342.3535 | 0 | 102003.2486 | 0 | 5029.4648 | 0 | 140195.9744 | 0 | 652.3768 | 0 | 1351.9157 | 0 | 4960.4109 | 0 | 279.3244 | 1698.5234 | 8942.5513 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.805 | 21.1071 | 17.9931 | 20.6509 | 21.1071 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7474 | 0 | 0 | 21.1071 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 16 | 1288 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7880.8945 | 0 | 6021.4742 | 0 | 28855.7253 | 0 | 4493.4925 | 0 | 47251.5865 | 0 | 582.8553 | 0 | 334.4182 | 0 | 1403.2519 | 0 | 249.5577 | 764.1172 | 3334.2004 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8176 | 21.1197 | 17.9451 | 20.6029 | 21.1197 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7473 | 0 | 0 | 21.1197 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 17 | 1289 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5491.4821 | 0 | 3131.1082 | 0 | 83036.587 | 0 | 4964.7371 | 0 | 96623.9145 | 0 | 406.1391 | 0 | 173.8942 | 0 | 4038.0635 | 0 | 275.7295 | 777.2164 | 5671.0428 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9764 | 21.2785 | 18.1249 | 20.7827 | 21.2785 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7472 | 0 | 0 | 21.2785 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 18 | 1290 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1739.35 | 0 | 991.7347 | 0 | 7315.8496 | 0 | 1614.9607 | 0 | 11661.895 | 0 | 128.6389 | 0 | 55.0786 | 0 | 355.7693 | 0 | 89.691 | 144.0907 | 773.2684 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8997 | 21.2028 | 17.9902 | 20.647 | 21.2028 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7471 | 0 | 0 | 21.2028 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 19 | 1291 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7721 | 21.0751 | 17.8036 | 20.4604 | 21.0751 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7470 | 0 | 0 | 21.0751 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 20 | 1292 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6292 | 20.9323 | 17.6116 | 20.2684 | 20.9323 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7469 | 0 | 0 | 20.9323 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 21 | 1293 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4832 | 20.7862 | 17.4551 | 20.1119 | 20.7862 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7468 | 0 | 0 | 20.7862 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 22 | 1294 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.334 | 20.637 | 17.2955 | 19.9523 | 20.637 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7467 | 0 | 0 | 20.637 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 23 | 1295 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1871 | 20.4902 | 17.156 | 19.8128 | 20.4902 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7466 | 0 | 0 | 20.4902 | 0 | 0 | 0
|  | 2004 | 2 | 23 | 24 | 1296 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0417 | 20.3448 | 17.0148 | 19.6717 | 20.3448 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7465 | 0 | 0 | 20.3448 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 1 | 1297 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8499 | 20.153 | 16.828 | 19.4849 | 20.153 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7464 | 0 | 0 | 20.153 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 2 | 1298 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6873 | 19.9904 | 16.7592 | 19.416 | 19.9904 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7463 | 0 | 0 | 19.9904 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 3 | 1299 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5199 | 19.823 | 16.576 | 19.2328 | 19.823 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7462 | 0 | 0 | 19.823 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 4 | 1300 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3578 | 19.6609 | 16.4305 | 19.0873 | 19.6609 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7461 | 0 | 0 | 19.6609 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 5 | 1301 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1799 | 19.4829 | 16.2016 | 18.8584 | 19.4829 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7460 | 0 | 0 | 19.4829 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 6 | 1302 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0183 | 19.3214 | 16.0922 | 18.749 | 19.3214 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7459 | 0 | 0 | 19.3214 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 7 | 1303 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8619 | 19.165 | 15.9523 | 18.6091 | 19.165 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7458 | 0 | 0 | 19.165 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 8 | 1304 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0936 | 0 | 90.1411 | 0 | 210.7914 | 0 | 90.1411 | 0 | 549.1671 | 0 | 11.6923 | 0 | 5.0062 | 0 | 10.2508 | 0 | 5.0062 | 13.0992 | 45.0546 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.7637 | 19.0668 | 15.8814 | 18.5383 | 20 |  | 346.0341 | 0 | 346.0341 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7457 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 9 | 1305 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 15118.0162 | 0 | 16378.0131 | 0 | 3146.3759 | 0 | 1345.4897 | 0 | 35987.895 | 0 | 1118.0985 | 0 | 909.5954 | 0 | 153.008 | 0 | 74.7253 | 279.4486 | 2534.8758 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7021 | 20.0052 | 16.8232 | 19.48 | 20.0052 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7456 | 0 | 0 | 20.0052 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 10 | 1306 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 15831.6289 | 0 | 25958.2975 | 0 | 8587.87 | 0 | 3672.4444 | 0 | 54050.2407 | 0 | 1170.8759 | 0 | 1441.6613 | 0 | 417.6275 | 0 | 203.9587 | 777.2164 | 4011.3399 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7727 | 20.0757 | 16.9339 | 19.5908 | 20.0757 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7455 | 0 | 0 | 20.0757 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 11 | 1307 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8254.8448 | 0 | 15248.3539 | 0 | 10921.9245 | 0 | 4670.5598 | 0 | 39095.683 | 0 | 610.512 | 0 | 846.8568 | 0 | 531.1324 | 0 | 259.3916 | 825.2466 | 3073.1395 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8061 | 20.1092 | 16.9865 | 19.6433 | 20.1092 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7454 | 0 | 0 | 20.1092 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 12 | 1308 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10786.8113 | 0 | 31574.7905 | 0 | 29673.4734 | 0 | 6150.3749 | 0 | 78185.45 | 0 | 797.7712 | 0 | 1753.5878 | 0 | 1443.019 | 0 | 341.577 | 1419.0749 | 5755.0298 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9601 | 20.2632 | 17.1642 | 19.8211 | 20.2632 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7453 | 0 | 0 | 20.2632 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 13 | 1309 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11598.301 | 0 | 22379.7799 | 0 | 37025.3455 | 0 | 6613.0664 | 0 | 77616.4929 | 0 | 857.7874 | 0 | 1242.9191 | 0 | 1800.54 | 0 | 367.2738 | 1357.9455 | 5626.4657 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1162 | 20.4192 | 17.3334 | 19.9903 | 20.4192 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7452 | 0 | 0 | 20.4192 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 14 | 1310 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9585.3626 | 0 | 7981.3755 | 0 | 19085.4621 | 0 | 5465.3383 | 0 | 42117.5385 | 0 | 708.9144 | 0 | 443.2664 | 0 | 928.1247 | 0 | 303.5317 | 873.2768 | 3257.1141 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1604 | 20.4635 | 17.3482 | 20.005 | 20.4635 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7451 | 0 | 0 | 20.4635 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 15 | 1311 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6054.719 | 0 | 3570.5149 | 0 | 8628.3881 | 0 | 3452.2521 | 0 | 21705.8741 | 0 | 447.795 | 0 | 198.2978 | 0 | 419.5979 | 0 | 191.7298 | 497.7678 | 1755.1883 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1442 | 20.4473 | 17.3286 | 19.9855 | 20.4473 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7450 | 0 | 0 | 20.4473 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 16 | 1312 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2900.889 | 0 | 1673.3672 | 0 | 4103.9998 | 0 | 1654.0157 | 0 | 10332.2717 | 0 | 214.544 | 0 | 92.9348 | 0 | 199.5772 | 0 | 91.86 | 244.5175 | 843.4336 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0859 | 20.389 | 17.2419 | 19.8988 | 20.389 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7449 | 0 | 0 | 20.389 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 17 | 1313 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1273.3995 | 0 | 726.0611 | 0 | 1812.5422 | 0 | 729.0174 | 0 | 4541.0202 | 0 | 94.1781 | 0 | 40.3237 | 0 | 88.1438 | 0 | 40.4879 | 109.1596 | 372.2931 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0067 | 20.3098 | 17.15 | 19.8069 | 20.3098 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7448 | 0 | 0 | 20.3098 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 18 | 1314 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 300.492 | 0 | 171.3332 | 0 | 448.0913 | 0 | 177.3386 | 0 | 1097.2551 | 0 | 22.2238 | 0 | 9.5154 | 0 | 21.7907 | 0 | 9.849 | 26.1983 | 89.5771 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9137 | 20.2168 | 17.0448 | 19.7016 | 20.2168 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7447 | 0 | 0 | 20.2168 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 19 | 1315 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8184 | 20.1214 | 16.9522 | 19.609 | 20.1214 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7446 | 0 | 0 | 20.1214 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 20 | 1316 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7212 | 20.0242 | 16.849 | 19.5059 | 20.0242 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7445 | 0 | 0 | 20.0242 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 21 | 1317 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6168 | 19.9198 | 16.721 | 19.3779 | 20 |  | 29.734 | 0 | 29.734 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7444 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 22 | 1318 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5864 | 19.8894 | 16.6708 | 19.3276 | 20 |  | 41.0071 | 0 | 41.0071 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7443 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 23 | 1319 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5864 | 19.8894 | 16.6708 | 19.3276 | 20 |  | 41.0071 | 0 | 41.0071 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7442 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 24 | 24 | 1320 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5873 | 19.8903 | 16.6746 | 19.3315 | 20 |  | 40.6687 | 0 | 40.6687 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7441 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 1 | 1321 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5422 | 19.8453 | 16.6391 | 19.2959 | 19.8453 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7440 | 0 | 0 | 19.8453 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 2 | 1322 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3863 | 19.6893 | 16.4789 | 19.1357 | 19.6893 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7439 | 0 | 0 | 19.6893 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 3 | 1323 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2273 | 19.5303 | 16.3098 | 18.9666 | 19.5303 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7438 | 0 | 0 | 19.5303 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 4 | 1324 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0661 | 19.3692 | 16.1415 | 18.7984 | 19.3692 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7437 | 0 | 0 | 19.3692 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 5 | 1325 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9111 | 19.2142 | 16.0059 | 18.6628 | 19.2142 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7436 | 0 | 0 | 19.2142 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 6 | 1326 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7448 | 19.0479 | 15.8031 | 18.4599 | 19.0479 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7435 | 0 | 0 | 19.0479 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 7 | 1327 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5883 | 18.8914 | 15.6779 | 18.3347 | 18.8914 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7434 | 0 | 0 | 18.8914 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 8 | 1328 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 316.4387 | 0 | 180.4256 | 0 | 421.9182 | 0 | 180.4256 | 0 | 1099.2081 | 0 | 23.4032 | 0 | 10.0204 | 0 | 20.5179 | 0 | 10.0204 | 26.1983 | 90.1601 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.4807 | 18.7837 | 15.5623 | 18.2192 | 20 |  | 450.9873 | 0 | 450.9873 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7433 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 9 | 1329 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11010.8145 | 0 | 11539.2878 | 0 | 2954.9051 | 0 | 1263.6107 | 0 | 26768.6181 | 0 | 814.338 | 0 | 640.8642 | 0 | 143.6968 | 0 | 70.1779 | 231.4184 | 1900.4954 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6591 | 19.9622 | 16.7277 | 19.3845 | 20 |  | 14.0298 | 0 | 14.0298 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7432 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 10 | 1330 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13564.966 | 0 | 20844.4635 | 0 | 8224.528 | 0 | 3517.0679 | 0 | 46151.0254 | 0 | 1003.238 | 0 | 1157.6513 | 0 | 399.9582 | 0 | 195.3295 | 681.1559 | 3437.333 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7228 | 20.0259 | 16.8141 | 19.4709 | 20.0259 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7431 | 0 | 0 | 20.0259 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 11 | 1331 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5510.971 | 0 | 4602.06 | 0 | 7327.9155 | 0 | 3133.6481 | 0 | 20574.5946 | 0 | 407.5805 | 0 | 255.5873 | 0 | 356.356 | 0 | 174.0353 | 471.5695 | 1665.1286 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6683 | 19.9714 | 16.7393 | 19.3962 | 20 |  | 10.6169 | 0 | 10.6169 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7430 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 12 | 1332 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10863.6046 | 0 | 25888.5545 | 0 | 26251.3644 | 0 | 6194.1605 | 0 | 69197.684 | 0 | 803.4507 | 0 | 1437.788 | 0 | 1276.602 | 0 | 344.0088 | 1309.9153 | 5171.7647 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8024 | 20.1055 | 16.9338 | 19.5906 | 20.1055 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7429 | 0 | 0 | 20.1055 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 13 | 1333 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11718.9323 | 0 | 22355.0819 | 0 | 37035.8525 | 0 | 6681.8474 | 0 | 77791.7141 | 0 | 866.709 | 0 | 1241.5474 | 0 | 1801.0509 | 0 | 371.0937 | 1371.0446 | 5651.4457 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9396 | 20.2426 | 17.0939 | 19.7508 | 20.2426 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7428 | 0 | 0 | 20.2426 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 14 | 1334 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11661.0275 | 0 | 18689.2713 | 0 | 45772.8146 | 0 | 6648.8315 | 0 | 82771.9449 | 0 | 862.4265 | 0 | 1037.9571 | 0 | 2225.9288 | 0 | 369.2601 | 1357.9455 | 5853.518 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0876 | 20.3906 | 17.2318 | 19.8886 | 20.3906 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7427 | 0 | 0 | 20.3906 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 15 | 1335 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9204.8764 | 0 | 7977.2784 | 0 | 25157.8717 | 0 | 5248.3945 | 0 | 47588.421 | 0 | 680.7744 | 0 | 443.0388 | 0 | 1223.4256 | 0 | 291.4832 | 860.1777 | 3498.8997 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.111 | 20.4141 | 17.1819 | 19.8387 | 20.4141 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7426 | 0 | 0 | 20.4141 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 16 | 1336 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7694.2665 | 0 | 5528.0773 | 0 | 24418.6267 | 0 | 4387.0818 | 0 | 42028.0523 | 0 | 569.0527 | 0 | 307.0161 | 0 | 1187.4761 | 0 | 243.648 | 716.087 | 3023.2799 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1307 | 20.4337 | 17.2423 | 19.8991 | 20.4337 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7425 | 0 | 0 | 20.4337 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 17 | 1337 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4955.6006 | 0 | 2825.5617 | 0 | 16228.4264 | 0 | 3088.9483 | 0 | 27098.5371 | 0 | 366.5064 | 0 | 156.9249 | 0 | 789.1873 | 0 | 171.5528 | 436.6384 | 1920.8097 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0997 | 20.4027 | 17.1878 | 19.8446 | 20.4027 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7424 | 0 | 0 | 20.4027 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 18 | 1338 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1277.5438 | 0 | 728.4241 | 0 | 2429.5594 | 0 | 821.7487 | 0 | 5257.276 | 0 | 94.4846 | 0 | 40.4549 | 0 | 118.1493 | 0 | 45.6379 | 109.1596 | 407.8864 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9977 | 20.3008 | 17.0613 | 19.7181 | 20.3008 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7423 | 0 | 0 | 20.3008 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 19 | 1339 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.876 | 20.1791 | 16.9252 | 19.582 | 20.1791 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7422 | 0 | 0 | 20.1791 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 20 | 1340 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7518 | 20.0549 | 16.7928 | 19.4497 | 20.0549 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7421 | 0 | 0 | 20.0549 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 21 | 1341 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6243 | 19.9273 | 16.6542 | 19.3111 | 20 |  | 26.9406 | 0 | 26.9406 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7420 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 22 | 1342 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5699 | 19.873 | 16.6015 | 19.2583 | 20 |  | 47.0977 | 0 | 47.0977 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7419 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 23 | 1343 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5626 | 19.8657 | 16.5707 | 19.2275 | 20 |  | 49.8046 | 0 | 49.8046 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7418 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 25 | 24 | 1344 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5645 | 19.8675 | 16.5784 | 19.2352 | 20 |  | 49.1279 | 0 | 49.1279 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7417 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 1 | 1345 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5222 | 19.8252 | 16.5544 | 19.2113 | 19.8252 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7416 | 0 | 0 | 19.8252 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 2 | 1346 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3518 | 19.6548 | 16.398 | 19.0548 | 19.6548 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7415 | 0 | 0 | 19.6548 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 3 | 1347 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1776 | 19.4806 | 16.2112 | 18.868 | 19.4806 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7414 | 0 | 0 | 19.4806 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 4 | 1348 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0023 | 19.3054 | 16.0322 | 18.6891 | 19.3054 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7413 | 0 | 0 | 19.3054 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 5 | 1349 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8333 | 19.1364 | 15.8831 | 18.5399 | 19.1364 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7412 | 0 | 0 | 19.1364 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 6 | 1350 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6632 | 18.9663 | 15.7091 | 18.3659 | 18.9663 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7411 | 0 | 0 | 18.9663 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 7 | 1351 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.4938 | 18.7969 | 15.5418 | 18.1986 | 18.7969 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7410 | 0 | 0 | 18.7969 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 8 | 1352 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 158.0937 | 0 | 90.1411 | 0 | 210.7916 | 0 | 90.1411 | 0 | 549.1675 | 0 | 11.6923 | 0 | 5.0062 | 0 | 10.2508 | 0 | 5.0062 | 13.0992 | 45.0547 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.3595 | 18.6616 | 15.4393 | 18.0971 | 20 |  | 496.0839 | 0 | 496.0839 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7409 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 9 | 1353 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4435.5168 | 0 | 4289.5206 | 0 | 1925.6214 | 0 | 823.4565 | 0 | 11474.1153 | 0 | 328.042 | 0 | 238.2296 | 0 | 93.6428 | 0 | 45.7328 | 135.3579 | 841.0052 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5928 | 19.8949 | 16.6691 | 19.3269 | 20 |  | 38.9672 | 0 | 38.9672 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7408 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 10 | 1354 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11071.7195 | 0 | 15300.835 | 0 | 7885.8152 | 0 | 3372.2236 | 0 | 37630.5933 | 0 | 818.8424 | 0 | 849.7715 | 0 | 383.4866 | 0 | 187.2852 | 606.9274 | 2846.3132 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6864 | 19.9885 | 16.8233 | 19.4811 | 20 |  | 4.2593 | 0 | 4.2593 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7407 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 11 | 1355 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8364.5379 | 0 | 53001.3119 | 0 | 10215.4071 | 0 | 4368.4307 | 0 | 75949.6875 | 0 | 618.6247 | 0 | 2943.5652 | 0 | 496.7745 | 0 | 242.6121 | 1563.1655 | 5864.7421 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8106 | 20.1126 | 16.9899 | 19.6477 | 20.1126 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7406 | 0 | 0 | 20.1126 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 12 | 1356 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9533.8202 | 0 | 46130.6004 | 0 | 36866.129 | 0 | 5435.9501 | 0 | 97966.4998 | 0 | 705.1025 | 0 | 2561.9824 | 0 | 1792.7973 | 0 | 301.8996 | 1781.4847 | 7143.2665 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9935 | 20.2956 | 17.1979 | 19.8557 | 20.2956 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7405 | 0 | 0 | 20.2956 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 13 | 1357 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10682.8885 | 0 | 13098.1867 | 0 | 23806.828 | 0 | 6091.1206 | 0 | 53679.0238 | 0 | 790.0853 | 0 | 727.4417 | 0 | 1157.7244 | 0 | 338.2862 | 1043.5658 | 4057.1034 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.02 | 20.3221 | 17.127 | 19.7848 | 20.3221 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7404 | 0 | 0 | 20.3221 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 14 | 1358 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4671.3766 | 0 | 2747.1768 | 0 | 6438.9343 | 0 | 2663.5042 | 0 | 16520.9919 | 0 | 345.4858 | 0 | 152.5716 | 0 | 313.1249 | 0 | 147.9246 | 388.6082 | 1347.7151 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.943 | 20.2451 | 17.0654 | 19.7232 | 20.2451 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7403 | 0 | 0 | 20.2451 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 15 | 1359 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9097.6145 | 0 | 24256.269 | 0 | 102665.2474 | 0 | 5187.2364 | 0 | 141206.3672 | 0 | 672.8416 | 0 | 1347.1348 | 0 | 4992.6039 | 0 | 288.0866 | 1772.752 | 9073.4188 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.234 | 20.536 | 17.3886 | 20.0464 | 20.536 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7402 | 0 | 0 | 20.536 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 16 | 1360 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7642.6342 | 0 | 5386.1833 | 0 | 23179.832 | 0 | 4357.6423 | 0 | 40566.2918 | 0 | 565.2341 | 0 | 299.1356 | 0 | 1127.2336 | 0 | 242.013 | 702.9879 | 2936.6042 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.225 | 20.5271 | 17.3431 | 20.0009 | 20.5271 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7401 | 0 | 0 | 20.5271 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 17 | 1361 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5800.1854 | 0 | 3307.1232 | 0 | 86318.3809 | 0 | 5586.5871 | 0 | 101012.2766 | 0 | 428.9702 | 0 | 183.6697 | 0 | 4197.6569 | 0 | 310.2656 | 847.0785 | 5967.6409 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3916 | 20.6937 | 17.5221 | 20.1799 | 20.6937 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7400 | 0 | 0 | 20.6937 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 18 | 1362 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2624.2191 | 0 | 1496.2653 | 0 | 56601.1151 | 0 | 8424.3913 | 0 | 69145.9908 | 0 | 194.082 | 0 | 83.099 | 0 | 2752.5083 | 0 | 467.8704 | 301.2805 | 3798.8402 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4801 | 20.7832 | 17.5735 | 20.2304 | 20.7832 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7399 | 0 | 0 | 20.7832 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 19 | 1363 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3638 | 20.6668 | 17.4311 | 20.0879 | 20.6668 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7398 | 0 | 0 | 20.6668 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 20 | 1364 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2431 | 20.5462 | 17.2962 | 19.9531 | 20.5462 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7397 | 0 | 0 | 20.5462 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 21 | 1365 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1227 | 20.4258 | 17.1764 | 19.8332 | 20.4258 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7396 | 0 | 0 | 20.4258 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 22 | 1366 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9971 | 20.3001 | 17.0337 | 19.6906 | 20.3001 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7395 | 0 | 0 | 20.3001 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 23 | 1367 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8717 | 20.1748 | 16.9091 | 19.566 | 20.1748 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7394 | 0 | 0 | 20.1748 | 0 | 0 | 0
|  | 2004 | 2 | 26 | 24 | 1368 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7457 | 20.0488 | 16.781 | 19.4378 | 20.0488 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7393 | 0 | 0 | 20.0488 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 1 | 1369 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.575 | 19.8781 | 16.6206 | 19.2774 | 19.8781 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7392 | 0 | 0 | 19.8781 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 2 | 1370 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4078 | 19.7109 | 16.4642 | 19.1211 | 19.7109 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7391 | 0 | 0 | 19.7109 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 3 | 1371 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.234 | 19.537 | 16.2689 | 18.9257 | 19.537 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7390 | 0 | 0 | 19.537 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 4 | 1372 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0554 | 19.3585 | 16.0749 | 18.7317 | 19.3585 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7389 | 0 | 0 | 19.3585 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 5 | 1373 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.875 | 19.178 | 15.8879 | 18.5447 | 19.178 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7388 | 0 | 0 | 19.178 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 6 | 1374 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6972 | 19.0002 | 15.7183 | 18.3752 | 19.0002 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7387 | 0 | 0 | 19.0002 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 7 | 1375 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5256 | 18.8287 | 15.5667 | 18.2235 | 18.8287 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7386 | 0 | 0 | 18.8287 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 8 | 1376 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 158.0937 | 0 | 90.1412 | 0 | 210.7916 | 0 | 90.1412 | 0 | 549.1677 | 0 | 11.6923 | 0 | 5.0062 | 0 | 10.2508 | 0 | 5.0062 | 13.0992 | 45.0547 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.3793 | 18.6813 | 15.417 | 18.0748 | 20 |  | 488.768 | 0 | 488.768 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7385 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 9 | 1377 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10306.2561 | 0 | 10727.6409 | 0 | 2570.3966 | 0 | 1099.1827 | 0 | 24703.4763 | 0 | 762.2303 | 0 | 595.7873 | 0 | 124.9982 | 0 | 61.046 | 205.2201 | 1749.2819 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6116 | 19.9137 | 16.6197 | 19.2775 | 20 |  | 31.9992 | 0 | 31.9992 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7384 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 10 | 1378 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6636.3567 | 0 | 7358.9047 | 0 | 6067.2482 | 0 | 2594.5469 | 0 | 22657.0565 | 0 | 490.8118 | 0 | 408.6958 | 0 | 295.0499 | 0 | 144.0949 | 423.5393 | 1762.1917 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6103 | 19.9124 | 16.6332 | 19.291 | 20 |  | 32.4741 | 0 | 32.4741 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7383 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 11 | 1379 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5341.737 | 0 | 3993.4072 | 0 | 7098.5056 | 0 | 3035.5451 | 0 | 19469.1949 | 0 | 395.0643 | 0 | 221.7842 | 0 | 345.1998 | 0 | 168.5869 | 449.7376 | 1580.3728 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6012 | 19.9033 | 16.6243 | 19.2821 | 20 |  | 35.8437 | 0 | 35.8437 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7382 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 12 | 1380 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5632.5128 | 0 | 3408.192 | 0 | 7625.997 | 0 | 3211.5205 | 0 | 19878.2223 | 0 | 416.5695 | 0 | 189.2828 | 0 | 370.8517 | 0 | 178.3601 | 462.8367 | 1617.9008 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6058 | 19.9079 | 16.6406 | 19.2984 | 20 |  | 34.1503 | 0 | 34.1503 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7381 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 13 | 1381 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6219.8648 | 0 | 3723.3358 | 0 | 8534.4028 | 0 | 3546.4142 | 0 | 22024.0176 | 0 | 460.0089 | 0 | 206.7851 | 0 | 415.0274 | 0 | 196.9593 | 510.8669 | 1789.6477 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6162 | 19.9183 | 16.6656 | 19.3234 | 20 |  | 30.2742 | 0 | 30.2742 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7380 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 14 | 1382 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6322.2018 | 0 | 3750.2079 | 0 | 8796.1122 | 0 | 3604.7642 | 0 | 22473.286 | 0 | 467.5775 | 0 | 208.2775 | 0 | 427.7543 | 0 | 200.1999 | 519.5997 | 1823.409 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6201 | 19.9221 | 16.6783 | 19.3361 | 20 |  | 28.856 | 0 | 28.856 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7379 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 15 | 1383 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6327.5718 | 0 | 3724.3373 | 0 | 8993.109 | 0 | 3607.826 | 0 | 22652.8441 | 0 | 467.9747 | 0 | 206.8407 | 0 | 437.3343 | 0 | 200.37 | 519.5997 | 1832.1194 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6231 | 19.9252 | 16.6901 | 19.3479 | 20 |  | 27.7326 | 0 | 27.7326 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7378 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 16 | 1384 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4849.6967 | 0 | 2809.9653 | 0 | 7042.3133 | 0 | 2765.178 | 0 | 17467.1533 | 0 | 358.674 | 0 | 156.0587 | 0 | 342.4672 | 0 | 153.5713 | 401.7073 | 1412.4785 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6088 | 19.9109 | 16.679 | 19.3368 | 20 |  | 33.0262 | 0 | 33.0262 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7377 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 17 | 1385 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5007.8142 | 0 | 2855.3327 | 0 | 15278.5471 | 0 | 3119.1369 | 0 | 26260.8309 | 0 | 370.368 | 0 | 158.5783 | 0 | 742.9947 | 0 | 173.2293 | 436.6384 | 1881.8088 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6363 | 19.9384 | 16.7149 | 19.3727 | 20 |  | 22.828 | 0 | 22.828 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7376 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 18 | 1386 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 401.6598 | 0 | 229.0166 | 0 | 594.4729 | 0 | 236.8217 | 0 | 1461.971 | 0 | 29.706 | 0 | 12.719 | 0 | 28.9092 | 0 | 13.1525 | 34.9311 | 119.4177 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5861 | 19.8891 | 16.6557 | 19.3126 | 20 |  | 41.1175 | 0 | 41.1175 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7375 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 19 | 1387 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5781 | 19.8812 | 16.6361 | 19.293 | 20 |  | 44.0524 | 0 | 44.0524 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7374 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 20 | 1388 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5699 | 19.873 | 16.6015 | 19.2583 | 20 |  | 47.0977 | 0 | 47.0977 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7373 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 21 | 1389 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5608 | 19.8639 | 16.563 | 19.2198 | 20 |  | 50.4814 | 0 | 50.4814 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7372 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 22 | 1390 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5544 | 19.8575 | 16.5361 | 19.1929 | 20 |  | 52.8499 | 0 | 52.8499 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7371 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 23 | 1391 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5407 | 19.8438 | 16.4783 | 19.1352 | 20 |  | 57.9255 | 0 | 57.9255 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7370 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 27 | 24 | 1392 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5453 | 19.8483 | 16.4976 | 19.1544 | 20 |  | 56.2336 | 0 | 56.2336 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7369 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 1 | 1393 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4948 | 19.7978 | 16.439 | 19.0958 | 19.7978 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7368 | 0 | 0 | 19.7978 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 2 | 1394 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2891 | 19.5921 | 16.2216 | 18.8784 | 19.5921 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7367 | 0 | 0 | 19.5921 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 3 | 1395 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0817 | 19.3848 | 16.0085 | 18.6654 | 19.3848 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7366 | 0 | 0 | 19.3848 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 4 | 1396 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8718 | 19.1749 | 15.79 | 18.4468 | 19.1749 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7365 | 0 | 0 | 19.1749 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 5 | 1397 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6539 | 18.9569 | 15.5459 | 18.2028 | 18.9569 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7364 | 0 | 0 | 18.9569 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 6 | 1398 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.4344 | 18.7374 | 15.3211 | 17.9779 | 18.7374 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7363 | 0 | 0 | 18.7374 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 7 | 1399 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.2124 | 18.5155 | 15.0909 | 17.7478 | 18.5155 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7362 | 0 | 0 | 18.5155 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 8 | 1400 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 580.9083 | 0 | 331.2197 | 0 | 774.5444 | 0 | 331.2197 | 0 | 2017.8921 | 0 | 42.9628 | 0 | 18.3951 | 0 | 37.666 | 0 | 18.3951 | 48.0302 | 165.4494 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.0286 | 18.3307 | 14.9197 | 17.5775 | 20 |  | 618.7462 | 0 | 618.7462 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7361 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 9 | 1401 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 48319.7949 | 0 | 53596.7403 | 0 | 3463.2681 | 0 | 1481.0028 | 0 | 106860.8062 | 0 | 3573.6363 | 0 | 2976.6339 | 0 | 168.4185 | 0 | 82.2513 | 654.9576 | 7455.8976 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.831 | 20.1331 | 16.7739 | 19.4317 | 20.1331 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7360 | 0 | 0 | 20.1331 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 10 | 1402 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 27625.5739 | 0 | 52731.3168 | 0 | 7585.7675 | 0 | 3243.9137 | 0 | 91186.572 | 0 | 2043.1327 | 0 | 2928.5703 | 0 | 368.8953 | 0 | 180.1592 | 1174.5573 | 6695.3149 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9471 | 20.2492 | 16.9867 | 19.6445 | 20.2492 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7359 | 0 | 0 | 20.2492 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 11 | 1403 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9592.1532 | 0 | 65536.1627 | 0 | 10939.0624 | 0 | 4677.8885 | 0 | 90745.2668 | 0 | 709.4167 | 0 | 3639.7206 | 0 | 531.9658 | 0 | 259.7987 | 1929.9418 | 7070.8436 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0763 | 20.3784 | 17.1624 | 19.8202 | 20.3784 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7358 | 0 | 0 | 20.3784 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 12 | 1404 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11258.9976 | 0 | 31863.9465 | 0 | 29920.9016 | 0 | 6419.6039 | 0 | 79463.4496 | 0 | 832.6932 | 0 | 1769.6468 | 0 | 1455.0514 | 0 | 356.5293 | 1493.3034 | 5907.2241 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.175 | 20.4771 | 17.2725 | 19.9303 | 20.4771 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7357 | 0 | 0 | 20.4771 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 13 | 1405 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11662.3781 | 0 | 16434.3851 | 0 | 28882.2113 | 0 | 6649.6015 | 0 | 63628.576 | 0 | 862.5264 | 0 | 912.7262 | 0 | 1404.5399 | 0 | 369.3029 | 1226.954 | 4776.0493 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2329 | 20.535 | 17.3488 | 20.0066 | 20.535 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7356 | 0 | 0 | 20.535 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 14 | 1406 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11709.1608 | 0 | 26238.1961 | 0 | 65011.0922 | 0 | 6676.2759 | 0 | 109634.725 | 0 | 865.9863 | 0 | 1457.2062 | 0 | 3161.4849 | 0 | 370.7843 | 1685.4243 | 7540.886 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.432 | 20.7341 | 17.5795 | 20.2373 | 20.7341 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7355 | 0 | 0 | 20.7341 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 15 | 1407 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10494.2454 | 0 | 10196.9733 | 0 | 34231.4389 | 0 | 5983.561 | 0 | 60906.2186 | 0 | 776.1336 | 0 | 566.3153 | 0 | 1664.6725 | 0 | 332.3126 | 1065.3977 | 4404.8318 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.486 | 20.7881 | 17.6179 | 20.2757 | 20.7881 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7354 | 0 | 0 | 20.7881 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 16 | 1408 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8355.6577 | 0 | 11200.6857 | 0 | 95516.5944 | 0 | 4764.1908 | 0 | 119837.1286 | 0 | 617.9679 | 0 | 622.0591 | 0 | 4644.9654 | 0 | 264.5917 | 1357.9455 | 7507.5295 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7136 | 21.0157 | 17.865 | 20.5228 | 21.0157 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7353 | 0 | 0 | 21.0157 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 17 | 1409 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6489.871 | 0 | 3700.3651 | 0 | 60867.7284 | 0 | 5390.3242 | 0 | 76448.2887 | 0 | 479.978 | 0 | 205.5094 | 0 | 2959.9934 | 0 | 299.3656 | 764.1172 | 4708.9636 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8079 | 21.1099 | 17.9309 | 20.5887 | 21.1099 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7352 | 0 | 0 | 21.1099 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 18 | 1410 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1697.4762 | 0 | 967.8592 | 0 | 3201.2363 | 0 | 1093.9941 | 0 | 6960.5658 | 0 | 125.542 | 0 | 53.7526 | 0 | 155.6759 | 0 | 60.7578 | 144.0907 | 539.8189 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7058 | 21.0089 | 17.7573 | 20.4142 | 21.0089 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7351 | 0 | 0 | 21.0089 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 19 | 1411 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5645 | 20.8676 | 17.5518 | 20.2086 | 20.8676 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7350 | 0 | 0 | 20.8676 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 20 | 1412 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.41 | 20.713 | 17.3544 | 20.0112 | 20.713 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7349 | 0 | 0 | 20.713 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 21 | 1413 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2469 | 20.5499 | 17.1635 | 19.8204 | 20.5499 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7348 | 0 | 0 | 20.5499 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 22 | 1414 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0808 | 20.3838 | 16.9876 | 19.6444 | 20.3838 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7347 | 0 | 0 | 20.3838 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 23 | 1415 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9154 | 20.2184 | 16.8241 | 19.4809 | 20.2184 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7346 | 0 | 0 | 20.2184 | 0 | 0 | 0
|  | 2004 | 2 | 28 | 24 | 1416 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7461 | 20.0492 | 16.6421 | 19.2989 | 20.0492 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7345 | 0 | 0 | 20.0492 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 1 | 1417 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5325 | 19.8356 | 16.44 | 19.0969 | 19.8356 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7344 | 0 | 0 | 19.8356 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 2 | 1418 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3356 | 19.6386 | 16.2963 | 18.9532 | 19.6386 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7343 | 0 | 0 | 19.6386 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 3 | 1419 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1488 | 19.4518 | 16.1417 | 18.7986 | 19.4518 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7342 | 0 | 0 | 19.4518 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 4 | 1420 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.961 | 19.2641 | 15.9507 | 18.6075 | 19.2641 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7341 | 0 | 0 | 19.2641 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 5 | 1421 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7568 | 19.0599 | 15.6932 | 18.3501 | 19.0599 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7340 | 0 | 0 | 19.0599 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 6 | 1422 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5491 | 18.8522 | 15.4739 | 18.1308 | 18.8522 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7339 | 0 | 0 | 18.8522 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 7 | 1423 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.3516 | 18.6547 | 15.3089 | 17.9658 | 18.6547 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7338 | 0 | 0 | 18.6547 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 8 | 1424 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 899.1963 | 0 | 512.6996 | 0 | 1198.9284 | 0 | 512.6996 | 0 | 3123.524 | 0 | 66.5028 | 0 | 28.4741 | 0 | 58.3038 | 0 | 28.4741 | 74.2285 | 255.9833 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.1883 | 18.4903 | 15.1399 | 17.7977 | 20 |  | 559.5635 | 0 | 559.5635 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7337 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 9 | 1425 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 40158.3584 | 0 | 43765.2268 | 0 | 3898.9843 | 0 | 1667.3288 | 0 | 89489.8982 | 0 | 2970.0327 | 0 | 2430.6153 | 0 | 189.6073 | 0 | 92.5994 | 593.8282 | 6276.6829 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.802 | 20.104 | 16.8191 | 19.4769 | 20.104 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7336 | 0 | 0 | 20.104 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 10 | 1426 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 29558.7987 | 0 | 56477.1395 | 0 | 7555.9446 | 0 | 3231.1605 | 0 | 96823.0433 | 0 | 2186.1102 | 0 | 3136.6043 | 0 | 367.4451 | 0 | 179.4509 | 1248.7859 | 7118.3963 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9465 | 20.2485 | 17.0278 | 19.6856 | 20.2485 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7335 | 0 | 0 | 20.2485 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 11 | 1427 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9357.797 | 0 | 51159.7006 | 0 | 10805.4061 | 0 | 4620.7329 | 0 | 75943.6365 | 0 | 692.0841 | 0 | 2841.2865 | 0 | 525.4661 | 0 | 256.6244 | 1602.463 | 5917.9242 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0436 | 20.3456 | 17.1685 | 19.8263 | 20.3456 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7334 | 0 | 0 | 20.3456 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 12 | 1428 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11137.7689 | 0 | 35592.7169 | 0 | 31876.2141 | 0 | 6350.4822 | 0 | 84957.1821 | 0 | 823.7273 | 0 | 1976.7338 | 0 | 1550.1381 | 0 | 352.6905 | 1602.463 | 6305.7527 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1761 | 20.4782 | 17.3361 | 19.9938 | 20.4782 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7333 | 0 | 0 | 20.4782 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 13 | 1429 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12237.5287 | 0 | 23359.8446 | 0 | 38623.8084 | 0 | 6977.5383 | 0 | 81198.72 | 0 | 905.0634 | 0 | 1297.3495 | 0 | 1878.2731 | 0 | 387.5157 | 1467.1051 | 5935.3068 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.298 | 20.6001 | 17.4601 | 20.1179 | 20.6001 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7332 | 0 | 0 | 20.6001 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 14 | 1430 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11196.3861 | 0 | 30003.6713 | 0 | 74707.5299 | 0 | 6383.9044 | 0 | 122291.4918 | 0 | 828.0625 | 0 | 1666.3316 | 0 | 3633.022 | 0 | 354.5467 | 1842.6141 | 8324.577 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5412 | 20.8432 | 17.7156 | 20.3734 | 20.8432 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7331 | 0 | 0 | 20.8432 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 15 | 1431 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9982.7997 | 0 | 22207.4489 | 0 | 93131.8962 | 0 | 5691.9472 | 0 | 131014.092 | 0 | 738.3081 | 0 | 1233.3482 | 0 | 4528.9977 | 0 | 316.117 | 1733.4545 | 8550.2255 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8088 | 21.1109 | 17.9845 | 20.6423 | 21.1109 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7330 | 0 | 0 | 21.1109 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 16 | 1432 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9352.9337 | 0 | 9109.342 | 0 | 62968.0387 | 0 | 5332.8131 | 0 | 86763.1275 | 0 | 691.7245 | 0 | 505.9109 | 0 | 3062.1314 | 0 | 296.1716 | 1126.5271 | 5682.4654 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9495 | 21.2516 | 18.128 | 20.7858 | 21.2516 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7329 | 0 | 0 | 21.2516 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 17 | 1433 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5346.4773 | 0 | 3048.43 | 0 | 16722.9635 | 0 | 3375.5372 | 0 | 28493.408 | 0 | 395.4149 | 0 | 169.3025 | 0 | 813.2366 | 0 | 187.4692 | 471.5695 | 2036.9926 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9143 | 21.2164 | 18.0648 | 20.7226 | 21.2164 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7328 | 0 | 0 | 21.2164 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 18 | 1434 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1592.4642 | 0 | 907.984 | 0 | 2839.6479 | 0 | 1005.7982 | 0 | 6345.8943 | 0 | 117.7755 | 0 | 50.4272 | 0 | 138.0919 | 0 | 55.8596 | 135.3579 | 497.5121 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8377 | 21.1408 | 17.9772 | 20.634 | 21.1408 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7327 | 0 | 0 | 21.1408 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 19 | 1435 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7353 | 21.0384 | 17.8479 | 20.5048 | 21.0384 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7326 | 0 | 0 | 21.0384 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 20 | 1436 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6348 | 20.9379 | 17.7533 | 20.4102 | 20.9379 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7325 | 0 | 0 | 20.9379 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 21 | 1437 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5343 | 20.8374 | 17.6529 | 20.3097 | 20.8374 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7324 | 0 | 0 | 20.8374 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 22 | 1438 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4348 | 20.7379 | 17.5563 | 20.2132 | 20.7379 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7323 | 0 | 0 | 20.7379 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 23 | 1439 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3317 | 20.6348 | 17.4415 | 20.0983 | 20.6348 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7322 | 0 | 0 | 20.6348 | 0 | 0 | 0
|  | 2004 | 3 | 1 | 24 | 1440 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2241 | 20.5272 | 17.3193 | 19.9761 | 20.5272 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7321 | 0 | 0 | 20.5272 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 1 | 1441 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0671 | 20.3701 | 17.1573 | 19.8141 | 20.3701 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7320 | 0 | 0 | 20.3701 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 2 | 1442 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9097 | 20.2128 | 16.9987 | 19.6555 | 20.2128 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7319 | 0 | 0 | 20.2128 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 3 | 1443 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.753 | 20.056 | 16.8436 | 19.5004 | 20.056 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7318 | 0 | 0 | 20.056 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 4 | 1444 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5977 | 19.9008 | 16.6929 | 19.3498 | 19.9008 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7317 | 0 | 0 | 19.9008 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 5 | 1445 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4339 | 19.737 | 16.5014 | 19.1582 | 19.737 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7316 | 0 | 0 | 19.737 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 6 | 1446 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2799 | 19.583 | 16.3786 | 19.0355 | 19.583 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7315 | 0 | 0 | 19.583 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 7 | 1447 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.132 | 19.435 | 16.2499 | 18.9067 | 19.435 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7314 | 0 | 0 | 19.435 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 8 | 1448 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 316.4399 | 0 | 180.4262 | 0 | 421.9198 | 0 | 180.4262 | 0 | 1099.2122 | 0 | 23.4033 | 0 | 10.0204 | 0 | 20.5179 | 0 | 10.0204 | 26.1983 | 90.1604 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.0121 | 19.3141 | 16.1377 | 18.7955 | 20 |  | 254.2144 | 0 | 254.2144 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7313 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 9 | 1449 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8148.8626 | 0 | 7985.635 | 0 | 2790.3116 | 0 | 1193.2253 | 0 | 20118.0346 | 0 | 602.6737 | 0 | 443.5029 | 0 | 135.6927 | 0 | 66.2689 | 205.2201 | 1453.3583 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6413 | 19.9434 | 16.7995 | 19.4573 | 20 |  | 20.9828 | 0 | 20.9828 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7312 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 10 | 1450 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11016.5124 | 0 | 13994.929 | 0 | 8386.086 | 0 | 3586.1552 | 0 | 36983.6825 | 0 | 814.7594 | 0 | 777.2446 | 0 | 407.8148 | 0 | 199.1664 | 628.7593 | 2827.7446 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7065 | 20.0086 | 16.9198 | 19.5776 | 20.0086 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7311 | 0 | 0 | 20.0086 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 11 | 1451 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10346.7508 | 0 | 26803.5566 | 0 | 12914.6715 | 0 | 5522.7214 | 0 | 55587.7003 | 0 | 765.2252 | 0 | 1488.605 | 0 | 628.0396 | 0 | 306.7186 | 1174.5573 | 4363.1457 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7803 | 20.0823 | 17.0307 | 19.6885 | 20.0823 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7310 | 0 | 0 | 20.0823 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 12 | 1452 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11441.6082 | 0 | 32922.3167 | 0 | 30529.4817 | 0 | 6523.724 | 0 | 81417.1306 | 0 | 846.1987 | 0 | 1828.4262 | 0 | 1484.6466 | 0 | 362.3119 | 1554.4328 | 6076.0161 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9353 | 20.2373 | 17.2089 | 19.8667 | 20.2373 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7309 | 0 | 0 | 20.2373 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 13 | 1453 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11365.4871 | 0 | 37183.0066 | 0 | 56936.7363 | 0 | 6480.3216 | 0 | 111965.5516 | 0 | 840.5689 | 0 | 2065.0546 | 0 | 2768.8295 | 0 | 359.9015 | 1890.6444 | 7924.9989 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1754 | 20.4775 | 17.4403 | 20.0981 | 20.4775 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7308 | 0 | 0 | 20.4775 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 14 | 1454 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11334.6587 | 0 | 29772.9899 | 0 | 74247.2041 | 0 | 6462.744 | 0 | 121817.5967 | 0 | 838.2889 | 0 | 1653.5201 | 0 | 3610.6364 | 0 | 358.9252 | 1855.7133 | 8317.084 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4419 | 20.744 | 17.7022 | 20.36 | 20.744 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7307 | 0 | 0 | 20.744 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 15 | 1455 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10255.1869 | 0 | 9144.0898 | 0 | 29709.2361 | 0 | 5847.2557 | 0 | 54955.7685 | 0 | 758.4533 | 0 | 507.8407 | 0 | 1444.7581 | 0 | 324.7425 | 995.5356 | 4031.3302 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5065 | 20.8086 | 17.7354 | 20.3932 | 20.8086 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7306 | 0 | 0 | 20.8086 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 16 | 1456 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5730.3792 | 0 | 3320.0567 | 0 | 8360.3628 | 0 | 3267.3215 | 0 | 20678.1202 | 0 | 423.8075 | 0 | 184.388 | 0 | 406.5639 | 0 | 181.4592 | 471.5695 | 1667.788 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4667 | 20.7688 | 17.6775 | 20.3353 | 20.7688 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7305 | 0 | 0 | 20.7688 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 17 | 1457 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2427.4693 | 0 | 1384.0833 | 0 | 3541.2029 | 0 | 1395.0035 | 0 | 8747.759 | 0 | 179.5308 | 0 | 76.8687 | 0 | 172.2085 | 0 | 77.4751 | 205.2201 | 711.3031 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3873 | 20.6894 | 17.5822 | 20.24 | 20.6894 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7304 | 0 | 0 | 20.6894 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 18 | 1458 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 707.3452 | 0 | 403.3109 | 0 | 1075.4952 | 0 | 421.6624 | 0 | 2607.8137 | 0 | 52.3139 | 0 | 22.3989 | 0 | 52.3013 | 0 | 23.4181 | 61.1294 | 211.5615 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3142 | 20.6172 | 17.4986 | 20.1555 | 20.6172 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7303 | 0 | 0 | 20.6172 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 19 | 1459 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.225 | 20.528 | 17.3794 | 20.0362 | 20.528 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7302 | 0 | 0 | 20.528 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 20 | 1460 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1321 | 20.4352 | 17.2744 | 19.9313 | 20.4352 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7301 | 0 | 0 | 20.4352 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 21 | 1461 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0374 | 20.3405 | 17.1737 | 19.8305 | 20.3405 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7300 | 0 | 0 | 20.3405 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 22 | 1462 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9409 | 20.2439 | 17.0711 | 19.7279 | 20.2439 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7299 | 0 | 0 | 20.2439 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 23 | 1463 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8298 | 20.1328 | 16.9129 | 19.5697 | 20.1328 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7298 | 0 | 0 | 20.1328 | 0 | 0 | 0
|  | 2004 | 3 | 2 | 24 | 1464 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6969 | 19.9999 | 16.7099 | 19.3667 | 20 |  | 0.021173 | 0 | 0.021173 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7297 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 1 | 1465 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.513 | 19.8161 | 16.5159 | 19.1728 | 19.8161 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7296 | 0 | 0 | 19.8161 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 2 | 1466 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3263 | 19.6294 | 16.32 | 18.9768 | 19.6294 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7295 | 0 | 0 | 19.6294 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 3 | 1467 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1405 | 19.4436 | 16.1367 | 18.7935 | 19.4436 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7294 | 0 | 0 | 19.4436 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 4 | 1468 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9656 | 19.2687 | 15.9966 | 18.6534 | 19.2687 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7293 | 0 | 0 | 19.2687 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 5 | 1469 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7997 | 19.1027 | 15.8593 | 18.5161 | 19.1027 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7292 | 0 | 0 | 19.1027 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 6 | 1470 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6345 | 18.9375 | 15.696 | 18.3529 | 18.9375 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7291 | 0 | 0 | 18.9375 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 7 | 1471 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.4745 | 18.7775 | 15.5526 | 18.2095 | 18.7775 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7290 | 0 | 0 | 18.7775 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 8 | 1472 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 422.1443 | 0 | 240.6963 | 0 | 562.8591 | 0 | 240.6963 | 0 | 1466.3961 | 0 | 31.221 | 0 | 13.3677 | 0 | 27.3718 | 0 | 13.3677 | 34.9311 | 120.2592 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.369 | 18.672 | 15.454 | 18.1108 | 20 |  | 492.391 | 0 | 492.391 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7289 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 9 | 1473 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12492.1276 | 0 | 12298.3968 | 0 | 3935.5493 | 0 | 1682.9652 | 0 | 30409.0388 | 0 | 923.893 | 0 | 683.0233 | 0 | 191.3855 | 0 | 93.4678 | 292.5477 | 2184.3174 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6697 | 19.9727 | 16.7381 | 19.395 | 20 |  | 10.1056 | 0 | 10.1056 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7288 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 10 | 1474 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8955.6083 | 0 | 10588.5444 | 0 | 7389.0382 | 0 | 3159.7861 | 0 | 30092.977 | 0 | 662.3391 | 0 | 588.0623 | 0 | 359.3284 | 0 | 175.4869 | 545.798 | 2331.0147 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6756 | 19.9787 | 16.7646 | 19.4215 | 20 |  | 7.9064 | 0 | 7.9064 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7287 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 11 | 1475 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8003.6632 | 0 | 9839.8532 | 0 | 10419.3284 | 0 | 4455.6338 | 0 | 32718.4786 | 0 | 591.9351 | 0 | 546.4817 | 0 | 506.6912 | 0 | 247.4552 | 737.9189 | 2630.4821 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6863 | 19.9893 | 16.7839 | 19.4408 | 20 |  | 3.9663 | 0 | 3.9663 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7286 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 12 | 1476 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9346.9466 | 0 | 9370.3174 | 0 | 14786.1618 | 0 | 5329.3994 | 0 | 38832.8252 | 0 | 691.2817 | 0 | 520.4049 | 0 | 719.05 | 0 | 295.982 | 860.1777 | 3086.8962 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.724 | 20.0271 | 16.8861 | 19.5429 | 20.0271 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7285 | 0 | 0 | 20.0271 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 13 | 1477 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12344.1912 | 0 | 29712.0473 | 0 | 47300.424 | 0 | 7038.3546 | 0 | 96395.0172 | 0 | 912.9519 | 0 | 1650.1355 | 0 | 2300.2163 | 0 | 390.8933 | 1685.4243 | 6939.6214 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9421 | 20.2451 | 17.183 | 19.8399 | 20.2451 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7284 | 0 | 0 | 20.2451 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 14 | 1478 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11093.988 | 0 | 31652.7848 | 0 | 79201.8289 | 0 | 6325.5195 | 0 | 128274.1212 | 0 | 820.4894 | 0 | 1757.9194 | 0 | 3851.5795 | 0 | 351.3041 | 1951.7737 | 8733.0661 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2643 | 20.5674 | 17.5475 | 20.2043 | 20.5674 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7283 | 0 | 0 | 20.5674 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 15 | 1479 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9853.2713 | 0 | 22804.6801 | 0 | 97283.3446 | 0 | 5618.0933 | 0 | 135559.3893 | 0 | 728.7284 | 0 | 1266.517 | 0 | 4730.8823 | 0 | 312.0154 | 1829.515 | 8867.6581 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6062 | 20.9093 | 17.8884 | 20.5453 | 20.9093 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7282 | 0 | 0 | 20.9093 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 16 | 1480 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9230.5943 | 0 | 10097.8484 | 0 | 79739.7756 | 0 | 5263.0582 | 0 | 104331.2766 | 0 | 682.6765 | 0 | 560.8102 | 0 | 3877.7398 | 0 | 292.2976 | 1296.8161 | 6710.3401 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8502 | 21.1533 | 18.109 | 20.7659 | 21.1533 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7281 | 0 | 0 | 21.1533 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 17 | 1481 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6919.1335 | 0 | 3945.12 | 0 | 55308.5987 | 0 | 5679.8924 | 0 | 71852.7447 | 0 | 511.7254 | 0 | 219.1025 | 0 | 2689.6533 | 0 | 315.4475 | 777.2164 | 4513.1451 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9837 | 21.2868 | 18.1898 | 20.8466 | 21.2868 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7280 | 0 | 0 | 21.2868 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 18 | 1482 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2596.3528 | 0 | 1480.3766 | 0 | 9133.2441 | 0 | 2278.7602 | 0 | 15488.7338 | 0 | 192.0211 | 0 | 82.2166 | 0 | 444.149 | 0 | 126.5569 | 218.3192 | 1063.2628 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9419 | 21.2449 | 18.1053 | 20.7622 | 21.2449 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7279 | 0 | 0 | 21.2449 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 19 | 1483 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.9158 | 0 | 86.0485 | 0 | 201.2211 | 0 | 86.0485 | 0 | 524.234 | 0 | 11.1614 | 0 | 4.7789 | 0 | 9.7854 | 0 | 4.7789 | 13.0992 | 43.6038 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8309 | 21.1339 | 17.911 | 20.5678 | 21.1339 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7278 | 0 | 0 | 21.1339 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 20 | 1484 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7103 | 21.0133 | 17.7643 | 20.4212 | 21.0133 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7277 | 0 | 0 | 21.0133 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 21 | 1485 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5808 | 20.8838 | 17.6061 | 20.2629 | 20.8838 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7276 | 0 | 0 | 20.8838 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 22 | 1486 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4425 | 20.7455 | 17.4393 | 20.0961 | 20.7455 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7275 | 0 | 0 | 20.7455 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 23 | 1487 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3165 | 20.6196 | 17.3526 | 20.0094 | 20.6196 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7274 | 0 | 0 | 20.6196 | 0 | 0 | 0
|  | 2004 | 3 | 3 | 24 | 1488 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1999 | 20.503 | 17.2662 | 19.923 | 20.503 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7273 | 0 | 0 | 20.503 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 1 | 1489 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0322 | 20.3352 | 17.0878 | 19.7447 | 20.3352 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7272 | 0 | 0 | 20.3352 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 2 | 1490 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8742 | 20.1773 | 16.9613 | 19.6181 | 20.1773 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7271 | 0 | 0 | 20.1773 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 3 | 1491 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7187 | 20.0218 | 16.8133 | 19.4702 | 20.0218 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7270 | 0 | 0 | 20.0218 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 4 | 1492 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5611 | 19.8641 | 16.6485 | 19.3053 | 19.8641 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7269 | 0 | 0 | 19.8641 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 5 | 1493 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4049 | 19.708 | 16.497 | 19.1538 | 19.708 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7268 | 0 | 0 | 19.708 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 6 | 1494 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2503 | 19.5533 | 16.3469 | 19.0038 | 19.5533 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7267 | 0 | 0 | 19.5533 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 7 | 1495 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.099 | 19.402 | 16.206 | 18.8628 | 19.402 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7266 | 0 | 0 | 19.402 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 8 | 1496 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1495.6719 | 0 | 1031.8538 | 0 | 144.1777 | 0 | 61.6549 | 0 | 2733.3583 | 0 | 110.6169 | 0 | 57.3067 | 0 | 7.0114 | 0 | 3.4242 | 26.1983 | 204.5574 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.0112 | 19.3142 | 16.1424 | 18.7992 | 20 |  | 254.2772 | 0 | 254.2772 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7265 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 9 | 1497 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6985.6427 | 0 | 6549.7474 | 0 | 2902.3407 | 0 | 1241.1325 | 0 | 17678.8633 | 0 | 516.6443 | 0 | 363.7572 | 0 | 141.1406 | 0 | 68.9295 | 205.2201 | 1295.6917 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6576 | 19.9607 | 16.8059 | 19.4627 | 20 |  | 14.5884 | 0 | 14.5884 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7264 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 10 | 1498 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10775.1878 | 0 | 13042.7242 | 0 | 8547.325 | 0 | 3655.1061 | 0 | 36020.343 | 0 | 796.9115 | 0 | 724.3615 | 0 | 415.6558 | 0 | 202.9958 | 628.7593 | 2768.684 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7229 | 20.026 | 16.9085 | 19.5654 | 20.026 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7263 | 0 | 0 | 20.026 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 11 | 1499 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10619.4621 | 0 | 24259.8514 | 0 | 13186.1569 | 0 | 5638.8171 | 0 | 53704.2876 | 0 | 785.3944 | 0 | 1347.3337 | 0 | 641.2419 | 0 | 313.1663 | 1139.6263 | 4226.7626 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.813 | 20.1161 | 17.0382 | 19.6951 | 20.1161 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7262 | 0 | 0 | 20.1161 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 12 | 1500 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11716.856 | 0 | 24939.6897 | 0 | 26057.2696 | 0 | 6680.6635 | 0 | 69394.4788 | 0 | 866.5555 | 0 | 1385.0903 | 0 | 1267.1632 | 0 | 371.028 | 1384.1438 | 5273.9807 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9583 | 20.2614 | 17.2155 | 19.8723 | 20.2614 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7261 | 0 | 0 | 20.2614 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 13 | 1501 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12409.4452 | 0 | 20387.5058 | 0 | 34646.2624 | 0 | 7075.5608 | 0 | 74518.7741 | 0 | 917.778 | 0 | 1132.273 | 0 | 1684.8453 | 0 | 392.9596 | 1384.1438 | 5511.9997 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1286 | 20.4317 | 17.4194 | 20.0763 | 20.4317 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7260 | 0 | 0 | 20.4317 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 14 | 1502 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12455.7568 | 0 | 23069.02 | 0 | 57318.5806 | 0 | 7101.9666 | 0 | 99945.3241 | 0 | 921.2031 | 0 | 1281.1978 | 0 | 2787.3986 | 0 | 394.4261 | 1624.2949 | 7008.5206 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3817 | 20.6847 | 17.7046 | 20.3614 | 20.6847 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7259 | 0 | 0 | 20.6847 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 15 | 1503 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11480.5102 | 0 | 13392.6961 | 0 | 49057.2591 | 0 | 6545.905 | 0 | 80476.3703 | 0 | 849.0758 | 0 | 743.7981 | 0 | 2385.6511 | 0 | 363.5438 | 1296.8161 | 5638.8849 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5743 | 20.8774 | 17.8848 | 20.5416 | 20.8774 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7258 | 0 | 0 | 20.8774 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 16 | 1504 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8456.0659 | 0 | 5823.144 | 0 | 25562.5882 | 0 | 4821.4411 | 0 | 44663.2392 | 0 | 625.3939 | 0 | 323.4034 | 0 | 1243.1069 | 0 | 267.7712 | 790.3155 | 3249.9909 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.662 | 20.9651 | 17.9684 | 20.6252 | 20.9651 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7257 | 0 | 0 | 20.9651 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 17 | 1505 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4538.0914 | 0 | 2587.5082 | 0 | 7041.2974 | 0 | 2626.5995 | 0 | 16793.4966 | 0 | 335.6283 | 0 | 143.704 | 0 | 342.4178 | 0 | 145.875 | 375.509 | 1343.1341 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6641 | 20.9671 | 17.9543 | 20.6112 | 20.9671 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7256 | 0 | 0 | 20.9671 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 18 | 1506 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1433.4585 | 0 | 817.3228 | 0 | 2351.0653 | 0 | 880.186 | 0 | 5482.0326 | 0 | 106.0158 | 0 | 45.3921 | 0 | 114.3321 | 0 | 48.8834 | 122.2588 | 436.8822 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6313 | 20.9344 | 17.9161 | 20.573 | 20.9344 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7255 | 0 | 0 | 20.9344 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 19 | 1507 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.7806 | 0 | 85.9714 | 0 | 201.0409 | 0 | 85.9714 | 0 | 523.7644 | 0 | 11.1514 | 0 | 4.7746 | 0 | 9.7766 | 0 | 4.7746 | 13.0992 | 43.5765 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5689 | 20.872 | 17.805 | 20.4618 | 20.872 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7254 | 0 | 0 | 20.872 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 20 | 1508 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5019 | 20.805 | 17.7281 | 20.385 | 20.805 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7253 | 0 | 0 | 20.805 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 21 | 1509 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4301 | 20.7332 | 17.6406 | 20.2975 | 20.7332 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7252 | 0 | 0 | 20.7332 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 22 | 1510 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3544 | 20.6575 | 17.5524 | 20.2092 | 20.6575 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7251 | 0 | 0 | 20.6575 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 23 | 1511 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2767 | 20.5798 | 17.4681 | 20.125 | 20.5798 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7250 | 0 | 0 | 20.5798 | 0 | 0 | 0
|  | 2004 | 3 | 4 | 24 | 1512 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1907 | 20.4937 | 17.355 | 20.0118 | 20.4937 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7249 | 0 | 0 | 20.4937 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 1 | 1513 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0522 | 20.3552 | 17.2021 | 19.8589 | 20.3552 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7248 | 0 | 0 | 20.3552 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 2 | 1514 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9178 | 20.2208 | 17.0806 | 19.7374 | 20.2208 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7247 | 0 | 0 | 20.2208 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 3 | 1515 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7874 | 20.0905 | 16.9629 | 19.6198 | 20.0905 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7246 | 0 | 0 | 20.0905 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 4 | 1516 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6546 | 19.9577 | 16.8223 | 19.4791 | 19.9577 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7245 | 0 | 0 | 19.9577 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 5 | 1517 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5177 | 19.8207 | 16.6716 | 19.3284 | 19.8207 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7244 | 0 | 0 | 19.8207 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 6 | 1518 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3802 | 19.6832 | 16.5322 | 19.1891 | 19.6832 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7243 | 0 | 0 | 19.6832 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 7 | 1519 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2413 | 19.5444 | 16.3886 | 19.0454 | 19.5444 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7242 | 0 | 0 | 19.5444 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 8 | 1520 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2418.277 | 0 | 1646.5157 | 0 | 351.458 | 0 | 150.2945 | 0 | 4566.5452 | 0 | 178.851 | 0 | 91.4435 | 0 | 17.0914 | 0 | 8.347 | 34.9311 | 330.6639 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.1355 | 19.4376 | 16.2754 | 18.9332 | 20 |  | 208.4633 | 0 | 208.4633 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7241 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 9 | 1521 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9278.1218 | 0 | 8853.5236 | 0 | 3323.1808 | 0 | 1421.0971 | 0 | 22875.9233 | 0 | 686.1915 | 0 | 491.7034 | 0 | 161.6061 | 0 | 78.9243 | 244.5175 | 1662.9428 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6451 | 19.9472 | 16.7885 | 19.4463 | 20 |  | 19.5739 | 0 | 19.5739 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7240 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 10 | 1522 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8380.6882 | 0 | 9157.064 | 0 | 7422.2216 | 0 | 3173.9764 | 0 | 28133.9502 | 0 | 619.8191 | 0 | 508.5613 | 0 | 360.9421 | 0 | 176.275 | 532.6989 | 2198.2964 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6616 | 19.9637 | 16.8077 | 19.4655 | 20 |  | 13.4688 | 0 | 13.4688 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7239 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 11 | 1523 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7004.9181 | 0 | 6334.094 | 0 | 9201.5906 | 0 | 3934.8907 | 0 | 26475.4933 | 0 | 518.0699 | 0 | 351.7803 | 0 | 447.4727 | 0 | 218.5344 | 606.9274 | 2142.7847 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6628 | 19.9649 | 16.8296 | 19.4874 | 20 |  | 13.0008 | 0 | 13.0008 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7238 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 12 | 1524 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8791.0873 | 0 | 7540.109 | 0 | 13157.2083 | 0 | 5012.4621 | 0 | 34500.8667 | 0 | 650.1714 | 0 | 418.7595 | 0 | 639.8341 | 0 | 278.3801 | 777.2164 | 2764.3615 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6971 | 19.9992 | 16.9017 | 19.5595 | 20 |  | 0.30146 | 0 | 0.30146 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7237 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 13 | 1525 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11870.6619 | 0 | 14846.6306 | 0 | 26808.3453 | 0 | 6768.3598 | 0 | 60293.9977 | 0 | 877.9306 | 0 | 824.5461 | 0 | 1303.688 | 0 | 375.8984 | 1200.7556 | 4582.8188 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7859 | 20.088 | 17.0393 | 19.6971 | 20.088 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7236 | 0 | 0 | 20.088 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 14 | 1526 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10734.6412 | 0 | 10226.5277 | 0 | 24809.8849 | 0 | 6120.6288 | 0 | 51891.6826 | 0 | 793.9128 | 0 | 567.9567 | 0 | 1206.503 | 0 | 339.925 | 1008.6347 | 3916.9322 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8545 | 20.1566 | 17.1263 | 19.7841 | 20.1566 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7235 | 0 | 0 | 20.1566 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 15 | 1527 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9984.2688 | 0 | 8248.5105 | 0 | 25998.6439 | 0 | 5692.7848 | 0 | 49924.208 | 0 | 738.4167 | 0 | 458.1024 | 0 | 1264.3123 | 0 | 316.1636 | 934.4062 | 3711.4012 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9175 | 20.2196 | 17.1903 | 19.8481 | 20.2196 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7234 | 0 | 0 | 20.2196 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 16 | 1528 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6883.4602 | 0 | 4087.4982 | 0 | 11553.7535 | 0 | 3924.7799 | 0 | 26449.4917 | 0 | 509.0871 | 0 | 227.0098 | 0 | 561.8582 | 0 | 217.9728 | 580.7291 | 2096.657 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9131 | 20.2151 | 17.188 | 19.8458 | 20.2151 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7233 | 0 | 0 | 20.2151 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 17 | 1529 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2906.3606 | 0 | 1657.1354 | 0 | 4254.0317 | 0 | 1672.7899 | 0 | 10490.3176 | 0 | 214.9487 | 0 | 92.0333 | 0 | 206.8733 | 0 | 92.9027 | 244.5175 | 851.2755 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8572 | 20.1593 | 17.1153 | 19.7731 | 20.1593 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7232 | 0 | 0 | 20.1593 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 18 | 1530 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 300.789 | 0 | 171.5025 | 0 | 419.5553 | 0 | 174.1881 | 0 | 1066.0349 | 0 | 22.2458 | 0 | 9.5248 | 0 | 20.4029 | 0 | 9.674 | 26.1983 | 88.0458 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7965 | 20.0996 | 17.0348 | 19.6916 | 20.0996 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7231 | 0 | 0 | 20.0996 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 19 | 1531 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7297 | 20.0327 | 16.955 | 19.6119 | 20.0327 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7230 | 0 | 0 | 20.0327 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 20 | 1532 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6461 | 19.9492 | 16.8177 | 19.4745 | 20 |  | 18.8431 | 0 | 18.8431 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7229 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 21 | 1533 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6037 | 19.9067 | 16.7439 | 19.4007 | 20 |  | 34.5781 | 0 | 34.5781 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7228 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 22 | 1534 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5927 | 19.8958 | 16.6977 | 19.3546 | 20 |  | 38.6385 | 0 | 38.6385 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7227 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 23 | 1535 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5946 | 19.8976 | 16.7054 | 19.3623 | 20 |  | 37.9618 | 0 | 37.9618 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7226 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 5 | 24 | 1536 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5909 | 19.894 | 16.69 | 19.3469 | 20 |  | 39.3152 | 0 | 39.3152 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7225 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 1 | 1537 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5395 | 19.8426 | 16.6276 | 19.2844 | 19.8426 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7224 | 0 | 0 | 19.8426 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 2 | 1538 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3863 | 19.6894 | 16.4878 | 19.1446 | 19.6894 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7223 | 0 | 0 | 19.6894 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 3 | 1539 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2355 | 19.5385 | 16.3444 | 19.0013 | 19.5385 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7222 | 0 | 0 | 19.5385 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 4 | 1540 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0852 | 19.3883 | 16.1957 | 18.8525 | 19.3883 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7221 | 0 | 0 | 19.3883 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 5 | 1541 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9355 | 19.2386 | 16.0474 | 18.7042 | 19.2386 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7220 | 0 | 0 | 19.2386 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 6 | 1542 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7845 | 19.0875 | 15.892 | 18.5488 | 19.0875 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7219 | 0 | 0 | 19.0875 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 7 | 1543 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6331 | 18.9361 | 15.7391 | 18.396 | 18.9361 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7218 | 0 | 0 | 18.9361 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 8 | 1544 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3792.1781 | 0 | 2578.7577 | 0 | 407.4735 | 0 | 174.2485 | 0 | 6952.6579 | 0 | 280.462 | 0 | 143.218 | 0 | 19.8154 | 0 | 9.6773 | 74.2285 | 527.4013 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.5271 | 18.8291 | 15.6407 | 18.2985 | 20 |  | 433.9879 | 0 | 433.9879 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7217 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 9 | 1545 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2975.981 | 0 | 2290.9434 | 0 | 2434.7225 | 0 | 1041.1642 | 0 | 8742.8112 | 0 | 220.0977 | 0 | 127.2335 | 0 | 118.4004 | 0 | 57.8238 | 157.1898 | 680.7451 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.5875 | 19.8896 | 16.6727 | 19.3305 | 20 |  | 40.9236 | 0 | 40.9236 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7216 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 10 | 1546 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3659.8608 | 0 | 2271.2657 | 0 | 4719.2332 | 0 | 2018.0932 | 0 | 12668.4529 | 0 | 270.6761 | 0 | 126.1406 | 0 | 229.496 | 0 | 112.08 | 292.5477 | 1030.9404 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6041 | 19.9062 | 16.7068 | 19.3646 | 20 |  | 34.7775 | 0 | 34.7775 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7215 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 11 | 1547 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7775.7183 | 0 | 7975.6831 | 0 | 10138.2877 | 0 | 4335.452 | 0 | 30225.141 | 0 | 575.0767 | 0 | 442.9502 | 0 | 493.0242 | 0 | 240.7806 | 689.8887 | 2441.7204 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6603 | 19.9624 | 16.7799 | 19.4377 | 20 |  | 13.9397 | 0 | 13.9397 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7214 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 12 | 1548 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7130.0332 | 0 | 4701.4868 | 0 | 9865.8701 | 0 | 4065.3698 | 0 | 25762.7598 | 0 | 527.3231 | 0 | 261.1092 | 0 | 479.7766 | 0 | 225.7808 | 593.8282 | 2087.8181 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6515 | 19.9536 | 16.786 | 19.4438 | 20 |  | 17.1974 | 0 | 17.1974 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7213 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 13 | 1549 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9788.7064 | 0 | 7624.1048 | 0 | 15827.8323 | 0 | 5581.28 | 0 | 38821.9235 | 0 | 723.9533 | 0 | 423.4244 | 0 | 769.7064 | 0 | 309.9708 | 860.1777 | 3087.2327 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6962 | 19.9983 | 16.8536 | 19.5114 | 20 |  | 0.64505 | 0 | 0.64505 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7212 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 14 | 1550 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10764.0645 | 0 | 10140.7433 | 0 | 24615.7419 | 0 | 6137.4052 | 0 | 51657.9549 | 0 | 796.0889 | 0 | 563.1925 | 0 | 1197.0618 | 0 | 340.8567 | 1008.6347 | 3905.8346 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.744 | 20.046 | 16.939 | 19.5968 | 20.046 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7211 | 0 | 0 | 20.046 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 15 | 1551 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7849.3388 | 0 | 4794.9502 | 0 | 12062.9472 | 0 | 4475.5002 | 0 | 29182.7363 | 0 | 580.5216 | 0 | 266.3 | 0 | 586.6203 | 0 | 248.5585 | 654.9576 | 2336.9579 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7247 | 20.0268 | 16.9194 | 19.5772 | 20.0268 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7210 | 0 | 0 | 20.0268 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 16 | 1552 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8973.6708 | 0 | 6230.613 | 0 | 28631.8245 | 0 | 5116.5667 | 0 | 48952.6749 | 0 | 663.6749 | 0 | 346.0332 | 0 | 1392.3636 | 0 | 284.1618 | 860.1777 | 3546.4113 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7622 | 20.0643 | 16.9566 | 19.6144 | 20.0643 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7209 | 0 | 0 | 20.0643 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 17 | 1553 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4373.7558 | 0 | 2493.8082 | 0 | 6629.3078 | 0 | 2528.2642 | 0 | 16025.1359 | 0 | 323.4743 | 0 | 138.5001 | 0 | 322.3828 | 0 | 140.4137 | 362.4099 | 1287.1808 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6994 | 20.0015 | 16.8765 | 19.5343 | 20.0015 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7208 | 0 | 0 | 20.0015 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 18 | 1554 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2015.1578 | 0 | 1148.9935 | 0 | 3405.4784 | 0 | 1254.8984 | 0 | 7824.5282 | 0 | 149.0371 | 0 | 63.8123 | 0 | 165.6082 | 0 | 69.694 | 170.289 | 618.4406 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6362 | 19.9392 | 16.8024 | 19.4593 | 20 |  | 22.5313 | 0 | 22.5313 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7207 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 19 | 1555 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5991 | 19.9022 | 16.7247 | 19.3815 | 20 |  | 36.2699 | 0 | 36.2699 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7206 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 20 | 1556 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5918 | 19.8949 | 16.6939 | 19.3507 | 20 |  | 38.9769 | 0 | 38.9769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7205 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 21 | 1557 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5809 | 19.8839 | 16.6477 | 19.3045 | 20 |  | 43.0373 | 0 | 43.0373 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7204 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 22 | 1558 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5891 | 19.8921 | 16.6823 | 19.3392 | 20 |  | 39.992 | 0 | 39.992 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7203 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 23 | 1559 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5836 | 19.8867 | 16.6592 | 19.3161 | 20 |  | 42.0222 | 0 | 42.0222 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7202 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 6 | 24 | 1560 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5918 | 19.8949 | 16.6939 | 19.3507 | 20 |  | 38.9769 | 0 | 38.9769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7201 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 1 | 1561 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5559 | 19.859 | 16.6968 | 19.3537 | 19.859 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7200 | 0 | 0 | 19.859 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 2 | 1562 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4199 | 19.723 | 16.5767 | 19.2336 | 19.723 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7199 | 0 | 0 | 19.723 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 3 | 1563 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2806 | 19.5837 | 16.4268 | 19.0836 | 19.5837 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7198 | 0 | 0 | 19.5837 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 4 | 1564 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1482 | 19.4512 | 16.316 | 18.9729 | 19.4512 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7197 | 0 | 0 | 19.4512 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 5 | 1565 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.017 | 19.3201 | 16.1887 | 18.8456 | 19.3201 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7196 | 0 | 0 | 19.3201 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 6 | 1566 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8743 | 19.1774 | 16.0088 | 18.6656 | 19.1774 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7195 | 0 | 0 | 19.1774 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 7 | 1567 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7458 | 19.0489 | 15.9256 | 18.5824 | 19.0489 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7194 | 0 | 0 | 19.0489 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 8 | 1568 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1830.9597 | 0 | 1216.5225 | 0 | 436.7883 | 0 | 186.7845 | 0 | 3671.055 | 0 | 135.4142 | 0 | 67.5627 | 0 | 21.241 | 0 | 10.3736 | 34.9311 | 269.5225 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.6477 | 18.9498 | 15.8228 | 18.4806 | 20 |  | 389.2622 | 0 | 389.2622 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7193 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 9 | 1569 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8180.1276 | 0 | 7477.9577 | 0 | 3525.759 | 0 | 1507.7259 | 0 | 20691.5702 | 0 | 604.986 | 0 | 415.3078 | 0 | 171.4574 | 0 | 83.7355 | 253.2503 | 1528.737 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6506 | 19.9527 | 16.8353 | 19.4931 | 20 |  | 17.5284 | 0 | 17.5284 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7192 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 10 | 1570 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 16871.6602 | 0 | 23568.6672 | 0 | 10166.4597 | 0 | 4347.4992 | 0 | 54954.2863 | 0 | 1247.7946 | 0 | 1308.947 | 0 | 494.3942 | 0 | 241.4496 | 886.376 | 4178.9614 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.762 | 20.0641 | 16.9863 | 19.6441 | 20.0641 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7191 | 0 | 0 | 20.0641 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 11 | 1571 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9373.1783 | 0 | 12988.0925 | 0 | 11959.5513 | 0 | 5114.2818 | 0 | 39435.1039 | 0 | 693.2217 | 0 | 721.3274 | 0 | 581.5922 | 0 | 284.0349 | 860.1777 | 3140.3538 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7842 | 20.0863 | 17.019 | 19.6768 | 20.0863 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7190 | 0 | 0 | 20.0863 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 12 | 1572 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12120.8783 | 0 | 26856.1067 | 0 | 27355.4432 | 0 | 6911.0271 | 0 | 73243.4553 | 0 | 896.4362 | 0 | 1491.5235 | 0 | 1330.2933 | 0 | 383.8218 | 1493.3034 | 5595.3781 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9099 | 20.212 | 17.1632 | 19.821 | 20.212 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7189 | 0 | 0 | 20.212 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 13 | 1573 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12674.9402 | 0 | 17755.5655 | 0 | 31206.6254 | 0 | 7226.9396 | 0 | 68864.0707 | 0 | 937.4135 | 0 | 986.1013 | 0 | 1517.576 | 0 | 401.3668 | 1371.0446 | 5213.5023 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0275 | 20.3296 | 17.2979 | 19.9557 | 20.3296 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7188 | 0 | 0 | 20.3296 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 14 | 1574 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7676.0047 | 0 | 4584.795 | 0 | 10769.8231 | 0 | 4376.6694 | 0 | 27407.2922 | 0 | 567.7021 | 0 | 254.6285 | 0 | 523.7358 | 0 | 243.0697 | 628.7593 | 2217.8953 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0234 | 20.3254 | 17.2891 | 19.9469 | 20.3254 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7187 | 0 | 0 | 20.3254 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 15 | 1575 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11262.3512 | 0 | 19411.6566 | 0 | 80446.4765 | 0 | 6421.516 | 0 | 117542.0003 | 0 | 832.9412 | 0 | 1078.0767 | 0 | 3912.1066 | 0 | 356.6355 | 1711.6226 | 7891.3826 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2869 | 20.589 | 17.5813 | 20.2391 | 20.589 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7186 | 0 | 0 | 20.589 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 16 | 1576 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9170.2397 | 0 | 6365.2418 | 0 | 29668.6384 | 0 | 5228.6454 | 0 | 50432.7654 | 0 | 678.2128 | 0 | 353.5102 | 0 | 1442.7838 | 0 | 290.3864 | 886.376 | 3651.2692 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3313 | 20.6334 | 17.5355 | 20.1933 | 20.6334 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7185 | 0 | 0 | 20.6334 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 17 | 1577 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5187.6641 | 0 | 2957.8787 | 0 | 9051.3583 | 0 | 3054.1587 | 0 | 20251.0597 | 0 | 383.6694 | 0 | 164.2735 | 0 | 440.1669 | 0 | 169.6206 | 436.6384 | 1594.3688 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2858 | 20.5878 | 17.4812 | 20.139 | 20.5878 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7184 | 0 | 0 | 20.5878 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 18 | 1578 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1695.8544 | 0 | 966.9345 | 0 | 2735.49 | 0 | 1037.9186 | 0 | 6436.1974 | 0 | 125.422 | 0 | 53.7012 | 0 | 133.0267 | 0 | 57.6435 | 144.0907 | 513.8841 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2201 | 20.5232 | 17.3927 | 20.0496 | 20.5232 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7183 | 0 | 0 | 20.5232 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 19 | 1579 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.4736 | 0 | 85.7963 | 0 | 200.6314 | 0 | 85.7963 | 0 | 522.6977 | 0 | 11.1287 | 0 | 4.7649 | 0 | 9.7567 | 0 | 4.7649 | 13.0992 | 43.5144 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1352 | 20.4383 | 17.2982 | 19.9551 | 20.4383 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7182 | 0 | 0 | 20.4383 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 20 | 1580 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0414 | 20.3444 | 17.1805 | 19.8373 | 20.3444 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7181 | 0 | 0 | 20.3444 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 21 | 1581 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9466 | 20.2497 | 17.0826 | 19.7394 | 20.2497 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7180 | 0 | 0 | 20.2497 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 22 | 1582 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8418 | 20.1449 | 16.9454 | 19.6022 | 20.1449 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7179 | 0 | 0 | 20.1449 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 23 | 1583 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7308 | 20.0338 | 16.8139 | 19.4707 | 20.0338 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7178 | 0 | 0 | 20.0338 | 0 | 0 | 0
|  | 2004 | 3 | 7 | 24 | 1584 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6107 | 19.9138 | 16.6648 | 19.3216 | 20 |  | 31.9702 | 0 | 31.9702 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7177 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 1 | 1585 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5167 | 19.8197 | 16.5313 | 19.1882 | 19.8197 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7176 | 0 | 0 | 19.8197 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 2 | 1586 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3318 | 19.6348 | 16.3312 | 18.988 | 19.6348 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7175 | 0 | 0 | 19.6348 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 3 | 1587 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1514 | 19.4544 | 16.165 | 18.8218 | 19.4544 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7174 | 0 | 0 | 19.4544 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 4 | 1588 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9691 | 19.2721 | 15.9762 | 18.6331 | 19.2721 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7173 | 0 | 0 | 19.2721 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 5 | 1589 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7867 | 19.0897 | 15.7934 | 18.4502 | 19.0897 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7172 | 0 | 0 | 19.0897 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 6 | 1590 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5988 | 18.9018 | 15.5873 | 18.2441 | 18.9018 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7171 | 0 | 0 | 18.9018 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 7 | 1591 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.409 | 18.7121 | 15.3913 | 18.0482 | 18.7121 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7170 | 0 | 0 | 18.7121 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 8 | 1592 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12463.5326 | 0 | 8408.2382 | 0 | 858.8208 | 0 | 367.2589 | 0 | 22097.8505 | 0 | 921.7782 | 0 | 466.9733 | 0 | 41.7644 | 0 | 20.3967 | 96.0605 | 1546.973 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.3192 | 18.6212 | 15.3359 | 17.9937 | 20 |  | 511.0437 | 0 | 511.0437 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7169 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 9 | 1593 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 25836.5042 | 0 | 25422.3444 | 0 | 5943.9682 | 0 | 2541.8285 | 0 | 59744.6453 | 0 | 1910.8167 | 0 | 1411.8958 | 0 | 289.0548 | 0 | 141.167 | 606.9274 | 4359.8617 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7334 | 20.0354 | 16.8105 | 19.4683 | 20.0354 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7168 | 0 | 0 | 20.0354 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 10 | 1594 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 27294.4702 | 0 | 45928.6346 | 0 | 9139.0277 | 0 | 3908.1368 | 0 | 86270.2693 | 0 | 2018.645 | 0 | 2550.7657 | 0 | 444.4303 | 0 | 217.0485 | 1261.885 | 6492.7745 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.866 | 20.1681 | 17.0115 | 19.6693 | 20.1681 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7167 | 0 | 0 | 20.1681 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 11 | 1595 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11894.1381 | 0 | 38364.9215 | 0 | 13457.6049 | 0 | 5754.8968 | 0 | 69471.5614 | 0 | 879.6669 | 0 | 2130.6953 | 0 | 654.4424 | 0 | 319.6131 | 1515.1353 | 5499.553 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9629 | 20.2649 | 17.1522 | 19.81 | 20.2649 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7166 | 0 | 0 | 20.2649 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 12 | 1596 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12225.8474 | 0 | 25637.8645 | 0 | 26716.3426 | 0 | 6970.8779 | 0 | 71550.9323 | 0 | 904.1995 | 0 | 1423.8652 | 0 | 1299.2139 | 0 | 387.1458 | 1467.1051 | 5481.5294 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.072 | 20.3741 | 17.2849 | 19.9427 | 20.3741 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7165 | 0 | 0 | 20.3741 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 13 | 1597 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13081.51 | 0 | 23484.181 | 0 | 39216.9933 | 0 | 7458.7557 | 0 | 83241.44 | 0 | 967.4826 | 0 | 1304.2549 | 0 | 1907.1197 | 0 | 414.2413 | 1576.2647 | 6169.3631 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2153 | 20.5174 | 17.4303 | 20.0881 | 20.5174 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7164 | 0 | 0 | 20.5174 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 14 | 1598 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12951.2745 | 0 | 18498.0226 | 0 | 45931.255 | 0 | 7384.4986 | 0 | 84765.0507 | 0 | 957.8506 | 0 | 1027.3356 | 0 | 2233.6337 | 0 | 410.1173 | 1502.0362 | 6130.9734 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.368 | 20.6701 | 17.6023 | 20.2601 | 20.6701 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7163 | 0 | 0 | 20.6701 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 15 | 1599 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11997.8997 | 0 | 13796.3558 | 0 | 51298.9657 | 0 | 6840.9077 | 0 | 83934.1289 | 0 | 887.3409 | 0 | 766.2164 | 0 | 2494.6651 | 0 | 379.9275 | 1384.1438 | 5912.2937 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5165 | 20.8186 | 17.7463 | 20.4041 | 20.8186 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7162 | 0 | 0 | 20.8186 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 16 | 1600 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10152.2406 | 0 | 9247.5872 | 0 | 68041.7209 | 0 | 5788.5582 | 0 | 93230.1069 | 0 | 750.8396 | 0 | 513.5887 | 0 | 3308.8642 | 0 | 321.4826 | 1283.7169 | 6178.492 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6904 | 20.9924 | 17.9184 | 20.5762 | 20.9924 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7161 | 0 | 0 | 20.9924 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 17 | 1601 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6128.9192 | 0 | 3494.5592 | 0 | 18421.3486 | 0 | 3976.7405 | 0 | 32021.5674 | 0 | 453.2827 | 0 | 194.0794 | 0 | 895.8289 | 0 | 220.8586 | 545.798 | 2309.8476 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6829 | 20.985 | 17.8937 | 20.5515 | 20.985 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7160 | 0 | 0 | 20.985 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 18 | 1602 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3357.212 | 0 | 1914.1998 | 0 | 12905.3088 | 0 | 3194.9531 | 0 | 21371.6738 | 0 | 248.2928 | 0 | 106.31 | 0 | 627.5843 | 0 | 177.44 | 292.5477 | 1452.1748 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6672 | 20.9702 | 17.8627 | 20.5195 | 20.9702 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7159 | 0 | 0 | 20.9702 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 19 | 1603 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.3975 | 0 | 85.7529 | 0 | 200.5299 | 0 | 85.7529 | 0 | 522.4333 | 0 | 11.1231 | 0 | 4.7625 | 0 | 9.7518 | 0 | 4.7625 | 13.0992 | 43.499 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5898 | 20.8929 | 17.7779 | 20.4347 | 20.8929 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7158 | 0 | 0 | 20.8929 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 20 | 1604 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.509 | 20.812 | 17.6905 | 20.3473 | 20.812 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7157 | 0 | 0 | 20.812 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 21 | 1605 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4252 | 20.7283 | 17.5974 | 20.2542 | 20.7283 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7156 | 0 | 0 | 20.7283 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 22 | 1606 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3386 | 20.6417 | 17.5015 | 20.1583 | 20.6417 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7155 | 0 | 0 | 20.6417 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 23 | 1607 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.251 | 20.5541 | 17.4106 | 20.0674 | 20.5541 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7154 | 0 | 0 | 20.5541 | 0 | 0 | 0
|  | 2004 | 3 | 8 | 24 | 1608 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1607 | 20.4637 | 17.311 | 19.9679 | 20.4637 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7153 | 0 | 0 | 20.4637 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 1 | 1609 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.017 | 20.3201 | 17.1502 | 19.807 | 20.3201 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7152 | 0 | 0 | 20.3201 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 2 | 1610 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8601 | 20.1632 | 16.9505 | 19.6074 | 20.1632 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7151 | 0 | 0 | 20.1632 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 3 | 1611 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.692 | 19.995 | 16.7459 | 19.4027 | 19.995 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7150 | 0 | 0 | 19.995 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 4 | 1612 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5337 | 19.8367 | 16.6189 | 19.2758 | 19.8367 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7149 | 0 | 0 | 19.8367 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 5 | 1613 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3778 | 19.6808 | 16.4706 | 19.1275 | 19.6808 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7148 | 0 | 0 | 19.6808 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 6 | 1614 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2252 | 19.5283 | 16.3285 | 18.9854 | 19.5283 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7147 | 0 | 0 | 19.5283 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 7 | 1615 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0668 | 19.3699 | 16.1511 | 18.808 | 19.3699 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7146 | 0 | 0 | 19.3699 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 8 | 1616 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9159.9029 | 0 | 6112.3859 | 0 | 977.0411 | 0 | 417.8136 | 0 | 16667.1435 | 0 | 677.4483 | 0 | 339.4672 | 0 | 47.5134 | 0 | 23.2044 | 122.2588 | 1209.892 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.98 | 19.282 | 16.0628 | 18.7206 | 20 |  | 266.1183 | 0 | 266.1183 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7145 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 9 | 1617 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 31688.361 | 0 | 31457.643 | 0 | 5963.7328 | 0 | 2550.2805 | 0 | 71660.0172 | 0 | 2343.6084 | 0 | 1747.0817 | 0 | 290.0159 | 0 | 141.6364 | 668.0568 | 5190.3993 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7711 | 20.0732 | 16.8595 | 19.5173 | 20.0732 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7144 | 0 | 0 | 20.0732 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 10 | 1618 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 32180.6702 | 0 | 55885.7138 | 0 | 8702.7564 | 0 | 3721.5735 | 0 | 100490.7139 | 0 | 2380.0186 | 0 | 3103.7579 | 0 | 423.2144 | 0 | 206.6872 | 1445.2732 | 7558.9514 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9371 | 20.2391 | 17.0544 | 19.7122 | 20.2391 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7143 | 0 | 0 | 20.2391 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 11 | 1619 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12076.5251 | 0 | 41897.1824 | 0 | 13242.5236 | 0 | 5662.9213 | 0 | 72879.1524 | 0 | 893.1559 | 0 | 2326.8686 | 0 | 643.983 | 0 | 314.505 | 1602.463 | 5780.9755 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0248 | 20.3269 | 17.1472 | 19.805 | 20.3269 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7142 | 0 | 0 | 20.3269 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 12 | 1620 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10710.8836 | 0 | 45238.9819 | 0 | 35987.2352 | 0 | 6107.0828 | 0 | 98044.1835 | 0 | 792.1557 | 0 | 2512.4641 | 0 | 1750.0568 | 0 | 339.1727 | 2012.9031 | 7406.7524 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1915 | 20.4936 | 17.3368 | 19.9946 | 20.4936 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7141 | 0 | 0 | 20.4936 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 13 | 1621 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13206.1873 | 0 | 23740.3875 | 0 | 39635.5201 | 0 | 7529.8437 | 0 | 84111.9385 | 0 | 976.7035 | 0 | 1318.4839 | 0 | 1927.4726 | 0 | 418.1894 | 1602.463 | 6243.3124 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3186 | 20.6207 | 17.4684 | 20.1262 | 20.6207 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7140 | 0 | 0 | 20.6207 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 14 | 1622 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9305.5484 | 0 | 6154.9186 | 0 | 14604.2662 | 0 | 5305.7951 | 0 | 35370.5284 | 0 | 688.2199 | 0 | 341.8294 | 0 | 710.2045 | 0 | 294.6711 | 790.3155 | 2825.2404 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3022 | 20.6043 | 17.4444 | 20.1022 | 20.6043 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7139 | 0 | 0 | 20.6043 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 15 | 1623 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9051.5562 | 0 | 5822.0504 | 0 | 15450.337 | 0 | 5160.975 | 0 | 35484.9186 | 0 | 669.4352 | 0 | 323.3427 | 0 | 751.3488 | 0 | 286.6281 | 777.2164 | 2807.9712 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2861 | 20.5882 | 17.4289 | 20.0866 | 20.5882 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7138 | 0 | 0 | 20.5882 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 16 | 1624 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6868.066 | 0 | 4012.9628 | 0 | 10728.087 | 0 | 3916.0025 | 0 | 25525.1183 | 0 | 507.9486 | 0 | 222.8703 | 0 | 521.7061 | 0 | 217.4853 | 571.9963 | 2042.0067 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2404 | 20.5425 | 17.3811 | 20.0389 | 20.5425 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7137 | 0 | 0 | 20.5425 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 17 | 1625 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2583.9934 | 0 | 1473.3295 | 0 | 3701.1596 | 0 | 1485.8679 | 0 | 9244.3504 | 0 | 191.107 | 0 | 81.8252 | 0 | 179.9871 | 0 | 82.5215 | 218.3192 | 753.7601 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1469 | 20.449 | 17.2867 | 19.9445 | 20.449 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7136 | 0 | 0 | 20.449 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 18 | 1626 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1853.8129 | 0 | 1056.9986 | 0 | 2955.545 | 0 | 1131.6376 | 0 | 6997.9941 | 0 | 137.1043 | 0 | 58.7032 | 0 | 143.7279 | 0 | 62.8484 | 157.1898 | 559.5737 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0733 | 20.3764 | 17.2147 | 19.8716 | 20.3764 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7135 | 0 | 0 | 20.3764 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 19 | 1627 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 150.3317 | 0 | 85.7155 | 0 | 200.4423 | 0 | 85.7155 | 0 | 522.205 | 0 | 11.1182 | 0 | 4.7604 | 0 | 9.7475 | 0 | 4.7604 | 13.0992 | 43.4857 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9798 | 20.2828 | 17.1148 | 19.7716 | 20.2828 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7134 | 0 | 0 | 20.2828 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 20 | 1628 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8811 | 20.1841 | 17.0042 | 19.661 | 20.1841 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7133 | 0 | 0 | 20.1841 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 21 | 1629 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7815 | 20.0845 | 16.9016 | 19.5584 | 20.0845 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7132 | 0 | 0 | 20.0845 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 22 | 1630 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6801 | 19.9832 | 16.7943 | 19.4512 | 20 |  | 6.2447 | 0 | 6.2447 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7131 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 23 | 1631 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5918 | 19.8949 | 16.6939 | 19.3507 | 20 |  | 38.9769 | 0 | 38.9769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7130 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 9 | 24 | 1632 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5891 | 19.8921 | 16.6823 | 19.3392 | 20 |  | 39.992 | 0 | 39.992 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7129 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 1 | 1633 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5386 | 19.8416 | 16.6237 | 19.2806 | 19.8416 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7128 | 0 | 0 | 19.8416 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 2 | 1634 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3808 | 19.6839 | 16.4677 | 19.1245 | 19.6839 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7127 | 0 | 0 | 19.6839 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 3 | 1635 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2228 | 19.5258 | 16.3084 | 18.9652 | 19.5258 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7126 | 0 | 0 | 19.5258 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 4 | 1636 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0635 | 19.3666 | 16.1449 | 18.8018 | 19.3666 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7125 | 0 | 0 | 19.3666 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 5 | 1637 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9049 | 19.2079 | 15.988 | 18.6449 | 19.2079 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7124 | 0 | 0 | 19.2079 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 6 | 1638 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.745 | 19.0481 | 15.824 | 18.4809 | 19.0481 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7123 | 0 | 0 | 19.0481 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 7 | 1639 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5858 | 18.8888 | 15.6666 | 18.3234 | 18.8888 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7122 | 0 | 0 | 18.8888 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 8 | 1640 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 594.7876 | 0 | 370.314 | 0 | 381.6224 | 0 | 163.1938 | 0 | 1509.9178 | 0 | 43.9893 | 0 | 20.5663 | 0 | 18.5583 | 0 | 9.0634 | 26.1983 | 118.3756 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.483 | 18.786 | 15.5765 | 18.2333 | 20 |  | 450.1217 | 0 | 450.1217 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7121 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 9 | 1641 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5195.5777 | 0 | 4228.0636 | 0 | 3440.8378 | 0 | 1471.4109 | 0 | 14335.89 | 0 | 384.2546 | 0 | 234.8165 | 0 | 167.3277 | 0 | 81.7186 | 231.4184 | 1099.5358 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6271 | 19.9301 | 16.7079 | 19.3648 | 20 |  | 25.91 | 0 | 25.91 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7120 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 10 | 1642 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3911.9879 | 0 | 2367.619 | 0 | 5089.1597 | 0 | 2176.2854 | 0 | 13545.0519 | 0 | 289.3229 | 0 | 131.4919 | 0 | 247.4855 | 0 | 120.8656 | 314.3797 | 1103.5455 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6249 | 19.928 | 16.7058 | 19.3627 | 20 |  | 26.6969 | 0 | 26.6969 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7119 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 11 | 1643 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3775.4492 | 0 | 2250.0748 | 0 | 5025.4266 | 0 | 2149.0311 | 0 | 13199.9818 | 0 | 279.2247 | 0 | 124.9637 | 0 | 244.3861 | 0 | 119.352 | 314.3797 | 1082.3063 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6294 | 19.9325 | 16.728 | 19.3848 | 20 |  | 25.033 | 0 | 25.033 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7118 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 12 | 1644 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5886.7834 | 0 | 3517.9243 | 0 | 7938.0666 | 0 | 3356.4993 | 0 | 20699.2736 | 0 | 435.3748 | 0 | 195.377 | 0 | 386.0276 | 0 | 186.4119 | 484.6686 | 1687.86 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6531 | 19.9562 | 16.7572 | 19.414 | 20 |  | 16.2514 | 0 | 16.2514 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7117 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 13 | 1645 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4667.6843 | 0 | 2738.6228 | 0 | 6328.5244 | 0 | 2661.399 | 0 | 16396.2304 | 0 | 345.2127 | 0 | 152.0965 | 0 | 307.7557 | 0 | 147.8077 | 388.6082 | 1341.4808 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6433 | 19.9464 | 16.7564 | 19.4132 | 20 |  | 19.8857 | 0 | 19.8857 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7116 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 14 | 1646 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3589.6548 | 0 | 2082.8847 | 0 | 4880.043 | 0 | 2046.733 | 0 | 12599.3155 | 0 | 265.4838 | 0 | 115.6784 | 0 | 237.3162 | 0 | 113.6706 | 301.2805 | 1033.4294 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.635 | 19.938 | 16.757 | 19.4139 | 20 |  | 22.9756 | 0 | 22.9756 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7115 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 15 | 1647 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3162.8074 | 0 | 1824.5837 | 0 | 4326.5431 | 0 | 1803.3551 | 0 | 11117.2893 | 0 | 233.915 | 0 | 101.333 | 0 | 210.3995 | 0 | 100.154 | 266.3494 | 912.1509 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6316 | 19.9346 | 16.7566 | 19.4135 | 20 |  | 24.2405 | 0 | 24.2405 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7114 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 16 | 1648 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2159.2491 | 0 | 1236.2622 | 0 | 2964.2233 | 0 | 1231.1508 | 0 | 7590.8854 | 0 | 159.6938 | 0 | 68.659 | 0 | 144.15 | 0 | 68.3751 | 183.3881 | 624.2661 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6204 | 19.9234 | 16.7426 | 19.3995 | 20 |  | 28.3932 | 0 | 28.3932 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7113 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 17 | 1649 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 964.2308 | 0 | 549.7807 | 0 | 1321.1419 | 0 | 551.5913 | 0 | 3386.7448 | 0 | 71.3126 | 0 | 30.5335 | 0 | 64.247 | 0 | 30.6341 | 82.9613 | 279.6885 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6099 | 19.913 | 16.7382 | 19.3951 | 20 |  | 32.2651 | 0 | 32.2651 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7112 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 18 | 1650 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 554.2526 | 0 | 316.0212 | 0 | 780.9759 | 0 | 322.5959 | 0 | 1973.8456 | 0 | 40.9914 | 0 | 17.5511 | 0 | 37.9788 | 0 | 17.9162 | 48.0302 | 162.4677 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.604 | 19.907 | 16.7265 | 19.3833 | 20 |  | 34.472 | 0 | 34.472 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7111 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 19 | 1651 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5982 | 19.9013 | 16.7208 | 19.3776 | 20 |  | 36.6083 | 0 | 36.6083 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7110 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 20 | 1652 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5973 | 19.9004 | 16.717 | 19.3738 | 20 |  | 36.9467 | 0 | 36.9467 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7109 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 21 | 1653 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5964 | 19.8994 | 16.7131 | 19.3699 | 20 |  | 37.285 | 0 | 37.285 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7108 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 22 | 1654 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5946 | 19.8976 | 16.7054 | 19.3623 | 20 |  | 37.9618 | 0 | 37.9618 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7107 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 23 | 1655 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5937 | 19.8967 | 16.7016 | 19.3584 | 20 |  | 38.3001 | 0 | 38.3001 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7106 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 10 | 24 | 1656 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.5918 | 19.8949 | 16.6939 | 19.3507 | 20 |  | 38.9769 | 0 | 38.9769 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7105 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 1 | 1657 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5431 | 19.8462 | 16.643 | 19.2998 | 19.8462 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7104 | 0 | 0 | 19.8462 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 2 | 1658 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3881 | 19.6911 | 16.4836 | 19.1404 | 19.6911 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7103 | 0 | 0 | 19.6911 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 3 | 1659 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2327 | 19.5358 | 16.3269 | 18.9837 | 19.5358 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7102 | 0 | 0 | 19.5358 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 4 | 1660 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0797 | 19.3828 | 16.1814 | 18.8383 | 19.3828 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7101 | 0 | 0 | 19.3828 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 5 | 1661 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9273 | 19.2304 | 16.0306 | 18.6874 | 19.2304 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7100 | 0 | 0 | 19.2304 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 6 | 1662 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7764 | 19.0794 | 15.8841 | 18.5409 | 19.0794 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7099 | 0 | 0 | 19.0794 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 7 | 1663 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.6251 | 18.9281 | 15.7313 | 18.3882 | 18.9281 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7098 | 0 | 0 | 18.9281 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 8 | 1664 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1914.6834 | 0 | 1223.6436 | 0 | 731.5356 | 0 | 312.8277 | 0 | 4182.6902 | 0 | 141.6062 | 0 | 67.9582 | 0 | 35.5745 | 0 | 17.3737 | 61.1294 | 323.642 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.536 | 18.8391 | 15.6488 | 18.3056 | 20 |  | 430.4551 | 0 | 430.4551 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7097 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 9 | 1665 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8000.1339 | 0 | 6897.2057 | 0 | 4126.3602 | 0 | 1764.5619 | 0 | 20788.2616 | 0 | 591.6741 | 0 | 383.0542 | 0 | 200.6646 | 0 | 97.9995 | 292.5477 | 1565.9401 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6476 | 19.9506 | 16.734 | 19.3909 | 20 |  | 18.3145 | 0 | 18.3145 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7096 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 10 | 1666 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8284.9719 | 0 | 7940.4372 | 0 | 8026.349 | 0 | 3432.3203 | 0 | 27684.0785 | 0 | 612.7401 | 0 | 440.9928 | 0 | 390.3208 | 0 | 190.6228 | 558.8972 | 2193.5737 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6715 | 19.9745 | 16.7694 | 19.4262 | 20 |  | 9.4376 | 0 | 9.4376 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7095 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 11 | 1667 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10323.18 | 0 | 14397.6435 | 0 | 12972.8579 | 0 | 5547.6037 | 0 | 43241.2851 | 0 | 763.482 | 0 | 799.6104 | 0 | 630.8692 | 0 | 308.1005 | 956.2381 | 3458.3003 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7278 | 20.0309 | 16.8603 | 19.5171 | 20.0309 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7094 | 0 | 0 | 20.0309 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 12 | 1668 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12216.6677 | 0 | 18768.0264 | 0 | 22760.196 | 0 | 6965.6439 | 0 | 60710.5339 | 0 | 903.5206 | 0 | 1042.331 | 0 | 1106.8268 | 0 | 386.8551 | 1309.9153 | 4749.4486 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8172 | 20.1202 | 16.9744 | 19.6313 | 20.1202 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7093 | 0 | 0 | 20.1202 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 13 | 1669 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12742.7485 | 0 | 33248.9896 | 0 | 52307.6734 | 0 | 7265.6022 | 0 | 105565.0137 | 0 | 942.4284 | 0 | 1846.5688 | 0 | 2543.7185 | 0 | 403.514 | 1951.7737 | 7688.0035 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0437 | 20.3468 | 17.2258 | 19.8826 | 20.3468 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7092 | 0 | 0 | 20.3468 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 14 | 1670 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13087.8765 | 0 | 16911.0373 | 0 | 42058.1444 | 0 | 7462.3857 | 0 | 79519.444 | 0 | 967.9534 | 0 | 939.1983 | 0 | 2045.2846 | 0 | 414.4429 | 1445.2732 | 5812.1525 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1983 | 20.5013 | 17.3924 | 20.0492 | 20.5013 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7091 | 0 | 0 | 20.5013 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 15 | 1671 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11603.6245 | 0 | 10196.5868 | 0 | 34087.4065 | 0 | 6616.1017 | 0 | 62503.7194 | 0 | 858.1811 | 0 | 566.2939 | 0 | 1657.6682 | 0 | 367.4424 | 1165.8246 | 4615.4101 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.304 | 20.6071 | 17.5002 | 20.157 | 20.6071 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7090 | 0 | 0 | 20.6071 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 16 | 1672 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9748.2101 | 0 | 6645.4761 | 0 | 31681.2595 | 0 | 5558.19 | 0 | 53633.1357 | 0 | 720.9583 | 0 | 369.0737 | 0 | 1540.6575 | 0 | 308.6885 | 956.2381 | 3895.6161 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.381 | 20.6841 | 17.5687 | 20.2255 | 20.6841 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7089 | 0 | 0 | 20.6841 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 17 | 1673 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5380.749 | 0 | 3067.9709 | 0 | 8861.8537 | 0 | 3157.4412 | 0 | 20468.0147 | 0 | 397.9495 | 0 | 170.3877 | 0 | 430.9513 | 0 | 175.3567 | 449.7376 | 1624.3828 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3581 | 20.6612 | 17.5331 | 20.19 | 20.6612 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7088 | 0 | 0 | 20.6612 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 18 | 1674 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3624.1924 | 0 | 2066.4255 | 0 | 12723.6399 | 0 | 3321.4499 | 0 | 21735.7078 | 0 | 268.0381 | 0 | 114.7643 | 0 | 618.7497 | 0 | 184.4653 | 314.3797 | 1500.3971 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3312 | 20.6342 | 17.4834 | 20.1402 | 20.6342 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7087 | 0 | 0 | 20.6342 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 19 | 1675 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 174.4875 | 0 | 99.4885 | 0 | 4300.6015 | 0 | 1216.8462 | 0 | 5791.4237 | 0 | 12.9048 | 0 | 5.5254 | 0 | 209.138 | 0 | 67.5807 | 34.9311 | 330.0798 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2383 | 20.5413 | 17.3273 | 19.9842 | 20.5413 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7086 | 0 | 0 | 20.5413 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 20 | 1676 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1197 | 20.4228 | 17.1795 | 19.8363 | 20.4228 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7085 | 0 | 0 | 20.4228 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 21 | 1677 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0042 | 20.3072 | 17.0732 | 19.7301 | 20.3072 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7084 | 0 | 0 | 20.3072 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 22 | 1678 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8915 | 20.1946 | 16.9699 | 19.6267 | 20.1946 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7083 | 0 | 0 | 20.1946 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 23 | 1679 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.78 | 20.083 | 16.8616 | 19.5184 | 20.083 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7082 | 0 | 0 | 20.083 | 0 | 0 | 0
|  | 2004 | 3 | 11 | 24 | 1680 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.675 | 19.978 | 16.7775 | 19.4343 | 20 |  | 8.1549 | 0 | 8.1549 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7081 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 1 | 1681 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5386 | 19.8416 | 16.6237 | 19.2806 | 19.8416 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7080 | 0 | 0 | 19.8416 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 2 | 1682 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3827 | 19.6857 | 16.4754 | 19.1322 | 19.6857 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7079 | 0 | 0 | 19.6857 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 3 | 1683 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.22 | 19.5231 | 16.2909 | 18.9477 | 19.5231 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7078 | 0 | 0 | 19.5231 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 4 | 1684 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0608 | 19.3638 | 16.1423 | 18.7991 | 19.3638 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7077 | 0 | 0 | 19.3638 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 5 | 1685 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9086 | 19.2116 | 16.0124 | 18.6692 | 19.2116 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7076 | 0 | 0 | 19.2116 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 6 | 1686 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7532 | 19.0563 | 15.8468 | 18.5037 | 19.0563 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7075 | 0 | 0 | 19.0563 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 7 | 1687 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5976 | 18.9006 | 15.6898 | 18.3467 | 18.9006 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7074 | 0 | 0 | 18.9006 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 8 | 1688 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2381.7362 | 0 | 1516.4506 | 0 | 883.7273 | 0 | 377.9097 | 0 | 5159.8238 | 0 | 176.1485 | 0 | 84.22 | 0 | 42.9756 | 0 | 20.9882 | 74.2285 | 398.5608 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.4858 | 18.7879 | 15.5976 | 18.2554 | 20 |  | 449.267 | 0 | 449.267 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7073 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 9 | 1689 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8667.9686 | 0 | 7460.4497 | 0 | 4389.3028 | 0 | 1877.0045 | 0 | 22394.7255 | 0 | 641.0658 | 0 | 414.3354 | 0 | 213.4515 | 0 | 104.2443 | 314.3797 | 1687.4767 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6338 | 19.9359 | 16.7419 | 19.3997 | 20 |  | 23.7712 | 0 | 23.7712 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7072 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 10 | 1690 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 19467.2386 | 0 | 26304.4948 | 0 | 11465.8522 | 0 | 4903.1605 | 0 | 62140.7461 | 0 | 1439.7584 | 0 | 1460.8883 | 0 | 557.5836 | 0 | 272.3097 | 1030.4667 | 4761.0067 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7602 | 20.0623 | 16.9049 | 19.5627 | 20.0623 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7071 | 0 | 0 | 20.0623 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 11 | 1691 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12894.4533 | 0 | 32843.1243 | 0 | 14678.1689 | 0 | 6276.8485 | 0 | 66692.5951 | 0 | 953.6482 | 0 | 1824.028 | 0 | 713.7983 | 0 | 348.601 | 1467.1051 | 5307.1807 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8425 | 20.1446 | 17.0086 | 19.6664 | 20.1446 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7070 | 0 | 0 | 20.1446 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 12 | 1692 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12290.8523 | 0 | 18492.5741 | 0 | 22648.9192 | 0 | 7007.9421 | 0 | 60440.2877 | 0 | 909.0071 | 0 | 1027.033 | 0 | 1101.4154 | 0 | 389.2042 | 1309.9153 | 4736.575 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9123 | 20.2144 | 17.0998 | 19.7576 | 20.2144 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7069 | 0 | 0 | 20.2144 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 13 | 1693 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13115.2893 | 0 | 17050.1201 | 0 | 30501.0736 | 0 | 7478.0158 | 0 | 68144.4988 | 0 | 969.9808 | 0 | 946.9226 | 0 | 1483.2651 | 0 | 415.311 | 1392.8766 | 5208.3561 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0137 | 20.3158 | 17.2341 | 19.8918 | 20.3158 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7068 | 0 | 0 | 20.3158 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 14 | 1694 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13067.5774 | 0 | 14621.1202 | 0 | 36162.0737 | 0 | 7450.8117 | 0 | 71301.583 | 0 | 966.4521 | 0 | 812.0218 | 0 | 1758.5591 | 0 | 413.8001 | 1384.1438 | 5334.977 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1255 | 20.4276 | 17.3516 | 20.0094 | 20.4276 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7067 | 0 | 0 | 20.4276 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 15 | 1695 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10777.1193 | 0 | 8643.9362 | 0 | 27473.2522 | 0 | 6144.8487 | 0 | 53039.1564 | 0 | 797.0544 | 0 | 480.0634 | 0 | 1336.0223 | 0 | 341.2701 | 1017.3675 | 3971.7778 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1826 | 20.4847 | 17.4032 | 20.061 | 20.4847 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7066 | 0 | 0 | 20.4847 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 16 | 1696 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7129.4847 | 0 | 4155.1934 | 0 | 11104.4569 | 0 | 4065.0571 | 0 | 26454.1921 | 0 | 527.2826 | 0 | 230.7694 | 0 | 540.009 | 0 | 225.7635 | 593.8282 | 2117.6527 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1624 | 20.4645 | 17.3825 | 20.0403 | 20.4645 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7065 | 0 | 0 | 20.4645 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 17 | 1697 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2902.5441 | 0 | 1654.9594 | 0 | 4155.4017 | 0 | 1670.6709 | 0 | 10383.5761 | 0 | 214.6664 | 0 | 91.9125 | 0 | 202.0769 | 0 | 92.785 | 244.5175 | 845.9583 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0973 | 20.3994 | 17.3246 | 19.9824 | 20.3994 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7064 | 0 | 0 | 20.3994 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 18 | 1698 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 964.033 | 0 | 549.6679 | 0 | 1394.2385 | 0 | 567.2449 | 0 | 3475.1843 | 0 | 71.298 | 0 | 30.5272 | 0 | 67.8017 | 0 | 31.5034 | 82.9613 | 284.0916 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0395 | 20.3425 | 17.2647 | 19.9215 | 20.3425 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7063 | 0 | 0 | 20.3425 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 19 | 1699 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 179.8521 | 0 | 102.5472 | 0 | 989.3387 | 0 | 310.7436 | 0 | 1582.4816 | 0 | 13.3015 | 0 | 5.6952 | 0 | 48.1115 | 0 | 17.258 | 13.0992 | 97.4653 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9593 | 20.2624 | 17.1276 | 19.7844 | 20.2624 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7062 | 0 | 0 | 20.2624 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 20 | 1700 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8736 | 20.1766 | 17.0384 | 19.6952 | 20.1766 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7061 | 0 | 0 | 20.1766 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 21 | 1701 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7886 | 20.0917 | 16.956 | 19.6128 | 20.0917 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7060 | 0 | 0 | 20.0917 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 22 | 1702 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7045 | 20.0076 | 16.8744 | 19.5312 | 20.0076 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7059 | 0 | 0 | 20.0076 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 23 | 1703 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6222 | 19.9252 | 16.7974 | 19.4542 | 20 |  | 27.7267 | 0 | 27.7267 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7058 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 12 | 24 | 1704 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6192 | 19.9223 | 16.8093 | 19.4662 | 20 |  | 28.8258 | 0 | 28.8258 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7057 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 1 | 1705 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5751 | 19.8781 | 16.7777 | 19.4345 | 19.8781 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7056 | 0 | 0 | 19.8781 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 2 | 1706 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.459 | 19.762 | 16.6798 | 19.3366 | 19.762 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7055 | 0 | 0 | 19.762 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 3 | 1707 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3476 | 19.6507 | 16.5836 | 19.2404 | 19.6507 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7054 | 0 | 0 | 19.6507 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 4 | 1708 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2428 | 19.5459 | 16.4997 | 19.1565 | 19.5459 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7053 | 0 | 0 | 19.5459 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 5 | 1709 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1417 | 19.4448 | 16.4105 | 19.0674 | 19.4448 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7052 | 0 | 0 | 19.4448 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 6 | 1710 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.049 | 19.352 | 16.3442 | 19.001 | 19.352 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7051 | 0 | 0 | 19.352 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 7 | 1711 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9589 | 19.262 | 16.2627 | 18.9196 | 19.262 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7050 | 0 | 0 | 19.262 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 8 | 1712 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 217.3147 | 0 | 129.6007 | 0 | 203.3129 | 0 | 86.943 | 0 | 637.1713 | 0 | 16.0722 | 0 | 7.1977 | 0 | 9.8871 | 0 | 4.8286 | 13.0992 | 51.0847 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8939 | 19.196 | 16.2157 | 18.8735 | 20 |  | 298.0235 | 0 | 298.0235 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7049 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 9 | 1713 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6336.9049 | 0 | 5118.6766 | 0 | 4092.7254 | 0 | 1750.1786 | 0 | 17298.4855 | 0 | 468.6649 | 0 | 284.279 | 0 | 199.029 | 0 | 97.2007 | 279.4486 | 1328.6222 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6721 | 19.9741 | 16.9656 | 19.6233 | 20 |  | 9.588 | 0 | 9.588 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7048 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 10 | 1714 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5616.1111 | 0 | 4125.5238 | 0 | 6595.0987 | 0 | 2820.2725 | 0 | 19157.0061 | 0 | 415.3565 | 0 | 229.1217 | 0 | 320.7192 | 0 | 156.6311 | 423.5393 | 1545.3677 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.681 | 19.9831 | 16.9862 | 19.644 | 20 |  | 6.2658 | 0 | 6.2658 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7047 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 11 | 1715 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4540.1044 | 0 | 2715.5953 | 0 | 6040.2309 | 0 | 2582.9935 | 0 | 15878.924 | 0 | 335.7771 | 0 | 150.8176 | 0 | 293.736 | 0 | 143.4532 | 375.509 | 1299.293 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6732 | 19.9753 | 16.9844 | 19.6422 | 20 |  | 9.1666 | 0 | 9.1666 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7046 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 12 | 1716 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3485.5776 | 0 | 2041.9735 | 0 | 4677.025 | 0 | 1987.3908 | 0 | 12191.9669 | 0 | 257.7864 | 0 | 113.4063 | 0 | 227.4434 | 0 | 110.3749 | 292.5477 | 1001.5587 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6624 | 19.9645 | 16.9738 | 19.6316 | 20 |  | 13.1512 | 0 | 13.1512 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7045 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 13 | 1717 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5101.3529 | 0 | 2993.891 | 0 | 6917.7116 | 0 | 2908.6661 | 0 | 17921.6216 | 0 | 377.286 | 0 | 166.2735 | 0 | 336.4078 | 0 | 161.5403 | 423.5393 | 1465.0469 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.685 | 19.9871 | 17.0167 | 19.6745 | 20 |  | 4.7761 | 0 | 4.7761 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7044 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 14 | 1718 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9387.7368 | 0 | 6031.7034 | 0 | 14297.8948 | 0 | 5352.6569 | 0 | 35069.992 | 0 | 694.2984 | 0 | 334.9863 | 0 | 695.3056 | 0 | 297.2737 | 790.3155 | 2812.1795 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7366 | 20.0387 | 17.0734 | 19.7312 | 20.0387 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7043 | 0 | 0 | 20.0387 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 15 | 1719 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4827.5406 | 0 | 2796.2898 | 0 | 6668.0887 | 0 | 2752.5451 | 0 | 17044.4643 | 0 | 357.0353 | 0 | 155.2992 | 0 | 324.2687 | 0 | 152.8697 | 401.7073 | 1391.1803 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7217 | 20.0237 | 17.0552 | 19.713 | 20.0237 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7042 | 0 | 0 | 20.0237 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 16 | 1720 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6926.2298 | 0 | 4009.1649 | 0 | 10334.6649 | 0 | 3949.1661 | 0 | 25219.2257 | 0 | 512.2502 | 0 | 222.6594 | 0 | 502.574 | 0 | 219.3272 | 571.9963 | 2028.8071 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7289 | 20.031 | 17.0567 | 19.7144 | 20.031 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7041 | 0 | 0 | 20.031 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 17 | 1721 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4859.0758 | 0 | 2770.5257 | 0 | 7220.2581 | 0 | 2812.8867 | 0 | 17662.7463 | 0 | 359.3676 | 0 | 153.8683 | 0 | 351.1207 | 0 | 156.221 | 401.7073 | 1422.2849 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7183 | 20.0204 | 17.0608 | 19.7186 | 20.0204 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7040 | 0 | 0 | 20.0204 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 18 | 1722 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2438.7732 | 0 | 1390.5286 | 0 | 3874.7366 | 0 | 1492.6549 | 0 | 9196.6933 | 0 | 180.3668 | 0 | 77.2266 | 0 | 188.4282 | 0 | 82.8985 | 205.2201 | 734.1401 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7155 | 20.0185 | 17.0632 | 19.72 | 20.0185 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7039 | 0 | 0 | 20.0185 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 19 | 1723 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 453.4636 | 0 | 258.5538 | 0 | 6349.0033 | 0 | 1872.159 | 0 | 8933.1797 | 0 | 33.5373 | 0 | 14.3595 | 0 | 308.7516 | 0 | 103.9752 | 74.2285 | 534.852 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6978 | 20.0008 | 16.9985 | 19.6554 | 20.0008 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7038 | 0 | 0 | 20.0008 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 20 | 1724 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6419 | 19.945 | 16.9025 | 19.5593 | 20 |  | 20.406 | 0 | 20.406 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7037 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 21 | 1725 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6384 | 19.9414 | 16.8902 | 19.547 | 20 |  | 21.7201 | 0 | 21.7201 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7036 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 22 | 1726 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6356 | 19.9387 | 16.8786 | 19.5355 | 20 |  | 22.7352 | 0 | 22.7352 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7035 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 23 | 1727 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6302 | 19.9332 | 16.8555 | 19.5124 | 20 |  | 24.7654 | 0 | 24.7654 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7034 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 13 | 24 | 1728 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6229 | 19.9259 | 16.8247 | 19.4816 | 20 |  | 27.4724 | 0 | 27.4724 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7033 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 1 | 1729 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5906 | 19.8937 | 16.8431 | 19.4999 | 19.8937 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7032 | 0 | 0 | 19.8937 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 2 | 1730 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4743 | 19.7774 | 16.6947 | 19.3516 | 19.7774 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7031 | 0 | 0 | 19.7774 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 3 | 1731 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3601 | 19.6631 | 16.5868 | 19.2437 | 19.6631 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7030 | 0 | 0 | 19.6631 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 4 | 1732 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2442 | 19.5473 | 16.4655 | 19.1223 | 19.5473 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7029 | 0 | 0 | 19.5473 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 5 | 1733 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1304 | 19.4334 | 16.358 | 19.0148 | 19.4334 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7028 | 0 | 0 | 19.4334 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 6 | 1734 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0167 | 19.3198 | 16.2447 | 18.9016 | 19.3198 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7027 | 0 | 0 | 19.3198 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 7 | 1735 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9069 | 19.2099 | 16.147 | 18.8039 | 19.2099 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7026 | 0 | 0 | 19.2099 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 8 | 1736 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7970.511 | 0 | 5113.3551 | 0 | 1546.3048 | 0 | 661.2487 | 0 | 15291.4196 | 0 | 589.4832 | 0 | 283.9834 | 0 | 75.1967 | 0 | 36.7242 | 135.3579 | 1120.7454 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8662 | 19.1683 | 16.1243 | 18.7821 | 20 |  | 308.2694 | 0 | 308.2694 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7025 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 9 | 1737 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 29599.8207 | 0 | 27902.7254 | 0 | 7032.0035 | 0 | 3007.1068 | 0 | 67541.6564 | 0 | 2189.1441 | 0 | 1549.6502 | 0 | 341.9658 | 0 | 167.0075 | 729.1862 | 4976.9538 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8132 | 20.1153 | 17.0899 | 19.7477 | 20.1153 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7024 | 0 | 0 | 20.1153 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 10 | 1738 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11340.3711 | 0 | 11859.3672 | 0 | 9827.1399 | 0 | 4202.3953 | 0 | 37229.2735 | 0 | 838.7114 | 0 | 658.6407 | 0 | 477.8931 | 0 | 233.3909 | 702.9879 | 2911.624 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8469 | 20.149 | 17.145 | 19.8028 | 20.149 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7023 | 0 | 0 | 20.149 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 11 | 1739 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9654.9541 | 0 | 10583.0617 | 0 | 12314.6728 | 0 | 5266.143 | 0 | 37818.8317 | 0 | 714.0613 | 0 | 587.7578 | 0 | 598.8617 | 0 | 292.4689 | 873.2768 | 3066.4265 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8941 | 20.1961 | 17.2322 | 19.89 | 20.1961 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7022 | 0 | 0 | 20.1961 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 12 | 1740 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12715.7631 | 0 | 22209.9243 | 0 | 25017.8799 | 0 | 7250.2158 | 0 | 67193.7832 | 0 | 940.4327 | 0 | 1233.4857 | 0 | 1216.6178 | 0 | 402.6595 | 1419.0749 | 5212.2705 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0359 | 20.338 | 17.4067 | 20.0645 | 20.338 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7021 | 0 | 0 | 20.338 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 13 | 1741 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13436.3327 | 0 | 17593.9272 | 0 | 31429.3067 | 0 | 7661.0669 | 0 | 70120.6336 | 0 | 993.7246 | 0 | 977.1243 | 0 | 1528.405 | 0 | 425.4772 | 1445.2732 | 5370.0043 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2008 | 20.5029 | 17.6232 | 20.281 | 20.5029 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7020 | 0 | 0 | 20.5029 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 14 | 1742 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13662.9674 | 0 | 18886.0505 | 0 | 47424.1509 | 0 | 7790.2884 | 0 | 87763.4572 | 0 | 1010.486 | 0 | 1048.8858 | 0 | 2306.2332 | 0 | 432.6539 | 1611.1958 | 6409.4546 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4172 | 20.7193 | 17.8427 | 20.5005 | 20.7193 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7019 | 0 | 0 | 20.7193 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 15 | 1743 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12150.3923 | 0 | 10761.4632 | 0 | 36657.3477 | 0 | 6927.8553 | 0 | 66497.0585 | 0 | 898.619 | 0 | 597.6657 | 0 | 1782.6443 | 0 | 384.7564 | 1248.7859 | 4912.4713 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5677 | 20.8697 | 17.979 | 20.6368 | 20.8697 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7018 | 0 | 0 | 20.8697 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 16 | 1744 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10883.5997 | 0 | 8251.536 | 0 | 53328.9336 | 0 | 6205.5612 | 0 | 78669.6306 | 0 | 804.9295 | 0 | 458.2704 | 0 | 2593.3823 | 0 | 344.6419 | 1248.7859 | 5450.0101 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7511 | 21.0532 | 18.1575 | 20.8153 | 21.0532 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7017 | 0 | 0 | 21.0532 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 17 | 1745 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4857.49 | 0 | 2769.6215 | 0 | 7191.0003 | 0 | 2811.926 | 0 | 17630.0376 | 0 | 359.2503 | 0 | 153.8181 | 0 | 349.6978 | 0 | 156.1676 | 401.7073 | 1420.6412 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7489 | 21.051 | 18.1231 | 20.7809 | 21.051 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7016 | 0 | 0 | 21.051 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 18 | 1746 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2761.6769 | 0 | 1574.6404 | 0 | 4424.6845 | 0 | 1698.1834 | 0 | 10459.1852 | 0 | 204.2482 | 0 | 87.4517 | 0 | 215.1721 | 0 | 94.313 | 231.4184 | 832.6034 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7562 | 21.0593 | 18.1265 | 20.7833 | 21.0593 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7015 | 0 | 0 | 21.0593 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 19 | 1747 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 467.9724 | 0 | 266.8264 | 0 | 2561.401 | 0 | 817.2045 | 0 | 4113.4043 | 0 | 34.6103 | 0 | 14.8189 | 0 | 124.5608 | 0 | 45.3856 | 34.9311 | 254.3066 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7449 | 21.0479 | 18.1122 | 20.769 | 21.0479 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7014 | 0 | 0 | 21.0479 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 20 | 1748 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7209 | 21.024 | 18.0858 | 20.7427 | 21.024 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7013 | 0 | 0 | 21.024 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 21 | 1749 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6935 | 20.9966 | 18.0474 | 20.7042 | 20.9966 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7012 | 0 | 0 | 20.9966 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 22 | 1750 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6628 | 20.9658 | 18.0057 | 20.6625 | 20.9658 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7011 | 0 | 0 | 20.9658 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 23 | 1751 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6359 | 20.939 | 17.9915 | 20.6484 | 20.939 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7010 | 0 | 0 | 20.939 | 0 | 0 | 0
|  | 2004 | 3 | 14 | 24 | 1752 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6085 | 20.9115 | 17.9619 | 20.6187 | 20.9115 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7009 | 0 | 0 | 20.9115 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 1 | 1753 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.5344 | 20.8375 | 17.8923 | 20.5491 | 20.8375 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7008 | 0 | 0 | 20.8375 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 2 | 1754 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4601 | 20.7632 | 17.8173 | 20.4741 | 20.7632 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7007 | 0 | 0 | 20.7632 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 3 | 1755 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3866 | 20.6896 | 17.7459 | 20.4027 | 20.6896 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7006 | 0 | 0 | 20.6896 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 4 | 1756 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3137 | 20.6168 | 17.6752 | 20.332 | 20.6168 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7005 | 0 | 0 | 20.6168 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 5 | 1757 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2407 | 20.5437 | 17.6014 | 20.2582 | 20.5437 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7004 | 0 | 0 | 20.5437 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 6 | 1758 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1665 | 20.4696 | 17.5235 | 20.1803 | 20.4696 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7003 | 0 | 0 | 20.4696 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 7 | 1759 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0903 | 20.3934 | 17.4406 | 20.0975 | 20.3934 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7002 | 0 | 0 | 20.3934 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 8 | 1760 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 446.0804 | 0 | 265.5999 | 0 | 405.4051 | 0 | 173.364 | 0 | 1290.4493 | 0 | 32.9912 | 0 | 14.7508 | 0 | 19.7148 | 0 | 9.6282 | 26.1983 | 103.2833 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0339 | 20.336 | 17.3812 | 20.039 | 20.336 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7001 | 0 | 0 | 20.336 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 9 | 1761 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7179.0973 | 0 | 5771.5528 | 0 | 4553.0359 | 0 | 1947.0219 | 0 | 19450.708 | 0 | 530.9518 | 0 | 320.5381 | 0 | 221.4138 | 0 | 108.1329 | 314.3797 | 1495.4164 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.034 | 20.3361 | 17.3969 | 20.0547 | 20.3361 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7000 | 0 | 0 | 20.3361 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 10 | 1762 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7705.7976 | 0 | 6582.1379 | 0 | 8094.9717 | 0 | 3461.6655 | 0 | 25844.5728 | 0 | 569.9055 | 0 | 365.5561 | 0 | 393.6579 | 0 | 192.2526 | 545.798 | 2067.1701 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0571 | 20.3592 | 17.4344 | 20.0922 | 20.3592 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6999 | 0 | 0 | 20.3592 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 11 | 1763 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10392.3558 | 0 | 13017.9779 | 0 | 13035.8159 | 0 | 5574.5265 | 0 | 42020.6762 | 0 | 768.5981 | 0 | 722.9871 | 0 | 633.9308 | 0 | 309.5958 | 934.4062 | 3369.518 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1347 | 20.4368 | 17.5371 | 20.1949 | 20.4368 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6998 | 0 | 0 | 20.4368 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 12 | 1764 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10539.5745 | 0 | 9438.0259 | 0 | 15890.4537 | 0 | 6009.4065 | 0 | 41877.4606 | 0 | 779.4861 | 0 | 524.1652 | 0 | 772.7517 | 0 | 333.748 | 956.2381 | 3366.389 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2079 | 20.51 | 17.5962 | 20.254 | 20.51 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6997 | 0 | 0 | 20.51 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 13 | 1765 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8161.0159 | 0 | 4921.732 | 0 | 11246.8582 | 0 | 4653.2108 | 0 | 28982.817 | 0 | 603.5726 | 0 | 273.3411 | 0 | 546.9339 | 0 | 258.4281 | 668.0568 | 2350.3326 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2471 | 20.5492 | 17.6485 | 20.3063 | 20.5492 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6996 | 0 | 0 | 20.5492 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 14 | 1766 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8189.5906 | 0 | 4835.0038 | 0 | 11356.7267 | 0 | 4669.5034 | 0 | 29050.8245 | 0 | 605.6859 | 0 | 268.5245 | 0 | 552.2768 | 0 | 259.333 | 668.0568 | 2353.877 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2937 | 20.5958 | 17.7204 | 20.3782 | 20.5958 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6995 | 0 | 0 | 20.5958 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 15 | 1767 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7844.2456 | 0 | 4592.9471 | 0 | 11107.0663 | 0 | 4472.5962 | 0 | 28016.8552 | 0 | 580.1449 | 0 | 255.0812 | 0 | 540.1359 | 0 | 248.3972 | 641.8585 | 2265.6176 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3352 | 20.6372 | 17.7547 | 20.4125 | 20.6372 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6994 | 0 | 0 | 20.6372 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 16 | 1768 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10452.9168 | 0 | 7049.6091 | 0 | 35372.1128 | 0 | 5959.9964 | 0 | 58834.6351 | 0 | 773.077 | 0 | 391.5183 | 0 | 1720.1434 | 0 | 331.0038 | 1056.665 | 4272.4076 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4673 | 20.7694 | 17.8931 | 20.5509 | 20.7694 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6993 | 0 | 0 | 20.7694 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 17 | 1769 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6335.9521 | 0 | 3612.6043 | 0 | 12254.0811 | 0 | 3846.0583 | 0 | 26048.6957 | 0 | 468.5945 | 0 | 200.6353 | 0 | 595.9151 | 0 | 213.6008 | 545.798 | 2024.5438 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5013 | 20.8034 | 17.9158 | 20.5736 | 20.8034 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6992 | 0 | 0 | 20.8034 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 18 | 1770 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2760.6566 | 0 | 1574.0586 | 0 | 4377.9169 | 0 | 1691.7962 | 0 | 10404.4284 | 0 | 204.1727 | 0 | 87.4194 | 0 | 212.8978 | 0 | 93.9583 | 231.4184 | 829.8666 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5218 | 20.8248 | 17.9345 | 20.5914 | 20.8248 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6991 | 0 | 0 | 20.8248 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 19 | 1771 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 632.2576 | 0 | 360.4977 | 0 | 3728.3188 | 0 | 1189.4134 | 0 | 5910.4875 | 0 | 46.7605 | 0 | 20.0212 | 0 | 181.3079 | 0 | 66.0572 | 48.0302 | 362.177 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5269 | 20.83 | 17.9304 | 20.5873 | 20.83 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6990 | 0 | 0 | 20.83 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 20 | 1772 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5115 | 20.8145 | 17.9033 | 20.5602 | 20.8145 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6989 | 0 | 0 | 20.8145 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 21 | 1773 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.498 | 20.801 | 17.8962 | 20.553 | 20.801 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6988 | 0 | 0 | 20.801 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 22 | 1774 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4864 | 20.7895 | 17.8909 | 20.5477 | 20.7895 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6987 | 0 | 0 | 20.7895 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 23 | 1775 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4768 | 20.7799 | 17.8875 | 20.5443 | 20.7799 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6986 | 0 | 0 | 20.7799 | 0 | 0 | 0
|  | 2004 | 3 | 15 | 24 | 1776 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4682 | 20.7713 | 17.8821 | 20.5389 | 20.7713 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6985 | 0 | 0 | 20.7713 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 1 | 1777 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4128 | 20.7159 | 17.8306 | 20.4875 | 20.7159 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6984 | 0 | 0 | 20.7159 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 2 | 1778 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3525 | 20.6556 | 17.7543 | 20.4112 | 20.6556 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6983 | 0 | 0 | 20.6556 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 3 | 1779 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2946 | 20.5977 | 17.704 | 20.3609 | 20.5977 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6982 | 0 | 0 | 20.5977 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 4 | 1780 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2354 | 20.5385 | 17.6407 | 20.2975 | 20.5385 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6981 | 0 | 0 | 20.5385 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 5 | 1781 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1741 | 20.4771 | 17.5723 | 20.2291 | 20.4771 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6980 | 0 | 0 | 20.4771 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 6 | 1782 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1106 | 20.4136 | 17.5018 | 20.1586 | 20.4136 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6979 | 0 | 0 | 20.4136 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 7 | 1783 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0477 | 20.3508 | 17.4408 | 20.0976 | 20.3508 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6978 | 0 | 0 | 20.3508 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 8 | 1784 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 347.4573 | 0 | 200.7026 | 0 | 417.2397 | 0 | 178.4249 | 0 | 1143.8245 | 0 | 25.6973 | 0 | 11.1465 | 0 | 20.2903 | 0 | 9.9093 | 26.1983 | 93.2417 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.003 | 20.3051 | 17.3927 | 20.0505 | 20.3051 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6977 | 0 | 0 | 20.3051 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 9 | 1785 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1332.4253 | 0 | 778.6242 | 0 | 1719.0725 | 0 | 735.1297 | 0 | 4565.2516 | 0 | 98.5435 | 0 | 43.2429 | 0 | 83.5984 | 0 | 40.8273 | 109.1596 | 375.3718 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.967 | 20.269 | 17.3549 | 20.0127 | 20.269 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6976 | 0 | 0 | 20.269 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 10 | 1786 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2801.7835 | 0 | 1653.348 | 0 | 3679.2907 | 0 | 1573.3809 | 0 | 9707.803 | 0 | 207.2144 | 0 | 91.823 | 0 | 178.9237 | 0 | 87.3818 | 231.4184 | 796.7611 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9479 | 20.25 | 17.3426 | 20.0003 | 20.25 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6975 | 0 | 0 | 20.25 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 11 | 1787 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3933.1065 | 0 | 2330.9858 | 0 | 5233.4044 | 0 | 2237.969 | 0 | 13735.4657 | 0 | 290.8848 | 0 | 129.4573 | 0 | 254.5001 | 0 | 124.2914 | 327.4788 | 1126.6124 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.945 | 20.2471 | 17.3547 | 20.0125 | 20.2471 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6974 | 0 | 0 | 20.2471 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 12 | 1788 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4834.5886 | 0 | 2852.2622 | 0 | 6497.1236 | 0 | 2756.5637 | 0 | 16940.5381 | 0 | 357.5566 | 0 | 158.4078 | 0 | 315.9547 | 0 | 153.0929 | 401.7073 | 1386.7193 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9539 | 20.256 | 17.3724 | 20.0302 | 20.256 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6973 | 0 | 0 | 20.256 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 13 | 1789 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7586.5369 | 0 | 4495.607 | 0 | 10346.8325 | 0 | 4325.657 | 0 | 26754.6333 | 0 | 561.0852 | 0 | 249.6752 | 0 | 503.1657 | 0 | 240.2366 | 620.0266 | 2174.1893 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.999 | 20.3011 | 17.4432 | 20.101 | 20.3011 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6972 | 0 | 0 | 20.3011 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 14 | 1790 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11150.752 | 0 | 7942.8249 | 0 | 19071.359 | 0 | 6357.8849 | 0 | 44522.8209 | 0 | 824.6875 | 0 | 441.1254 | 0 | 927.4389 | 0 | 353.1016 | 982.4364 | 3528.7898 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1053 | 20.4074 | 17.5827 | 20.2405 | 20.4074 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6971 | 0 | 0 | 20.4074 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 15 | 1791 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7584.7442 | 0 | 4419.0878 | 0 | 10626.3533 | 0 | 4324.6349 | 0 | 26954.8201 | 0 | 560.9527 | 0 | 245.4255 | 0 | 516.7588 | 0 | 240.1798 | 620.0266 | 2183.3433 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1597 | 20.4618 | 17.6347 | 20.2925 | 20.4618 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6970 | 0 | 0 | 20.4618 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 16 | 1792 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8460.1655 | 0 | 5016.5202 | 0 | 15218.6662 | 0 | 4823.7785 | 0 | 33519.1304 | 0 | 625.6971 | 0 | 278.6055 | 0 | 740.0827 | 0 | 267.901 | 729.1862 | 2641.4724 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2401 | 20.5422 | 17.7397 | 20.3975 | 20.5422 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6969 | 0 | 0 | 20.5422 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 17 | 1793 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7599.1176 | 0 | 4332.8302 | 0 | 25448.6682 | 0 | 5305.0214 | 0 | 42685.6374 | 0 | 562.0157 | 0 | 240.635 | 0 | 1237.567 | 0 | 294.6281 | 716.087 | 3050.9327 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3464 | 20.6485 | 17.8462 | 20.504 | 20.6485 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6968 | 0 | 0 | 20.6485 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 18 | 1794 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3970.8053 | 0 | 2264.0557 | 0 | 12050.8285 | 0 | 3422.4361 | 0 | 21708.1256 | 0 | 293.6729 | 0 | 125.7402 | 0 | 586.031 | 0 | 190.0739 | 340.578 | 1536.0959 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.42 | 20.723 | 17.8984 | 20.5553 | 20.723 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6967 | 0 | 0 | 20.723 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 19 | 1795 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 791.0397 | 0 | 451.0314 | 0 | 4922.1278 | 0 | 1574.668 | 0 | 7738.8669 | 0 | 58.5037 | 0 | 25.0492 | 0 | 239.3627 | 0 | 87.4533 | 61.1294 | 471.4983 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4487 | 20.7517 | 17.9109 | 20.5677 | 20.7517 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6966 | 0 | 0 | 20.7517 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 20 | 1796 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4431 | 20.7461 | 17.8666 | 20.5234 | 20.7461 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6965 | 0 | 0 | 20.7461 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 21 | 1797 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4248 | 20.7278 | 17.8073 | 20.4642 | 20.7278 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6964 | 0 | 0 | 20.7278 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 22 | 1798 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4002 | 20.7033 | 17.7628 | 20.4196 | 20.7033 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6963 | 0 | 0 | 20.7033 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 23 | 1799 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3705 | 20.6735 | 17.7161 | 20.373 | 20.6735 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6962 | 0 | 0 | 20.6735 | 0 | 0 | 0
|  | 2004 | 3 | 16 | 24 | 1800 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3328 | 20.6358 | 17.6529 | 20.3097 | 20.6358 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6961 | 0 | 0 | 20.6358 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 1 | 1801 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2422 | 20.5452 | 17.5465 | 20.2033 | 20.5452 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6960 | 0 | 0 | 20.5452 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 2 | 1802 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1406 | 20.4437 | 17.4094 | 20.0663 | 20.4437 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6959 | 0 | 0 | 20.4437 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 3 | 1803 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.051 | 20.3541 | 17.358 | 20.0149 | 20.3541 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6958 | 0 | 0 | 20.3541 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 4 | 1804 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9495 | 20.2525 | 17.218 | 19.8748 | 20.2525 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6957 | 0 | 0 | 20.2525 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 5 | 1805 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8416 | 20.1446 | 17.0896 | 19.7465 | 20.1446 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6956 | 0 | 0 | 20.1446 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 6 | 1806 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7302 | 20.0333 | 16.9667 | 19.6235 | 20.0333 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6955 | 0 | 0 | 20.0333 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 7 | 1807 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6199 | 19.9229 | 16.8597 | 19.5165 | 19.9229 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6954 | 0 | 0 | 19.9229 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 8 | 1808 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12763.2291 | 0 | 8063.2406 | 0 | 2231.8969 | 0 | 954.4296 | 0 | 24012.7962 | 0 | 943.9432 | 0 | 447.813 | 0 | 108.537 | 0 | 53.0067 | 205.2201 | 1758.5199 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6434 | 19.9465 | 16.9346 | 19.5914 | 20 |  | 19.8503 | 0 | 19.8503 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6953 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 9 | 1809 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 26073.5729 | 0 | 23578.4216 | 0 | 7829.5184 | 0 | 3348.1493 | 0 | 60829.6622 | 0 | 1928.3498 | 0 | 1309.4887 | 0 | 380.7489 | 0 | 185.9481 | 716.087 | 4520.6227 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8529 | 20.156 | 17.2254 | 19.8823 | 20.156 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6952 | 0 | 0 | 20.156 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 10 | 1810 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 25446.5089 | 0 | 36219.9176 | 0 | 11673.2379 | 0 | 4991.8452 | 0 | 78331.5096 | 0 | 1881.9734 | 0 | 2011.567 | 0 | 567.6688 | 0 | 277.2351 | 1296.8161 | 6035.2603 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0897 | 20.3928 | 17.5567 | 20.2136 | 20.3928 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6951 | 0 | 0 | 20.3928 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 11 | 1811 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13980.7177 | 0 | 45924.4125 | 0 | 13814.1388 | 0 | 5907.362 | 0 | 79626.631 | 0 | 1033.9862 | 0 | 2550.5313 | 0 | 671.7806 | 0 | 328.0807 | 1855.7133 | 6440.092 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3453 | 20.6483 | 17.8581 | 20.515 | 20.6483 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6950 | 0 | 0 | 20.6483 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 12 | 1812 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11697.2381 | 0 | 44772.1061 | 0 | 35790.6463 | 0 | 6669.4778 | 0 | 98929.4684 | 0 | 865.1046 | 0 | 2486.5349 | 0 | 1740.4967 | 0 | 370.4067 | 2170.0929 | 7632.6358 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6664 | 20.9695 | 18.212 | 20.8689 | 20.9695 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6949 | 0 | 0 | 20.9695 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 13 | 1813 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12221.8964 | 0 | 38793.4551 | 0 | 59661.834 | 0 | 6968.6252 | 0 | 117645.8107 | 0 | 903.9073 | 0 | 2154.4951 | 0 | 2901.3509 | 0 | 387.0207 | 2305.4508 | 8652.2247 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.044 | 21.3471 | 18.6 | 21.2568 | 21.3471 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6948 | 0 | 0 | 21.3471 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 14 | 1814 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12463.9684 | 0 | 30545.0282 | 0 | 79027.7884 | 0 | 7106.6487 | 0 | 129143.4337 | 0 | 921.8104 | 0 | 1696.3973 | 0 | 3843.1159 | 0 | 394.6861 | 2244.3215 | 9100.3312 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.4503 | 21.7533 | 18.9947 | 21.6515 | 21.7533 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6947 | 0 | 0 | 21.7533 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 15 | 1815 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11955.031 | 0 | 19842.0436 | 0 | 87410.7047 | 0 | 6816.465 | 0 | 126024.2443 | 0 | 884.1704 | 0 | 1101.9793 | 0 | 4250.7765 | 0 | 378.5701 | 1991.0712 | 8606.5675 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.8437 | 22.1468 | 19.3793 | 22.0361 | 22.1468 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6946 | 0 | 0 | 22.1468 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 16 | 1816 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10989.025 | 0 | 9213.785 | 0 | 77346.9322 | 0 | 6265.6721 | 0 | 103815.4143 | 0 | 812.7265 | 0 | 511.7114 | 0 | 3761.376 | 0 | 347.9803 | 1528.2345 | 6962.0287 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.1636 | 22.4667 | 19.6709 | 22.3278 | 22.4667 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6945 | 0 | 0 | 22.4667 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 17 | 1817 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8577.9124 | 0 | 4890.915 | 0 | 47991.3964 | 0 | 7290.0541 | 0 | 68750.2778 | 0 | 634.4054 | 0 | 271.6296 | 0 | 2333.8183 | 0 | 404.872 | 947.5054 | 4592.2307 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.3703 | 22.6734 | 19.8404 | 22.4972 | 22.6734 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6944 | 0 | 0 | 22.6734 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 18 | 1818 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3743.2305 | 0 | 2134.2981 | 0 | 6782.4551 | 0 | 2446.0403 | 0 | 15106.024 | 0 | 276.8419 | 0 | 118.5338 | 0 | 329.8303 | 0 | 135.8472 | 314.3797 | 1175.4329 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.4056 | 22.7087 | 19.822 | 22.4789 | 22.7087 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6943 | 0 | 0 | 22.7087 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 19 | 1819 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 458.2889 | 0 | 261.3051 | 0 | 915.0568 | 0 | 350.6306 | 0 | 1985.2813 | 0 | 33.8941 | 0 | 14.5123 | 0 | 44.4991 | 0 | 19.4732 | 34.9311 | 147.3098 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.3696 | 22.6727 | 19.6798 | 22.3366 | 22.6727 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6942 | 0 | 0 | 22.6727 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 20 | 1820 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.3136 | 22.6166 | 19.5779 | 22.2348 | 22.6166 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6941 | 0 | 0 | 22.6166 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 21 | 1821 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.248 | 22.5511 | 19.4817 | 22.1386 | 22.5511 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6940 | 0 | 0 | 22.5511 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 22 | 1822 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.1749 | 22.4779 | 19.3841 | 22.0409 | 22.4779 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6939 | 0 | 0 | 22.4779 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 23 | 1823 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.0979 | 22.401 | 19.2946 | 21.9514 | 22.401 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6938 | 0 | 0 | 22.401 | 0 | 0 | 0
|  | 2004 | 3 | 17 | 24 | 1824 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.0125 | 22.3156 | 19.1821 | 21.8389 | 22.3156 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6937 | 0 | 0 | 22.3156 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 1 | 1825 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.8821 | 22.1851 | 19.0607 | 21.7175 | 22.1851 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6936 | 0 | 0 | 22.1851 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 2 | 1826 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.7519 | 22.055 | 18.9315 | 21.5883 | 22.055 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6935 | 0 | 0 | 22.055 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 3 | 1827 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.6148 | 21.9179 | 18.7717 | 21.4286 | 21.9179 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6934 | 0 | 0 | 21.9179 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 4 | 1828 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.4681 | 21.7711 | 18.5938 | 21.2506 | 21.7711 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6933 | 0 | 0 | 21.7711 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 5 | 1829 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.3191 | 21.6222 | 18.4374 | 21.0942 | 21.6222 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6932 | 0 | 0 | 21.6222 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 6 | 1830 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.1734 | 21.4765 | 18.3019 | 20.9588 | 21.4765 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6931 | 0 | 0 | 21.4765 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 7 | 1831 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.0364 | 21.3395 | 18.1927 | 20.8495 | 21.3395 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6930 | 0 | 0 | 21.3395 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 8 | 1832 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9042.3004 | 0 | 5670.5533 | 0 | 1772.9243 | 0 | 758.1584 | 0 | 17243.9364 | 0 | 668.7506 | 0 | 314.9289 | 0 | 86.2172 | 0 | 42.1063 | 135.3579 | 1247.3609 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0166 | 21.3197 | 18.2342 | 20.8911 | 21.3197 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6929 | 0 | 0 | 21.3197 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 9 | 1833 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4429.8307 | 0 | 3095.9616 | 0 | 4113.8679 | 0 | 1759.2198 | 0 | 13398.8801 | 0 | 327.6215 | 0 | 171.9423 | 0 | 200.0571 | 0 | 97.7028 | 266.3494 | 1063.6731 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9971 | 21.3002 | 18.2507 | 20.9075 | 21.3002 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6928 | 0 | 0 | 21.3002 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 10 | 1834 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9313.0486 | 0 | 8391.9975 | 0 | 9212.4875 | 0 | 3939.5506 | 0 | 30857.0841 | 0 | 688.7746 | 0 | 466.0713 | 0 | 448.0026 | 0 | 218.7931 | 641.8585 | 2463.5002 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0432 | 21.3463 | 18.3436 | 21.0004 | 21.3463 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6927 | 0 | 0 | 21.3463 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 11 | 1835 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8616.7425 | 0 | 7180.1151 | 0 | 11187.5808 | 0 | 4784.1628 | 0 | 31768.6013 | 0 | 637.2772 | 0 | 398.7663 | 0 | 544.0513 | 0 | 265.7009 | 737.9189 | 2583.7146 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1063 | 21.4094 | 18.4523 | 21.1091 | 21.4094 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6926 | 0 | 0 | 21.4094 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 12 | 1836 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10588.052 | 0 | 8955.5794 | 0 | 15655.5763 | 0 | 6037.0472 | 0 | 41236.255 | 0 | 783.0714 | 0 | 497.3713 | 0 | 761.3296 | 0 | 335.2831 | 947.5054 | 3324.5607 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.2109 | 21.514 | 18.6016 | 21.2584 | 21.514 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6925 | 0 | 0 | 21.514 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 13 | 1837 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13734.2116 | 0 | 16957.6064 | 0 | 30756.4599 | 0 | 7830.9101 | 0 | 69279.188 | 0 | 1015.7551 | 0 | 941.7846 | 0 | 1495.6845 | 0 | 434.9099 | 1454.0059 | 5342.14 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.4092 | 21.7123 | 18.8397 | 21.4965 | 21.7123 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6924 | 0 | 0 | 21.7123 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 14 | 1838 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12726.9531 | 0 | 12069.9973 | 0 | 29837.3191 | 0 | 7256.5961 | 0 | 61890.8656 | 0 | 941.2602 | 0 | 670.3386 | 0 | 1450.9868 | 0 | 403.0139 | 1248.7859 | 4714.3853 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.5832 | 21.8862 | 19.0052 | 21.662 | 21.8862 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6923 | 0 | 0 | 21.8862 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 15 | 1839 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2899.073 | 0 | 1666.7412 | 0 | 3941.6722 | 0 | 1652.9802 | 0 | 10160.4667 | 0 | 214.4097 | 0 | 92.5668 | 0 | 191.6832 | 0 | 91.8025 | 244.5175 | 834.9798 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.5954 | 21.8984 | 18.9822 | 21.6391 | 21.8984 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6922 | 0 | 0 | 21.8984 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 16 | 1840 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4667.8973 | 0 | 2675.3359 | 0 | 6530.2715 | 0 | 2661.5204 | 0 | 16535.025 | 0 | 345.2284 | 0 | 148.5817 | 0 | 317.5667 | 0 | 147.8144 | 388.6082 | 1347.7994 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6297 | 21.9327 | 19.0276 | 21.6845 | 21.9327 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6921 | 0 | 0 | 21.9327 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 17 | 1841 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6162.9432 | 0 | 3513.9589 | 0 | 10495.9775 | 0 | 3668.4842 | 0 | 23841.3637 | 0 | 455.7991 | 0 | 195.1568 | 0 | 510.4187 | 0 | 203.7388 | 519.5997 | 1884.713 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.683 | 21.9861 | 19.0738 | 21.7306 | 21.9861 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6920 | 0 | 0 | 21.9861 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 18 | 1842 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3192.0887 | 0 | 1820.0506 | 0 | 5027.9752 | 0 | 1956.3639 | 0 | 11996.4784 | 0 | 236.0806 | 0 | 101.0812 | 0 | 244.5101 | 0 | 108.6517 | 266.3494 | 956.673 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6995 | 22.0026 | 19.0834 | 21.7402 | 22.0026 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6919 | 0 | 0 | 22.0026 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 19 | 1843 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 401.2557 | 0 | 228.7861 | 0 | 770.0087 | 0 | 298.618 | 0 | 1698.6685 | 0 | 29.6761 | 0 | 12.7062 | 0 | 37.4455 | 0 | 16.5845 | 34.9311 | 131.3434 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6877 | 21.9908 | 19.0774 | 21.7343 | 21.9908 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6918 | 0 | 0 | 21.9908 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 20 | 1844 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6556 | 21.9587 | 18.9958 | 21.6526 | 21.9587 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6917 | 0 | 0 | 21.9587 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 21 | 1845 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6074 | 21.9104 | 18.8956 | 21.5525 | 21.9104 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6916 | 0 | 0 | 21.9104 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 22 | 1846 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.555 | 21.8581 | 18.83 | 21.4868 | 21.8581 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6915 | 0 | 0 | 21.8581 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 23 | 1847 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.505 | 21.808 | 18.7874 | 21.4442 | 21.808 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6914 | 0 | 0 | 21.808 | 0 | 0 | 0
|  | 2004 | 3 | 18 | 24 | 1848 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.4481 | 21.7512 | 18.7085 | 21.3654 | 21.7512 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6913 | 0 | 0 | 21.7512 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 1 | 1849 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.3459 | 21.649 | 18.6145 | 21.2714 | 21.649 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6912 | 0 | 0 | 21.649 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 2 | 1850 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.2428 | 21.5459 | 18.5086 | 21.1654 | 21.5459 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6911 | 0 | 0 | 21.5459 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 3 | 1851 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.1353 | 21.4383 | 18.3865 | 21.0433 | 21.4383 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6910 | 0 | 0 | 21.4383 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 4 | 1852 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.026 | 21.3291 | 18.2715 | 20.9284 | 21.3291 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6909 | 0 | 0 | 21.3291 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 5 | 1853 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.9151 | 21.2181 | 18.155 | 20.8118 | 21.2181 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6908 | 0 | 0 | 21.2181 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 6 | 1854 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.8089 | 21.1119 | 18.0638 | 20.7206 | 21.1119 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6907 | 0 | 0 | 21.1119 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 7 | 1855 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.7073 | 21.0104 | 17.9771 | 20.6339 | 21.0104 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6906 | 0 | 0 | 21.0104 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 8 | 1856 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 3642.9175 | 0 | 2249.7152 | 0 | 1185.2378 | 0 | 506.8451 | 0 | 7584.7155 | 0 | 269.423 | 0 | 124.9438 | 0 | 57.638 | 0 | 28.149 | 82.9613 | 563.115 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6477 | 20.9497 | 17.9207 | 20.5785 | 20.9497 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6905 | 0 | 0 | 20.9497 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 9 | 1857 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9959.9109 | 0 | 8051.6876 | 0 | 5693.8869 | 0 | 2434.8858 | 0 | 26140.3712 | 0 | 736.6153 | 0 | 447.1713 | 0 | 276.8933 | 0 | 135.2277 | 410.4401 | 2006.3478 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6483 | 20.9503 | 17.9458 | 20.6036 | 20.9503 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6904 | 0 | 0 | 20.9503 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 10 | 1858 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9233.1133 | 0 | 8147.9322 | 0 | 9269.122 | 0 | 3963.7693 | 0 | 30613.9368 | 0 | 682.8628 | 0 | 452.5165 | 0 | 450.7568 | 0 | 220.1382 | 641.8585 | 2448.1327 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6671 | 20.9692 | 17.9821 | 20.6399 | 20.9692 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6903 | 0 | 0 | 20.9692 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 11 | 1859 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10107.5026 | 0 | 10158.2898 | 0 | 12866.8166 | 0 | 5502.2571 | 0 | 38634.8661 | 0 | 747.5309 | 0 | 564.1669 | 0 | 625.7124 | 0 | 305.5821 | 899.4751 | 3142.4675 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7153 | 21.0174 | 18.0499 | 20.7077 | 21.0174 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6902 | 0 | 0 | 21.0174 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 12 | 1860 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13308.2726 | 0 | 22643.1332 | 0 | 25634.6033 | 0 | 7588.0502 | 0 | 69174.0593 | 0 | 984.2535 | 0 | 1257.5451 | 0 | 1246.609 | 0 | 421.422 | 1502.0362 | 5411.8657 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8624 | 21.1645 | 18.2325 | 20.8903 | 21.1645 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6901 | 0 | 0 | 21.1645 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 13 | 1861 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8846.9514 | 0 | 5459.1773 | 0 | 12361.9762 | 0 | 5044.3144 | 0 | 31712.4193 | 0 | 654.303 | 0 | 303.1896 | 0 | 601.162 | 0 | 280.1491 | 729.1862 | 2567.9898 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8961 | 21.1982 | 18.2518 | 20.9096 | 21.1982 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6900 | 0 | 0 | 21.1982 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 14 | 1862 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2584.6074 | 0 | 1488.6773 | 0 | 3486.4017 | 0 | 1473.6797 | 0 | 9033.3661 | 0 | 191.1524 | 0 | 82.6775 | 0 | 169.5435 | 0 | 81.8446 | 218.3192 | 743.5373 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8483 | 21.1504 | 18.1511 | 20.8089 | 21.1504 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6899 | 0 | 0 | 21.1504 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 15 | 1863 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2582.8741 | 0 | 1483.3098 | 0 | 3503.2485 | 0 | 1472.6914 | 0 | 9042.1239 | 0 | 191.0243 | 0 | 82.3795 | 0 | 170.3627 | 0 | 81.7897 | 218.3192 | 743.8754 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8035 | 21.1056 | 18.1164 | 20.7742 | 21.1056 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6898 | 0 | 0 | 21.1056 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 16 | 1864 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2422.6249 | 0 | 1384.9116 | 0 | 3313.4017 | 0 | 1381.3212 | 0 | 8502.2594 | 0 | 179.1725 | 0 | 76.9147 | 0 | 161.1305 | 0 | 76.7153 | 205.2201 | 699.153 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7591 | 21.0612 | 18.0793 | 20.7371 | 21.0612 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6897 | 0 | 0 | 21.0612 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 17 | 1865 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1429.0514 | 0 | 814.81 | 0 | 1960.7948 | 0 | 818.6882 | 0 | 5023.3443 | 0 | 105.6898 | 0 | 45.2526 | 0 | 95.3533 | 0 | 45.468 | 122.2588 | 414.0224 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7059 | 21.008 | 18.0304 | 20.6882 | 21.008 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6896 | 0 | 0 | 21.008 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 18 | 1866 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 554.5732 | 0 | 316.204 | 0 | 763.1484 | 0 | 320.4547 | 0 | 1954.3802 | 0 | 41.0151 | 0 | 17.5612 | 0 | 37.1119 | 0 | 17.7973 | 48.0302 | 161.5157 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.677 | 20.9801 | 18.0107 | 20.6675 | 20.9801 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6895 | 0 | 0 | 20.9801 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 19 | 1867 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6437 | 20.9467 | 17.9783 | 20.6351 | 20.9467 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6894 | 0 | 0 | 20.9467 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 20 | 1868 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.607 | 20.91 | 17.9308 | 20.5877 | 20.91 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6893 | 0 | 0 | 20.91 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 21 | 1869 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5652 | 20.8682 | 17.8725 | 20.5293 | 20.8682 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6892 | 0 | 0 | 20.8682 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 22 | 1870 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5201 | 20.8232 | 17.8169 | 20.4738 | 20.8232 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6891 | 0 | 0 | 20.8232 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 23 | 1871 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4719 | 20.7749 | 17.7582 | 20.4151 | 20.7749 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6890 | 0 | 0 | 20.7749 | 0 | 0 | 0
|  | 2004 | 3 | 19 | 24 | 1872 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.425 | 20.728 | 17.7157 | 20.3725 | 20.728 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6889 | 0 | 0 | 20.728 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 1 | 1873 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3271 | 20.6302 | 17.6082 | 20.265 | 20.6302 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6888 | 0 | 0 | 20.6302 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 2 | 1874 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2229 | 20.526 | 17.4834 | 20.1402 | 20.526 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6887 | 0 | 0 | 20.526 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 3 | 1875 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1197 | 20.4228 | 17.3832 | 20.0401 | 20.4228 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6886 | 0 | 0 | 20.4228 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 4 | 1876 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0166 | 20.3197 | 17.2802 | 19.937 | 20.3197 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6885 | 0 | 0 | 20.3197 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 5 | 1877 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9099 | 20.213 | 17.1619 | 19.8187 | 20.213 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6884 | 0 | 0 | 20.213 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 6 | 1878 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8088 | 20.1119 | 17.0786 | 19.7354 | 20.1119 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6883 | 0 | 0 | 20.1119 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 7 | 1879 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7096 | 20.0127 | 16.9853 | 19.6421 | 20.0127 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6882 | 0 | 0 | 20.0127 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 8 | 1880 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 327.5766 | 0 | 187.97 | 0 | 409.6246 | 0 | 175.1684 | 0 | 1100.3396 | 0 | 24.2269 | 0 | 10.4394 | 0 | 19.92 | 0 | 9.7284 | 26.1983 | 90.5131 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6334 | 19.9354 | 16.9125 | 19.5703 | 20 |  | 23.9278 | 0 | 23.9278 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6881 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 9 | 1881 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 562.6412 | 0 | 323.6968 | 0 | 740.7832 | 0 | 316.7823 | 0 | 1943.9036 | 0 | 41.6118 | 0 | 17.9773 | 0 | 36.0242 | 0 | 17.5933 | 48.0302 | 161.237 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6342 | 19.9363 | 16.9519 | 19.6097 | 20 |  | 23.6162 | 0 | 23.6162 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6880 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 10 | 1882 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1126.3835 | 0 | 650.5446 | 0 | 1492.9544 | 0 | 638.4345 | 0 | 3908.3169 | 0 | 83.3051 | 0 | 36.1297 | 0 | 72.6023 | 0 | 35.4571 | 96.0605 | 323.5546 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6542 | 19.9563 | 17.0218 | 19.6796 | 20 |  | 16.1902 | 0 | 16.1902 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6879 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 11 | 1883 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4257.0692 | 0 | 2519.3934 | 0 | 5662.7734 | 0 | 2421.5807 | 0 | 14860.8167 | 0 | 314.8444 | 0 | 139.921 | 0 | 275.3803 | 0 | 134.4888 | 353.6771 | 1218.3116 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6955 | 19.9975 | 17.0948 | 19.7526 | 20 |  | 0.91405 | 0 | 0.91405 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6878 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 12 | 1884 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5597.6116 | 0 | 3307.2754 | 0 | 7523.7566 | 0 | 3191.6206 | 0 | 19620.2641 | 0 | 413.9883 | 0 | 183.6781 | 0 | 365.8798 | 0 | 177.2549 | 462.8367 | 1603.6378 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7102 | 20.0123 | 17.1123 | 19.7701 | 20.0123 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6877 | 0 | 0 | 20.0123 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 13 | 1885 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2164.7289 | 0 | 1247.815 | 0 | 2904.7921 | 0 | 1234.2752 | 0 | 7551.6112 | 0 | 160.0991 | 0 | 69.3006 | 0 | 141.2598 | 0 | 68.5487 | 183.3881 | 622.5963 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.688 | 19.99 | 17.0932 | 19.751 | 20 |  | 3.6936 | 0 | 3.6936 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6876 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 14 | 1886 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2008.328 | 0 | 1153.9943 | 0 | 2701.7476 | 0 | 1145.0993 | 0 | 7009.1692 | 0 | 148.532 | 0 | 64.0901 | 0 | 131.3858 | 0 | 63.5961 | 170.289 | 577.8929 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.67 | 19.9721 | 17.0609 | 19.7187 | 20 |  | 10.3413 | 0 | 10.3413 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6875 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 15 | 1887 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 2006.5957 | 0 | 1150.365 | 0 | 2710.808 | 0 | 1144.1116 | 0 | 7011.8802 | 0 | 148.4038 | 0 | 63.8885 | 0 | 131.8264 | 0 | 63.5412 | 170.289 | 577.9489 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6759 | 19.978 | 17.0874 | 19.7452 | 20 |  | 8.1565 | 0 | 8.1565 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6874 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 16 | 1888 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 1847.1768 | 0 | 1055.1736 | 0 | 2510.4851 | 0 | 1053.2149 | 0 | 6466.0504 | 0 | 136.6135 | 0 | 58.6018 | 0 | 122.0847 | 0 | 58.493 | 157.1898 | 532.9829 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6735 | 19.9756 | 17.082 | 19.7398 | 20 |  | 9.059 | 0 | 9.059 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6873 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 17 | 1889 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 403.9798 | 0 | 230.3393 | 0 | 543.0109 | 0 | 230.6551 | 0 | 1407.9851 | 0 | 29.8775 | 0 | 12.7925 | 0 | 26.4066 | 0 | 12.81 | 34.9311 | 116.8177 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6579 | 19.9599 | 17.0637 | 19.7215 | 20 |  | 14.8449 | 0 | 14.8449 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6872 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 18 | 1890 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 402.4209 | 0 | 229.4505 | 0 | 548.4324 | 0 | 231.6094 | 0 | 1411.9133 | 0 | 29.7623 | 0 | 12.7431 | 0 | 26.6702 | 0 | 12.863 | 34.9311 | 116.9697 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6927 | 19.9957 | 17.1059 | 19.7628 | 20 |  | 1.581 | 0 | 1.581 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6871 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 19 | 1891 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 149.6145 | 0 | 85.3065 | 0 | 220.8786 | 0 | 91.8081 | 0 | 547.6077 | 0 | 11.0652 | 0 | 4.7377 | 0 | 10.7413 | 0 | 5.0988 | 13.0992 | 44.7422 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6929 | 19.9959 | 17.115 | 19.7718 | 20 |  | 1.5025 | 0 | 1.5025 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6870 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 20 | 1892 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6886 | 19.9916 | 17.1019 | 19.7587 | 20 |  | 3.1099 | 0 | 3.1099 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6869 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 21 | 1893 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6849 | 19.988 | 17.0865 | 19.7433 | 20 |  | 4.4634 | 0 | 4.4634 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6868 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 22 | 1894 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6794 | 19.9825 | 17.0634 | 19.7202 | 20 |  | 6.4936 | 0 | 6.4936 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6867 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 23 | 1895 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.674 | 19.977 | 17.0403 | 19.6971 | 20 |  | 8.5238 | 0 | 8.5238 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6866 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 20 | 24 | 1896 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6721 | 19.9752 | 17.0326 | 19.6894 | 20 |  | 9.2005 | 0 | 9.2005 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6865 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 1 | 1897 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6171 | 19.9201 | 16.9547 | 19.6116 | 19.9201 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6864 | 0 | 0 | 19.9201 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 2 | 1898 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5307 | 19.8337 | 16.8472 | 19.504 | 19.8337 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6863 | 0 | 0 | 19.8337 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 3 | 1899 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4414 | 19.7445 | 16.7487 | 19.4056 | 19.7445 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6862 | 0 | 0 | 19.7445 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 4 | 1900 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3512 | 19.6543 | 16.6553 | 19.3121 | 19.6543 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6861 | 0 | 0 | 19.6543 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 5 | 1901 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2583 | 19.5613 | 16.5532 | 19.21 | 19.5613 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6860 | 0 | 0 | 19.5613 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 6 | 1902 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1662 | 19.4692 | 16.4638 | 19.1207 | 19.4692 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6859 | 0 | 0 | 19.4692 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 7 | 1903 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0952 | 0 | 90.142 | 0 | 210.7936 | 0 | 90.142 | 0 | 549.1727 | 0 | 11.6924 | 0 | 5.0063 | 0 | 10.2509 | 0 | 5.0063 | 13.0992 | 45.055 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0729 | 19.376 | 16.3615 | 19.0184 | 19.376 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6858 | 0 | 0 | 19.376 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 8 | 1904 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12944.5461 | 0 | 7961.7965 | 0 | 3079.7684 | 0 | 1317.0062 | 0 | 25303.1173 | 0 | 957.353 | 0 | 442.179 | 0 | 149.7689 | 0 | 73.1434 | 253.2503 | 1875.6946 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.075 | 19.3771 | 16.3806 | 19.0384 | 20 |  | 230.8923 | 0 | 230.8923 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6857 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 9 | 1905 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 42604.4569 | 0 | 39246.5506 | 0 | 7350.611 | 0 | 3143.3534 | 0 | 92344.972 | 0 | 3150.9413 | 0 | 2179.6589 | 0 | 357.4597 | 0 | 174.5743 | 982.4364 | 6845.0706 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8978 | 20.1999 | 17.2175 | 19.8753 | 20.1999 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6856 | 0 | 0 | 20.1999 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 10 | 1906 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 19670.2267 | 0 | 23751.9287 | 0 | 12620.681 | 0 | 5397.0018 | 0 | 61439.8382 | 0 | 1454.771 | 0 | 1319.1249 | 0 | 613.7428 | 0 | 299.7365 | 1104.6952 | 4792.0704 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0053 | 20.3074 | 17.3146 | 19.9723 | 20.3074 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6855 | 0 | 0 | 20.3074 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 11 | 1907 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14210.4453 | 0 | 27148.4746 | 0 | 16081.6514 | 0 | 6877.022 | 0 | 64317.5933 | 0 | 1050.9764 | 0 | 1507.7609 | 0 | 782.0496 | 0 | 381.9332 | 1480.2042 | 5202.9243 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1292 | 20.4312 | 17.4645 | 20.1223 | 20.4312 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6854 | 0 | 0 | 20.4312 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 12 | 1908 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13669.6757 | 0 | 29700.0505 | 0 | 29578.6636 | 0 | 7794.1133 | 0 | 80742.5031 | 0 | 1010.9821 | 0 | 1649.4693 | 0 | 1438.4084 | 0 | 432.8663 | 1772.752 | 6304.478 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3059 | 20.608 | 17.6604 | 20.3182 | 20.608 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6853 | 0 | 0 | 20.608 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 13 | 1909 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11545.329 | 0 | 8650.5037 | 0 | 18219.0169 | 0 | 6582.863 | 0 | 44997.7127 | 0 | 853.8697 | 0 | 480.4281 | 0 | 885.9895 | 0 | 365.5964 | 1017.3675 | 3603.2512 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3706 | 20.6727 | 17.6979 | 20.3557 | 20.6727 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6852 | 0 | 0 | 20.6727 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 14 | 1910 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12259.0637 | 0 | 9020.6949 | 0 | 21843.0012 | 0 | 6989.817 | 0 | 50112.5768 | 0 | 906.6561 | 0 | 500.9877 | 0 | 1062.2236 | 0 | 388.1976 | 1104.6952 | 3962.7602 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4537 | 20.7558 | 17.7936 | 20.4514 | 20.7558 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6851 | 0 | 0 | 20.7558 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 15 | 1911 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12809.9625 | 0 | 10716.0313 | 0 | 36566.5676 | 0 | 7303.926 | 0 | 67396.4873 | 0 | 947.3995 | 0 | 595.1426 | 0 | 1778.2296 | 0 | 405.6425 | 1309.9153 | 5036.3294 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5932 | 20.8953 | 17.9564 | 20.6142 | 20.8953 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6850 | 0 | 0 | 20.8953 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 16 | 1912 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11405.3519 | 0 | 7679.3 | 0 | 45231.3398 | 0 | 6503.0515 | 0 | 70819.0432 | 0 | 843.5172 | 0 | 426.4898 | 0 | 2199.5969 | 0 | 361.1638 | 1213.8548 | 5044.6226 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.739 | 21.0411 | 18.092 | 20.7498 | 21.0411 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6849 | 0 | 0 | 21.0411 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 17 | 1913 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9149.4062 | 0 | 5216.7667 | 0 | 62471.4681 | 0 | 8960.5135 | 0 | 85798.1545 | 0 | 676.672 | 0 | 289.7267 | 0 | 3037.9832 | 0 | 497.6453 | 1104.6952 | 5606.7223 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9178 | 21.2199 | 18.2395 | 20.8973 | 21.2199 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6848 | 0 | 0 | 21.2199 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 18 | 1914 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3784.2709 | 0 | 2157.6983 | 0 | 6046.3783 | 0 | 2342.348 | 0 | 14330.6955 | 0 | 279.8772 | 0 | 119.8334 | 0 | 294.035 | 0 | 130.0884 | 314.3797 | 1138.2135 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9165 | 21.2196 | 18.2229 | 20.8798 | 21.2196 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6847 | 0 | 0 | 21.2196 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 19 | 1915 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 300.4817 | 0 | 171.3273 | 0 | 471.593 | 0 | 193.1339 | 0 | 1136.5359 | 0 | 22.223 | 0 | 9.5151 | 0 | 22.9335 | 0 | 10.7262 | 26.1983 | 91.5962 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8659 | 21.169 | 18.1347 | 20.7916 | 21.169 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6846 | 0 | 0 | 21.169 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 20 | 1916 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8016 | 21.1046 | 18.0367 | 20.6935 | 21.1046 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6845 | 0 | 0 | 21.1046 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 21 | 1917 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7442 | 21.0473 | 18.0018 | 20.6586 | 21.0473 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6844 | 0 | 0 | 21.0473 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 22 | 1918 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6774 | 20.9804 | 17.9043 | 20.5611 | 20.9804 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6843 | 0 | 0 | 20.9804 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 23 | 1919 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6084 | 20.9115 | 17.8285 | 20.4853 | 20.9115 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6842 | 0 | 0 | 20.9115 | 0 | 0 | 0
|  | 2004 | 3 | 21 | 24 | 1920 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5338 | 20.8368 | 17.7353 | 20.3922 | 20.8368 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6841 | 0 | 0 | 20.8368 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 1 | 1921 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4102 | 20.7133 | 17.6088 | 20.2656 | 20.7133 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6840 | 0 | 0 | 20.7133 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 2 | 1922 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2824 | 20.5855 | 17.467 | 20.1238 | 20.5855 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6839 | 0 | 0 | 20.5855 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 3 | 1923 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1732 | 20.4762 | 17.4173 | 20.0741 | 20.4762 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6838 | 0 | 0 | 20.4762 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 4 | 1924 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0613 | 20.3644 | 17.2969 | 19.9537 | 20.3644 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6837 | 0 | 0 | 20.3644 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 5 | 1925 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9569 | 20.26 | 17.2164 | 19.8732 | 20.26 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6836 | 0 | 0 | 20.26 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 6 | 1926 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8472 | 20.1502 | 17.0891 | 19.7459 | 20.1502 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6835 | 0 | 0 | 20.1502 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 7 | 1927 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7111 | 20.0141 | 16.8681 | 19.525 | 20.0141 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6834 | 0 | 0 | 20.0141 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 8 | 1928 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 321.8548 | 0 | 184.3444 | 0 | 407.2887 | 0 | 174.1695 | 0 | 1087.6574 | 0 | 23.8037 | 0 | 10.238 | 0 | 19.8064 | 0 | 9.673 | 26.1983 | 89.7195 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6003 | 19.9024 | 16.7589 | 19.4167 | 20 |  | 36.1835 | 0 | 36.1835 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6833 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 9 | 1929 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 719.92 | 0 | 414.6699 | 0 | 945.8011 | 0 | 404.4544 | 0 | 2484.8454 | 0 | 53.2439 | 0 | 23.0298 | 0 | 45.9942 | 0 | 22.4624 | 61.1294 | 205.8597 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6038 | 19.9059 | 16.8098 | 19.4676 | 20 |  | 34.876 | 0 | 34.876 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6832 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 10 | 1930 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6740.2818 | 0 | 4794.7287 | 0 | 7939.5106 | 0 | 3395.1855 | 0 | 22869.7065 | 0 | 498.4979 | 0 | 266.2877 | 0 | 386.0979 | 0 | 188.5604 | 510.8669 | 1850.3108 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6801 | 19.9822 | 16.944 | 19.6017 | 20 |  | 6.6123 | 0 | 6.6123 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6831 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 11 | 1931 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10306.8862 | 0 | 9821.3718 | 0 | 13125.7056 | 0 | 5612.9662 | 0 | 38866.9299 | 0 | 762.2769 | 0 | 545.4553 | 0 | 638.3022 | 0 | 311.7306 | 908.2079 | 3165.9729 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7327 | 20.0348 | 17.0164 | 19.6742 | 20.0348 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6830 | 0 | 0 | 20.0348 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 12 | 1932 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12129.9891 | 0 | 13919.831 | 0 | 19782.3972 | 0 | 6916.2219 | 0 | 52748.4392 | 0 | 897.11 | 0 | 773.0739 | 0 | 962.0166 | 0 | 384.1103 | 1174.5573 | 4190.8681 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8082 | 20.1103 | 17.0932 | 19.751 | 20.1103 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6829 | 0 | 0 | 20.1103 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 13 | 1933 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14302.1054 | 0 | 17677.6841 | 0 | 32092.066 | 0 | 8154.7092 | 0 | 72226.5647 | 0 | 1057.7554 | 0 | 981.776 | 0 | 1560.6349 | 0 | 452.8929 | 1541.3336 | 5594.3929 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9511 | 20.2532 | 17.2743 | 19.9321 | 20.2532 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6828 | 0 | 0 | 20.2532 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 14 | 1934 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13015.167 | 0 | 29574.4654 | 0 | 77582.4282 | 0 | 7420.9285 | 0 | 127592.9892 | 0 | 962.576 | 0 | 1642.4946 | 0 | 3772.8281 | 0 | 412.1405 | 2318.55 | 9108.5892 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.25 | 20.552 | 17.5607 | 20.2185 | 20.552 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6827 | 0 | 0 | 20.552 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 15 | 1935 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11741.4437 | 0 | 7956.9158 | 0 | 22940.0966 | 0 | 6694.6828 | 0 | 49333.1389 | 0 | 868.3739 | 0 | 441.9079 | 0 | 1115.5753 | 0 | 371.8066 | 1065.3977 | 3863.0615 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3133 | 20.6154 | 17.5921 | 20.2499 | 20.6154 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6826 | 0 | 0 | 20.6154 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 16 | 1936 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11768.4199 | 0 | 8067.9488 | 0 | 52219.794 | 0 | 6710.064 | 0 | 78766.2267 | 0 | 870.369 | 0 | 448.0744 | 0 | 2539.445 | 0 | 372.6608 | 1336.1136 | 5566.6628 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4617 | 20.7638 | 17.7433 | 20.4011 | 20.7638 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6825 | 0 | 0 | 20.7638 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 17 | 1937 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9286.4856 | 0 | 5294.926 | 0 | 59413.9608 | 0 | 8903.4486 | 0 | 82898.821 | 0 | 686.8101 | 0 | 294.0674 | 0 | 2889.2968 | 0 | 494.4761 | 1091.596 | 5456.2465 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6205 | 20.9226 | 17.9005 | 20.5583 | 20.9226 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6824 | 0 | 0 | 20.9226 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 18 | 1938 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5517.4846 | 0 | 3145.9342 | 0 | 26680.5083 | 0 | 6763.5462 | 0 | 42107.4733 | 0 | 408.0622 | 0 | 174.7176 | 0 | 1297.4713 | 0 | 375.6311 | 519.5997 | 2775.4819 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6813 | 20.9844 | 17.9307 | 20.5875 | 20.9844 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6823 | 0 | 0 | 20.9844 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 19 | 1939 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 708.4054 | 0 | 403.9154 | 0 | 1269.8485 | 0 | 505.026 | 0 | 2887.1954 | 0 | 52.3923 | 0 | 22.4325 | 0 | 61.7526 | 0 | 28.0479 | 61.1294 | 225.7547 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6198 | 20.9229 | 17.8367 | 20.4936 | 20.9229 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6822 | 0 | 0 | 20.9229 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 20 | 1940 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5432 | 20.8463 | 17.7386 | 20.3954 | 20.8463 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6821 | 0 | 0 | 20.8463 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 21 | 1941 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4665 | 20.7695 | 17.6611 | 20.318 | 20.7695 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6820 | 0 | 0 | 20.7695 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 22 | 1942 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3795 | 20.6825 | 17.5411 | 20.198 | 20.6825 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6819 | 0 | 0 | 20.6825 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 23 | 1943 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2751 | 20.5781 | 17.3806 | 20.0374 | 20.5781 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6818 | 0 | 0 | 20.5781 | 0 | 0 | 0
|  | 2004 | 3 | 22 | 24 | 1944 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1635 | 20.4665 | 17.2456 | 19.9025 | 20.4665 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6817 | 0 | 0 | 20.4665 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 1 | 1945 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9952 | 20.2982 | 17.049 | 19.7058 | 20.2982 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6816 | 0 | 0 | 20.2982 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 2 | 1946 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8211 | 20.1242 | 16.8564 | 19.5132 | 20.1242 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6815 | 0 | 0 | 20.1242 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 3 | 1947 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6479 | 19.9509 | 16.6853 | 19.3422 | 19.9509 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6814 | 0 | 0 | 19.9509 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 4 | 1948 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4772 | 19.7803 | 16.5227 | 19.1795 | 19.7803 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6813 | 0 | 0 | 19.7803 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 5 | 1949 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3036 | 19.6067 | 16.3394 | 18.9963 | 19.6067 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6812 | 0 | 0 | 19.6067 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 6 | 1950 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.1299 | 19.433 | 16.1649 | 18.8218 | 19.433 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6811 | 0 | 0 | 19.433 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 7 | 1951 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0953 | 0 | 90.1421 | 0 | 210.7938 | 0 | 90.1421 | 0 | 549.1732 | 0 | 11.6924 | 0 | 5.0063 | 0 | 10.2509 | 0 | 5.0063 | 13.0992 | 45.055 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9613 | 19.2643 | 16.0072 | 18.6641 | 19.2643 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6810 | 0 | 0 | 19.2643 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 8 | 1952 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8002.0206 | 0 | 4868.1731 | 0 | 1956.0685 | 0 | 836.4766 | 0 | 15662.7388 | 0 | 591.8136 | 0 | 270.3666 | 0 | 95.1235 | 0 | 46.4559 | 144.0907 | 1147.8503 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.8716 | 19.1737 | 15.9546 | 18.6124 | 20 |  | 306.28 | 0 | 306.28 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6809 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 9 | 1953 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10584.9248 | 0 | 8285.5024 | 0 | 6412.6571 | 0 | 2742.2547 | 0 | 28025.3391 | 0 | 782.8401 | 0 | 460.1568 | 0 | 311.8471 | 0 | 152.2982 | 462.8367 | 2169.9789 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6646 | 19.9667 | 16.8224 | 19.4802 | 20 |  | 12.3589 | 0 | 12.3589 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6808 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 10 | 1954 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14818.6885 | 0 | 15332.1654 | 0 | 12073.4544 | 0 | 5162.9904 | 0 | 47387.2986 | 0 | 1095.9609 | 0 | 851.5115 | 0 | 587.1313 | 0 | 286.74 | 921.3071 | 3742.6508 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7412 | 20.0433 | 16.9688 | 19.6266 | 20.0433 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6807 | 0 | 0 | 20.0433 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 11 | 1955 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 15228.463 | 0 | 33538.3149 | 0 | 16270.1036 | 0 | 6957.6101 | 0 | 71994.4916 | 0 | 1126.267 | 0 | 1862.6372 | 0 | 791.214 | 0 | 386.4089 | 1672.3251 | 5838.8523 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.868 | 20.1701 | 17.1343 | 19.7921 | 20.1701 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6806 | 0 | 0 | 20.1701 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 12 | 1956 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13767.3343 | 0 | 32028.8606 | 0 | 30745.7993 | 0 | 7849.7959 | 0 | 84391.79 | 0 | 1018.2048 | 0 | 1778.8058 | 0 | 1495.1661 | 0 | 435.9588 | 1890.6444 | 6618.7797 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0393 | 20.3413 | 17.3366 | 19.9944 | 20.3413 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6805 | 0 | 0 | 20.3413 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 13 | 1957 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14780.7596 | 0 | 24777.7131 | 0 | 42084.7341 | 0 | 8427.6261 | 0 | 90070.8328 | 0 | 1093.1557 | 0 | 1376.0945 | 0 | 2046.5777 | 0 | 468.0501 | 1868.8124 | 6852.6904 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2106 | 20.5127 | 17.4528 | 20.1106 | 20.5127 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6804 | 0 | 0 | 20.5127 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 14 | 1958 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14701.3183 | 0 | 20471.0243 | 0 | 52611.6845 | 0 | 8382.3306 | 0 | 96166.3577 | 0 | 1087.2804 | 0 | 1136.9114 | 0 | 2558.5026 | 0 | 465.5345 | 1855.7133 | 7103.9421 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4052 | 20.7073 | 17.6685 | 20.3263 | 20.7073 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6803 | 0 | 0 | 20.7073 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 15 | 1959 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13446.8114 | 0 | 16518.1936 | 0 | 69562.8514 | 0 | 7667.0416 | 0 | 107194.8979 | 0 | 994.4995 | 0 | 917.3807 | 0 | 3382.8366 | 0 | 425.809 | 1842.6141 | 7563.14 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6349 | 20.937 | 17.9126 | 20.5704 | 20.937 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6802 | 0 | 0 | 20.937 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 16 | 1960 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10429.8424 | 0 | 8970.1503 | 0 | 99906.2182 | 0 | 5946.84 | 0 | 125253.0509 | 0 | 771.3705 | 0 | 498.1805 | 0 | 4858.4325 | 0 | 330.2732 | 1881.9116 | 8340.1683 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9243 | 21.2264 | 18.2327 | 20.8905 | 21.2264 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6801 | 0 | 0 | 21.2264 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 17 | 1961 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8317.7298 | 0 | 4742.5652 | 0 | 96067.7741 | 0 | 11455.5392 | 0 | 120583.6084 | 0 | 615.1628 | 0 | 263.3906 | 0 | 4671.7692 | 0 | 636.2131 | 1405.9757 | 7592.5114 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.1856 | 21.4876 | 18.4475 | 21.1053 | 21.4876 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6800 | 0 | 0 | 21.4876 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 18 | 1962 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4838.318 | 0 | 2758.6901 | 0 | 14615.9509 | 0 | 4309.3391 | 0 | 26522.2981 | 0 | 357.8324 | 0 | 153.211 | 0 | 710.7727 | 0 | 239.3303 | 423.5393 | 1884.6857 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1837 | 21.4868 | 18.376 | 21.0329 | 21.4868 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6799 | 0 | 0 | 21.4868 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 19 | 1963 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 708.4872 | 0 | 403.962 | 0 | 1222.2332 | 0 | 491.2106 | 0 | 2825.8931 | 0 | 52.3983 | 0 | 22.4351 | 0 | 59.4371 | 0 | 27.2807 | 61.1294 | 222.6805 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1108 | 21.4139 | 18.2924 | 20.9493 | 21.4139 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6798 | 0 | 0 | 21.4139 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 20 | 1964 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0249 | 21.328 | 18.1912 | 20.848 | 21.328 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6797 | 0 | 0 | 21.328 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 21 | 1965 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9262 | 21.2292 | 18.0509 | 20.7077 | 21.2292 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6796 | 0 | 0 | 21.2292 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 22 | 1966 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8165 | 21.1196 | 17.906 | 20.5628 | 21.1196 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6795 | 0 | 0 | 21.1196 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 23 | 1967 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7015 | 21.0046 | 17.7736 | 20.4305 | 21.0046 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6794 | 0 | 0 | 21.0046 | 0 | 0 | 0
|  | 2004 | 3 | 23 | 24 | 1968 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5867 | 20.8898 | 17.6593 | 20.3161 | 20.8898 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6793 | 0 | 0 | 20.8898 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 1 | 1969 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4234 | 20.7265 | 17.4942 | 20.151 | 20.7265 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6792 | 0 | 0 | 20.7265 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 2 | 1970 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2608 | 20.5639 | 17.3334 | 19.9903 | 20.5639 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6791 | 0 | 0 | 20.5639 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 3 | 1971 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0934 | 20.3964 | 17.1502 | 19.807 | 20.3964 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6790 | 0 | 0 | 20.3964 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 4 | 1972 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9266 | 20.2297 | 16.9854 | 19.6423 | 20.2297 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6789 | 0 | 0 | 20.2297 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 5 | 1973 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7514 | 20.0545 | 16.7829 | 19.4397 | 20.0545 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6788 | 0 | 0 | 20.0545 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 6 | 1974 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5752 | 19.8783 | 16.603 | 19.2598 | 19.8783 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6787 | 0 | 0 | 19.8783 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 7 | 1975 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0954 | 0 | 90.1421 | 0 | 210.7939 | 0 | 90.1421 | 0 | 549.1735 | 0 | 11.6924 | 0 | 5.0063 | 0 | 10.2509 | 0 | 5.0063 | 13.0992 | 45.055 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4041 | 19.7072 | 16.4429 | 19.0997 | 19.7072 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6786 | 0 | 0 | 19.7072 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 8 | 1976 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 18354.3401 | 0 | 11131.7093 | 0 | 3748.1654 | 0 | 1602.8339 | 0 | 34837.0487 | 0 | 1357.4506 | 0 | 618.2283 | 0 | 182.273 | 0 | 89.0175 | 314.3797 | 2561.3492 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.4054 | 19.7085 | 16.5234 | 19.1802 | 20 |  | 108.0938 | 0 | 108.0938 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6785 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 9 | 1977 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 25739.7119 | 0 | 21911.4803 | 0 | 9128.2672 | 0 | 3903.5353 | 0 | 60682.9947 | 0 | 1903.6581 | 0 | 1216.9108 | 0 | 443.907 | 0 | 216.7929 | 799.0483 | 4580.3172 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.797 | 20.1001 | 16.9904 | 19.6473 | 20.1001 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6784 | 0 | 0 | 20.1001 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 10 | 1978 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10664.7521 | 0 | 9411.0919 | 0 | 10448.508 | 0 | 4468.112 | 0 | 34992.4639 | 0 | 788.7439 | 0 | 522.6694 | 0 | 508.1102 | 0 | 248.1482 | 737.9189 | 2805.5906 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.834 | 20.137 | 17.0637 | 19.7205 | 20.137 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6783 | 0 | 0 | 20.137 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 11 | 1979 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 8755.4519 | 0 | 6607.851 | 0 | 11401.9813 | 0 | 4875.8473 | 0 | 31641.1315 | 0 | 647.5359 | 0 | 366.9841 | 0 | 554.4776 | 0 | 270.7928 | 737.9189 | 2577.7093 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8618 | 20.1648 | 17.0935 | 19.7503 | 20.1648 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6782 | 0 | 0 | 20.1648 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 12 | 1980 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7424.5272 | 0 | 4414.971 | 0 | 9991.9361 | 0 | 4233.2831 | 0 | 26064.7173 | 0 | 549.1033 | 0 | 245.1969 | 0 | 485.9072 | 0 | 235.1063 | 606.9274 | 2122.2411 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8813 | 20.1843 | 17.1389 | 19.7957 | 20.1843 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6781 | 0 | 0 | 20.1843 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 13 | 1981 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7576.6087 | 0 | 4461.3535 | 0 | 10295.7745 | 0 | 4319.9962 | 0 | 26653.7329 | 0 | 560.351 | 0 | 247.7728 | 0 | 500.6828 | 0 | 239.9222 | 620.0266 | 2168.7553 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9032 | 20.2063 | 17.1631 | 19.82 | 20.2063 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6780 | 0 | 0 | 20.2063 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 14 | 1982 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5260.433 | 0 | 3052.2652 | 0 | 7158.9935 | 0 | 2999.3697 | 0 | 18471.0614 | 0 | 389.0512 | 0 | 169.5155 | 0 | 348.1414 | 0 | 166.5778 | 436.6384 | 1509.9242 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8938 | 20.1969 | 17.1299 | 19.7868 | 20.1969 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6779 | 0 | 0 | 20.1969 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 15 | 1983 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11560.103 | 0 | 7603.7866 | 0 | 21384.7769 | 0 | 6591.2868 | 0 | 47139.9533 | 0 | 854.9623 | 0 | 422.296 | 0 | 1039.9402 | 0 | 366.0642 | 1030.4667 | 3713.7294 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9833 | 20.2863 | 17.2683 | 19.9252 | 20.2863 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6778 | 0 | 0 | 20.2863 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 16 | 1984 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11998.5478 | 0 | 8063.0824 | 0 | 52885.5127 | 0 | 6841.2772 | 0 | 79788.4202 | 0 | 887.3888 | 0 | 447.8042 | 0 | 2571.8188 | 0 | 379.9481 | 1371.0446 | 5658.0045 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1715 | 20.4746 | 17.4732 | 20.13 | 20.4746 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6777 | 0 | 0 | 20.4746 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 17 | 1985 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 7679.1311 | 0 | 4378.452 | 0 | 16302.1268 | 0 | 4871.3078 | 0 | 33231.0177 | 0 | 567.9333 | 0 | 243.1687 | 0 | 792.7713 | 0 | 270.5407 | 681.1559 | 2555.5699 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2113 | 20.5143 | 17.4683 | 20.1251 | 20.5143 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6776 | 0 | 0 | 20.5143 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 18 | 1986 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5329.7545 | 0 | 3038.8951 | 0 | 18506.8994 | 0 | 5235.1688 | 0 | 32110.7178 | 0 | 394.1781 | 0 | 168.7729 | 0 | 899.9892 | 0 | 290.7487 | 484.6686 | 2238.3575 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2459 | 20.5489 | 17.4988 | 20.1556 | 20.5489 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6775 | 0 | 0 | 20.5489 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 19 | 1987 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2127.0747 | 0 | 1212.8057 | 0 | 19482.3983 | 0 | 6503.7631 | 0 | 29326.0417 | 0 | 157.3142 | 0 | 67.3563 | 0 | 947.4277 | 0 | 361.2033 | 183.3881 | 1716.6897 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2657 | 20.5688 | 17.5002 | 20.157 | 20.5688 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6774 | 0 | 0 | 20.5688 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 20 | 1988 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1871 | 20.4901 | 17.3752 | 20.032 | 20.4901 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6773 | 0 | 0 | 20.4901 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 21 | 1989 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.0818 | 20.3848 | 17.1841 | 19.8409 | 20.3848 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6772 | 0 | 0 | 20.3848 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 22 | 1990 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.983 | 20.286 | 17.106 | 19.7629 | 20.286 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6771 | 0 | 0 | 20.286 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 23 | 1991 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8788 | 20.1818 | 16.9841 | 19.641 | 20.1818 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6770 | 0 | 0 | 20.1818 | 0 | 0 | 0
|  | 2004 | 3 | 24 | 24 | 1992 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7628 | 20.0658 | 16.8301 | 19.4869 | 20.0658 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6769 | 0 | 0 | 20.0658 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 1 | 1993 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5965 | 19.8995 | 16.6562 | 19.313 | 19.8995 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6768 | 0 | 0 | 19.8995 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 2 | 1994 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4199 | 19.723 | 16.4463 | 19.1032 | 19.723 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6767 | 0 | 0 | 19.723 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 3 | 1995 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2451 | 19.5481 | 16.2767 | 18.9335 | 19.5481 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6766 | 0 | 0 | 19.5481 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 4 | 1996 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0783 | 19.3813 | 16.1356 | 18.7924 | 19.3813 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6765 | 0 | 0 | 19.3813 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 5 | 1997 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.9131 | 19.2162 | 15.9753 | 18.6321 | 19.2162 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6764 | 0 | 0 | 19.2162 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 6 | 1998 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.7504 | 19.0535 | 15.8204 | 18.4772 | 19.0535 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6763 | 0 | 0 | 19.0535 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 7 | 1999 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0955 | 0 | 90.1422 | 0 | 210.794 | 0 | 90.1422 | 0 | 549.1737 | 0 | 11.6924 | 0 | 5.0063 | 0 | 10.2509 | 0 | 5.0063 | 13.0992 | 45.055 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.5964 | 18.8995 | 15.6887 | 18.3456 | 18.8995 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6762 | 0 | 0 | 18.8995 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 8 | 2000 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12710.1406 | 0 | 7655.5679 | 0 | 2990.0673 | 0 | 1278.6472 | 0 | 24634.423 | 0 | 940.0168 | 0 | 425.1718 | 0 | 145.4068 | 0 | 71.013 | 218.3192 | 1799.9276 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 21.5741 | 18.8771 | 15.7103 | 18.3672 | 20 |  | 416.3425 | 0 | 416.3425 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6761 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 9 | 2001 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5944.727 | 0 | 4106.0415 | 0 | 5387.8883 | 0 | 2304.0312 | 0 | 17742.6881 | 0 | 439.6602 | 0 | 228.0397 | 0 | 262.0126 | 0 | 127.9603 | 353.6771 | 1411.35 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.6608 | 19.9639 | 16.8179 | 19.4747 | 20 |  | 13.3939 | 0 | 13.3939 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6760 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 10 | 2002 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 10425.6787 | 0 | 8965.8169 | 0 | 10431.0326 | 0 | 4460.6389 | 0 | 34283.1672 | 0 | 771.0626 | 0 | 497.9399 | 0 | 507.2604 | 0 | 247.7331 | 729.1862 | 2753.1821 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.7182 | 20.0212 | 16.9039 | 19.5607 | 20.0212 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6759 | 0 | 0 | 20.0212 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 11 | 2003 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 14801.3567 | 0 | 26049.2927 | 0 | 16664.4974 | 0 | 7126.2653 | 0 | 64641.4121 | 0 | 1094.679 | 0 | 1446.715 | 0 | 810.3934 | 0 | 395.7756 | 1502.0362 | 5249.5991 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.8433 | 20.1464 | 17.077 | 19.7338 | 20.1464 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6758 | 0 | 0 | 20.1464 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 12 | 2004 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13099.9984 | 0 | 16022.2622 | 0 | 21799.2119 | 0 | 7469.2973 | 0 | 58390.7698 | 0 | 968.8499 | 0 | 889.8379 | 0 | 1060.0942 | 0 | 414.8268 | 1323.0144 | 4656.6231 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 22.9479 | 20.2509 | 17.1752 | 19.8321 | 20.2509 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6757 | 0 | 0 | 20.2509 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 13 | 2005 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 13591.8142 | 0 | 35671.1027 | 0 | 56402.3911 | 0 | 7749.7186 | 0 | 113415.0266 | 0 | 1005.2237 | 0 | 1981.0871 | 0 | 2742.8444 | 0 | 430.4007 | 2340.3819 | 8499.9378 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2239 | 20.527 | 17.4899 | 20.1467 | 20.527 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6756 | 0 | 0 | 20.527 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 14 | 2006 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 14215.4716 | 0 | 25470.945 | 0 | 66800.0245 | 0 | 8105.3127 | 0 | 114591.7538 | 0 | 1051.3481 | 0 | 1414.5949 | 0 | 3248.4806 | 0 | 450.1495 | 2156.9938 | 8321.567 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4908 | 20.7939 | 17.7193 | 20.3761 | 20.7939 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6755 | 0 | 0 | 20.7939 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 15 | 2007 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12934.0429 | 0 | 10305.5248 | 0 | 34723.5089 | 0 | 7374.6736 | 0 | 65337.7501 | 0 | 956.5762 | 0 | 572.344 | 0 | 1688.6018 | 0 | 409.5716 | 1296.8161 | 4923.9098 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6132 | 20.9162 | 17.8359 | 20.4928 | 20.9162 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6754 | 0 | 0 | 20.9162 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 16 | 2008 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11983.552 | 0 | 8584.7931 | 0 | 72356.0898 | 0 | 6832.727 | 0 | 99757.1619 | 0 | 886.2798 | 0 | 476.7787 | 0 | 3518.6716 | 0 | 379.4732 | 1602.463 | 6863.6663 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8406 | 21.1437 | 18.0847 | 20.7416 | 21.1437 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6753 | 0 | 0 | 21.1437 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 17 | 2009 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 9120.7923 | 0 | 5200.4518 | 0 | 82772.3259 | 0 | 11102.7443 | 0 | 108196.3143 | 0 | 674.5557 | 0 | 288.8206 | 0 | 4025.2125 | 0 | 616.6197 | 1336.1136 | 6941.322 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0916 | 21.3946 | 18.3375 | 20.9943 | 21.3946 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6752 | 0 | 0 | 21.3946 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 18 | 2010 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6182.6513 | 0 | 3525.1959 | 0 | 36938.2397 | 0 | 9131.994 | 0 | 55778.0809 | 0 | 457.2566 | 0 | 195.7809 | 0 | 1796.304 | 0 | 507.169 | 641.8585 | 3598.369 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1788 | 21.4818 | 18.3843 | 21.0412 | 21.4818 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6751 | 0 | 0 | 21.4818 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 19 | 2011 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2032.523 | 0 | 1158.8947 | 0 | 11353.6503 | 0 | 3937.0253 | 0 | 18482.0932 | 0 | 150.3214 | 0 | 64.3622 | 0 | 552.1272 | 0 | 218.6529 | 170.289 | 1155.7527 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.147 | 21.4501 | 18.3164 | 20.9732 | 21.4501 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6750 | 0 | 0 | 21.4501 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 20 | 2012 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0489 | 21.352 | 18.1759 | 20.8328 | 21.352 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6749 | 0 | 0 | 21.352 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 21 | 2013 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9554 | 21.2585 | 18.097 | 20.7539 | 21.2585 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6748 | 0 | 0 | 21.2585 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 22 | 2014 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8546 | 21.1577 | 17.9725 | 20.6294 | 21.1577 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6747 | 0 | 0 | 21.1577 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 23 | 2015 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7465 | 21.0496 | 17.841 | 20.4979 | 21.0496 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6746 | 0 | 0 | 21.0496 | 0 | 0 | 0
|  | 2004 | 3 | 25 | 24 | 2016 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6304 | 20.9334 | 17.6987 | 20.3555 | 20.9334 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6745 | 0 | 0 | 20.9334 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 1 | 2017 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4621 | 20.7652 | 17.5169 | 20.1737 | 20.7652 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6744 | 0 | 0 | 20.7652 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 2 | 2018 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2781 | 20.5812 | 17.2821 | 19.9389 | 20.5812 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6743 | 0 | 0 | 20.5812 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 3 | 2019 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0841 | 20.3871 | 17.0552 | 19.7121 | 20.3871 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6742 | 0 | 0 | 20.3871 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 4 | 2020 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8937 | 20.1967 | 16.8764 | 19.5332 | 20.1967 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6741 | 0 | 0 | 20.1967 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 5 | 2021 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7024 | 20.0054 | 16.6819 | 19.3387 | 20.0054 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6740 | 0 | 0 | 20.0054 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 6 | 2022 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5084 | 19.8114 | 16.4788 | 19.1357 | 19.8114 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6739 | 0 | 0 | 19.8114 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 7 | 2023 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 422.1555 | 0 | 240.7027 | 0 | 562.874 | 0 | 240.7027 | 0 | 1466.4349 | 0 | 31.2218 | 0 | 13.368 | 0 | 27.3725 | 0 | 13.368 | 34.9311 | 120.2615 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3233 | 19.6263 | 16.3082 | 18.965 | 19.6263 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6738 | 0 | 0 | 19.6263 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 8 | 2024 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 49052.1236 | 0 | 29601.72 | 0 | 3554.4981 | 0 | 1520.0156 | 0 | 83728.3573 | 0 | 3627.7979 | 0 | 1644.0082 | 0 | 172.855 | 0 | 84.418 | 484.6686 | 6013.7478 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.4347 | 19.7368 | 16.5306 | 19.1884 | 20 |  | 97.5654 | 0 | 97.5654 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6737 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 9 | 2025 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 47429.0655 | 0 | 42394.6167 | 0 | 7890.0459 | 0 | 3374.0328 | 0 | 101087.7609 | 0 | 3507.7598 | 0 | 2354.4949 | 0 | 383.6924 | 0 | 187.3857 | 1126.5271 | 7559.8598 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8838 | 20.1859 | 17.065 | 19.7228 | 20.1859 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6736 | 0 | 0 | 20.1859 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 10 | 2026 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 35777.0617 | 0 | 51913.3872 | 0 | 10996.899 | 0 | 4702.6213 | 0 | 103389.9691 | 0 | 2646.0006 | 0 | 2883.1445 | 0 | 534.7784 | 0 | 261.1723 | 1781.4847 | 8106.5806 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0909 | 20.3929 | 17.3193 | 19.9771 | 20.3929 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6735 | 0 | 0 | 20.3929 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 11 | 2027 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11328.5598 | 0 | 11141.683 | 0 | 14259.6817 | 0 | 6097.8902 | 0 | 42827.8147 | 0 | 837.8378 | 0 | 618.7822 | 0 | 693.4473 | 0 | 338.6621 | 1008.6347 | 3497.3643 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.116 | 20.4181 | 17.3263 | 19.9841 | 20.4181 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6734 | 0 | 0 | 20.4181 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 12 | 2028 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5101.8616 | 0 | 2993.637 | 0 | 6845.1291 | 0 | 2908.9562 | 0 | 17849.5839 | 0 | 377.3236 | 0 | 166.2594 | 0 | 332.8782 | 0 | 161.5564 | 423.5393 | 1461.5568 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0479 | 20.35 | 17.188 | 19.8458 | 20.35 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6733 | 0 | 0 | 20.35 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 13 | 2029 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11693.744 | 0 | 8364.6183 | 0 | 17920.5036 | 0 | 6667.4856 | 0 | 44646.3514 | 0 | 864.8461 | 0 | 464.5508 | 0 | 871.4728 | 0 | 370.2961 | 1017.3675 | 3588.5334 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0795 | 20.3815 | 17.2939 | 19.9517 | 20.3815 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6732 | 0 | 0 | 20.3815 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 14 | 2030 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13172.0425 | 0 | 29790.7873 | 0 | 79231.1042 | 0 | 7510.3751 | 0 | 129704.3091 | 0 | 974.1782 | 0 | 1654.5086 | 0 | 3853.0031 | 0 | 417.1081 | 2436.4424 | 9335.2404 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3708 | 20.6729 | 17.6336 | 20.2914 | 20.6729 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6731 | 0 | 0 | 20.6729 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 15 | 2031 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13786.9032 | 0 | 12840.0098 | 0 | 48412.8572 | 0 | 7860.9536 | 0 | 82900.7236 | 0 | 1019.6521 | 0 | 713.1032 | 0 | 2354.3139 | 0 | 436.5784 | 1541.3336 | 6064.9812 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5186 | 20.8207 | 17.7543 | 20.4121 | 20.8207 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6730 | 0 | 0 | 20.8207 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 16 | 2032 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11318.2243 | 0 | 6985.4568 | 0 | 33426.281 | 0 | 6453.3735 | 0 | 58183.3357 | 0 | 837.0735 | 0 | 387.9554 | 0 | 1625.5177 | 0 | 358.4048 | 1117.7944 | 4326.7458 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5963 | 20.8984 | 17.8375 | 20.4953 | 20.8984 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6729 | 0 | 0 | 20.8984 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 17 | 2033 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8882.4672 | 0 | 5064.5646 | 0 | 29213.4237 | 0 | 6556.763 | 0 | 49717.2184 | 0 | 656.9297 | 0 | 281.2737 | 0 | 1420.6468 | 0 | 364.1468 | 860.1777 | 3583.1747 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6467 | 20.9488 | 17.8801 | 20.5379 | 20.9488 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6728 | 0 | 0 | 20.9488 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 18 | 2034 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6235.8412 | 0 | 3555.5235 | 0 | 33902.7284 | 0 | 8626.1659 | 0 | 52320.2589 | 0 | 461.1905 | 0 | 197.4652 | 0 | 1648.6873 | 0 | 479.0765 | 628.7593 | 3415.1788 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7274 | 21.0304 | 17.9462 | 20.603 | 21.0304 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6727 | 0 | 0 | 21.0304 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 19 | 2035 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1281.6 | 0 | 730.7368 | 0 | 2293.9167 | 0 | 920.9002 | 0 | 5227.1537 | 0 | 94.7846 | 0 | 40.5834 | 0 | 111.553 | 0 | 51.1446 | 109.1596 | 407.2252 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.665 | 20.968 | 17.8569 | 20.5137 | 20.968 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6726 | 0 | 0 | 20.968 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 20 | 2036 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5697 | 20.8727 | 17.705 | 20.3618 | 20.8727 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6725 | 0 | 0 | 20.8727 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 21 | 2037 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4625 | 20.7656 | 17.5595 | 20.2163 | 20.7656 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6724 | 0 | 0 | 20.7656 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 22 | 2038 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3564 | 20.6595 | 17.4565 | 20.1134 | 20.6595 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6723 | 0 | 0 | 20.6595 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 23 | 2039 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2413 | 20.5444 | 17.3122 | 19.9691 | 20.5444 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6722 | 0 | 0 | 20.5444 | 0 | 0 | 0
|  | 2004 | 3 | 26 | 24 | 2040 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1291 | 20.4322 | 17.2093 | 19.8661 | 20.4322 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6721 | 0 | 0 | 20.4322 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 1 | 2041 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9693 | 20.2724 | 17.0506 | 19.7074 | 20.2724 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6720 | 0 | 0 | 20.2724 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 2 | 2042 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7956 | 20.0986 | 16.8316 | 19.4884 | 20.0986 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6719 | 0 | 0 | 20.0986 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 3 | 2043 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.6116 | 19.9147 | 16.6146 | 19.2714 | 19.9147 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6718 | 0 | 0 | 19.9147 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 4 | 2044 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.423 | 19.7261 | 16.4108 | 19.0677 | 19.7261 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6717 | 0 | 0 | 19.7261 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 5 | 2045 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.2299 | 19.533 | 16.2027 | 18.8595 | 19.533 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6716 | 0 | 0 | 19.533 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 6 | 2046 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.0368 | 19.3399 | 16.0094 | 18.6662 | 19.3399 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6715 | 0 | 0 | 19.3399 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 7 | 2047 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 580.9329 | 0 | 331.2337 | 0 | 774.5772 | 0 | 331.2337 | 0 | 2017.9773 | 0 | 42.9646 | 0 | 18.3959 | 0 | 37.6676 | 0 | 18.3959 | 48.0302 | 165.4543 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 21.8578 | 19.1609 | 15.8565 | 18.5134 | 19.1609 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6714 | 0 | 0 | 19.1609 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 8 | 2048 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 40495.6467 | 0 | 24271.7988 | 0 | 3839.1635 | 0 | 1641.7475 | 0 | 70248.3565 | 0 | 2994.9778 | 0 | 1347.9972 | 0 | 186.6983 | 0 | 91.1787 | 471.5695 | 5092.4215 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 21.9295 | 19.2316 | 16.0221 | 18.6799 | 20 |  | 284.8113 | 0 | 284.8113 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6713 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 9 | 2049 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 49769.9953 | 0 | 44314.3327 | 0 | 7879.007 | 0 | 3369.3122 | 0 | 105332.6472 | 0 | 3680.8903 | 0 | 2461.1113 | 0 | 383.1556 | 0 | 187.1235 | 1174.5573 | 7886.838 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8844 | 20.1864 | 17.0242 | 19.682 | 20.1864 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6712 | 0 | 0 | 20.1864 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 10 | 2050 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 36641.5812 | 0 | 52928.4455 | 0 | 11012.3998 | 0 | 4709.2499 | 0 | 105291.6764 | 0 | 2709.9388 | 0 | 2939.5184 | 0 | 535.5322 | 0 | 261.5404 | 1829.515 | 8276.0448 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0987 | 20.4008 | 17.3329 | 19.9907 | 20.4008 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6711 | 0 | 0 | 20.4008 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 11 | 2051 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 16354.7437 | 0 | 45883.3167 | 0 | 14983.0434 | 0 | 6407.2225 | 0 | 83628.3262 | 0 | 1209.5645 | 0 | 2548.2489 | 0 | 728.6244 | 0 | 355.8417 | 2074.0325 | 6916.3119 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2498 | 20.5519 | 17.4816 | 20.1394 | 20.5519 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6710 | 0 | 0 | 20.5519 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 12 | 2052 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14273.8792 | 0 | 24063.7947 | 0 | 27005.0813 | 0 | 8138.6153 | 0 | 73481.3705 | 0 | 1055.6678 | 0 | 1336.4452 | 0 | 1313.2552 | 0 | 451.9991 | 1672.3251 | 5829.6925 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3752 | 20.6772 | 17.6236 | 20.2814 | 20.6772 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6709 | 0 | 0 | 20.6772 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 13 | 2053 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13003.9054 | 0 | 12768.9357 | 0 | 24692.7334 | 0 | 7414.5075 | 0 | 57880.082 | 0 | 961.7431 | 0 | 709.1559 | 0 | 1200.8059 | 0 | 411.7839 | 1248.7859 | 4532.2747 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4572 | 20.7593 | 17.7143 | 20.3721 | 20.7593 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6708 | 0 | 0 | 20.7593 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 14 | 2054 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14015.7559 | 0 | 13190.5154 | 0 | 33144.4919 | 0 | 7991.4398 | 0 | 68342.203 | 0 | 1036.5776 | 0 | 732.5695 | 0 | 1611.8143 | 0 | 443.8253 | 1419.0749 | 5243.8615 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5737 | 20.8757 | 17.8456 | 20.5034 | 20.8757 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6707 | 0 | 0 | 20.8757 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 15 | 2055 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10314.6799 | 0 | 6302.9052 | 0 | 16325.9213 | 0 | 5881.1771 | 0 | 38824.6835 | 0 | 762.8533 | 0 | 350.0482 | 0 | 793.9284 | 0 | 326.6264 | 873.2768 | 3106.7331 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6037 | 20.9058 | 17.8735 | 20.5313 | 20.9058 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6706 | 0 | 0 | 20.9058 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 16 | 2056 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 7586.6427 | 0 | 4342.8127 | 0 | 10749.8407 | 0 | 4325.7173 | 0 | 27005.0135 | 0 | 561.0931 | 0 | 241.1894 | 0 | 522.764 | 0 | 240.2399 | 620.0266 | 2185.3129 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6008 | 20.9028 | 17.876 | 20.5338 | 20.9028 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6705 | 0 | 0 | 20.9028 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 17 | 2057 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9588.7809 | 0 | 5467.2874 | 0 | 42656.246 | 0 | 8103.0245 | 0 | 65815.3387 | 0 | 709.1672 | 0 | 303.64 | 0 | 2074.3703 | 0 | 450.0225 | 1008.6347 | 4545.8347 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.7073 | 21.0093 | 17.9751 | 20.6329 | 21.0093 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6704 | 0 | 0 | 21.0093 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 18 | 2058 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 4727.3187 | 0 | 2695.401 | 0 | 8777.2156 | 0 | 3192.5733 | 0 | 19392.5086 | 0 | 349.6231 | 0 | 149.6961 | 0 | 426.8354 | 0 | 177.3078 | 401.7073 | 1505.1698 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7062 | 21.0093 | 17.9657 | 20.6225 | 21.0093 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6703 | 0 | 0 | 21.0093 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 19 | 2059 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2153.6517 | 0 | 1227.9593 | 0 | 8556.8401 | 0 | 3096.2763 | 0 | 15034.7273 | 0 | 159.2798 | 0 | 68.1979 | 0 | 416.1185 | 0 | 171.9597 | 183.3881 | 998.9441 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.6738 | 20.9769 | 17.8719 | 20.5287 | 20.9769 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6702 | 0 | 0 | 20.9769 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 20 | 2060 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.5821 | 20.8852 | 17.7289 | 20.3857 | 20.8852 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6701 | 0 | 0 | 20.8852 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 21 | 2061 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.4721 | 20.7752 | 17.5599 | 20.2168 | 20.7752 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6700 | 0 | 0 | 20.7752 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 22 | 2062 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.3541 | 20.6571 | 17.4157 | 20.0726 | 20.6571 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6699 | 0 | 0 | 20.6571 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 23 | 2063 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.2408 | 20.5438 | 17.3177 | 19.9745 | 20.5438 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6698 | 0 | 0 | 20.5438 | 0 | 0 | 0
|  | 2004 | 3 | 27 | 24 | 2064 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.1377 | 20.4408 | 17.2473 | 19.9041 | 20.4408 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6697 | 0 | 0 | 20.4408 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 1 | 2065 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9934 | 20.2964 | 17.1243 | 19.7811 | 20.2964 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6696 | 0 | 0 | 20.2964 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 2 | 2066 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.854 | 20.1571 | 17.0009 | 19.6578 | 20.1571 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6695 | 0 | 0 | 20.1571 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 3 | 2067 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.7197 | 20.0228 | 16.8825 | 19.5393 | 20.0228 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6694 | 0 | 0 | 20.0228 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 4 | 2068 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.5913 | 19.8943 | 16.7726 | 19.4295 | 19.8943 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6693 | 0 | 0 | 19.8943 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 5 | 2069 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.4659 | 19.7689 | 16.6569 | 19.3137 | 19.7689 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6692 | 0 | 0 | 19.7689 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 6 | 2070 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.3417 | 19.6447 | 16.5363 | 19.1932 | 19.6447 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6691 | 0 | 0 | 19.6447 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 7 | 2071 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 158.0957 | 0 | 90.1423 | 0 | 210.7943 | 0 | 90.1423 | 0 | 549.1745 | 0 | 11.6924 | 0 | 5.0063 | 0 | 10.2509 | 0 | 5.0063 | 13.0992 | 45.0551 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.223 | 19.526 | 16.4301 | 19.087 | 19.526 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6690 | 0 | 0 | 19.526 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 8 | 2072 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 4413.7865 | 0 | 2593.656 | 0 | 2173.7887 | 0 | 929.5807 | 0 | 10110.8119 | 0 | 326.4349 | 0 | 144.0454 | 0 | 105.7112 | 0 | 51.6267 | 144.0907 | 771.9089 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.1604 | 19.4625 | 16.3947 | 19.0525 | 20 |  | 199.2311 | 0 | 199.2311 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6689 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 9 | 2073 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8023.288 | 0 | 5715.3764 | 0 | 6436.6839 | 0 | 2752.5293 | 0 | 22927.8776 | 0 | 593.3865 | 0 | 317.4182 | 0 | 313.0155 | 0 | 152.8688 | 436.6384 | 1813.3275 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.6751 | 19.9772 | 16.9213 | 19.5791 | 20 |  | 8.4614 | 0 | 8.4614 | 20 | 24 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6688 | 0 | 0 | 20 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 10 | 2074 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10383.121 | 0 | 8559.8316 | 0 | 10681.8766 | 0 | 4567.9078 | 0 | 34192.737 | 0 | 767.9151 | 0 | 475.3924 | 0 | 519.4589 | 0 | 253.6906 | 737.9189 | 2754.3759 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.7181 | 20.0202 | 16.9991 | 19.6569 | 20.0202 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6687 | 0 | 0 | 20.0202 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 11 | 2075 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13127.8375 | 0 | 16108.6683 | 0 | 15840.57 | 0 | 6773.9279 | 0 | 51851.0038 | 0 | 970.9089 | 0 | 894.6366 | 0 | 770.3258 | 0 | 376.2076 | 1200.7556 | 4212.8346 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8015 | 20.1036 | 17.1223 | 19.7801 | 20.1036 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6686 | 0 | 0 | 20.1036 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 12 | 2076 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14305.9265 | 0 | 30230.0809 | 0 | 30060.4093 | 0 | 8156.8879 | 0 | 82753.3047 | 0 | 1058.038 | 0 | 1678.9059 | 0 | 1461.8356 | 0 | 453.0139 | 1903.7435 | 6555.5369 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9839 | 20.286 | 17.3362 | 19.9939 | 20.286 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6685 | 0 | 0 | 20.286 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 13 | 2077 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13857.3011 | 0 | 35251.116 | 0 | 56075.883 | 0 | 7901.0927 | 0 | 113085.3927 | 0 | 1024.8585 | 0 | 1957.7621 | 0 | 2726.9663 | 0 | 438.8077 | 2388.4121 | 8536.8067 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.2628 | 20.5649 | 17.6466 | 20.3044 | 20.5649 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6684 | 0 | 0 | 20.5649 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 14 | 2078 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12091.7929 | 0 | 35094.1201 | 0 | 94903.0763 | 0 | 6894.4433 | 0 | 148983.4326 | 0 | 894.2851 | 0 | 1949.0429 | 0 | 4615.13 | 0 | 382.9008 | 2921.111 | 10762.4698 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.6403 | 20.9424 | 18.0086 | 20.6664 | 20.9424 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6683 | 0 | 0 | 20.9424 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 15 | 2079 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11867.5961 | 0 | 20520.2715 | 0 | 100723.712 | 0 | 6766.6118 | 0 | 139878.1914 | 0 | 877.7039 | 0 | 1139.6465 | 0 | 4898.1871 | 0 | 375.8013 | 2436.4424 | 9727.7812 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9889 | 21.291 | 18.3523 | 21.0101 | 21.291 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6682 | 0 | 0 | 21.291 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 16 | 2080 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11227.4482 | 0 | 8422.9734 | 0 | 96240.4268 | 0 | 6401.6152 | 0 | 122292.4636 | 0 | 830.3598 | 0 | 467.7917 | 0 | 4680.1653 | 0 | 355.5303 | 1929.9418 | 8263.7889 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.2812 | 21.5833 | 18.6293 | 21.2871 | 21.5833 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6681 | 0 | 0 | 21.5833 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 17 | 2081 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9509.6589 | 0 | 5422.1739 | 0 | 80478.5201 | 0 | 11563.3953 | 0 | 106973.7483 | 0 | 703.3155 | 0 | 301.1345 | 0 | 3913.6649 | 0 | 642.2031 | 1371.0446 | 6931.3626 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.5218 | 21.8239 | 18.8473 | 21.5051 | 21.8239 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6680 | 0 | 0 | 21.8239 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 18 | 2082 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6588.008 | 0 | 3756.3203 | 0 | 39825.6194 | 0 | 10081.1145 | 0 | 60251.0622 | 0 | 487.236 | 0 | 208.617 | 0 | 1936.7171 | 0 | 559.8808 | 702.9879 | 3895.4388 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6478 | 21.9509 | 18.9404 | 21.5972 | 21.9509 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6679 | 0 | 0 | 21.9509 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 19 | 2083 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2058.5346 | 0 | 1173.7259 | 0 | 6440.4552 | 0 | 2401.7162 | 0 | 12074.4319 | 0 | 152.2451 | 0 | 65.1859 | 0 | 313.1989 | 0 | 133.3855 | 170.289 | 834.3045 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.6217 | 21.9247 | 18.8685 | 21.5254 | 21.9247 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6678 | 0 | 0 | 21.9247 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 20 | 2084 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.5354 | 21.8385 | 18.7013 | 21.3582 | 21.8385 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6677 | 0 | 0 | 21.8385 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 21 | 2085 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.4299 | 21.733 | 18.5338 | 21.1906 | 21.733 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6676 | 0 | 0 | 21.733 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 22 | 2086 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.3154 | 21.6185 | 18.3901 | 21.0469 | 21.6185 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6675 | 0 | 0 | 21.6185 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 23 | 2087 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.1993 | 21.5023 | 18.2685 | 20.9253 | 21.5023 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6674 | 0 | 0 | 21.5023 | 0 | 0 | 0
|  | 2004 | 3 | 28 | 24 | 2088 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0724 | 21.3754 | 18.1068 | 20.7636 | 21.3754 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6673 | 0 | 0 | 21.3754 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 1 | 2089 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.8934 | 21.1965 | 17.9147 | 20.5715 | 21.1965 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6672 | 0 | 0 | 21.1965 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 2 | 2090 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.7144 | 21.0175 | 17.7351 | 20.3919 | 21.0175 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6671 | 0 | 0 | 21.0175 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 3 | 2091 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.549 | 20.852 | 17.6131 | 20.2699 | 20.852 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6670 | 0 | 0 | 20.852 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 4 | 2092 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4016 | 20.7046 | 17.5234 | 20.1802 | 20.7046 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6669 | 0 | 0 | 20.7046 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 5 | 2093 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.2602 | 20.5632 | 17.4009 | 20.0578 | 20.5632 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6668 | 0 | 0 | 20.5632 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 6 | 2094 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1237 | 20.4268 | 17.2804 | 19.9373 | 20.4268 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6667 | 0 | 0 | 20.4268 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 7 | 2095 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 316.4473 | 0 | 180.4305 | 0 | 421.9297 | 0 | 180.4305 | 0 | 1099.2379 | 0 | 23.4038 | 0 | 10.0207 | 0 | 20.5184 | 0 | 10.0207 | 26.1983 | 90.1619 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.9882 | 20.2913 | 17.1371 | 19.7939 | 20.2913 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6666 | 0 | 0 | 20.2913 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 8 | 2096 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12544.9934 | 0 | 7390.5053 | 0 | 3493.6517 | 0 | 1493.9958 | 0 | 24923.1462 | 0 | 927.8029 | 0 | 410.4509 | 0 | 169.896 | 0 | 82.9729 | 244.5175 | 1835.6402 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9574 | 20.2595 | 17.1539 | 19.8117 | 20.2595 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6665 | 0 | 0 | 20.2595 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 9 | 2097 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10404.4504 | 0 | 7682.6904 | 0 | 7215.859 | 0 | 3085.7292 | 0 | 28388.729 | 0 | 769.4925 | 0 | 426.6781 | 0 | 350.9067 | 0 | 171.374 | 510.8669 | 2229.3183 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.9515 | 20.2536 | 17.2016 | 19.8594 | 20.2536 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6664 | 0 | 0 | 20.2536 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 10 | 2098 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14605.5506 | 0 | 13977.62 | 0 | 12609.4742 | 0 | 5392.2094 | 0 | 46584.8541 | 0 | 1080.1976 | 0 | 776.2833 | 0 | 613.1979 | 0 | 299.4703 | 934.4062 | 3703.5553 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0147 | 20.3167 | 17.32 | 19.9778 | 20.3167 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6663 | 0 | 0 | 20.3167 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 11 | 2099 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 15821.78 | 0 | 28174.6718 | 0 | 17280.9839 | 0 | 7389.8944 | 0 | 68667.3302 | 0 | 1170.1475 | 0 | 1564.7534 | 0 | 840.373 | 0 | 410.4169 | 1637.3941 | 5623.085 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.1605 | 20.4626 | 17.5277 | 20.1855 | 20.4626 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6662 | 0 | 0 | 20.4626 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 12 | 2100 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 13721.3894 | 0 | 36583.7943 | 0 | 32523.1427 | 0 | 7823.5992 | 0 | 90651.9256 | 0 | 1014.8068 | 0 | 2031.7758 | 0 | 1581.5982 | 0 | 434.5039 | 2156.9938 | 7219.6784 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3771 | 20.6792 | 17.7685 | 20.4263 | 20.6792 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6661 | 0 | 0 | 20.6792 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 13 | 2101 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11773.1831 | 0 | 8223.7344 | 0 | 17776.7044 | 0 | 6712.7798 | 0 | 44486.4016 | 0 | 870.7213 | 0 | 456.7264 | 0 | 864.4799 | 0 | 372.8116 | 1017.3675 | 3582.1067 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.4608 | 20.7629 | 17.8595 | 20.5173 | 20.7629 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6660 | 0 | 0 | 20.7629 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 14 | 2102 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14462.82 | 0 | 13821.5346 | 0 | 34932.6845 | 0 | 8246.3447 | 0 | 71463.3837 | 0 | 1069.6415 | 0 | 767.6147 | 0 | 1698.774 | 0 | 457.9821 | 1493.3034 | 5487.3158 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.625 | 20.9271 | 18.0319 | 20.6897 | 20.9271 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6659 | 0 | 0 | 20.9271 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 15 | 2103 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 14153.17 | 0 | 13068.2017 | 0 | 50094.7801 | 0 | 8069.7899 | 0 | 85385.9417 | 0 | 1046.7404 | 0 | 725.7764 | 0 | 2436.1057 | 0 | 448.1767 | 1611.1958 | 6267.995 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8325 | 21.1345 | 18.2515 | 20.9093 | 21.1345 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6658 | 0 | 0 | 21.1345 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 16 | 2104 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9595.5341 | 0 | 5557.5528 | 0 | 16586.8685 | 0 | 5471.1379 | 0 | 37211.0933 | 0 | 709.6667 | 0 | 308.6531 | 0 | 806.6183 | 0 | 303.8538 | 825.2466 | 2954.0385 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8983 | 21.2004 | 18.3104 | 20.9682 | 21.2004 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6657 | 0 | 0 | 21.2004 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 17 | 2105 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 8705.859 | 0 | 4963.867 | 0 | 25205.4227 | 0 | 6227.5537 | 0 | 45102.7024 | 0 | 643.8681 | 0 | 275.6812 | 0 | 1225.738 | 0 | 345.8633 | 812.1475 | 3303.2981 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.9841 | 21.2862 | 18.3881 | 21.0459 | 21.2862 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6656 | 0 | 0 | 21.2862 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 18 | 2106 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3780.0287 | 0 | 2155.2795 | 0 | 5658.6071 | 0 | 2283.0584 | 0 | 13876.9737 | 0 | 279.5634 | 0 | 119.699 | 0 | 275.1777 | 0 | 126.7956 | 314.3797 | 1115.6154 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.0074 | 21.3104 | 18.397 | 21.0538 | 21.3104 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6655 | 0 | 0 | 21.3104 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 19 | 2107 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1598.6934 | 0 | 911.5357 | 0 | 2768.9225 | 0 | 1125.6459 | 0 | 6404.7975 | 0 | 118.2362 | 0 | 50.6245 | 0 | 134.6525 | 0 | 62.5157 | 135.3579 | 501.3868 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9949 | 21.298 | 18.3372 | 20.994 | 21.298 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6654 | 0 | 0 | 21.298 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 20 | 2108 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.9512 | 21.2543 | 18.253 | 20.9098 | 21.2543 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6653 | 0 | 0 | 21.2543 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 21 | 2109 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8961 | 21.1991 | 18.161 | 20.8178 | 21.1991 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6652 | 0 | 0 | 21.1991 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 22 | 2110 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.8314 | 21.1345 | 18.0656 | 20.7225 | 21.1345 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6651 | 0 | 0 | 21.1345 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 23 | 2111 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7683 | 21.0713 | 18.0073 | 20.6642 | 21.0713 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6650 | 0 | 0 | 21.0713 | 0 | 0 | 0
|  | 2004 | 3 | 29 | 24 | 2112 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 23.7012 | 21.0043 | 17.9274 | 20.5843 | 21.0043 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6649 | 0 | 0 | 21.0043 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 1 | 2113 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.5788 | 20.8819 | 17.7813 | 20.4381 | 20.8819 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6648 | 0 | 0 | 20.8819 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 2 | 2114 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.4512 | 20.7542 | 17.6367 | 20.2935 | 20.7542 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6647 | 0 | 0 | 20.7542 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 3 | 2115 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.3221 | 20.6251 | 17.5025 | 20.1593 | 20.6251 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6646 | 0 | 0 | 20.6251 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 4 | 2116 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.1923 | 20.4954 | 17.3707 | 20.0275 | 20.4954 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6645 | 0 | 0 | 20.4954 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 5 | 2117 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 23.0584 | 20.3615 | 17.223 | 19.8798 | 20.3615 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6644 | 0 | 0 | 20.3615 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 6 | 2118 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.923 | 20.2261 | 17.0827 | 19.7395 | 20.2261 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6643 | 0 | 0 | 20.2261 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 7 | 2119 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 580.9358 | 0 | 331.2353 | 0 | 774.5811 | 0 | 331.2353 | 0 | 2017.9876 | 0 | 42.9649 | 0 | 18.396 | 0 | 37.6678 | 0 | 18.396 | 48.0302 | 165.4549 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 22.8031 | 20.1061 | 16.993 | 19.6499 | 20.1061 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6642 | 0 | 0 | 20.1061 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 8 | 2120 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 31136.9934 | 0 | 18309.9616 | 0 | 4876.7393 | 0 | 2085.4477 | 0 | 56409.1421 | 0 | 2302.8304 | 0 | 1016.8912 | 0 | 237.1555 | 0 | 115.8207 | 471.5695 | 4144.2673 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 22.8744 | 20.1764 | 17.1072 | 19.765 | 20.1764 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6641 | 0 | 0 | 20.1764 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 9 | 2121 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 43630.8311 | 0 | 37551.0348 | 0 | 9093.0128 | 0 | 3888.4594 | 0 | 94163.3381 | 0 | 3226.8499 | 0 | 2085.494 | 0 | 442.1926 | 0 | 215.9557 | 1139.6263 | 7110.1184 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.0808 | 20.3829 | 17.404 | 20.0618 | 20.3829 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6640 | 0 | 0 | 20.3829 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 10 | 2122 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 35319.5905 | 0 | 48785.7893 | 0 | 11792.1981 | 0 | 5042.7163 | 0 | 100940.294 | 0 | 2612.167 | 0 | 2709.4452 | 0 | 573.4538 | 0 | 280.0603 | 1807.6831 | 7982.8093 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.3237 | 20.6258 | 17.7023 | 20.3601 | 20.6258 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6639 | 0 | 0 | 20.6258 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 11 | 2123 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 17216.014 | 0 | 53788.0029 | 0 | 13916.9754 | 0 | 5951.3382 | 0 | 90872.3305 | 0 | 1273.2623 | 0 | 2987.2561 | 0 | 676.7816 | 0 | 330.523 | 2388.4121 | 7656.2351 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.5474 | 20.8495 | 17.9574 | 20.6152 | 20.8495 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6638 | 0 | 0 | 20.8495 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 12 | 2124 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11813.8583 | 0 | 50469.3689 | 0 | 37255.23 | 0 | 6735.9718 | 0 | 106274.4289 | 0 | 873.7296 | 0 | 2802.9472 | 0 | 1811.7193 | 0 | 374.0997 | 2755.1884 | 8617.6841 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 23.8241 | 21.1262 | 18.2651 | 20.9229 | 21.1262 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6637 | 0 | 0 | 21.1262 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 13 | 2125 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12362.6671 | 0 | 43957.5167 | 0 | 67318.7215 | 0 | 7048.8891 | 0 | 130687.7944 | 0 | 914.3184 | 0 | 2441.2946 | 0 | 3273.7048 | 0 | 391.4783 | 2934.2102 | 9955.0062 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.1771 | 21.4792 | 18.6412 | 21.299 | 21.4792 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6636 | 0 | 0 | 21.4792 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 14 | 2126 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12285.3441 | 0 | 33819.6949 | 0 | 92006.0031 | 0 | 7004.8014 | 0 | 145115.8435 | 0 | 908.5997 | 0 | 1878.2644 | 0 | 4474.2456 | 0 | 389.0298 | 2899.2791 | 10549.4186 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.57 | 21.8721 | 19.032 | 21.6898 | 21.8721 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6635 | 0 | 0 | 21.8721 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 15 | 2127 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 11536.8783 | 0 | 21325.0728 | 0 | 108623.3327 | 0 | 6578.0446 | 0 | 148063.3283 | 0 | 853.2447 | 0 | 1184.3432 | 0 | 5282.3451 | 0 | 365.3288 | 2619.8305 | 10305.0923 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 24.9709 | 22.2729 | 19.4359 | 22.0937 | 22.2729 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6634 | 0 | 0 | 22.2729 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 16 | 2128 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 10635.7377 | 0 | 8003.2728 | 0 | 107911.5042 | 0 | 6064.2364 | 0 | 132614.751 | 0 | 786.5981 | 0 | 444.4825 | 0 | 5247.729 | 0 | 336.7931 | 2122.0627 | 8937.6654 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 25.3245 | 22.6266 | 19.7843 | 22.4421 | 22.6266 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6633 | 0 | 0 | 22.6266 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 17 | 2129 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 9245.4779 | 0 | 5271.5444 | 0 | 93028.2951 | 0 | 12962.3188 | 0 | 120507.6363 | 0 | 683.7772 | 0 | 292.7689 | 0 | 4523.9595 | 0 | 719.896 | 1515.1353 | 7735.5369 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 25.6357 | 22.9378 | 20.0739 | 22.7317 | 22.9378 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6632 | 0 | 0 | 22.9378 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 18 | 2130 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6968.7494 | 0 | 3973.4097 | 0 | 54020.3543 | 0 | 13339.8963 | 0 | 78302.4097 | 0 | 515.3949 | 0 | 220.6736 | 0 | 2627.0061 | 0 | 740.8657 | 812.1475 | 4916.0878 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.8516 | 23.1547 | 20.2693 | 22.9262 | 23.1547 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6631 | 0 | 0 | 23.1547 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 19 | 2131 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 2527.6738 | 0 | 1441.2175 | 0 | 9856.8092 | 0 | 3644.3851 | 0 | 17470.0855 | 0 | 186.9417 | 0 | 80.0417 | 0 | 479.3359 | 0 | 202.4004 | 218.3192 | 1167.039 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.8786 | 23.1817 | 20.2485 | 22.9053 | 23.1817 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6630 | 0 | 0 | 23.1817 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 20 | 2132 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.8423 | 23.1454 | 20.171 | 22.8279 | 23.1454 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6629 | 0 | 0 | 23.1454 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 21 | 2133 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.7991 | 23.1021 | 20.1053 | 22.7622 | 23.1021 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6628 | 0 | 0 | 23.1021 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 22 | 2134 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.7462 | 23.0492 | 20.0214 | 22.6783 | 23.0492 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6627 | 0 | 0 | 23.0492 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 23 | 2135 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.6874 | 22.9905 | 19.9436 | 22.6005 | 22.9905 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6626 | 0 | 0 | 22.9905 | 0 | 0 | 0
|  | 2004 | 3 | 30 | 24 | 2136 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.6246 | 22.9277 | 19.8679 | 22.5248 | 22.9277 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6625 | 0 | 0 | 22.9277 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 1 | 2137 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.5056 | 22.8087 | 19.7221 | 22.3789 | 22.8087 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6624 | 0 | 0 | 22.8087 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 2 | 2138 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.3795 | 22.6825 | 19.573 | 22.2299 | 22.6825 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6623 | 0 | 0 | 22.6825 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 3 | 2139 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.2464 | 22.5494 | 19.4172 | 22.074 | 22.5494 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6622 | 0 | 0 | 22.5494 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 4 | 2140 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.1118 | 22.4149 | 19.2777 | 21.9346 | 22.4149 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6621 | 0 | 0 | 22.4149 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 5 | 2141 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.9722 | 22.2752 | 19.1215 | 21.7783 | 22.2752 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6620 | 0 | 0 | 22.2752 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 6 | 2142 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.8284 | 22.1314 | 18.9642 | 21.621 | 22.1314 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6619 | 0 | 0 | 22.1314 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 7 | 2143 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1005.5985 | 0 | 573.3676 | 0 | 1340.798 | 0 | 573.3676 | 0 | 3493.1316 | 0 | 74.3721 | 0 | 31.8435 | 0 | 65.2029 | 0 | 31.8435 | 82.9613 | 286.2232 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 24.7089 | 22.012 | 18.8899 | 21.5467 | 22.012 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6618 | 0 | 0 | 22.012 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 8 | 2144 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 47644.5833 | 0 | 27902.8767 | 0 | 4241.6442 | 0 | 1813.861 | 0 | 81602.9652 | 0 | 3523.699 | 0 | 1549.6586 | 0 | 206.2709 | 0 | 100.7375 | 620.0266 | 6000.3925 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 24.891 | 22.194 | 19.1565 | 21.8134 | 22.194 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6617 | 0 | 0 | 22.194 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 9 | 2145 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 49088.319 | 0 | 42410.5116 | 0 | 8570.2978 | 0 | 3664.93 | 0 | 103734.0585 | 0 | 3630.4749 | 0 | 2355.3777 | 0 | 416.773 | 0 | 203.5414 | 1235.6867 | 7841.8536 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.1514 | 22.4544 | 19.4606 | 22.1174 | 22.4544 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6616 | 0 | 0 | 22.4544 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 10 | 2146 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 36839.839 | 0 | 50992.4248 | 0 | 11643.002 | 0 | 4978.9153 | 0 | 104454.1812 | 0 | 2724.6015 | 0 | 2831.9965 | 0 | 566.1984 | 0 | 276.517 | 1881.9116 | 8281.2249 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.427 | 22.7301 | 19.7755 | 22.4323 | 22.7301 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6615 | 0 | 0 | 22.7301 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 11 | 2147 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 17164.9255 | 0 | 47817.8394 | 0 | 14824.8664 | 0 | 6339.581 | 0 | 86147.2123 | 0 | 1269.4839 | 0 | 2655.6876 | 0 | 720.9322 | 0 | 352.0851 | 2231.2223 | 7229.4111 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.6679 | 22.971 | 20.0736 | 22.7305 | 22.971 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6614 | 0 | 0 | 22.971 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 12 | 2148 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11871.1341 | 0 | 50610.575 | 0 | 37251.3903 | 0 | 6768.6291 | 0 | 106501.7285 | 0 | 877.9656 | 0 | 2810.7894 | 0 | 1811.5325 | 0 | 375.9134 | 2790.1195 | 8666.3204 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.9698 | 23.2728 | 20.3823 | 23.0391 | 23.2728 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6613 | 0 | 0 | 23.2728 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 13 | 2149 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12429.1174 | 0 | 43854.2155 | 0 | 67260.2311 | 0 | 7086.7775 | 0 | 130630.3414 | 0 | 919.2329 | 0 | 2435.5575 | 0 | 3270.8604 | 0 | 393.5826 | 2960.4085 | 9979.6418 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.3465 | 23.6495 | 20.7784 | 23.4353 | 23.6495 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6612 | 0 | 0 | 23.6495 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 14 | 2150 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12480.6944 | 0 | 32676.541 | 0 | 89075.1093 | 0 | 7116.1854 | 0 | 141348.5302 | 0 | 923.0474 | 0 | 1814.7764 | 0 | 4331.7164 | 0 | 395.2158 | 2851.2489 | 10316.0049 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.7548 | 24.0579 | 21.1929 | 23.8498 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6611 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 15 | 2151 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5936.91 | 0 | 10263.1778 | 0 | 51940.76 | 0 | 3385.0803 | 0 | 71525.9281 | 0 | 878.1642 | 0 | 1139.9844 | 0 | 5051.7511 | 0 | 375.9984 | 2558.7011 | 10004.5992 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.8192 | 24.1223 | 21.2704 | 23.9272 | 23.9272 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6610 | 0 | 0 | 23.9272 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 16 | 2152 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6249.3184 | 0 | 4106.4862 | 0 | 37566.752 | 0 | 3563.2078 | 0 | 51485.7644 | 0 | 924.3744 | 0 | 456.1287 | 0 | 3653.7371 | 0 | 395.784 | 1733.4545 | 7163.4787 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.7836 | 24.0866 | 21.2319 | 23.8887 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6609 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 17 | 2153 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5100.4565 | 0 | 2908.155 | 0 | 24573.2477 | 0 | 4644.0868 | 0 | 37225.946 | 0 | 754.4393 | 0 | 323.0239 | 0 | 2389.9907 | 0 | 515.8428 | 1139.6263 | 5122.9229 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.7136 | 24.0166 | 21.1663 | 23.8231 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6608 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 18 | 2154 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3503.0456 | 0 | 1997.3506 | 0 | 30389.6343 | 0 | 7456.3409 | 0 | 43346.3714 | 0 | 518.1566 | 0 | 221.8561 | 0 | 2955.6916 | 0 | 828.2144 | 873.2768 | 5397.1956 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.7226 | 24.0256 | 21.1486 | 23.8055 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6607 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 19 | 2155 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1220.8453 | 0 | 696.096 | 0 | 3909.5596 | 0 | 1479.6021 | 0 | 7306.103 | 0 | 180.5826 | 0 | 77.319 | 0 | 380.2432 | 0 | 164.3471 | 205.2201 | 1007.712 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5834 | 23.8865 | 20.9142 | 23.571 | 23.8865 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6606 | 0 | 0 | 23.8865 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 20 | 2156 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5485 | 23.8516 | 20.883 | 23.5398 | 23.8516 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6605 | 0 | 0 | 23.8516 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 21 | 2157 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5003 | 23.8034 | 20.7917 | 23.4486 | 23.8034 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6604 | 0 | 0 | 23.8034 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 22 | 2158 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.4343 | 23.7373 | 20.6684 | 23.3252 | 23.7373 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6603 | 0 | 0 | 23.7373 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 23 | 2159 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.3661 | 23.6692 | 20.5934 | 23.2502 | 23.6692 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6602 | 0 | 0 | 23.6692 | 0 | 0 | 0
|  | 2004 | 3 | 31 | 24 | 2160 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.295 | 23.5981 | 20.5125 | 23.1693 | 23.5981 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6601 | 0 | 0 | 23.5981 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 1 | 2161 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 26.175 | 23.478 | 20.3894 | 23.0462 | 23.478 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6600 | 0 | 0 | 23.478 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 2 | 2162 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 26.0598 | 23.3628 | 20.2894 | 22.9463 | 23.3628 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6599 | 0 | 0 | 23.3628 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 3 | 2163 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.9484 | 23.2514 | 20.1903 | 22.8471 | 23.2514 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6598 | 0 | 0 | 23.2514 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 4 | 2164 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.829 | 23.132 | 20.0447 | 22.7016 | 23.132 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6597 | 0 | 0 | 23.132 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 5 | 2165 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.687 | 22.99 | 19.8299 | 22.4867 | 22.99 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6596 | 0 | 0 | 22.99 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 6 | 2166 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.5463 | 22.8494 | 19.6934 | 22.3503 | 22.8494 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6595 | 0 | 0 | 22.8494 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 7 | 2167 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 422.1586 | 0 | 240.7045 | 0 | 562.8782 | 0 | 240.7045 | 0 | 1466.4457 | 0 | 31.222 | 0 | 13.3681 | 0 | 27.3727 | 0 | 13.3681 | 34.9311 | 120.2621 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.4067 | 22.7098 | 19.5432 | 22.2001 | 22.7098 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6594 | 0 | 0 | 22.7098 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 8 | 2168 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 26098.9072 | 0 | 15166.6561 | 0 | 5345.1787 | 0 | 2285.7672 | 0 | 48896.5092 | 0 | 1930.2235 | 0 | 842.3195 | 0 | 259.9357 | 0 | 126.946 | 449.7376 | 3609.1623 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.4874 | 22.7904 | 19.7339 | 22.3907 | 22.7904 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6593 | 0 | 0 | 22.7904 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 9 | 2169 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12096.1043 | 0 | 8918.3029 | 0 | 8006.775 | 0 | 3423.9499 | 0 | 32445.1321 | 0 | 894.6039 | 0 | 495.3011 | 0 | 389.3689 | 0 | 190.1579 | 580.7291 | 2550.1609 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.5301 | 22.8331 | 19.8072 | 22.464 | 22.8331 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6592 | 0 | 0 | 22.8331 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 10 | 2170 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 16408 | 0 | 15934.2549 | 0 | 13538.3623 | 0 | 5789.4312 | 0 | 51670.0484 | 0 | 1213.5032 | 0 | 884.9501 | 0 | 658.3696 | 0 | 321.5311 | 1043.5658 | 4121.9198 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.6366 | 22.9397 | 19.9381 | 22.5949 | 22.9397 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6591 | 0 | 0 | 22.9397 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 11 | 2171 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 17354.3723 | 0 | 41228.7064 | 0 | 16292.6691 | 0 | 6967.2598 | 0 | 81843.0077 | 0 | 1283.495 | 0 | 2289.743 | 0 | 792.3114 | 0 | 386.9448 | 2047.8342 | 6800.3284 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 25.8481 | 23.1512 | 20.2009 | 22.8577 | 23.1512 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6590 | 0 | 0 | 23.1512 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 12 | 2172 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 11869.8385 | 0 | 50153.2561 | 0 | 36892.8874 | 0 | 6767.8904 | 0 | 105683.8724 | 0 | 877.8697 | 0 | 2785.391 | 0 | 1794.0986 | 0 | 375.8723 | 2755.1884 | 8588.4201 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.1431 | 23.4461 | 20.5415 | 23.1983 | 23.4461 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6589 | 0 | 0 | 23.4461 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 13 | 2173 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12507.273 | 0 | 43517.3685 | 0 | 66885.2459 | 0 | 7131.3399 | 0 | 130041.2273 | 0 | 925.0131 | 0 | 2416.8498 | 0 | 3252.6249 | 0 | 396.0574 | 2973.5076 | 9964.0529 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5138 | 23.8168 | 20.9318 | 23.5887 | 23.8168 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6588 | 0 | 0 | 23.8168 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 14 | 2174 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 12384.2174 | 0 | 34116.3498 | 0 | 93554.0277 | 0 | 7061.1766 | 0 | 147115.7714 | 0 | 915.9122 | 0 | 1894.7399 | 0 | 4549.5259 | 0 | 392.1607 | 2995.3395 | 10747.6783 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.939 | 24.2421 | 21.3778 | 24.0347 | 24 |  | 0 | -13.0547 | -13.0547 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6587 | 0 | 0 | 24 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 15 | 2175 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 6763.7869 | 0 | 8824.3905 | 0 | 41214.7389 | 0 | 3856.5451 | 0 | 60659.4614 | 0 | 1000.4726 | 0 | 980.1708 | 0 | 4008.5398 | 0 | 428.3665 | 2196.2912 | 8613.8408 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.8816 | 24.1846 | 21.3185 | 23.9754 | 23.9754 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6586 | 0 | 0 | 23.9754 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 16 | 2176 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5946.6794 | 0 | 4000.6863 | 0 | 44960.3433 | 0 | 3390.6505 | 0 | 58298.3595 | 0 | 879.6093 | 0 | 444.377 | 0 | 4372.8368 | 0 | 376.6171 | 1929.9418 | 8003.3819 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.8473 | 24.1504 | 21.2793 | 23.9361 | 23.9361 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6585 | 0 | 0 | 23.9361 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 17 | 2177 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 5183.6858 | 0 | 2955.6103 | 0 | 27054.8769 | 0 | 4971.1046 | 0 | 40165.2777 | 0 | 766.7503 | 0 | 328.295 | 0 | 2631.3536 | 0 | 552.1664 | 1213.8548 | 5492.42 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.7537 | 24.0567 | 21.1905 | 23.8474 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6584 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 18 | 2178 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 3546.4521 | 0 | 2022.0999 | 0 | 21260.0007 | 0 | 5578.3084 | 0 | 32406.8611 | 0 | 524.5772 | 0 | 224.6051 | 0 | 2067.7447 | 0 | 619.6116 | 777.2164 | 4213.755 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.689 | 23.992 | 21.1126 | 23.7694 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6583 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 19 | 2179 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 1346.3738 | 0 | 767.6693 | 0 | 4800.931 | 0 | 1811.0528 | 0 | 8726.0268 | 0 | 199.1503 | 0 | 85.269 | 0 | 466.9379 | 0 | 201.163 | 231.4184 | 1183.9385 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5996 | 23.9027 | 20.9685 | 23.6253 | 23.9 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6582 | 0 | 0 | 23.9 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 20 | 2180 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.5419 | 23.8449 | 20.8113 | 23.4681 | 23.8449 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6581 | 0 | 0 | 23.8449 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 21 | 2181 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.4718 | 23.7748 | 20.6929 | 23.3497 | 23.7748 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6580 | 0 | 0 | 23.7748 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 22 | 2182 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.4051 | 23.7082 | 20.6371 | 23.2939 | 23.7082 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6579 | 0 | 0 | 23.7082 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 23 | 2183 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.3336 | 23.6367 | 20.5499 | 23.2068 | 23.6367 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6578 | 0 | 0 | 23.6367 | 0 | 0 | 0
|  | 2002 | 4 | 1 | 24 | 2184 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 11070 | 11070 | 61.5 | 24569.25 | 26.2564 | 23.5595 | 20.4543 | 23.1111 | 23.5595 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6577 | 0 | 0 | 23.5595 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 1 | 2185 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 26.1322 | 23.4352 | 20.333 | 22.9899 | 23.4352 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6576 | 0 | 0 | 23.4352 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 2 | 2186 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 26.0055 | 23.3086 | 20.1983 | 22.8551 | 23.3086 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6575 | 0 | 0 | 23.3086 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 3 | 2187 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.8901 | 23.1931 | 20.1189 | 22.7757 | 23.1931 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6574 | 0 | 0 | 23.1931 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 4 | 2188 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.7776 | 23.0807 | 20.0157 | 22.6725 | 23.0807 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6573 | 0 | 0 | 23.0807 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 5 | 2189 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.6617 | 22.9647 | 19.8883 | 22.5452 | 22.9647 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6572 | 0 | 0 | 22.9647 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 6 | 2190 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.5395 | 22.8426 | 19.7461 | 22.4029 | 22.8426 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6571 | 0 | 0 | 22.8426 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 7 | 2191 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 444.1284 | 11547.3384 | 3383.6757 | 14486.8857 | 189.625 | 0 | 499.5879 | 0 | 213.9475 | 0 | 170.9814 | 0 | 73.117 | 0 | 957.6338 | 0 | 36.9485 | 0 | 11.8821 | 0 | 8.3148 | 0 | 4.0607 | 34.9311 | 96.1373 | 2398.5 | 2214 | 2214 | 61.5 | 6857.25 | 25.4269 | 22.7299 | 19.6546 | 22.3114 | 22.7299 |  | 0 | 0 | 0 | 16 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6570 | 0 | 0 | 22.7299 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 8 | 2192 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 29304.9939 | 0 | 16943.2561 | 0 | 5537.8256 | 0 | 2368.1491 | 0 | 54154.2248 | 0 | 2167.3393 | 0 | 940.9876 | 0 | 269.3041 | 0 | 131.5213 | 484.6686 | 3993.821 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 25.5061 | 22.8082 | 19.7942 | 22.452 | 22.8082 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6569 | 0 | 0 | 22.8082 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 9 | 2193 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 41218.4047 | 0 | 34527.5717 | 0 | 9824.754 | 0 | 4201.3751 | 0 | 89772.1055 | 0 | 3048.4316 | 0 | 1917.5782 | 0 | 477.7771 | 0 | 233.3343 | 1152.7254 | 6829.8465 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 25.7017 | 23.0038 | 20.0359 | 22.6937 | 23.0038 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6568 | 0 | 0 | 23.0038 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 10 | 2194 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 34832.0264 | 0 | 46326.6164 | 0 | 12416.9039 | 0 | 5309.8602 | 0 | 98885.4069 | 0 | 2576.1077 | 0 | 2572.8687 | 0 | 603.8332 | 0 | 294.8968 | 1820.7822 | 7868.4886 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 25.9423 | 23.2444 | 20.338 | 22.9958 | 23.2444 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6567 | 0 | 0 | 23.2444 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 11 | 2195 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 17783.685 | 0 | 50750.131 | 0 | 14569.6937 | 0 | 6230.4611 | 0 | 89333.9708 | 0 | 1315.2461 | 0 | 2818.54 | 0 | 708.5232 | 0 | 346.0248 | 2366.5802 | 7554.9144 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.1743 | 23.4764 | 20.6338 | 23.2916 | 23.4764 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6566 | 0 | 0 | 23.4764 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 12 | 2196 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12079.0703 | 0 | 49269.4977 | 0 | 36552.6217 | 0 | 6887.1892 | 0 | 104788.3789 | 0 | 893.3441 | 0 | 2736.3092 | 0 | 1777.5515 | 0 | 382.4979 | 2790.1195 | 8579.8222 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.4614 | 23.7634 | 20.9575 | 23.6153 | 23.7634 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6565 | 0 | 0 | 23.7634 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 13 | 2197 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 12883.4181 | 0 | 40736.6967 | 0 | 63296.1339 | 0 | 7345.8085 | 0 | 124262.0572 | 0 | 952.8321 | 0 | 2262.418 | 0 | 3078.0866 | 0 | 407.9685 | 2803.2186 | 9504.5239 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.8067 | 24.1088 | 21.3142 | 23.972 | 23.972 |  | 0 | 0 | 0 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6564 | 0 | 0 | 23.972 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 14 | 2198 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 6260.8748 | 0 | 16357.5118 | 0 | 44939.3806 | 0 | 3569.797 | 0 | 71127.5643 | 0 | 926.0838 | 0 | 1816.9136 | 0 | 4370.7979 | 0 | 396.5159 | 2873.0808 | 10383.392 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.88 | 24.1821 | 21.4099 | 24.0676 | 24 |  | 0 | -25.4531 | -25.4531 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6563 | 0 | 0 | 24 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 15 | 2199 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5997.1019 | 0 | 10119.4762 | 0 | 51971.2257 | 0 | 3419.4002 | 0 | 71507.204 | 0 | 887.0676 | 0 | 1124.0227 | 0 | 5054.7142 | 0 | 379.8105 | 2606.7314 | 10052.3463 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.9088 | 24.2108 | 21.4407 | 24.0985 | 24 |  | 0 | -37.0651 | -37.0651 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6562 | 0 | 0 | 24 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 16 | 2200 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5560.1239 | 0 | 3800.2433 | 0 | 51291.3537 | 0 | 3170.2461 | 0 | 63821.967 | 0 | 822.4315 | 0 | 422.1127 | 0 | 4988.59 | 0 | 352.1357 | 2122.0627 | 8707.3326 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.8852 | 24.1873 | 21.4205 | 24.0783 | 24 |  | 0 | -29.4569 | -29.4569 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6561 | 0 | 0 | 24 | 0 | 0 | 0
|  | 2002 | 4 | 2 | 17 | 2201 | 1411.344 | 656.9978 | 130.9915 | 2199.3333 | 740.214 | 177.6514 | 11280.8614 | 3117.1986 | 14220.4086 | 189.625 | 0 | 5050.0993 | 0 | 2879.4426 | 0 | 38835.9235 | 0 | 6168.3055 | 0 | 52933.7709 | 0 | 746.9907 | 0 | 319.8346 | 0 | 3777.1765 | 0 | 685.1457 | 1432.174 | 6961.3215 | 959.4 | 4428 | 4428 | 24.6 | 9827.7 | 26.8478 | 24.1499 | 21.3718 | 24.0296 | 24 |  | 0 | -11.1345 | -11.1345 | 20 | 24 | 23.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6560 | 0 | 0 | 24 | 0 | 0 | 0